## Collaboration-Full-DR-Measures
End-Use Category | Sub-Category | DF (Demand Flexibility) Control Strategy | Strategy Description | Recommended Control Sequence | GEB - Load Flexibility | DF Control Settings | Level of Response |  |  | Service variables impacted; relevant standard(s) (cost - applicable to all) | Key References
[7 empty] | Low (1) | Medium (2) | High (3)
Building Envelope | Exterior Wall, Interior Wall and Thermal Mass | Passive thermal mass storage (pre-cooling) | Precool the building during the night or early morning to store cooling energy and thus to flatten out the thermal energy flows over the daily ambient temperature fluctuations. | Start the HVAC system earlier than normal operation | Energy Efficiency; Shift; Shed | Start time | ~7am | ~5am | ~3am | ASHRAE 55; 62.1 | Motegi, N., Piette, M. A., Watson, D. S., Kiliccote, S., & Xu, P. (2007). Introduction to Commercial Building Control Strategies and Techniques for Demand Response. LBNL-59975
|  | Active thermal mass storage (pre-cooling) | Use of phase change materials to precool the building during the night or early morning to store cooling energy and thus to flatten out the thermal energy flows over the daily ambient temperature fluctuations. | Precool the phase change materials by 2-6ºF | Energy Efficiency; Shift; Shed | Adjustment (Decrease) | 2ºF | 4ºF | 6ºF
|  | Night flushing/economizer (pre-cooling) | Passively or semi-passively increase air movement at night to cool the structural elements of buildings and improve air quality | N/A | Energy Efficiency | N/A | N/A | N/A | N/A
| Smart Windows | Blind control | Control the blind angle and shade with motorized roller screen | Control blind to reduce the cooling load while maintaining the daylight level | Energy Efficiency; Shed | N/A | N/A | N/A | N/A |  | TBD
|  | Electrochromic | Control window thermal performance to reduce heat gains as much as possible during the event hours whille maintaining sufficient daylights | Control thermal performance to reduce the cooling load while maintaining the daylight level | Energy Efficiency; Shed | N/A | N/A | N/A | N/A
|  | Photovoltaic Windows | n/a
HVAC Systems | Variable Air Volume (VAV) | Global temperature adjustment (cooling) | Increase zone temperature setpoints for an adjustment entire facility | Precool 2 ºF and raise zone temperature by 2-6ºF | Shift; Shed | Adjustment (Increase) | 2ºF | 4ºF | 6ºF |  | Motegi, N., Piette, M. A., Watson, D. S., Kiliccote, S., & Xu, P. (2007). Introduction to Commercial Building Control Strategies and Techniques for Demand Response. LBNL-59975 Cai, J., & Braun, J. E. (2019). Laboratory-based assessment of HVAC equipment for power grid frequency regulation: Methods, regulation performance, economics, indoor comfort and energy efficiency. Energy and Buildings, 185, 148–161. https://doi.org/10.1016/j.enbuild.2018.12.022 Cai, Jie and Braun, James E., "Using HVAC Systems for Providing Power Grid Ancillary Services" (2018). International High Performance Buildings Conference. Paper 309 Lin, Y., Mathieu, J. L., Johnson, J. X., Hiskens, I. A. & Backhaus, S. Explaining inefficiencies in commercial buildings providing power system ancillary services. Energy Build. 152, 216–226 (2017). Keskar, A., Anderson, D., Johnson, J. X., Hiskens, I. A., & Mathieu, J. L. (2020). Do commercial buildings become less efficient when they provide grid ancillary services? Energy Efficiency, 13(3), 487–501. https://doi.org/10.1007/s12053-019-09787-x
|  | Global temperature adjustment (heating) | Decrease zone temperature setpoints for an adjustment entire facility | Decrease thermostat heating setpoint by 2-6ºF | Shift; Shed | Adjustment (Decrease) | 2ºF | 4ºF | 6ºF
|  | Duct static pressure decrease | Decrease duct static pressure setpoints to reduce fan power. | DSP setpoint decreased from 1.5" to 1.0" | Shed | Setpoint | 1.4" | 1.2" | 1.0"
|  | Supply air temperature adjustment | Increase SAT setpoints to reduce cooling load. | SAT increased from 55 ºF to 65 ºF | Energy Efficiency; Shed | Adjustment (Increase) | 2ºF | 6ºF | 10ºF
|  | Lock cooling valve position at the AHU | Lock cooling valve position at the AHU to reduce the chiller power. | Limit to 70%. | Shed | Setpoint (Limit) | 90% | 80% | 70%
|  | VFD fans and pumps speed adjustment | Limit or decrease fans/pumps variable drive speeds to reduce fan power. | Limit to 70%. | Shed | Setpoint (Limit) | 90% | 80% | 70%
| Constant Air Volume (CAV) | Supply air temperature adjustment | Increase SAT setpoints to reduce cooling load. | SAT increased from 55 ºF to 65 ºF | Energy Efficiency; Shed | N/A | N/A | N/A | N/A
|  | Lock cooling valve position at the AHU | Lock cooling valve position at the AHU to reduce the chiller power. | Limit to 70%. | Shed | Setpoint (Limit) | 90% | 80% | 70%
| Fan Coil Unit (FCU) | Thermostat setpoint adjustment | Increase zone temperature setpoints for an adjustment entire facility. | Increase zone temperature setpoints for an adjustment entire facility. | Shed | Adjustment (Increase) | 2ºF | 4ºF | 6ºF
|  | Fan coil speed adjustment | Adjust two- or three-stage fan coil speed to change fan power. | Adjust two- or three-stage fan coil speed to change fan power. | Shed | Setpoint (Limit) | 90% | 80% | 70%
|  | Staged control of multiple FCUs | Staged control of multiple FCUs to reduce the aggregated power. | Staged control of multiple FCUs to reduce the aggregated power. | Shed | Setpoint (Limit) | 90% | 80% | 70%
| Variable Refrigerant Flow (VRF) | Thermostat setpoint adjustment | Increase zone temperature setpoints for an adjustment entire facility. | Increase zone temperature setpoints for an adjustment entire facility. | Shed | Adjustment (Increase) | 2ºF | 4ºF | 6ºF
|  | Compressor speed adjustment | Adjust two- or three-stage compressor speed to change compressor power. | Adjust two- or three-stage compressor speed to change compressor power. | Shed | Setpoint (Limit) | 90% | 80% | 70%
|  | Cycle on/off VRF indoor and outdoor units | Cycle on/off VRF indoor and outdoor units. | Cycle on/off VRF indoor and outdoor units. | Shed | Cycle On/Off | 30% | 50% | 100%
HVAC Plant | Water/Air-Cooled Chiller | Chilled water temperature reset | Increase chilled water temperature to improve chiller efficiency and reduce cooling load. | CHW setpoint increased 5 ºF | Energy Efficiency; Shed | Adjustment (Increase) | 2ºF | 4ºF | 6ºF
|  | Chiller demand limit | Limit the chiller capacity to reduce the chiller power during the peak period. | Limit to 50% or 70%. | Shed | Setpoint (Limit) | 90% | 70% | 50%
| Packaged Rooftop Unit | Cycle on/off compressors | Cycle on/off or lock out compressors | Cycle on/off HVAC plants by 30%, 50% and 100% | Shed | Cycle On/Off | 50% | 67% | 100%
| Ice/Water Thermal Storage | Shift of charging period | Shift of TES charging period. | N/A | Energy Efficiency; Shift | [5 empty] | Yin, R., Black, D., Piette, M. A., & Schiess, K. (2015). Control of Thermal Energy Storage in Commercial Buildings for California Utility Tariffs and Demand Response. LBNL-1003740
|  | Cycle off the partial chiller | Shut off the partial chiller to reduce the chiller power. | Shut off 1/3 or 1/2 of multiple chillers | Shed | Cycle On/Off | N/A | 2019-01-03 | 2019-01-02 |  | Motegi, N., Piette, M. A., Watson, D. S., Kiliccote, S., & Xu, P. (2007). Introduction to Commercial Building Control Strategies and Techniques for Demand Response. LBNL-59975
HVAC | Rebound avoidance | Slow recovery | Slowly restore HVAC control parameters modified by DF strategies
|  | Sequential equipment recovery | Restore HVAC control to equipment sequentially within a certain time interval
|  | Extended DR control Period | Extend DF control period until after the occupancy period
Lighting | Interior Lighting | Dimming control (continuous and step) | Dimming the lighting by 40%~60% (interior zones) | 40%~60% | Shed | Adjustment (Decrease) | 20% | 40% | 60% |  | Newsham et. Al., 2008. Detection and Acceptance of Demand-Responsive Lighting in Offices with and without Daylight. Leukos 2008. Newsham, Guy and Birt, Benjamin, 2010. “Demand-responsive Lighting – A Field Study.” Leukos, Vol. 6 No. 3.
|  | Switch on/off | Turn off all day light zones, public areas and perimeter lights. | 100% | Shed | Adjustment (Decrease) | N/A | N/A | 100%
| Task Lighting | Switch on/off | Turn off all task lights. | 100% | Shed | Adjustment (Decrease) | N/A | N/A | 100%
Water Heater | Electric | Setpoint adjustment | Reduce hot water temperature setpoint to reduce the electric water heater power. | Decrease water temperature setpoint by 5~15ºF (from 120ºF) | Shed | Adjustment (Decrease) | 5ºF | 10ºF | 15ºF |  | https://www.bpa.gov/EE/Technology/demand-response/Documents/20181118_CTA-2045_Final_Report.pdf Coninck, R. De et al. (2014) ‘Rule-based demand-side management of domestic hot water production with heat pumps in zero energy neighbourhoods’, 1493. doi: 10.1080/19401493.2013.801518.
|  | Setpoint adjustment along with valve control | Increase water temperature setpoint to the high limit before the event and turn it off during the event. | Increase water temperature setpoint by ~20 ºF (from 120ºF to 140ºF) | Shift | Adjustment (Increase) | 10ºF | 15ºF | 20ºF
|  | Switch on/off | Turn off the electric water heater. | N/A | Shed | Switch on/off | N/A | N/A | 100%
MELs (Miscellaneous electric loads) | Non-critical Process Load | Stand-by equipment load reduction | Unplug equipment/appliances operating in stand-by mode, e.g., toasters, pool pumps and heaters | N/A | Shed | Switch on/off | TBD | TBD | TBD
|  | Activities limit | Turn off TV, internet routers, or use only one screen of the desktop computer; reduce elevator cycling, disable laundry services
Refrigeration | Setpoint | Setpoint temperature adjustment | Increase the setpoint temperature (Ideal one would be 38ºF for refrigerator and 0ºF for freeze)
| behavioral use | Operation limit | Reduce the frequency of door opening to reduce the operation of compressor
Electric Storage | Battery Storage | Electric battery | Charge electric battery for energy storage
| EV battery | EV charging | Increase the use frequency during the daytime at working place
Occupant behavior (need pre-notice and motivation) | Window Operation | Window operation limit | Close windows to avoid convective heat gains and reduce cooling loads
| Window Operation | Shading operation | Manipulate the shading to reduce solar heat gains and cooling loads