## Collaboration-Full-DR-Measures
End-Use Category | Sub-Category | DF (Demand Flexibility) Control Strategy | Strategy Description | Recommended Control Sequence | GEB - Load Flexibility | DF Control Settings | Level of Response |  |  | Service variables impacted; relevant standard(s) (cost - applicable to all) | Key References
[7 empty] | Low (1) | Medium (2) | High (3)
Building Envelope | Exterior Wall, Interior Wall and Thermal Mass | Passive thermal mass storage (pre-cooling) | Precool the building during the night or early morning to store cooling energy and thus to flatten out the thermal energy flows over the daily ambient temperature fluctuations. | Start the HVAC system earlier than normal operation | Energy Efficiency; Shift; Shed | Start time | ~7am | ~5am | ~3am | ASHRAE 55; 62.1 | Motegi, N., Piette, M. A., Watson, D. S., Kiliccote, S., & Xu, P. (2007). Introduction to Commercial Building Control Strategies and Techniques for Demand Response. LBNL-59975
|  | Active thermal mass storage (pre-cooling) | Use of phase change materials to precool the building during the night or early morning to store cooling energy and thus to flatten out the thermal energy flows over the daily ambient temperature fluctuations. | Precool the phase change materials by 2-6ºF | Energy Efficiency; Shift; Shed | Adjustment (Decrease) | 2ºF | 4ºF | 6ºF
|  | Night flushing/economizer (pre-cooling) | Passively or semi-passively increase air movement at night to cool the structural elements of buildings and improve air quality | N/A | Energy Efficiency | N/A | N/A | N/A | N/A
| Smart Windows | Blind control | Control the blind angle and shade with motorized roller screen | Control blind to reduce the cooling load while maintaining the daylight level | Energy Efficiency; Shed | N/A | N/A | N/A | N/A |  | TBD
|  | Electrochromic | Control window thermal performance to reduce heat gains as much as possible during the event hours whille maintaining sufficient daylights | Control thermal performance to reduce the cooling load while maintaining the daylight level | Energy Efficiency; Shed | N/A | N/A | N/A | N/A
|  | Photovoltaic Windows | n/a
HVAC Systems | Variable Air Volume (VAV) | Global temperature adjustment (cooling) | Increase zone temperature setpoints for an adjustment entire facility | Precool 2 ºF and raise zone temperature by 2-6ºF | Shift; Shed | Adjustment (Increase) | 2ºF | 4ºF | 6ºF |  | Motegi, N., Piette, M. A., Watson, D. S., Kiliccote, S., & Xu, P. (2007). Introduction to Commercial Building Control Strategies and Techniques for Demand Response. LBNL-59975 Cai, J., & Braun, J. E. (2019). Laboratory-based assessment of HVAC equipment for power grid frequency regulation: Methods, regulation performance, economics, indoor comfort and energy efficiency. Energy and Buildings, 185, 148–161. https://doi.org/10.1016/j.enbuild.2018.12.022 Cai, Jie and Braun, James E., "Using HVAC Systems for Providing Power Grid Ancillary Services" (2018). International High Performance Buildings Conference. Paper 309 Lin, Y., Mathieu, J. L., Johnson, J. X., Hiskens, I. A. & Backhaus, S. Explaining inefficiencies in commercial buildings providing power system ancillary services. Energy Build. 152, 216–226 (2017). Keskar, A., Anderson, D., Johnson, J. X., Hiskens, I. A., & Mathieu, J. L. (2020). Do commercial buildings become less efficient when they provide grid ancillary services? Energy Efficiency, 13(3), 487–501. https://doi.org/10.1007/s12053-019-09787-x
|  | Global temperature adjustment (heating) | Decrease zone temperature setpoints for an adjustment entire facility | Decrease thermostat heating setpoint by 2-6ºF | Shift; Shed | Adjustment (Decrease) | 2ºF | 4ºF | 6ºF
|  | Duct static pressure decrease | Decrease duct static pressure setpoints to reduce fan power. | DSP setpoint decreased from 1.5" to 1.0" | Shed | Setpoint | 1.4" | 1.2" | 1.0"
|  | Supply air temperature adjustment | Increase SAT setpoints to reduce cooling load. | SAT increased from 55 ºF to 65 ºF | Energy Efficiency; Shed | Adjustment (Increase) | 2ºF | 6ºF | 10ºF
|  | Lock cooling valve position at the AHU | Lock cooling valve position at the AHU to reduce the chiller power. | Limit to 70%. | Shed | Setpoint (Limit) | 90% | 80% | 70%
|  | VFD fans and pumps speed adjustment | Limit or decrease fans/pumps variable drive speeds to reduce fan power. | Limit to 70%. | Shed | Setpoint (Limit) | 90% | 80% | 70%
| Constant Air Volume (CAV) | Supply air temperature adjustment | Increase SAT setpoints to reduce cooling load. | SAT increased from 55 ºF to 65 ºF | Energy Efficiency; Shed | N/A | N/A | N/A | N/A
|  | Lock cooling valve position at the AHU | Lock cooling valve position at the AHU to reduce the chiller power. | Limit to 70%. | Shed | Setpoint (Limit) | 90% | 80% | 70%
| Fan Coil Unit (FCU) | Thermostat setpoint adjustment | Increase zone temperature setpoints for an adjustment entire facility. | Increase zone temperature setpoints for an adjustment entire facility. | Shed | Adjustment (Increase) | 2ºF | 4ºF | 6ºF
|  | Fan coil speed adjustment | Adjust two- or three-stage fan coil speed to change fan power. | Adjust two- or three-stage fan coil speed to change fan power. | Shed | Setpoint (Limit) | 90% | 80% | 70%
|  | Staged control of multiple FCUs | Staged control of multiple FCUs to reduce the aggregated power. | Staged control of multiple FCUs to reduce the aggregated power. | Shed | Setpoint (Limit) | 90% | 80% | 70%
| Variable Refrigerant Flow (VRF) | Thermostat setpoint adjustment | Increase zone temperature setpoints for an adjustment entire facility. | Increase zone temperature setpoints for an adjustment entire facility. | Shed | Adjustment (Increase) | 2ºF | 4ºF | 6ºF
|  | Compressor speed adjustment | Adjust two- or three-stage compressor speed to change compressor power. | Adjust two- or three-stage compressor speed to change compressor power. | Shed | Setpoint (Limit) | 90% | 80% | 70%
|  | Cycle on/off VRF indoor and outdoor units | Cycle on/off VRF indoor and outdoor units. | Cycle on/off VRF indoor and outdoor units. | Shed | Cycle On/Off | 30% | 50% | 100%
HVAC Plant | Water/Air-Cooled Chiller | Chilled water temperature reset | Increase chilled water temperature to improve chiller efficiency and reduce cooling load. | CHW setpoint increased 5 ºF | Energy Efficiency; Shed | Adjustment (Increase) | 2ºF | 4ºF | 6ºF
|  | Chiller demand limit | Limit the chiller capacity to reduce the chiller power during the peak period. | Limit to 50% or 70%. | Shed | Setpoint (Limit) | 90% | 70% | 50%
| Packaged Rooftop Unit | Cycle on/off compressors | Cycle on/off or lock out compressors | Cycle on/off HVAC plants by 30%, 50% and 100% | Shed | Cycle On/Off | 50% | 67% | 100%
| Ice/Water Thermal Storage | Shift of charging period | Shift of TES charging period. | N/A | Energy Efficiency; Shift | [5 empty] | Yin, R., Black, D., Piette, M. A., & Schiess, K. (2015). Control of Thermal Energy Storage in Commercial Buildings for California Utility Tariffs and Demand Response. LBNL-1003740
|  | Cycle off the partial chiller | Shut off the partial chiller to reduce the chiller power. | Shut off 1/3 or 1/2 of multiple chillers | Shed | Cycle On/Off | N/A | 2019-01-03 | 2019-01-02 |  | Motegi, N., Piette, M. A., Watson, D. S., Kiliccote, S., & Xu, P. (2007). Introduction to Commercial Building Control Strategies and Techniques for Demand Response. LBNL-59975
HVAC | Rebound avoidance | Slow recovery | Slowly restore HVAC control parameters modified by DF strategies
|  | Sequential equipment recovery | Restore HVAC control to equipment sequentially within a certain time interval
|  | Extended DR control Period | Extend DF control period until after the occupancy period
Lighting | Interior Lighting | Dimming control (continuous and step) | Dimming the lighting by 40%~60% (interior zones) | 40%~60% | Shed | Adjustment (Decrease) | 20% | 40% | 60% |  | Newsham et. Al., 2008. Detection and Acceptance of Demand-Responsive Lighting in Offices with and without Daylight. Leukos 2008. Newsham, Guy and Birt, Benjamin, 2010. “Demand-responsive Lighting – A Field Study.” Leukos, Vol. 6 No. 3.
|  | Switch on/off | Turn off all day light zones, public areas and perimeter lights. | 100% | Shed | Adjustment (Decrease) | N/A | N/A | 100%
| Task Lighting | Switch on/off | Turn off all task lights. | 100% | Shed | Adjustment (Decrease) | N/A | N/A | 100%
Water Heater | Electric | Setpoint adjustment | Reduce hot water temperature setpoint to reduce the electric water heater power. | Decrease water temperature setpoint by 5~15ºF (from 120ºF) | Shed | Adjustment (Decrease) | 5ºF | 10ºF | 15ºF |  | https://www.bpa.gov/EE/Technology/demand-response/Documents/20181118_CTA-2045_Final_Report.pdf Coninck, R. De et al. (2014) ‘Rule-based demand-side management of domestic hot water production with heat pumps in zero energy neighbourhoods’, 1493. doi: 10.1080/19401493.2013.801518.
|  | Setpoint adjustment along with valve control | Increase water temperature setpoint to the high limit before the event and turn it off during the event. | Increase water temperature setpoint by ~20 ºF (from 120ºF to 140ºF) | Shift | Adjustment (Increase) | 10ºF | 15ºF | 20ºF
|  | Switch on/off | Turn off the electric water heater. | N/A | Shed | Switch on/off | N/A | N/A | 100%
MELs (Miscellaneous electric loads) | Non-critical Process Load | Stand-by equipment load reduction | Unplug equipment/appliances operating in stand-by mode, e.g., toasters, pool pumps and heaters | N/A | Shed | Switch on/off | TBD | TBD | TBD
|  | Activities limit | Turn off TV, internet routers, or use only one screen of the desktop computer; reduce elevator cycling, disable laundry services
Refrigeration | Setpoint | Setpoint temperature adjustment | Increase the setpoint temperature (Ideal one would be 38ºF for refrigerator and 0ºF for freeze)
| behavioral use | Operation limit | Reduce the frequency of door opening to reduce the operation of compressor
Electric Storage | Battery Storage | Electric battery | Charge electric battery for energy storage
| EV battery | EV charging | Increase the use frequency during the daytime at working place
Occupant behavior (need pre-notice and motivation) | Window Operation | Window operation limit | Close windows to avoid convective heat gains and reduce cooling loads
| Window Operation | Shading operation | Manipulate the shading to reduce solar heat gains and cooling loads

## Sheet12
End-use sategory | Sub-category | DF control strategy | Level of response |  |  | Strategy Id
|  |  | Low (1) | Medium (2) | High (3)
Building envelope | Exterior wall, interior Wall and thermal mass | Passive thermal mass storage (start HVAC system earlier than normal operation for pre-cooling) | 2 hours | 4 hours | 6 hours | BE-A1
|  | Active thermal mass storage (pre-cooling phase change materials by 2-6ºF) | 2ºF | 4ºF | 6ºF | BE-A2
|  | Night flushing/economizer (pre-cooling) | N/A | N/A | N/A | BE-A3
| Smart Windows | Blind control to reduce the cooling load while maintaining the daylight level | N/A | N/A | N/A | BE-B1
|  | Electrochromic - control thermal performance to reduce the cooling load while maintaining the daylight level | N/A | N/A | N/A | BE-B2
HVAC systems | VAV | Global temperature adjustment (cooling - raise zone temperature by 2-6ºF) | 2ºF | 4ºF | 6ºF | HVAC-A1
|  | Global temperature adjustment (heating - Decrease thermostat heating setpoint by 2-4ºF) | 2ºF | 3ºF | 4ºF | HVAC-A2
|  | Duct static pressure decrease from 1.5" to 1.0" | 1.4" | 1.2" | 1.0" | HVAC-A3
|  | Supply air temperature increased from 55 ºF to 65 ºF | 2ºF | 6ºF | 10ºF | HVAC-A4
|  | Limit AHU cooling valve position to 70% | 90% | 80% | 70% | HVAC-A5
|  | Limit VFD fans and pumps speed to 70% | 90% | 80% | 70% | HVAC-A6
| CAV | Supply air temperature increased from 55 ºF to 65 ºF | N/A | N/A | N/A | HVAC-C1
|  | Lock cooling valve position at the AHU | 90% | 80% | 70% | HVAC-C2
HVAC plant | Water/Air-Cooled Chiller | Chilled water temperature reset (increase 5 ºF) | 2ºF | 4ºF | 6ºF | HVAC-P1
|  | Chiller demand limit to 50-90% | 90% | 70% | 50% | HVAC-P2
| Packaged RTU | Cycle on/off compressors by 30%, 50% and 100% | 30% | 50% | 100% | HVAC-P3
| Partial TES system | Shut off 1/3 or 1/2 of multiple chillers | N/A | 2019-01-03 | 2019-01-02 | HVAC-P4
Lighting | Interior Lightinl | Dimming control (continuous and step 20-60%) | 20% | 40% | 60% | LTG-A1
|  | Switch on/off | N/A | N/A | 100% | LTG-A2
| Task lighting | Switch on/off | N/A | N/A | 100% | LTG-A3
Water heater | Electric | Setpoint adjustment (Decrease water temperature setpoint by 5-15ºF from 120ºF) | 5ºF | 10ºF | 15ºF | WH-A1
|  | Setpoint adjustment (Decrease water temperature setpoint by 5-15ºF from 120ºF) with preheat (increase water temperature by 10ºF) | 5ºF | 10ºF | 15ºF | WH-A2
|  | Switch on/off | N/A | N/A | 100% | WH-A3
| Heat pump | Setpoint adjustment (Decrease water temperature setpoint by 5-15ºF from 120ºF) | 5ºF | 10ºF | 15ºF | HPWH-A1
|  | Reduce deadband for heat pump to 1ºF | 1ºF | 1ºF | 1ºF | HPWH-A2
|  | Limit heat pump duty cycling (0-100%) | 30% | 20% | 10% | HPWH-A3
MELs (miscellaneous electric loads) | Non-critical process load | Stand-by equipment load reduction | N/A | N/A | 100% | MEL-A1

## Topic 4-DR-Measures
Category |  | DR Strategy | Definition | Service variables impacted; relevant standard(s) (cost - applicable to all) | Level of Response
[5 empty] | Low (1 hour duration) | Medium (3 hour duration) | High (6 hour duration)
HVAC | Zone control | Global temperature adjustment: cooling | Increase zone temperature setpoints for an entire facility (from 76ºF) | Ambient temperature; ASHRAE Std. 55 | 2ºF | 3ºF | 6ºF
|  | Global temperature adjustment: heating | Decrease zone temperature setpoints for an entire facility |  | 2ºF | 4ºF | 8ºF
|  | Passive thermal mass storage (pre-cooling) | Decrease zone temperature setpoints (to 67ºF) prior to DR operation to store cooling energy in the building mass, and increase zone setpoints to unload fan and cooling system during DR |  | Start from 7am | ~5am | ~3am
|  | Passive thermal mass storage (pre-heating) | Increase zone temperature setpoints prior to DR operation to store cooling energy in the building mass, and increase zone setpoints to unload fan and cooling system during DR |  | Start from 7am | ~5am | ~3am
|  | Active thermal mass storage (pre-cooling) | Use of ice storage/phase change materials to store cooling energy, allowing decrease of zone temperature prior to DR operation and increase during DR. |  | Start from 7am | ~5am | ~3am
|  | Active thermal mass storage (pre-heating) | Use of phase change materials to store cooling energy, allowing decrease of zone temperature prior to DR operation and increase during DR. |  | Start from 7am | ~5am | ~3am
|  | Night flushing/economizer | Passively or semi-passively increase air movement at night to cool the structural elements of buildings and improve air quality | [3]Ambient temperature, humidity, CO2/VOC concentration; ASHRAE Stds. 55, 62.1
| Air distribution | Supply air temperature increase | Increase SAT setpoints to reduce cooling load | Ambient temperature; ASHRAE Std. 55
|  | Cooling valve limit | Limit or reduce cooling valve positions to reduce cooling loads
|  | Demand controlled ventilation (DCV) | Decrease ventilation setpoints or change time schedules to insure the minimum indoor air quality | CO2/VOC concentration; ASHRAE Std. 62.1
|  | Outdoor air reduction | Turn off the outdoor air damper to reduce cooling loads |  | N/A
|  | Duct static pressure decrease | Decrease duct static pressure setpoints to reduce fan power | CO2/VOC concentration; ASHRAE Std. 55, 62.1
|  | Fan variable frequency drive limit | Limit or decrease fan variable frequency drive speeds or inlet guide vane positions to reduce fan power
|  | Fan quantity reduction | Shut off some of multiple fans or package units to reduce fan and cooling loads
|  | Humidity control | Shut off/reduce the dedicated dehumidification function
| Central plant | Chilled water temperature increase | Increase chilled water temperature to improve chiller efficiency and reduce cooling load | Ambient temperature, humidity; ASHRAE Std. 55
|  | Chiller demand limit | Limit or reduce chiller demand or capacity
|  | Chiller quantity Reduction | Shut off some of multiple chiller units
| Rebound avoidance | Slow recovery | Slowly restore HVAC control parameters modified by DR strategies | Ambient temperature, humidity, CO2/VOC concentration; ASHRAE Std. 55, 62.1
|  | Sequential equipment recovery | Restore HVAC control to equipment sequentially within a certain time interval
|  | Extended DR control Period | Extend DR control period until after the occupancy period
Lighting |  | Zone switching | Turn off the lights within specific zones | Task illuminance; IESNA Lighting Handbook | N/A
|  | Fixture switching | Turn off the light fixture when bi-level switching function available |  | N/A
|  | Lamp switching | Turn off the lamp switching when bi-level infrastructure function available |  | N/A
|  | Stepped dimming | Dim the lighting by two/three lighting levels (step dimming capability needed) |  | One level, | Two levels | Three levels
|  | Continuous dimming | Dim the lighting by a certain percent (dimmable ballast needed) |  | 30% | 50% | 70%
MELs (Miscellaneous electric loads) |  | Stand-by equipment load reduction | Unplug equipment/appliances operating in stand-by mode, e.g., toasters, pool pumps and heaters | ? | N/A
|  | Activities limit | Turn off TV, internet routers, or use only one screen of the desktop computer; reduce elevator cycling, disable laundry services
Domestic water heating |  | Supply water temperature | Decrease the supply water temperature setpoints
|  | On-demand circulation/pumping | Decrease the pumping frequency
Refrigeration |  | Setpoint temperature adjustment | Increase the setpoint temperature (Ideal one would be 38ºF for refrigerator and 0ºF for freeze) | Food temperature; USDA Food and Safety Guidelines | 1ºF | 2ºF | 3ºF
|  | Operation limit | Reduce the frequency of door opening to reduce the operation of compressor |  | N/A
Electric Storage |  | Electric battery | Charge electric battery for energy storage | Power Capacity
|  | EV charging | Increase the use frequency during the daytime at working place
Occupant behavior (need pre-notice and motivation) |  | Window operation limit | Close windows to avoid convective heat gains and reduce cooling loads | ASHRAE Std. 62.1 | N/A
|  | Shading operation | Manipulate the shading to reduce solar heat gains and cooling loads | ASHRAE Std. 55, IESNA
Packages |  | HVAC and lighting | Increase cooling setpoint by 2F; decrease heating setpoint by 2F; Dim lights to reduce power by 30%;
|  | HVAC, lighting and MELs /w behavior measures | Increase cooling setpoint by 4F; decrease heating setpoint by 4F; Dim lights to reduce power by 50%; Include MELs and OB categories

## Topic 8-ListofDR-V3
End-Use Category | Sub-Category | DR Control Strategy | Strategy Description | Recommended Control Sequence | Response Speed | Sensitivity to Thermal Mass | Sensitivity to Thermal/Visual Comfort | Testing Facility | FLEXLAB Testing Capability Description | GEB - Load Flexibility | Grid Service | Existing literatures
Building Envelope | Exterior Wall | Passive thermal mass storage (precooling) | Precool the building during the night or early morning to store cooling energy and thus to flatten out the thermal energy flows over the daily ambient temperature fluctuations. | Precool 2 ºF and raise zone temperature by 2-6ºF | ~15 minutes | Yes | Yes | FLEXLAB | Changable/configurable building envelope elements and enabled building automation system (BAS). | Energy Efficiency; Shift; Shed | Peak Capacity Management
| Interior Wall and Thermal Mass | Passive thermal mass storage (precooling) | See D2. | See E2. | ~15 minutes | Yes | Yes | FLEXLAB | See J2. | Energy Efficiency; Shift; Shed | Peak Capacity Management
| Phase Change Material (PCM) | Passive/Active thermal mass storage (precooling) | See D2. | See E2. | ~15 minutes | Yes | Yes | FLEXLAB | See J2. | Energy Efficiency; Shift; Shed | Peak Capacity Management
HVAC Systems | Variable Air Volume (VAV) | Global temperature adjustment | Increase zone temperature setpoints for an adjustment entire facility | See E2. | ~15 minutes | Yes | Yes | FLEXLAB | Smart thermostat along with BAS. | Shift; Shed | Peak Capacity Management
|  | Passive thermal mass storage (precooling) | See D2. | See E2. | ~15 minutes | Yes | Yes | FLEXLAB | See J2. | Energy Efficiency; Shift; Shed | Peak Capacity Management
|  | Duct static pressure decrease | Decrease duct static pressure setpoints to reduce fan power. | DSP setpoint decreased from 1.5" to 1.0" | ~5 minutes | Yes | Yes | FLEXLAB | BAS with OpenADR embedded smart gateway. | Shed | Peak Capacity Management; Spinning and Non-spinning reserve
|  | Supply air temperature adjustment | Increase SAT setpoints to reduce cooling load. | SAT increased from 55 ºF to 65 ºF | ~5 minutes | Yes | Yes | FLEXLAB | See J7. | Energy Efficiency; Shed | Peak Capacity Management; Spinning and Non-spinning reserve
|  | Lock cooling valve position at the AHU | Lock cooling valve position at the AHU to reduce the chiller power. | Limit to 70%. | ~15 minutes | Yes | Yes | FLEXLAB | See J7. | Shed | Peak Capacity Management
|  | Fans and pumps quantity reduction | Shut off some of multiple fans/pumps to reduce fans/pumps power. | Shut off 1/3 of multiple fans/pumps | Seconds | Yes | Yes | FLEXLAB | See J7. | Shed | Peak Capacity Management; Spinning and Non-spinning reserve
|  | VFD fans and pumps speed adjustment | Limit or decrease fans/pumps variable drive speeds to reduce fan power. | Limit to 70%. | Seconds | Yes | Yes | FLEXLAB | See J7. | Shed | Peak Capacity Management; Spinning and Non-spinning reserve; Frequency Regulation
| Constant Air Volume (CAV) | Supply air temperature adjustment | Increase SAT setpoints to reduce cooling load. | See E8. | ~5 minutes | Yes | Yes | FLEXLAB | See J7. | Energy Efficiency; Shed | Peak Capacity Management; Spinning and Non-spinning reserve
|  | Lock cooling valve position at the AHU | Lock cooling valve position at the AHU to reduce the chiller power. | Limit to 70%. | ~15 minutes | Yes | Yes | FLEXLAB | See J7. | Shed | Peak Capacity Management
|  | Multi-fans quantity reduction | Shut off some of multiple fans to reduce fans power. | See E10. | Seconds | Yes | Yes | FLEXLAB | See J7. | Shed | Peak Capacity Management; Spinning and Non-spinning reserve
| Fan Coil Unit (FCU) | Thermostat setpoint adjustment | Increase zone temperature setpoints for an adjustment entire facility. | See E2. | ~15 minutes | Yes | Yes | FLEXLAB | Configurable. | Shed | Peak Capacity Management
|  | Fan coil speed adjustment | Adjust two- or three-stage fan coil speed to change fan power. | Fan coil speed reset to 1/3. | Seconds | Yes | Yes | FLEXLAB | Configurable. | Shed | Peak Capacity Management; Spinning and Non-spinning reserve
|  | Staged control of multiple FCUs | Staged control of multiple FCUs to reduce the aggregated power. | Staged control of multiple FCUs by 20 mins. | Seconds to minute | Yes | Yes | FLEXLAB | Configurable. | Shed | Peak Capacity Management; Spinning and Non-spinning reserve
| Variable Refrigerant Flow (VRF) | Thermostat setpoint adjustment | Increase zone temperature setpoints for an adjustment entire facility. | See E2. | ~5 minutes | Yes | Yes |  | FLEXLAB is set up to allow for a VRF install at the testbeds, but it would need to be procured and installed. Would need to coordinate with VRF manufacturer and controls to be able to manipulate the other variables mentioned. | Shed | Peak Capacity Management; Spinning and Non-spinning reserve
|  | Compressor speed adjustment | Adjust two- or three-stage compressor speed to change compressor power. | Limit to 70%. | Seconds | Yes | Yes |  |  | Shed | Peak Capacity Management; Spinning and Non-spinning reserve; Frequency Regulation
|  | Cycle on/off VRF indoor and outdoor units | Cycle on/off VRF indoor and outdoor units. | Cycle on/off VRF indoor and outdoor units by 30%, 50% and 100% | Seconds to minute | Yes | Yes |  |  | Shed | Peak Capacity Management; Spinning and Non-spinning reserve
HVAC Plant | Water/Air-Cooled Chiller | Chilled water temperature reset (air-cooled) | Increase chilled water temperature to improve chiller efficiency and reduce cooling load. | CHW setpoint increased 5 ºF | ~15 minutes | Yes | Yes | FLEXLAB | See J7. | Energy Efficiency; Shed | Peak Capacity Management
|  | Condenser and chilled water temperature reset (water-cooled) | See D19. | See E19. | ~15 minutes | Yes | Yes | FLEXLAB | See J7. | Shed | Peak Capacity Management
|  | Chiller demand limit | Limit the chiller capacity to reduce the chiller power during the peak period. | Limit to 70%. | ~5 minutes | Yes | Yes | FLEXLAB | See J7. | Shed | Peak Capacity Management; Spinning and Non-spinning reserve
|  | Chiller quantity reduction | Shut off some of multiple chillers to reduce chillers power. | Shut off 1/3 or 1/2 of multiple chillers | ~5 minutes | Yes | Yes | FLEXLAB | See J7. | Shed | Peak Capacity Management; Spinning and Non-spinning reserve
| Packaged Rooftop Unit | Cycle on/off compressors | Cycle on/off or lock out compressors | Cycle on/off HVAC plants by 30%, 50% and 100% | Seconds to minute | Yes | Yes | LBNL | See J7. | Shed | Peak Capacity Management; Spinning and Non-spinning reserve
| Heat Pump | Cycle on/off HP units | Cycle on/off HP units or lock out compressors. | Cycle on/off HP units by 30%, 50% and 100% | Seconds to minute | Yes | Yes |  | FLEXLAB doesn't currently have this but is possible to incorporate. | Shed | Peak Capacity Management; Spinning and Non-spinning reserve
|  | Chilled water temperature reset (water or air to water) | See D19. | See E19. | ~5 minutes | Yes | Yes |  |  | Energy Efficiency; Shed | Peak Capacity Management; Spinning and Non-spinning reserve
| Water Source Heat Pump | Chilled water temperature reset | See D19. | See E19. | ~5 minutes | Yes | No |  | Water source heat pump would require condenser water for heat rejection/absorbtion and a cooling tower. We don't currently have but is possible to incorporate. | Energy Efficiency; Shed | Peak Capacity Management; Spinning and Non-spinning reserve
| Ice/Water Thermal Storage | Shift of charging period | Shift of TES charging period. | N/A | ~15 minutes | Yes | Yes |  | FLEXLAB doesn't currently have this but is possible to incorporate. | Energy Efficiency; Shift | Peak Capacity Management
|  | Cycle off the partial chiller | Shut off the partial chiller to reduce the chiller power. | Shut off 1/3 or 1/2 of multiple chillers | ~5 minutes | Yes | Yes |  |  | Shed | Peak Capacity Management; Spinning and Non-spinning reserve
Lighting | Interior Lighting | Dimming control (continuous and step) | Dimming the lighting by 40%~60% | 40%~60% | Seconds | No | Yes | FLEXLAB | See J7. | Shed | Peak Capacity Management; Spinning and Non-spinning reserve; Frequency Regulation
|  | Switch on/off | Turn off all day light zones, public areas and perimeter lights. | 100% | Seconds | No | Yes | FLEXLAB | See J7. | Shed | Peak Capacity Management; Spinning and Non-spinning reserve
| Task Lighting | Switch on/off | Turn off all task lights. | 100% | Seconds | No | Yes | FLEXLAB | See J7. | Shed | Peak Capacity Management; Spinning and Non-spinning reserve
Water Heater | Electric | Setpoint adjustment | Reduce hot water temperature setpoint to reduce the electric water heater power. | Decrease water temperature setpoint by 1-5 ºF | ~5 minutes | No | No | FLEXLAB |  | Shed | Peak Capacity Management; Spinning and Non-spinning reserve
|  | Setpoint adjustment along with valve control | Increase water temperature setpoint to the high limit before the event and turn it off during the event. | Increase water temperature setpoint by ~20 ºF (from 120ºF to 140ºF) | Seconds | No | No | FLEXLAB | CTA-2045 | Shift
|  | Switch on/off | Turn off the electric water heater. | N/A | Seconds | No | No | FLEXLAB | CTA-2045 | Shed | Peak Capacity Management; Spinning and Non-spinning reserve
Plug Loads | Non-critical Process Load | Switch on/off | Shutdown auxiliary equipment. | N/A | Seconds | No | No | FLEXLAB | Smart plugs. | Shed | Peak Capacity Management; Spinning and Non-spinning reserve