## Welcome to DR Tool
ADR Estimation Tool Framework
Instructions for LBNL ADR Tool V2.1:
This tool provides DR shed magnitudes for a range of OATs for one of the major DR strategies: 1) HVAC Temp Reset (Precool with Zone Temp Setback).
Step 1: Copy 15-min electricity meter data into the "IDAR Meter Data" sheet. First column is date and time in format "MM/DD/YYYY HH:MM". Second column is meter demand in units of kW in any number format.
Step 2: In the "User Inputs and DR Shed Results" sheet's "ADR Site Description" block: 1. Enter the site name (if desired), 2. Select building type--Office or Retail, 3. Select HVAC type--Rooftop unit(s) or Central Plant and 4. Enter the site's zip code.
Step 3:If HVAC temp reset is strategy of intereset, in the "User Inputs and DR Shed Results" sheet's "HVAC Temp Reset DR Shed Capacity Calculation": 1. Enter the percent of the floor area of the building for which the HVAC temp reset will be applied (0-100), 2. Select the "Precool Period Temp Offset"; either 0 or -2 °F, and 3. Select the "DR Event Period Temp Offset", either 2, 4, or 6 °F.
Estimated kW sheds are calculated in tables and figures in "User Inputs and DR Shed Results".
Temperature ranges shown in HVAC Temp Reset DR Shed Estimates (kW) are Peak Outside Air Temperatures on weekdays in the following ranges: 1 (60-65°F), 2 (65-70°F), 3 (70-75°F), 4 (75-80°F), 5 (80-85°F), 6 (85-90°F), and 7 (Above 90°F).
Note: Only weekdays are selected for DR shed calculations. Weekends, holidays and ADR days in 2015 (if customer has enrolled into 2015 ADR programs) are excluded.

## IDAR Meter Data
Date
2015-05-01 | 232
2015-05-01 00:15 | 232
2015-05-01 00:30 | 207
2015-05-01 00:45 | 224
2015-05-01 01:00 | 208
2015-05-01 01:15 | 208
2015-05-01 01:30 | 196
2015-05-01 01:45 | 205
2015-05-01 02:00 | 196
2015-05-01 02:15 | 205
2015-05-01 02:30 | 187
2015-05-01 02:45 | 185
2015-05-01 03:00 | 169
2015-05-01 03:15 | 180
2015-05-01 03:30 | 171
2015-05-01 03:45 | 180
2015-05-01 04:00 | 163
2015-05-01 04:15 | 174
2015-05-01 04:30 | 172
2015-05-01 04:45 | 167
2015-05-01 05:00 | 166
2015-05-01 05:15 | 163
2015-05-01 05:30 | 161
2015-05-01 05:45 | 169
2015-05-01 06:00 | 158
2015-05-01 06:15 | 167
2015-05-01 06:30 | 173
2015-05-01 06:45 | 164
2015-05-01 07:00 | 176
2015-05-01 07:15 | 168
2015-05-01 07:30 | 179
2015-05-01 07:45 | 178
2015-05-01 08:00 | 183
2015-05-01 08:15 | 223
2015-05-01 08:30 | 210
2015-05-01 08:45 | 251
2015-05-01 09:00 | 249
2015-05-01 09:15 | 243
2015-05-01 09:30 | 262
2015-05-01 09:45 | 259
2015-05-01 10:00 | 263
2015-05-01 10:15 | 278
2015-05-01 10:30 | 257
2015-05-01 10:45 | 266
2015-05-01 11:00 | 260
2015-05-01 11:15 | 279
2015-05-01 11:30 | 282
2015-05-01 11:45 | 293
2015-05-01 12:00 | 290
2015-05-01 12:15 | 289
2015-05-01 12:30 | 297
2015-05-01 12:45 | 288
2015-05-01 13:00 | 297
2015-05-01 13:15 | 288
2015-05-01 13:30 | 305
2015-05-01 13:45 | 299
2015-05-01 14:00 | 309
2015-05-01 14:15 | 318
2015-05-01 14:30 | 320
2015-05-01 14:45 | 314
2015-05-01 15:00 | 312
2015-05-01 15:15 | 315
2015-05-01 15:30 | 319
2015-05-01 15:45 | 317
2015-05-01 16:00 | 319
2015-05-01 16:15 | 304
2015-05-01 16:30 | 295
2015-05-01 16:45 | 301
2015-05-01 17:00 | 307
2015-05-01 17:15 | 296
2015-05-01 17:30 | 282
2015-05-01 17:45 | 284
2015-05-01 18:00 | 282
2015-05-01 18:15 | 283
2015-05-01 18:30 | 278
2015-05-01 18:45 | 262
2015-05-01 19:00 | 272
2015-05-01 19:15 | 256
2015-05-01 19:30 | 258
2015-05-01 19:45 | 241
2015-05-01 20:00 | 250
2015-05-01 20:15 | 227
2015-05-01 20:30 | 206
2015-05-01 20:45 | 209
2015-05-01 21:00 | 202
2015-05-01 21:15 | 183
2015-05-01 21:30 | 182
2015-05-01 21:45 | 181
2015-05-01 22:00 | 189
2015-05-01 22:15 | 191
2015-05-01 22:30 | 167
2015-05-01 22:45 | 179
2015-05-01 23:00 | 178
2015-05-01 23:15 | 172
2015-05-01 23:30 | 183
2015-05-01 23:45 | 184
2015-05-02 | 178
2015-05-02 00:15 | 187
2015-05-02 00:30 | 167
2015-05-02 00:45 | 167
2015-05-02 01:00 | 171
2015-05-02 01:15 | 169
2015-05-02 01:30 | 164
2015-05-02 01:45 | 169
2015-05-02 02:00 | 162
2015-05-02 02:15 | 163
2015-05-02 02:30 | 162
2015-05-02 02:45 | 159
2015-05-02 03:00 | 156
2015-05-02 03:15 | 160
2015-05-02 03:30 | 157
2015-05-02 03:45 | 161
2015-05-02 04:00 | 158
2015-05-02 04:15 | 160
2015-05-02 04:30 | 168
2015-05-02 04:45 | 161
2015-05-02 05:00 | 156
2015-05-02 05:15 | 156
2015-05-02 05:30 | 151
2015-05-02 05:45 | 155
2015-05-02 06:00 | 155
2015-05-02 06:15 | 161
2015-05-02 06:30 | 169
2015-05-02 06:45 | 158
2015-05-02 07:00 | 167
2015-05-02 07:15 | 160
2015-05-02 07:30 | 162
2015-05-02 07:45 | 160
2015-05-02 08:00 | 155
2015-05-02 08:15 | 161
2015-05-02 08:30 | 168
2015-05-02 08:45 | 159
2015-05-02 09:00 | 167
2015-05-02 09:15 | 157
2015-05-02 09:30 | 189
2015-05-02 09:45 | 166
2015-05-02 10:00 | 178
2015-05-02 10:15 | 180
2015-05-02 10:30 | 180
2015-05-02 10:45 | 192
2015-05-02 11:00 | 214
2015-05-02 11:15 | 213
2015-05-02 11:30 | 207
2015-05-02 11:45 | 217
2015-05-02 12:00 | 221
2015-05-02 12:15 | 210
2015-05-02 12:30 | 222
2015-05-02 12:45 | 214
2015-05-02 13:00 | 212
2015-05-02 13:15 | 221
2015-05-02 13:30 | 219
2015-05-02 13:45 | 220
2015-05-02 14:00 | 238
2015-05-02 14:15 | 225
2015-05-02 14:30 | 225
2015-05-02 14:45 | 222
2015-05-02 15:00 | 239
2015-05-02 15:15 | 237
2015-05-02 15:30 | 234
2015-05-02 15:45 | 235
2015-05-02 16:00 | 227
2015-05-02 16:15 | 245
2015-05-02 16:30 | 229
2015-05-02 16:45 | 242
2015-05-02 17:00 | 226
2015-05-02 17:15 | 228
2015-05-02 17:30 | 230
2015-05-02 17:45 | 226
2015-05-02 18:00 | 234
2015-05-02 18:15 | 217
2015-05-02 18:30 | 219
2015-05-02 18:45 | 215
2015-05-02 19:00 | 212
2015-05-02 19:15 | 190
2015-05-02 19:30 | 189
2015-05-02 19:45 | 194
2015-05-02 20:00 | 184
2015-05-02 20:15 | 180
2015-05-02 20:30 | 187
2015-05-02 20:45 | 171
2015-05-02 21:00 | 172
2015-05-02 21:15 | 170
2015-05-02 21:30 | 171
2015-05-02 21:45 | 169
2015-05-02 22:00 | 161
2015-05-02 22:15 | 153
2015-05-02 22:30 | 162
2015-05-02 22:45 | 159
2015-05-02 23:00 | 162
2015-05-02 23:15 | 158
2015-05-02 23:30 | 169
2015-05-02 23:45 | 160
2015-05-03 | 156
2015-05-03 00:15 | 154
2015-05-03 00:30 | 162
2015-05-03 00:45 | 155
2015-05-03 01:00 | 153
2015-05-03 01:15 | 150
2015-05-03 01:30 | 159
2015-05-03 01:45 | 157
2015-05-03 02:00 | 147
2015-05-03 02:15 | 150
2015-05-03 02:30 | 149
2015-05-03 02:45 | 152
2015-05-03 03:00 | 162
2015-05-03 03:15 | 157
2015-05-03 03:30 | 161
2015-05-03 03:45 | 152
2015-05-03 04:00 | 163
2015-05-03 04:15 | 147
2015-05-03 04:30 | 162
2015-05-03 04:45 | 152
2015-05-03 05:00 | 151
2015-05-03 05:15 | 146
2015-05-03 05:30 | 163
2015-05-03 05:45 | 147
2015-05-03 06:00 | 152
2015-05-03 06:15 | 151
2015-05-03 06:30 | 154
2015-05-03 06:45 | 163
2015-05-03 07:00 | 161
2015-05-03 07:15 | 156
2015-05-03 07:30 | 164
2015-05-03 07:45 | 161
2015-05-03 08:00 | 165
2015-05-03 08:15 | 169
2015-05-03 08:30 | 170
2015-05-03 08:45 | 179
2015-05-03 09:00 | 172
2015-05-03 09:15 | 170
2015-05-03 09:30 | 169
2015-05-03 09:45 | 174
2015-05-03 10:00 | 173
2015-05-03 10:15 | 174
2015-05-03 10:30 | 174
2015-05-03 10:45 | 186
2015-05-03 11:00 | 174
2015-05-03 11:15 | 187
2015-05-03 11:30 | 227
2015-05-03 11:45 | 202
2015-05-03 12:00 | 214
2015-05-03 12:15 | 218
2015-05-03 12:30 | 216
2015-05-03 12:45 | 224
2015-05-03 13:00 | 233
2015-05-03 13:15 | 214
2015-05-03 13:30 | 228
2015-05-03 13:45 | 221
2015-05-03 14:00 | 218
2015-05-03 14:15 | 229
2015-05-03 14:30 | 222
2015-05-03 14:45 | 231
2015-05-03 15:00 | 228
2015-05-03 15:15 | 228
2015-05-03 15:30 | 242
2015-05-03 15:45 | 226
2015-05-03 16:00 | 237
2015-05-03 16:15 | 219
2015-05-03 16:30 | 226
2015-05-03 16:45 | 227
2015-05-03 17:00 | 236
2015-05-03 17:15 | 223
2015-05-03 17:30 | 220
2015-05-03 17:45 | 216
2015-05-03 18:00 | 225
2015-05-03 18:15 | 212
2015-05-03 18:30 | 203
2015-05-03 18:45 | 194
2015-05-03 19:00 | 194
2015-05-03 19:15 | 186
2015-05-03 19:30 | 191
2015-05-03 19:45 | 178
2015-05-03 20:00 | 200
2015-05-03 20:15 | 182
2015-05-03 20:30 | 181
2015-05-03 20:45 | 176
2015-05-03 21:00 | 183
2015-05-03 21:15 | 163
2015-05-03 21:30 | 158
2015-05-03 21:45 | 167
2015-05-03 22:00 | 162
2015-05-03 22:15 | 156
2015-05-03 22:30 | 156
2015-05-03 22:45 | 159
2015-05-03 23:00 | 164
2015-05-03 23:15 | 156
2015-05-03 23:30 | 158
2015-05-03 23:45 | 149
2015-05-04 | 157
2015-05-04 00:15 | 157
2015-05-04 00:30 | 155
2015-05-04 00:45 | 163
2015-05-04 01:00 | 153
2015-05-04 01:15 | 153
2015-05-04 01:30 | 153
2015-05-04 01:45 | 158
2015-05-04 02:00 | 161
2015-05-04 02:15 | 151
2015-05-04 02:30 | 152
2015-05-04 02:45 | 152
2015-05-04 03:00 | 164
2015-05-04 03:15 | 146
2015-05-04 03:30 | 150
2015-05-04 03:45 | 146
2015-05-04 04:00 | 160
2015-05-04 04:15 | 147
2015-05-04 04:30 | 149
2015-05-04 04:45 | 149
2015-05-04 05:00 | 146
2015-05-04 05:15 | 160
2015-05-04 05:30 | 144
2015-05-04 05:45 | 145
2015-05-04 06:00 | 152
2015-05-04 06:15 | 155
2015-05-04 06:30 | 149
2015-05-04 06:45 | 152
2015-05-04 07:00 | 80
2015-05-04 07:15 | 47
2015-05-04 07:30 | 47
2015-05-04 07:45 | 57
2015-05-04 08:00 | 63
2015-05-04 08:15 | 64
2015-05-04 08:30 | 63
2015-05-04 08:45 | 62
2015-05-04 09:00 | 71
2015-05-04 09:15 | 130
2015-05-04 09:30 | 165
2015-05-04 09:45 | 169
2015-05-04 10:00 | 173
2015-05-04 10:15 | 178
2015-05-04 10:30 | 178
2015-05-04 10:45 | 178
2015-05-04 11:00 | 175
2015-05-04 11:15 | 187
2015-05-04 11:30 | 204
2015-05-04 11:45 | 208
2015-05-04 12:00 | 212
2015-05-04 12:15 | 192
2015-05-04 12:30 | 213
2015-05-04 12:45 | 203
2015-05-04 13:00 | 206
2015-05-04 13:15 | 213
2015-05-04 13:30 | 200
2015-05-04 13:45 | 212
2015-05-04 14:00 | 211
2015-05-04 14:15 | 209
2015-05-04 14:30 | 227
2015-05-04 14:45 | 209
2015-05-04 15:00 | 219
2015-05-04 15:15 | 227
2015-05-04 15:30 | 215
2015-05-04 15:45 | 230
2015-05-04 16:00 | 210
2015-05-04 16:15 | 224
2015-05-04 16:30 | 227
2015-05-04 16:45 | 214
2015-05-04 17:00 | 227
2015-05-04 17:15 | 211
2015-05-04 17:30 | 216
2015-05-04 17:45 | 215
2015-05-04 18:00 | 209
2015-05-04 18:15 | 203
2015-05-04 18:30 | 195
2015-05-04 18:45 | 204
2015-05-04 19:00 | 195
2015-05-04 19:15 | 189
2015-05-04 19:30 | 184
2015-05-04 19:45 | 185
2015-05-04 20:00 | 171
2015-05-04 20:15 | 171
2015-05-04 20:30 | 171
2015-05-04 20:45 | 170
2015-05-04 21:00 | 172
2015-05-04 21:15 | 163
2015-05-04 21:30 | 148
2015-05-04 21:45 | 148
2015-05-04 22:00 | 146
2015-05-04 22:15 | 152
2015-05-04 22:30 | 151
2015-05-04 22:45 | 151
2015-05-04 23:00 | 150
2015-05-04 23:15 | 150
2015-05-04 23:30 | 154
2015-05-04 23:45 | 151
2015-05-05 | 158
2015-05-05 00:15 | 153
2015-05-05 00:30 | 149
2015-05-05 00:45 | 145
2015-05-05 01:00 | 142
2015-05-05 01:15 | 142
2015-05-05 01:30 | 133
2015-05-05 01:45 | 138
2015-05-05 02:00 | 133
2015-05-05 02:15 | 138
2015-05-05 02:30 | 133
2015-05-05 02:45 | 135
2015-05-05 03:00 | 135
2015-05-05 03:15 | 134
2015-05-05 03:30 | 135
2015-05-05 03:45 | 133
2015-05-05 04:00 | 136
2015-05-05 04:15 | 131
2015-05-05 04:30 | 136
2015-05-05 04:45 | 130
2015-05-05 05:00 | 134
2015-05-05 05:15 | 130
2015-05-05 05:30 | 133
2015-05-05 05:45 | 131
2015-05-05 06:00 | 134
2015-05-05 06:15 | 136
2015-05-05 06:30 | 136
2015-05-05 06:45 | 133
2015-05-05 07:00 | 135
2015-05-05 07:15 | 134
2015-05-05 07:30 | 140
2015-05-05 07:45 | 149
2015-05-05 08:00 | 157
2015-05-05 08:15 | 156
2015-05-05 08:30 | 158
2015-05-05 08:45 | 161
2015-05-05 09:00 | 167
2015-05-05 09:15 | 178
2015-05-05 09:30 | 175
2015-05-05 09:45 | 174
2015-05-05 10:00 | 177
2015-05-05 10:15 | 187
2015-05-05 10:30 | 198
2015-05-05 10:45 | 199
2015-05-05 11:00 | 191
2015-05-05 11:15 | 202
2015-05-05 11:30 | 205
2015-05-05 11:45 | 209
2015-05-05 12:00 | 216
2015-05-05 12:15 | 206
2015-05-05 12:30 | 218
2015-05-05 12:45 | 216
2015-05-05 13:00 | 214
2015-05-05 13:15 | 219
2015-05-05 13:30 | 226
2015-05-05 13:45 | 216
2015-05-05 14:00 | 232
2015-05-05 14:15 | 228
2015-05-05 14:30 | 216
2015-05-05 14:45 | 230
2015-05-05 15:00 | 222
2015-05-05 15:15 | 229
2015-05-05 15:30 | 241
2015-05-05 15:45 | 228
2015-05-05 16:00 | 220
2015-05-05 16:15 | 244
2015-05-05 16:30 | 228
2015-05-05 16:45 | 232
2015-05-05 17:00 | 233
2015-05-05 17:15 | 234
2015-05-05 17:30 | 222
2015-05-05 17:45 | 209
2015-05-05 18:00 | 219
2015-05-05 18:15 | 213
2015-05-05 18:30 | 205
2015-05-05 18:45 | 196
2015-05-05 19:00 | 201
2015-05-05 19:15 | 193
2015-05-05 19:30 | 197
2015-05-05 19:45 | 190
2015-05-05 20:00 | 185
2015-05-05 20:15 | 185
2015-05-05 20:30 | 182
2015-05-05 20:45 | 173
2015-05-05 21:00 | 176
2015-05-05 21:15 | 159
2015-05-05 21:30 | 162
2015-05-05 21:45 | 154
2015-05-05 22:00 | 158
2015-05-05 22:15 | 153
2015-05-05 22:30 | 158
2015-05-05 22:45 | 158
2015-05-05 23:00 | 163
2015-05-05 23:15 | 155
2015-05-05 23:30 | 155
2015-05-05 23:45 | 155
2015-05-06 | 154
2015-05-06 00:15 | 153
2015-05-06 00:30 | 152
2015-05-06 00:45 | 147
2015-05-06 01:00 | 152
2015-05-06 01:15 | 145
2015-05-06 01:30 | 149
2015-05-06 01:45 | 144
2015-05-06 02:00 | 146
2015-05-06 02:15 | 145
2015-05-06 02:30 | 145
2015-05-06 02:45 | 146
2015-05-06 03:00 | 140
2015-05-06 03:15 | 143
2015-05-06 03:30 | 142
2015-05-06 03:45 | 145
2015-05-06 04:00 | 143
2015-05-06 04:15 | 141
2015-05-06 04:30 | 144
2015-05-06 04:45 | 143
2015-05-06 05:00 | 134
2015-05-06 05:15 | 141
2015-05-06 05:30 | 135
2015-05-06 05:45 | 139
2015-05-06 06:00 | 141
2015-05-06 06:15 | 141
2015-05-06 06:30 | 143
2015-05-06 06:45 | 146
2015-05-06 07:00 | 144
2015-05-06 07:15 | 145
2015-05-06 07:30 | 150
2015-05-06 07:45 | 151
2015-05-06 08:00 | 165
2015-05-06 08:15 | 166
2015-05-06 08:30 | 170
2015-05-06 08:45 | 179
2015-05-06 09:00 | 179
2015-05-06 09:15 | 188
2015-05-06 09:30 | 184
2015-05-06 09:45 | 192
2015-05-06 10:00 | 189
2015-05-06 10:15 | 199
2015-05-06 10:30 | 199
2015-05-06 10:45 | 203
2015-05-06 11:00 | 203
2015-05-06 11:15 | 205
2015-05-06 11:30 | 210
2015-05-06 11:45 | 210
2015-05-06 12:00 | 203
2015-05-06 12:15 | 212
2015-05-06 12:30 | 211
2015-05-06 12:45 | 203
2015-05-06 13:00 | 210
2015-05-06 13:15 | 217
2015-05-06 13:30 | 211
2015-05-06 13:45 | 227
2015-05-06 14:00 | 232
2015-05-06 14:15 | 217
2015-05-06 14:30 | 236
2015-05-06 14:45 | 233
2015-05-06 15:00 | 230
2015-05-06 15:15 | 249
2015-05-06 15:30 | 238
2015-05-06 15:45 | 248
2015-05-06 16:00 | 244
2015-05-06 16:15 | 248
2015-05-06 16:30 | 252
2015-05-06 16:45 | 249
2015-05-06 17:00 | 253
2015-05-06 17:15 | 240
2015-05-06 17:30 | 243
2015-05-06 17:45 | 245
2015-05-06 18:00 | 232
2015-05-06 18:15 | 244
2015-05-06 18:30 | 229
2015-05-06 18:45 | 227
2015-05-06 19:00 | 226
2015-05-06 19:15 | 217
2015-05-06 19:30 | 219
2015-05-06 19:45 | 212
2015-05-06 20:00 | 211
2015-05-06 20:15 | 200
2015-05-06 20:30 | 201
2015-05-06 20:45 | 192
2015-05-06 21:00 | 194
2015-05-06 21:15 | 172
2015-05-06 21:30 | 164
2015-05-06 21:45 | 167
2015-05-06 22:00 | 169
2015-05-06 22:15 | 168
2015-05-06 22:30 | 161
2015-05-06 22:45 | 159
2015-05-06 23:00 | 163
2015-05-06 23:15 | 158
2015-05-06 23:30 | 154
2015-05-06 23:45 | 152
2015-05-07 | 148
2015-05-07 00:15 | 150
2015-05-07 00:30 | 143
2015-05-07 00:45 | 146
2015-05-07 01:00 | 148
2015-05-07 01:15 | 143
2015-05-07 01:30 | 147
2015-05-07 01:45 | 142
2015-05-07 02:00 | 141
2015-05-07 02:15 | 142
2015-05-07 02:30 | 140
2015-05-07 02:45 | 138
2015-05-07 03:00 | 135
2015-05-07 03:15 | 137
2015-05-07 03:30 | 137
2015-05-07 03:45 | 135
2015-05-07 04:00 | 141
2015-05-07 04:15 | 137
2015-05-07 04:30 | 139
2015-05-07 04:45 | 142
2015-05-07 05:00 | 137
2015-05-07 05:15 | 141
2015-05-07 05:30 | 138
2015-05-07 05:45 | 141
2015-05-07 06:00 | 133
2015-05-07 06:15 | 137
2015-05-07 06:30 | 138
2015-05-07 06:45 | 138
2015-05-07 07:00 | 137
2015-05-07 07:15 | 137
2015-05-07 07:30 | 138
2015-05-07 07:45 | 148
2015-05-07 08:00 | 152
2015-05-07 08:15 | 159
2015-05-07 08:30 | 160
2015-05-07 08:45 | 172
2015-05-07 09:00 | 172
2015-05-07 09:15 | 175
2015-05-07 09:30 | 176
2015-05-07 09:45 | 181
2015-05-07 10:00 | 170
2015-05-07 10:15 | 173
2015-05-07 10:30 | 176
2015-05-07 10:45 | 179
2015-05-07 11:00 | 190
2015-05-07 11:15 | 185
2015-05-07 11:30 | 200
2015-05-07 11:45 | 186
2015-05-07 12:00 | 196
2015-05-07 12:15 | 185
2015-05-07 12:30 | 187
2015-05-07 12:45 | 178
2015-05-07 13:00 | 189
2015-05-07 13:15 | 183
2015-05-07 13:30 | 185
2015-05-07 13:45 | 181
2015-05-07 14:00 | 182
2015-05-07 14:15 | 185
2015-05-07 14:30 | 179
2015-05-07 14:45 | 186
2015-05-07 15:00 | 188
2015-05-07 15:15 | 196
2015-05-07 15:30 | 195
2015-05-07 15:45 | 205
2015-05-07 16:00 | 204
2015-05-07 16:15 | 191
2015-05-07 16:30 | 193
2015-05-07 16:45 | 178
2015-05-07 17:00 | 180
2015-05-07 17:15 | 176
2015-05-07 17:30 | 183
2015-05-07 17:45 | 174
2015-05-07 18:00 | 185
2015-05-07 18:15 | 175
2015-05-07 18:30 | 186
2015-05-07 18:45 | 166
2015-05-07 19:00 | 180
2015-05-07 19:15 | 168
2015-05-07 19:30 | 179
2015-05-07 19:45 | 164
2015-05-07 20:00 | 166
2015-05-07 20:15 | 165
2015-05-07 20:30 | 172
2015-05-07 20:45 | 168
2015-05-07 21:00 | 165
2015-05-07 21:15 | 153
2015-05-07 21:30 | 151
2015-05-07 21:45 | 158
2015-05-07 22:00 | 157
2015-05-07 22:15 | 146
2015-05-07 22:30 | 146
2015-05-07 22:45 | 145
2015-05-07 23:00 | 165
2015-05-07 23:15 | 149
2015-05-07 23:30 | 152
2015-05-07 23:45 | 143
2015-05-08 | 160
2015-05-08 00:15 | 145
2015-05-08 00:30 | 147
2015-05-08 00:45 | 140
2015-05-08 01:00 | 144
2015-05-08 01:15 | 142
2015-05-08 01:30 | 156
2015-05-08 01:45 | 141
2015-05-08 02:00 | 141
2015-05-08 02:15 | 144
2015-05-08 02:30 | 141
2015-05-08 02:45 | 138
2015-05-08 03:00 | 139
2015-05-08 03:15 | 133
2015-05-08 03:30 | 137
2015-05-08 03:45 | 138
2015-05-08 04:00 | 138
2015-05-08 04:15 | 136
2015-05-08 04:30 | 132
2015-05-08 04:45 | 133
2015-05-08 05:00 | 134
2015-05-08 05:15 | 137
2015-05-08 05:30 | 138
2015-05-08 05:45 | 136
2015-05-08 06:00 | 133
2015-05-08 06:15 | 136
2015-05-08 06:30 | 142
2015-05-08 06:45 | 143
2015-05-08 07:00 | 142
2015-05-08 07:15 | 141
2015-05-08 07:30 | 140
2015-05-08 07:45 | 145
2015-05-08 08:00 | 152
2015-05-08 08:15 | 159
2015-05-08 08:30 | 161
2015-05-08 08:45 | 166
2015-05-08 09:00 | 169
2015-05-08 09:15 | 175
2015-05-08 09:30 | 179
2015-05-08 09:45 | 180
2015-05-08 10:00 | 174
2015-05-08 10:15 | 191
2015-05-08 10:30 | 197
2015-05-08 10:45 | 211
2015-05-08 11:00 | 199
2015-05-08 11:15 | 207
2015-05-08 11:30 | 204
2015-05-08 11:45 | 194
2015-05-08 12:00 | 188
2015-05-08 12:15 | 198
2015-05-08 12:30 | 193
2015-05-08 12:45 | 198
2015-05-08 13:00 | 199
2015-05-08 13:15 | 199
2015-05-08 13:30 | 214
2015-05-08 13:45 | 209
2015-05-08 14:00 | 212
2015-05-08 14:15 | 226
2015-05-08 14:30 | 222
2015-05-08 14:45 | 219
2015-05-08 15:00 | 230
2015-05-08 15:15 | 220
2015-05-08 15:30 | 222
2015-05-08 15:45 | 261
2015-05-08 16:00 | 291
2015-05-08 16:15 | 232
2015-05-08 16:30 | 217
2015-05-08 16:45 | 218
2015-05-08 17:00 | 222
2015-05-08 17:15 | 205
2015-05-08 17:30 | 213
2015-05-08 17:45 | 208
2015-05-08 18:00 | 212
2015-05-08 18:15 | 218
2015-05-08 18:30 | 198
2015-05-08 18:45 | 208
2015-05-08 19:00 | 193
2015-05-08 19:15 | 207
2015-05-08 19:30 | 193
2015-05-08 19:45 | 187
2015-05-08 20:00 | 196
2015-05-08 20:15 | 191
2015-05-08 20:30 | 189
2015-05-08 20:45 | 179
2015-05-08 21:00 | 183
2015-05-08 21:15 | 164
2015-05-08 21:30 | 154
2015-05-08 21:45 | 149
2015-05-08 22:00 | 154
2015-05-08 22:15 | 156
2015-05-08 22:30 | 150
2015-05-08 22:45 | 149
2015-05-08 23:00 | 149
2015-05-08 23:15 | 160
2015-05-08 23:30 | 150
2015-05-08 23:45 | 147
2015-05-09 | 146
2015-05-09 00:15 | 152
2015-05-09 00:30 | 155
2015-05-09 00:45 | 146
2015-05-09 01:00 | 145
2015-05-09 01:15 | 146
2015-05-09 01:30 | 161
2015-05-09 01:45 | 146
2015-05-09 02:00 | 147
2015-05-09 02:15 | 142
2015-05-09 02:30 | 148
2015-05-09 02:45 | 157
2015-05-09 03:00 | 144
2015-05-09 03:15 | 141
2015-05-09 03:30 | 148
2015-05-09 03:45 | 150
2015-05-09 04:00 | 143
2015-05-09 04:15 | 142
2015-05-09 04:30 | 141
2015-05-09 04:45 | 148
2015-05-09 05:00 | 155
2015-05-09 05:15 | 143
2015-05-09 05:30 | 143
2015-05-09 05:45 | 145
2015-05-09 06:00 | 158
2015-05-09 06:15 | 146
2015-05-09 06:30 | 145
2015-05-09 06:45 | 148
2015-05-09 07:00 | 150
2015-05-09 07:15 | 152
2015-05-09 07:30 | 143
2015-05-09 07:45 | 143
2015-05-09 08:00 | 140
2015-05-09 08:15 | 143
2015-05-09 08:30 | 154
2015-05-09 08:45 | 144
2015-05-09 09:00 | 146
2015-05-09 09:15 | 149
2015-05-09 09:30 | 162
2015-05-09 09:45 | 149
2015-05-09 10:00 | 147
2015-05-09 10:15 | 144
2015-05-09 10:30 | 141
2015-05-09 10:45 | 140
2015-05-09 11:00 | 165
2015-05-09 11:15 | 147
2015-05-09 11:30 | 155
2015-05-09 11:45 | 152
2015-05-09 12:00 | 157
2015-05-09 12:15 | 167
2015-05-09 12:30 | 157
2015-05-09 12:45 | 162
2015-05-09 13:00 | 159
2015-05-09 13:15 | 155
2015-05-09 13:30 | 168
2015-05-09 13:45 | 161
2015-05-09 14:00 | 164
2015-05-09 14:15 | 161
2015-05-09 14:30 | 157
2015-05-09 14:45 | 169
2015-05-09 15:00 | 168
2015-05-09 15:15 | 177
2015-05-09 15:30 | 179
2015-05-09 15:45 | 169
2015-05-09 16:00 | 174
2015-05-09 16:15 | 181
2015-05-09 16:30 | 170
2015-05-09 16:45 | 180
2015-05-09 17:00 | 178
2015-05-09 17:15 | 170
2015-05-09 17:30 | 181
2015-05-09 17:45 | 169
2015-05-09 18:00 | 180
2015-05-09 18:15 | 186
2015-05-09 18:30 | 167
2015-05-09 18:45 | 185
2015-05-09 19:00 | 170
2015-05-09 19:15 | 170
2015-05-09 19:30 | 170
2015-05-09 19:45 | 169
2015-05-09 20:00 | 163
2015-05-09 20:15 | 164
2015-05-09 20:30 | 161
2015-05-09 20:45 | 159
2015-05-09 21:00 | 163
2015-05-09 21:15 | 169
2015-05-09 21:30 | 154
2015-05-09 21:45 | 160
2015-05-09 22:00 | 155
2015-05-09 22:15 | 167
2015-05-09 22:30 | 151
2015-05-09 22:45 | 155
2015-05-09 23:00 | 154
2015-05-09 23:15 | 163
2015-05-09 23:30 | 158
2015-05-09 23:45 | 153
2015-05-10 | 153
2015-05-10 00:15 | 170
2015-05-10 00:30 | 155
2015-05-10 00:45 | 151
2015-05-10 01:00 | 147
2015-05-10 01:15 | 164
2015-05-10 01:30 | 149
2015-05-10 01:45 | 150
2015-05-10 02:00 | 146
2015-05-10 02:15 | 155
2015-05-10 02:30 | 150
2015-05-10 02:45 | 142
2015-05-10 03:00 | 150
2015-05-10 03:15 | 145
2015-05-10 03:30 | 142
2015-05-10 03:45 | 143
2015-05-10 04:00 | 157
2015-05-10 04:15 | 142
2015-05-10 04:30 | 140
2015-05-10 04:45 | 141
2015-05-10 05:00 | 156
2015-05-10 05:15 | 144
2015-05-10 05:30 | 151
2015-05-10 05:45 | 155
2015-05-10 06:00 | 162
2015-05-10 06:15 | 147
2015-05-10 06:30 | 149
2015-05-10 06:45 | 146
2015-05-10 07:00 | 154
2015-05-10 07:15 | 161
2015-05-10 07:30 | 155
2015-05-10 07:45 | 156
2015-05-10 08:00 | 156
2015-05-10 08:15 | 172
2015-05-10 08:30 | 155
2015-05-10 08:45 | 159
2015-05-10 09:00 | 154
2015-05-10 09:15 | 161
2015-05-10 09:30 | 162
2015-05-10 09:45 | 175
2015-05-10 10:00 | 162
2015-05-10 10:15 | 177
2015-05-10 10:30 | 174
2015-05-10 10:45 | 178
2015-05-10 11:00 | 185
2015-05-10 11:15 | 182
2015-05-10 11:30 | 184
2015-05-10 11:45 | 176
2015-05-10 12:00 | 178
2015-05-10 12:15 | 196
2015-05-10 12:30 | 169
2015-05-10 12:45 | 184
2015-05-10 13:00 | 181
2015-05-10 13:15 | 176
2015-05-10 13:30 | 184
2015-05-10 13:45 | 180
2015-05-10 14:00 | 177
2015-05-10 14:15 | 187
2015-05-10 14:30 | 174
2015-05-10 14:45 | 178
2015-05-10 15:00 | 185
2015-05-10 15:15 | 199
2015-05-10 15:30 | 186
2015-05-10 15:45 | 192
2015-05-10 16:00 | 191
2015-05-10 16:15 | 190
2015-05-10 16:30 | 197
2015-05-10 16:45 | 187
2015-05-10 17:00 | 186
2015-05-10 17:15 | 194
2015-05-10 17:30 | 188
2015-05-10 17:45 | 179
2015-05-10 18:00 | 197
2015-05-10 18:15 | 178
2015-05-10 18:30 | 195
2015-05-10 18:45 | 180
2015-05-10 19:00 | 172
2015-05-10 19:15 | 183
2015-05-10 19:30 | 174
2015-05-10 19:45 | 169
2015-05-10 20:00 | 177
2015-05-10 20:15 | 166
2015-05-10 20:30 | 176
2015-05-10 20:45 | 168
2015-05-10 21:00 | 167
2015-05-10 21:15 | 155
2015-05-10 21:30 | 154
2015-05-10 21:45 | 153
2015-05-10 22:00 | 147
2015-05-10 22:15 | 147
2015-05-10 22:30 | 146
2015-05-10 22:45 | 151
2015-05-10 23:00 | 154
2015-05-10 23:15 | 147
2015-05-10 23:30 | 161
2015-05-10 23:45 | 155
2015-05-11 | 157
2015-05-11 00:15 | 151
2015-05-11 00:30 | 141
2015-05-11 00:45 | 140
2015-05-11 01:00 | 143
2015-05-11 01:15 | 152
2015-05-11 01:30 | 145
2015-05-11 01:45 | 152
2015-05-11 02:00 | 145
2015-05-11 02:15 | 154
2015-05-11 02:30 | 140
2015-05-11 02:45 | 147
2015-05-11 03:00 | 146
2015-05-11 03:15 | 140
2015-05-11 03:30 | 155
2015-05-11 03:45 | 140
2015-05-11 04:00 | 153
2015-05-11 04:15 | 142
2015-05-11 04:30 | 158
2015-05-11 04:45 | 139
2015-05-11 05:00 | 154
2015-05-11 05:15 | 149
2015-05-11 05:30 | 148
2015-05-11 05:45 | 145
2015-05-11 06:00 | 150
2015-05-11 06:15 | 141
2015-05-11 06:30 | 142
2015-05-11 06:45 | 157
2015-05-11 07:00 | 141
2015-05-11 07:15 | 142
2015-05-11 07:30 | 147
2015-05-11 07:45 | 150
2015-05-11 08:00 | 159
2015-05-11 08:15 | 157
2015-05-11 08:30 | 166
2015-05-11 08:45 | 166
2015-05-11 09:00 | 177
2015-05-11 09:15 | 178
2015-05-11 09:30 | 180
2015-05-11 09:45 | 175
2015-05-11 10:00 | 192
2015-05-11 10:15 | 206
2015-05-11 10:30 | 205
2015-05-11 10:45 | 207
2015-05-11 11:00 | 203
2015-05-11 11:15 | 207
2015-05-11 11:30 | 222
2015-05-11 11:45 | 219
2015-05-11 12:00 | 225
2015-05-11 12:15 | 217
2015-05-11 12:30 | 214
2015-05-11 12:45 | 205
2015-05-11 13:00 | 208
2015-05-11 13:15 | 194
2015-05-11 13:30 | 208
2015-05-11 13:45 | 206
2015-05-11 14:00 | 201
2015-05-11 14:15 | 209
2015-05-11 14:30 | 196
2015-05-11 14:45 | 214
2015-05-11 15:00 | 211
2015-05-11 15:15 | 201
2015-05-11 15:30 | 212
2015-05-11 15:45 | 204
2015-05-11 16:00 | 202
2015-05-11 16:15 | 196
2015-05-11 16:30 | 192
2015-05-11 16:45 | 197
2015-05-11 17:00 | 190
2015-05-11 17:15 | 200
2015-05-11 17:30 | 186
2015-05-11 17:45 | 187
2015-05-11 18:00 | 184
2015-05-11 18:15 | 186
2015-05-11 18:30 | 181
2015-05-11 18:45 | 178
2015-05-11 19:00 | 177
2015-05-11 19:15 | 172
2015-05-11 19:30 | 176
2015-05-11 19:45 | 175
2015-05-11 20:00 | 169
2015-05-11 20:15 | 169
2015-05-11 20:30 | 167
2015-05-11 20:45 | 172
2015-05-11 21:00 | 164
2015-05-11 21:15 | 158
2015-05-11 21:30 | 151
2015-05-11 21:45 | 154
2015-05-11 22:00 | 153
2015-05-11 22:15 | 155
2015-05-11 22:30 | 151
2015-05-11 22:45 | 149
2015-05-11 23:00 | 150
2015-05-11 23:15 | 152
2015-05-11 23:30 | 145
2015-05-11 23:45 | 147
2015-05-12 | 145
2015-05-12 00:15 | 148
2015-05-12 00:30 | 140
2015-05-12 00:45 | 148
2015-05-12 01:00 | 139
2015-05-12 01:15 | 145
2015-05-12 01:30 | 139
2015-05-12 01:45 | 145
2015-05-12 02:00 | 137
2015-05-12 02:15 | 142
2015-05-12 02:30 | 138
2015-05-12 02:45 | 139
2015-05-12 03:00 | 141
2015-05-12 03:15 | 139
2015-05-12 03:30 | 137
2015-05-12 03:45 | 141
2015-05-12 04:00 | 138
2015-05-12 04:15 | 138
2015-05-12 04:30 | 139
2015-05-12 04:45 | 140
2015-05-12 05:00 | 143
2015-05-12 05:15 | 138
2015-05-12 05:30 | 137
2015-05-12 05:45 | 140
2015-05-12 06:00 | 138
2015-05-12 06:15 | 138
2015-05-12 06:30 | 140
2015-05-12 06:45 | 138
2015-05-12 07:00 | 141
2015-05-12 07:15 | 141
2015-05-12 07:30 | 140
2015-05-12 07:45 | 155
2015-05-12 08:00 | 153
2015-05-12 08:15 | 158
2015-05-12 08:30 | 157
2015-05-12 08:45 | 158
2015-05-12 09:00 | 162
2015-05-12 09:15 | 167
2015-05-12 09:30 | 172
2015-05-12 09:45 | 177
2015-05-12 10:00 | 177
2015-05-12 10:15 | 192
2015-05-12 10:30 | 183
2015-05-12 10:45 | 181
2015-05-12 11:00 | 189
2015-05-12 11:15 | 193
2015-05-12 11:30 | 184
2015-05-12 11:45 | 187
2015-05-12 12:00 | 188
2015-05-12 12:15 | 183
2015-05-12 12:30 | 184
2015-05-12 12:45 | 189
2015-05-12 13:00 | 195
2015-05-12 13:15 | 186
2015-05-12 13:30 | 196
2015-05-12 13:45 | 191
2015-05-12 14:00 | 188
2015-05-12 14:15 | 190
2015-05-12 14:30 | 232
2015-05-12 14:45 | 225
2015-05-12 15:00 | 239
2015-05-12 15:15 | 231
2015-05-12 15:30 | 238
2015-05-12 15:45 | 228
2015-05-12 16:00 | 244
2015-05-12 16:15 | 238
2015-05-12 16:30 | 230
2015-05-12 16:45 | 232
2015-05-12 17:00 | 240
2015-05-12 17:15 | 220
2015-05-12 17:30 | 209
2015-05-12 17:45 | 219
2015-05-12 18:00 | 193
2015-05-12 18:15 | 199
2015-05-12 18:30 | 188
2015-05-12 18:45 | 183
2015-05-12 19:00 | 181
2015-05-12 19:15 | 176
2015-05-12 19:30 | 173
2015-05-12 19:45 | 173
2015-05-12 20:00 | 168
2015-05-12 20:15 | 169
2015-05-12 20:30 | 169
2015-05-12 20:45 | 165
2015-05-12 21:00 | 165
2015-05-12 21:15 | 153
2015-05-12 21:30 | 148
2015-05-12 21:45 | 151
2015-05-12 22:00 | 150
2015-05-12 22:15 | 158
2015-05-12 22:30 | 154
2015-05-12 22:45 | 154
2015-05-12 23:00 | 156
2015-05-12 23:15 | 150
2015-05-12 23:30 | 151
2015-05-12 23:45 | 147
2015-05-13 | 146
2015-05-13 00:15 | 149
2015-05-13 00:30 | 144
2015-05-13 00:45 | 150
2015-05-13 01:00 | 145
2015-05-13 01:15 | 147
2015-05-13 01:30 | 144
2015-05-13 01:45 | 144
2015-05-13 02:00 | 147
2015-05-13 02:15 | 141
2015-05-13 02:30 | 141
2015-05-13 02:45 | 142
2015-05-13 03:00 | 143
2015-05-13 03:15 | 143
2015-05-13 03:30 | 142
2015-05-13 03:45 | 141
2015-05-13 04:00 | 144
2015-05-13 04:15 | 141
2015-05-13 04:30 | 147
2015-05-13 04:45 | 138
2015-05-13 05:00 | 143
2015-05-13 05:15 | 142
2015-05-13 05:30 | 142
2015-05-13 05:45 | 142
2015-05-13 06:00 | 145
2015-05-13 06:15 | 141
2015-05-13 06:30 | 147
2015-05-13 06:45 | 143
2015-05-13 07:00 | 147
2015-05-13 07:15 | 146
2015-05-13 07:30 | 145
2015-05-13 07:45 | 155
2015-05-13 08:00 | 152
2015-05-13 08:15 | 159
2015-05-13 08:30 | 158
2015-05-13 08:45 | 166
2015-05-13 09:00 | 178
2015-05-13 09:15 | 182
2015-05-13 09:30 | 192
2015-05-13 09:45 | 187
2015-05-13 10:00 | 200
2015-05-13 10:15 | 210
2015-05-13 10:30 | 215
2015-05-13 10:45 | 206
2015-05-13 11:00 | 214
2015-05-13 11:15 | 211
2015-05-13 11:30 | 206
2015-05-13 11:45 | 220
2015-05-13 12:00 | 214
2015-05-13 12:15 | 211
2015-05-13 12:30 | 221
2015-05-13 12:45 | 210
2015-05-13 13:00 | 217
2015-05-13 13:15 | 223
2015-05-13 13:30 | 217
2015-05-13 13:45 | 219
2015-05-13 14:00 | 228
2015-05-13 14:15 | 218
2015-05-13 14:30 | 219
2015-05-13 14:45 | 227
2015-05-13 15:00 | 227
2015-05-13 15:15 | 214
2015-05-13 15:30 | 227
2015-05-13 15:45 | 225
2015-05-13 16:00 | 213
2015-05-13 16:15 | 228
2015-05-13 16:30 | 224
2015-05-13 16:45 | 223
2015-05-13 17:00 | 223
2015-05-13 17:15 | 229
2015-05-13 17:30 | 221
2015-05-13 17:45 | 221
2015-05-13 18:00 | 226
2015-05-13 18:15 | 224
2015-05-13 18:30 | 210
2015-05-13 18:45 | 218
2015-05-13 19:00 | 209
2015-05-13 19:15 | 200
2015-05-13 19:30 | 213
2015-05-13 19:45 | 192
2015-05-13 20:00 | 200
2015-05-13 20:15 | 193
2015-05-13 20:30 | 182
2015-05-13 20:45 | 182
2015-05-13 21:00 | 183
2015-05-13 21:15 | 174
2015-05-13 21:30 | 157
2015-05-13 21:45 | 162
2015-05-13 22:00 | 154
2015-05-13 22:15 | 163
2015-05-13 22:30 | 160
2015-05-13 22:45 | 165
2015-05-13 23:00 | 161
2015-05-13 23:15 | 160
2015-05-13 23:30 | 158
2015-05-13 23:45 | 157
2015-05-14 | 154
2015-05-14 00:15 | 149
2015-05-14 00:30 | 153
2015-05-14 00:45 | 147
2015-05-14 01:00 | 151
2015-05-14 01:15 | 145
2015-05-14 01:30 | 150
2015-05-14 01:45 | 142
2015-05-14 02:00 | 149
2015-05-14 02:15 | 143
2015-05-14 02:30 | 145
2015-05-14 02:45 | 146
2015-05-14 03:00 | 143
2015-05-14 03:15 | 146
2015-05-14 03:30 | 142
2015-05-14 03:45 | 146
2015-05-14 04:00 | 142
2015-05-14 04:15 | 147
2015-05-14 04:30 | 144
2015-05-14 04:45 | 140
2015-05-14 05:00 | 142
2015-05-14 05:15 | 138
2015-05-14 05:30 | 145
2015-05-14 05:45 | 143
2015-05-14 06:00 | 148
2015-05-14 06:15 | 142
2015-05-14 06:30 | 147
2015-05-14 06:45 | 143
2015-05-14 07:00 | 149
2015-05-14 07:15 | 146
2015-05-14 07:30 | 148
2015-05-14 07:45 | 152
2015-05-14 08:00 | 161
2015-05-14 08:15 | 162
2015-05-14 08:30 | 164
2015-05-14 08:45 | 164
2015-05-14 09:00 | 170
2015-05-14 09:15 | 174
2015-05-14 09:30 | 191
2015-05-14 09:45 | 193
2015-05-14 10:00 | 203
2015-05-14 10:15 | 215
2015-05-14 10:30 | 208
2015-05-14 10:45 | 212
2015-05-14 11:00 | 216
2015-05-14 11:15 | 215
2015-05-14 11:30 | 223
2015-05-14 11:45 | 209
2015-05-14 12:00 | 215
2015-05-14 12:15 | 211
2015-05-14 12:30 | 209
2015-05-14 12:45 | 198
2015-05-14 13:00 | 188
2015-05-14 13:15 | 185
2015-05-14 13:30 | 182
2015-05-14 13:45 | 189
2015-05-14 14:00 | 193
2015-05-14 14:15 | 187
2015-05-14 14:30 | 204
2015-05-14 14:45 | 223
2015-05-14 15:00 | 196
2015-05-14 15:15 | 192
2015-05-14 15:30 | 186
2015-05-14 15:45 | 192
2015-05-14 16:00 | 196
2015-05-14 16:15 | 191
2015-05-14 16:30 | 177
2015-05-14 16:45 | 189
2015-05-14 17:00 | 189
2015-05-14 17:15 | 191
2015-05-14 17:30 | 184
2015-05-14 17:45 | 187
2015-05-14 18:00 | 196
2015-05-14 18:15 | 182
2015-05-14 18:30 | 180
2015-05-14 18:45 | 177
2015-05-14 19:00 | 178
2015-05-14 19:15 | 191
2015-05-14 19:30 | 176
2015-05-14 19:45 | 185
2015-05-14 20:00 | 173
2015-05-14 20:15 | 176
2015-05-14 20:30 | 172
2015-05-14 20:45 | 186
2015-05-14 21:00 | 175
2015-05-14 21:15 | 158
2015-05-14 21:30 | 154
2015-05-14 21:45 | 158
2015-05-14 22:00 | 167
2015-05-14 22:15 | 166
2015-05-14 22:30 | 155
2015-05-14 22:45 | 159
2015-05-14 23:00 | 157
2015-05-14 23:15 | 170
2015-05-14 23:30 | 153
2015-05-14 23:45 | 151
2015-05-15 | 146
2015-05-15 00:15 | 162
2015-05-15 00:30 | 146
2015-05-15 00:45 | 149
2015-05-15 01:00 | 144
2015-05-15 01:15 | 148
2015-05-15 01:30 | 152
2015-05-15 01:45 | 159
2015-05-15 02:00 | 147
2015-05-15 02:15 | 147
2015-05-15 02:30 | 144
2015-05-15 02:45 | 149
2015-05-15 03:00 | 144
2015-05-15 03:15 | 157
2015-05-15 03:30 | 144
2015-05-15 03:45 | 145
2015-05-15 04:00 | 138
2015-05-15 04:15 | 141
2015-05-15 04:30 | 143
2015-05-15 04:45 | 142
2015-05-15 05:00 | 139
2015-05-15 05:15 | 137
2015-05-15 05:30 | 147
2015-05-15 05:45 | 139
2015-05-15 06:00 | 136
2015-05-15 06:15 | 141
2015-05-15 06:30 | 143
2015-05-15 06:45 | 145
2015-05-15 07:00 | 149
2015-05-15 07:15 | 147
2015-05-15 07:30 | 146
2015-05-15 07:45 | 154
2015-05-15 08:00 | 156
2015-05-15 08:15 | 155
2015-05-15 08:30 | 159
2015-05-15 08:45 | 157
2015-05-15 09:00 | 158
2015-05-15 09:15 | 165
2015-05-15 09:30 | 170
2015-05-15 09:45 | 185
2015-05-15 10:00 | 196
2015-05-15 10:15 | 198
2015-05-15 10:30 | 190
2015-05-15 10:45 | 203
2015-05-15 11:00 | 194
2015-05-15 11:15 | 202
2015-05-15 11:30 | 187
2015-05-15 11:45 | 191
2015-05-15 12:00 | 212
2015-05-15 12:15 | 193
2015-05-15 12:30 | 202
2015-05-15 12:45 | 185
2015-05-15 13:00 | 203
2015-05-15 13:15 | 212
2015-05-15 13:30 | 198
2015-05-15 13:45 | 211
2015-05-15 14:00 | 200
2015-05-15 14:15 | 207
2015-05-15 14:30 | 217
2015-05-15 14:45 | 205
2015-05-15 15:00 | 215
2015-05-15 15:15 | 206
2015-05-15 15:30 | 201
2015-05-15 15:45 | 211
2015-05-15 16:00 | 217
2015-05-15 16:15 | 207
2015-05-15 16:30 | 210
2015-05-15 16:45 | 205
2015-05-15 17:00 | 202
2015-05-15 17:15 | 205
2015-05-15 17:30 | 207
2015-05-15 17:45 | 202
2015-05-15 18:00 | 195
2015-05-15 18:15 | 194
2015-05-15 18:30 | 197
2015-05-15 18:45 | 192
2015-05-15 19:00 | 183
2015-05-15 19:15 | 182
2015-05-15 19:30 | 174
2015-05-15 19:45 | 165
2015-05-15 20:00 | 168
2015-05-15 20:15 | 156
2015-05-15 20:30 | 162
2015-05-15 20:45 | 156
2015-05-15 21:00 | 164
2015-05-15 21:15 | 142
2015-05-15 21:30 | 138
2015-05-15 21:45 | 136
2015-05-15 22:00 | 139
2015-05-15 22:15 | 146
2015-05-15 22:30 | 141
2015-05-15 22:45 | 140
2015-05-15 23:00 | 140
2015-05-15 23:15 | 140
2015-05-15 23:30 | 139
2015-05-15 23:45 | 143
2015-05-16 | 138
2015-05-16 00:15 | 136
2015-05-16 00:30 | 135
2015-05-16 00:45 | 134
2015-05-16 01:00 | 134
2015-05-16 01:15 | 137
2015-05-16 01:30 | 136
2015-05-16 01:45 | 132
2015-05-16 02:00 | 132
2015-05-16 02:15 | 130
2015-05-16 02:30 | 136
2015-05-16 02:45 | 134
2015-05-16 03:00 | 144
2015-05-16 03:15 | 133
2015-05-16 03:30 | 133
2015-05-16 03:45 | 131
2015-05-16 04:00 | 134
2015-05-16 04:15 | 132
2015-05-16 04:30 | 133
2015-05-16 04:45 | 130
2015-05-16 05:00 | 138
2015-05-16 05:15 | 133
2015-05-16 05:30 | 138
2015-05-16 05:45 | 135
2015-05-16 06:00 | 136
2015-05-16 06:15 | 133
2015-05-16 06:30 | 135
2015-05-16 06:45 | 132
2015-05-16 07:00 | 135
2015-05-16 07:15 | 136
2015-05-16 07:30 | 131
2015-05-16 07:45 | 132
2015-05-16 08:00 | 132
2015-05-16 08:15 | 131
2015-05-16 08:30 | 135
2015-05-16 08:45 | 132
2015-05-16 09:00 | 134
2015-05-16 09:15 | 139
2015-05-16 09:30 | 138
2015-05-16 09:45 | 140
2015-05-16 10:00 | 150
2015-05-16 10:15 | 149
2015-05-16 10:30 | 151
2015-05-16 10:45 | 144
2015-05-16 11:00 | 161
2015-05-16 11:15 | 157
2015-05-16 11:30 | 173
2015-05-16 11:45 | 152
2015-05-16 12:00 | 166
2015-05-16 12:15 | 161
2015-05-16 12:30 | 161
2015-05-16 12:45 | 168
2015-05-16 13:00 | 171
2015-05-16 13:15 | 182
2015-05-16 13:30 | 170
2015-05-16 13:45 | 178
2015-05-16 14:00 | 175
2015-05-16 14:15 | 181
2015-05-16 14:30 | 179
2015-05-16 14:45 | 172
2015-05-16 15:00 | 173
2015-05-16 15:15 | 195
2015-05-16 15:30 | 173
2015-05-16 15:45 | 185
2015-05-16 16:00 | 180
2015-05-16 16:15 | 185
2015-05-16 16:30 | 201
2015-05-16 16:45 | 186
2015-05-16 17:00 | 185
2015-05-16 17:15 | 187
2015-05-16 17:30 | 188
2015-05-16 17:45 | 192
2015-05-16 18:00 | 175
2015-05-16 18:15 | 177
2015-05-16 18:30 | 171
2015-05-16 18:45 | 179
2015-05-16 19:00 | 171
2015-05-16 19:15 | 165
2015-05-16 19:30 | 166
2015-05-16 19:45 | 159
2015-05-16 20:00 | 171
2015-05-16 20:15 | 147
2015-05-16 20:30 | 143
2015-05-16 20:45 | 140
2015-05-16 21:00 | 143
2015-05-16 21:15 | 141
2015-05-16 21:30 | 154
2015-05-16 21:45 | 138
2015-05-16 22:00 | 138
2015-05-16 22:15 | 136
2015-05-16 22:30 | 137
2015-05-16 22:45 | 144
2015-05-16 23:00 | 152
2015-05-16 23:15 | 139
2015-05-16 23:30 | 137
2015-05-16 23:45 | 142
2015-05-17 | 144
2015-05-17 00:15 | 139
2015-05-17 00:30 | 135
2015-05-17 00:45 | 135
2015-05-17 01:00 | 141
2015-05-17 01:15 | 135
2015-05-17 01:30 | 136
2015-05-17 01:45 | 132
2015-05-17 02:00 | 134
2015-05-17 02:15 | 132
2015-05-17 02:30 | 140
2015-05-17 02:45 | 136
2015-05-17 03:00 | 131
2015-05-17 03:15 | 133
2015-05-17 03:30 | 139
2015-05-17 03:45 | 133
2015-05-17 04:00 | 147
2015-05-17 04:15 | 136
2015-05-17 04:30 | 143
2015-05-17 04:45 | 135
2015-05-17 05:00 | 148
2015-05-17 05:15 | 135
2015-05-17 05:30 | 135
2015-05-17 05:45 | 134
2015-05-17 06:00 | 137
2015-05-17 06:15 | 134
2015-05-17 06:30 | 152
2015-05-17 06:45 | 139
2015-05-17 07:00 | 146
2015-05-17 07:15 | 145
2015-05-17 07:30 | 148
2015-05-17 07:45 | 147
2015-05-17 08:00 | 159
2015-05-17 08:15 | 147
2015-05-17 08:30 | 146
2015-05-17 08:45 | 144
2015-05-17 09:00 | 149
2015-05-17 09:15 | 151
2015-05-17 09:30 | 156
2015-05-17 09:45 | 147
2015-05-17 10:00 | 154
2015-05-17 10:15 | 152
2015-05-17 10:30 | 160
2015-05-17 10:45 | 171
2015-05-17 11:00 | 181
2015-05-17 11:15 | 160
2015-05-17 11:30 | 175
2015-05-17 11:45 | 183
2015-05-17 12:00 | 182
2015-05-17 12:15 | 177
2015-05-17 12:30 | 172
2015-05-17 12:45 | 189
2015-05-17 13:00 | 174
2015-05-17 13:15 | 196
2015-05-17 13:30 | 184
2015-05-17 13:45 | 179
2015-05-17 14:00 | 187
2015-05-17 14:15 | 172
2015-05-17 14:30 | 186
2015-05-17 14:45 | 193
2015-05-17 15:00 | 191
2015-05-17 15:15 | 192
2015-05-17 15:30 | 176
2015-05-17 15:45 | 196
2015-05-17 16:00 | 194
2015-05-17 16:15 | 183
2015-05-17 16:30 | 188
2015-05-17 16:45 | 184
2015-05-17 17:00 | 194
2015-05-17 17:15 | 185
2015-05-17 17:30 | 193
2015-05-17 17:45 | 176
2015-05-17 18:00 | 176
2015-05-17 18:15 | 180
2015-05-17 18:30 | 189
2015-05-17 18:45 | 181
2015-05-17 19:00 | 179
2015-05-17 19:15 | 175
2015-05-17 19:30 | 165
2015-05-17 19:45 | 169
2015-05-17 20:00 | 156
2015-05-17 20:15 | 166
2015-05-17 20:30 | 160
2015-05-17 20:45 | 158
2015-05-17 21:00 | 168
2015-05-17 21:15 | 145
2015-05-17 21:30 | 141
2015-05-17 21:45 | 136
2015-05-17 22:00 | 138
2015-05-17 22:15 | 136
2015-05-17 22:30 | 138
2015-05-17 22:45 | 140
2015-05-17 23:00 | 138
2015-05-17 23:15 | 135
2015-05-17 23:30 | 138
2015-05-17 23:45 | 142
2015-05-18 | 139
2015-05-18 00:15 | 136
2015-05-18 00:30 | 134
2015-05-18 00:45 | 132
2015-05-18 01:00 | 133
2015-05-18 01:15 | 137
2015-05-18 01:30 | 134
2015-05-18 01:45 | 135
2015-05-18 02:00 | 135
2015-05-18 02:15 | 137
2015-05-18 02:30 | 135
2015-05-18 02:45 | 142
2015-05-18 03:00 | 137
2015-05-18 03:15 | 136
2015-05-18 03:30 | 134
2015-05-18 03:45 | 132
2015-05-18 04:00 | 135
2015-05-18 04:15 | 139
2015-05-18 04:30 | 136
2015-05-18 04:45 | 134
2015-05-18 05:00 | 131
2015-05-18 05:15 | 135
2015-05-18 05:30 | 135
2015-05-18 05:45 | 134
2015-05-18 06:00 | 135
2015-05-18 06:15 | 129
2015-05-18 06:30 | 134
2015-05-18 06:45 | 138
2015-05-18 07:00 | 137
2015-05-18 07:15 | 136
2015-05-18 07:30 | 132
2015-05-18 07:45 | 137
2015-05-18 08:00 | 144
2015-05-18 08:15 | 151
2015-05-18 08:30 | 155
2015-05-18 08:45 | 151
2015-05-18 09:00 | 157
2015-05-18 09:15 | 158
2015-05-18 09:30 | 162
2015-05-18 09:45 | 166
2015-05-18 10:00 | 172
2015-05-18 10:15 | 172
2015-05-18 10:30 | 171
2015-05-18 10:45 | 177
2015-05-18 11:00 | 181
2015-05-18 11:15 | 188
2015-05-18 11:30 | 185
2015-05-18 11:45 | 176
2015-05-18 12:00 | 179
2015-05-18 12:15 | 184
2015-05-18 12:30 | 184
2015-05-18 12:45 | 179
2015-05-18 13:00 | 181
2015-05-18 13:15 | 202
2015-05-18 13:30 | 187
2015-05-18 13:45 | 190
2015-05-18 14:00 | 184
2015-05-18 14:15 | 196
2015-05-18 14:30 | 188
2015-05-18 14:45 | 207
2015-05-18 15:00 | 202
2015-05-18 15:15 | 194
2015-05-18 15:30 | 202
2015-05-18 15:45 | 196
2015-05-18 16:00 | 207
2015-05-18 16:15 | 197
2015-05-18 16:30 | 191
2015-05-18 16:45 | 197
2015-05-18 17:00 | 183
2015-05-18 17:15 | 200
2015-05-18 17:30 | 186
2015-05-18 17:45 | 195
2015-05-18 18:00 | 181
2015-05-18 18:15 | 189
2015-05-18 18:30 | 190
2015-05-18 18:45 | 183
2015-05-18 19:00 | 183
2015-05-18 19:15 | 168
2015-05-18 19:30 | 169
2015-05-18 19:45 | 160
2015-05-18 20:00 | 168
2015-05-18 20:15 | 166
2015-05-18 20:30 | 158
2015-05-18 20:45 | 156
2015-05-18 21:00 | 162
2015-05-18 21:15 | 156
2015-05-18 21:30 | 146
2015-05-18 21:45 | 145
2015-05-18 22:00 | 147
2015-05-18 22:15 | 157
2015-05-18 22:30 | 149
2015-05-18 22:45 | 149
2015-05-18 23:00 | 151
2015-05-18 23:15 | 149
2015-05-18 23:30 | 149
2015-05-18 23:45 | 157
2015-05-19 | 155
2015-05-19 00:15 | 145
2015-05-19 00:30 | 142
2015-05-19 00:45 | 144
2015-05-19 01:00 | 153
2015-05-19 01:15 | 149
2015-05-19 01:30 | 145
2015-05-19 01:45 | 145
2015-05-19 02:00 | 140
2015-05-19 02:15 | 150
2015-05-19 02:30 | 148
2015-05-19 02:45 | 146
2015-05-19 03:00 | 141
2015-05-19 03:15 | 145
2015-05-19 03:30 | 152
2015-05-19 03:45 | 146
2015-05-19 04:00 | 143
2015-05-19 04:15 | 144
2015-05-19 04:30 | 145
2015-05-19 04:45 | 145
2015-05-19 05:00 | 156
2015-05-19 05:15 | 147
2015-05-19 05:30 | 141
2015-05-19 05:45 | 143
2015-05-19 06:00 | 145
2015-05-19 06:15 | 158
2015-05-19 06:30 | 145
2015-05-19 06:45 | 148
2015-05-19 07:00 | 143
2015-05-19 07:15 | 154
2015-05-19 07:30 | 153
2015-05-19 07:45 | 145
2015-05-19 08:00 | 150
2015-05-19 08:15 | 155
2015-05-19 08:30 | 167
2015-05-19 08:45 | 172
2015-05-19 09:00 | 162
2015-05-19 09:15 | 162
2015-05-19 09:30 | 160
2015-05-19 09:45 | 176
2015-05-19 10:00 | 176
2015-05-19 10:15 | 175
2015-05-19 10:30 | 175
2015-05-19 10:45 | 178
2015-05-19 11:00 | 187
2015-05-19 11:15 | 190
2015-05-19 11:30 | 172
2015-05-19 11:45 | 183
2015-05-19 12:00 | 188
2015-05-19 12:15 | 213
2015-05-19 12:30 | 192
2015-05-19 12:45 | 193
2015-05-19 13:00 | 187
2015-05-19 13:15 | 197
2015-05-19 13:30 | 220
2015-05-19 13:45 | 198
2015-05-19 14:00 | 206
2015-05-19 14:15 | 206
2015-05-19 14:30 | 217
2015-05-19 14:45 | 208
2015-05-19 15:00 | 207
2015-05-19 15:15 | 215
2015-05-19 15:30 | 213
2015-05-19 15:45 | 219
2015-05-19 16:00 | 219
2015-05-19 16:15 | 212
2015-05-19 16:30 | 212
2015-05-19 16:45 | 215
2015-05-19 17:00 | 220
2015-05-19 17:15 | 219
2015-05-19 17:30 | 212
2015-05-19 17:45 | 204
2015-05-19 18:00 | 208
2015-05-19 18:15 | 202
2015-05-19 18:30 | 199
2015-05-19 18:45 | 190
2015-05-19 19:00 | 190
2015-05-19 19:15 | 192
2015-05-19 19:30 | 194
2015-05-19 19:45 | 183
2015-05-19 20:00 | 174
2015-05-19 20:15 | 162
2015-05-19 20:30 | 158
2015-05-19 20:45 | 159
2015-05-19 21:00 | 169
2015-05-19 21:15 | 152
2015-05-19 21:30 | 148
2015-05-19 21:45 | 148
2015-05-19 22:00 | 154
2015-05-19 22:15 | 163
2015-05-19 22:30 | 149
2015-05-19 22:45 | 150
2015-05-19 23:00 | 160
2015-05-19 23:15 | 153
2015-05-19 23:30 | 148
2015-05-19 23:45 | 148
2015-05-20 | 153
2015-05-20 00:15 | 150
2015-05-20 00:30 | 143
2015-05-20 00:45 | 142
2015-05-20 01:00 | 140
2015-05-20 01:15 | 143
2015-05-20 01:30 | 146
2015-05-20 01:45 | 142
2015-05-20 02:00 | 141
2015-05-20 02:15 | 144
2015-05-20 02:30 | 149
2015-05-20 02:45 | 143
2015-05-20 03:00 | 139
2015-05-20 03:15 | 137
2015-05-20 03:30 | 136
2015-05-20 03:45 | 138
2015-05-20 04:00 | 147
2015-05-20 04:15 | 144
2015-05-20 04:30 | 141
2015-05-20 04:45 | 137
2015-05-20 05:00 | 139
2015-05-20 05:15 | 139
2015-05-20 05:30 | 143
2015-05-20 05:45 | 148
2015-05-20 06:00 | 136
2015-05-20 06:15 | 137
2015-05-20 06:30 | 138
2015-05-20 06:45 | 144
2015-05-20 07:00 | 138
2015-05-20 07:15 | 143
2015-05-20 07:30 | 138
2015-05-20 07:45 | 139
2015-05-20 08:00 | 151
2015-05-20 08:15 | 169
2015-05-20 08:30 | 162
2015-05-20 08:45 | 163
2015-05-20 09:00 | 178
2015-05-20 09:15 | 175
2015-05-20 09:30 | 182
2015-05-20 09:45 | 180
2015-05-20 10:00 | 182
2015-05-20 10:15 | 188
2015-05-20 10:30 | 200
2015-05-20 10:45 | 201
2015-05-20 11:00 | 199
2015-05-20 11:15 | 200
2015-05-20 11:30 | 198
2015-05-20 11:45 | 208
2015-05-20 12:00 | 211
2015-05-20 12:15 | 219
2015-05-20 12:30 | 212
2015-05-20 12:45 | 219
2015-05-20 13:00 | 214
2015-05-20 13:15 | 227
2015-05-20 13:30 | 229
2015-05-20 13:45 | 214
2015-05-20 14:00 | 221
2015-05-20 14:15 | 211
2015-05-20 14:30 | 235
2015-05-20 14:45 | 224
2015-05-20 15:00 | 220
2015-05-20 15:15 | 223
2015-05-20 15:30 | 223
2015-05-20 15:45 | 219
2015-05-20 16:00 | 226
2015-05-20 16:15 | 229
2015-05-20 16:30 | 212
2015-05-20 16:45 | 224
2015-05-20 17:00 | 211
2015-05-20 17:15 | 216
2015-05-20 17:30 | 228
2015-05-20 17:45 | 203
2015-05-20 18:00 | 215
2015-05-20 18:15 | 197
2015-05-20 18:30 | 222
2015-05-20 18:45 | 194
2015-05-20 19:00 | 187
2015-05-20 19:15 | 197
2015-05-20 19:30 | 192
2015-05-20 19:45 | 182
2015-05-20 20:00 | 171
2015-05-20 20:15 | 168
2015-05-20 20:30 | 167
2015-05-20 20:45 | 174
2015-05-20 21:00 | 171
2015-05-20 21:15 | 156
2015-05-20 21:30 | 151
2015-05-20 21:45 | 161
2015-05-20 22:00 | 165
2015-05-20 22:15 | 157
2015-05-20 22:30 | 159
2015-05-20 22:45 | 161
2015-05-20 23:00 | 172
2015-05-20 23:15 | 154
2015-05-20 23:30 | 150
2015-05-20 23:45 | 148
2015-05-21 | 151
2015-05-21 00:15 | 159
2015-05-21 00:30 | 148
2015-05-21 00:45 | 146
2015-05-21 01:00 | 145
2015-05-21 01:15 | 155
2015-05-21 01:30 | 152
2015-05-21 01:45 | 141
2015-05-21 02:00 | 141
2015-05-21 02:15 | 137
2015-05-21 02:30 | 146
2015-05-21 02:45 | 144
2015-05-21 03:00 | 140
2015-05-21 03:15 | 144
2015-05-21 03:30 | 150
2015-05-21 03:45 | 148
2015-05-21 04:00 | 142
2015-05-21 04:15 | 144
2015-05-21 04:30 | 138
2015-05-21 04:45 | 144
2015-05-21 05:00 | 142
2015-05-21 05:15 | 154
2015-05-21 05:30 | 138
2015-05-21 05:45 | 140
2015-05-21 06:00 | 141
2015-05-21 06:15 | 156
2015-05-21 06:30 | 140
2015-05-21 06:45 | 143
2015-05-21 07:00 | 143
2015-05-21 07:15 | 154
2015-05-21 07:30 | 140
2015-05-21 07:45 | 149
2015-05-21 08:00 | 147
2015-05-21 08:15 | 149
2015-05-21 08:30 | 157
2015-05-21 08:45 | 176
2015-05-21 09:00 | 166
2015-05-21 09:15 | 174
2015-05-21 09:30 | 176
2015-05-21 09:45 | 198
2015-05-21 10:00 | 203
2015-05-21 10:15 | 210
2015-05-21 10:30 | 212
2015-05-21 10:45 | 202
2015-05-21 11:00 | 221
2015-05-21 11:15 | 204
2015-05-21 11:30 | 210
2015-05-21 11:45 | 214
2015-05-21 12:00 | 207
2015-05-21 12:15 | 230
2015-05-21 12:30 | 210
2015-05-21 12:45 | 210
2015-05-21 13:00 | 219
2015-05-21 13:15 | 203
2015-05-21 13:30 | 223
2015-05-21 13:45 | 217
2015-05-21 14:00 | 212
2015-05-21 14:15 | 219
2015-05-21 14:30 | 210
2015-05-21 14:45 | 216
2015-05-21 15:00 | 206
2015-05-21 15:15 | 204
2015-05-21 15:30 | 201
2015-05-21 15:45 | 221
2015-05-21 16:00 | 201
2015-05-21 16:15 | 199
2015-05-21 16:30 | 195
2015-05-21 16:45 | 197
2015-05-21 17:00 | 215
2015-05-21 17:15 | 198
2015-05-21 17:30 | 203
2015-05-21 17:45 | 203
2015-05-21 18:00 | 203
2015-05-21 18:15 | 214
2015-05-21 18:30 | 199
2015-05-21 18:45 | 197
2015-05-21 19:00 | 194
2015-05-21 19:15 | 194
2015-05-21 19:30 | 190
2015-05-21 19:45 | 187
2015-05-21 20:00 | 185
2015-05-21 20:15 | 185
2015-05-21 20:30 | 191
2015-05-21 20:45 | 179
2015-05-21 21:00 | 183
2015-05-21 21:15 | 160
2015-05-21 21:30 | 158
2015-05-21 21:45 | 162
2015-05-21 22:00 | 171
2015-05-21 22:15 | 154
2015-05-21 22:30 | 159
2015-05-21 22:45 | 155
2015-05-21 23:00 | 168
2015-05-21 23:15 | 153
2015-05-21 23:30 | 156
2015-05-21 23:45 | 146
2015-05-22 | 156
2015-05-22 00:15 | 164
2015-05-22 00:30 | 148
2015-05-22 00:45 | 147
2015-05-22 01:00 | 150
2015-05-22 01:15 | 149
2015-05-22 01:30 | 162
2015-05-22 01:45 | 143
2015-05-22 02:00 | 148
2015-05-22 02:15 | 142
2015-05-22 02:30 | 155
2015-05-22 02:45 | 148
2015-05-22 03:00 | 148
2015-05-22 03:15 | 145
2015-05-22 03:30 | 149
2015-05-22 03:45 | 157
2015-05-22 04:00 | 145
2015-05-22 04:15 | 142
2015-05-22 04:30 | 142
2015-05-22 04:45 | 144
2015-05-22 05:00 | 155
2015-05-22 05:15 | 147
2015-05-22 05:30 | 146
2015-05-22 05:45 | 143
2015-05-22 06:00 | 154
2015-05-22 06:15 | 140
2015-05-22 06:30 | 142
2015-05-22 06:45 | 137
2015-05-22 07:00 | 140
2015-05-22 07:15 | 150
2015-05-22 07:30 | 147
2015-05-22 07:45 | 142
2015-05-22 08:00 | 146
2015-05-22 08:15 | 154
2015-05-22 08:30 | 160
2015-05-22 08:45 | 151
2015-05-22 09:00 | 153
2015-05-22 09:15 | 165
2015-05-22 09:30 | 183
2015-05-22 09:45 | 189
2015-05-22 10:00 | 194
2015-05-22 10:15 | 190
2015-05-22 10:30 | 198
2015-05-22 10:45 | 202
2015-05-22 11:00 | 199
2015-05-22 11:15 | 200
2015-05-22 11:30 | 189
2015-05-22 11:45 | 192
2015-05-22 12:00 | 202
2015-05-22 12:15 | 204
2015-05-22 12:30 | 187
2015-05-22 12:45 | 198
2015-05-22 13:00 | 188
2015-05-22 13:15 | 197
2015-05-22 13:30 | 206
2015-05-22 13:45 | 189
2015-05-22 14:00 | 203
2015-05-22 14:15 | 194
2015-05-22 14:30 | 213
2015-05-22 14:45 | 209
2015-05-22 15:00 | 201
2015-05-22 15:15 | 199
2015-05-22 15:30 | 208
2015-05-22 15:45 | 206
2015-05-22 16:00 | 204
2015-05-22 16:15 | 197
2015-05-22 16:30 | 202
2015-05-22 16:45 | 205
2015-05-22 17:00 | 216
2015-05-22 17:15 | 205
2015-05-22 17:30 | 216
2015-05-22 17:45 | 202
2015-05-22 18:00 | 197
2015-05-22 18:15 | 183
2015-05-22 18:30 | 189
2015-05-22 18:45 | 197
2015-05-22 19:00 | 184
2015-05-22 19:15 | 180
2015-05-22 19:30 | 177
2015-05-22 19:45 | 177
2015-05-22 20:00 | 180
2015-05-22 20:15 | 185
2015-05-22 20:30 | 166
2015-05-22 20:45 | 165
2015-05-22 21:00 | 161
2015-05-22 21:15 | 152
2015-05-22 21:30 | 145
2015-05-22 21:45 | 142
2015-05-22 22:00 | 144
2015-05-22 22:15 | 140
2015-05-22 22:30 | 155
2015-05-22 22:45 | 140
2015-05-22 23:00 | 141
2015-05-22 23:15 | 139
2015-05-22 23:30 | 144
2015-05-22 23:45 | 152
2015-05-23 | 143
2015-05-23 00:15 | 147
2015-05-23 00:30 | 140
2015-05-23 00:45 | 138
2015-05-23 01:00 | 140
2015-05-23 01:15 | 149
2015-05-23 01:30 | 140
2015-05-23 01:45 | 139
2015-05-23 02:00 | 137
2015-05-23 02:15 | 137
2015-05-23 02:30 | 145
2015-05-23 02:45 | 151
2015-05-23 03:00 | 136
2015-05-23 03:15 | 141
2015-05-23 03:30 | 140
2015-05-23 03:45 | 146
2015-05-23 04:00 | 148
2015-05-23 04:15 | 140
2015-05-23 04:30 | 141
2015-05-23 04:45 | 140
2015-05-23 05:00 | 144
2015-05-23 05:15 | 149
2015-05-23 05:30 | 138
2015-05-23 05:45 | 138
2015-05-23 06:00 | 137
2015-05-23 06:15 | 146
2015-05-23 06:30 | 146
2015-05-23 06:45 | 139
2015-05-23 07:00 | 141
2015-05-23 07:15 | 139
2015-05-23 07:30 | 145
2015-05-23 07:45 | 142
2015-05-23 08:00 | 134
2015-05-23 08:15 | 134
2015-05-23 08:30 | 137
2015-05-23 08:45 | 147
2015-05-23 09:00 | 139
2015-05-23 09:15 | 145
2015-05-23 09:30 | 151
2015-05-23 09:45 | 162
2015-05-23 10:00 | 148
2015-05-23 10:15 | 148
2015-05-23 10:30 | 145
2015-05-23 10:45 | 153
2015-05-23 11:00 | 170
2015-05-23 11:15 | 161
2015-05-23 11:30 | 162
2015-05-23 11:45 | 157
2015-05-23 12:00 | 168
2015-05-23 12:15 | 172
2015-05-23 12:30 | 160
2015-05-23 12:45 | 160
2015-05-23 13:00 | 168
2015-05-23 13:15 | 174
2015-05-23 13:30 | 181
2015-05-23 13:45 | 172
2015-05-23 14:00 | 171
2015-05-23 14:15 | 172
2015-05-23 14:30 | 177
2015-05-23 14:45 | 184
2015-05-23 15:00 | 170
2015-05-23 15:15 | 177
2015-05-23 15:30 | 179
2015-05-23 15:45 | 191
2015-05-23 16:00 | 181
2015-05-23 16:15 | 180
2015-05-23 16:30 | 189
2015-05-23 16:45 | 175
2015-05-23 17:00 | 192
2015-05-23 17:15 | 187
2015-05-23 17:30 | 176
2015-05-23 17:45 | 190
2015-05-23 18:00 | 171
2015-05-23 18:15 | 178
2015-05-23 18:30 | 187
2015-05-23 18:45 | 177
2015-05-23 19:00 | 171
2015-05-23 19:15 | 175
2015-05-23 19:30 | 181
2015-05-23 19:45 | 174
2015-05-23 20:00 | 171
2015-05-23 20:15 | 166
2015-05-23 20:30 | 180
2015-05-23 20:45 | 163
2015-05-23 21:00 | 166
2015-05-23 21:15 | 149
2015-05-23 21:30 | 156
2015-05-23 21:45 | 151
2015-05-23 22:00 | 148
2015-05-23 22:15 | 143
2015-05-23 22:30 | 142
2015-05-23 22:45 | 142
2015-05-23 23:00 | 140
2015-05-23 23:15 | 136
2015-05-23 23:30 | 141
2015-05-23 23:45 | 135
2015-05-24 | 148
2015-05-24 00:15 | 136
2015-05-24 00:30 | 138
2015-05-24 00:45 | 136
2015-05-24 01:00 | 138
2015-05-24 01:15 | 139
2015-05-24 01:30 | 140
2015-05-24 01:45 | 136
2015-05-24 02:00 | 134
2015-05-24 02:15 | 134
2015-05-24 02:30 | 139
2015-05-24 02:45 | 135
2015-05-24 03:00 | 150
2015-05-24 03:15 | 133
2015-05-24 03:30 | 134
2015-05-24 03:45 | 133
2015-05-24 04:00 | 136
2015-05-24 04:15 | 139
2015-05-24 04:30 | 146
2015-05-24 04:45 | 137
2015-05-24 05:00 | 138
2015-05-24 05:15 | 133
2015-05-24 05:30 | 139
2015-05-24 05:45 | 136
2015-05-24 06:00 | 142
2015-05-24 06:15 | 135
2015-05-24 06:30 | 134
2015-05-24 06:45 | 138
2015-05-24 07:00 | 134
2015-05-24 07:15 | 145
2015-05-24 07:30 | 148
2015-05-24 07:45 | 148
2015-05-24 08:00 | 150
2015-05-24 08:15 | 146
2015-05-24 08:30 | 154
2015-05-24 08:45 | 150
2015-05-24 09:00 | 159
2015-05-24 09:15 | 151
2015-05-24 09:30 | 157
2015-05-24 09:45 | 158
2015-05-24 10:00 | 173
2015-05-24 10:15 | 176
2015-05-24 10:30 | 166
2015-05-24 10:45 | 175
2015-05-24 11:00 | 178
2015-05-24 11:15 | 182
2015-05-24 11:30 | 186
2015-05-24 11:45 | 177
2015-05-24 12:00 | 181
2015-05-24 12:15 | 196
2015-05-24 12:30 | 178
2015-05-24 12:45 | 187
2015-05-24 13:00 | 181
2015-05-24 13:15 | 177
2015-05-24 13:30 | 194
2015-05-24 13:45 | 186
2015-05-24 14:00 | 186
2015-05-24 14:15 | 189
2015-05-24 14:30 | 186
2015-05-24 14:45 | 196
2015-05-24 15:00 | 192
2015-05-24 15:15 | 192
2015-05-24 15:30 | 189
2015-05-24 15:45 | 199
2015-05-24 16:00 | 196
2015-05-24 16:15 | 203
2015-05-24 16:30 | 194
2015-05-24 16:45 | 191
2015-05-24 17:00 | 197
2015-05-24 17:15 | 195
2015-05-24 17:30 | 202
2015-05-24 17:45 | 187
2015-05-24 18:00 | 201
2015-05-24 18:15 | 183
2015-05-24 18:30 | 191
2015-05-24 18:45 | 179
2015-05-24 19:00 | 188
2015-05-24 19:15 | 175
2015-05-24 19:30 | 162
2015-05-24 19:45 | 166
2015-05-24 20:00 | 156
2015-05-24 20:15 | 172
2015-05-24 20:30 | 160
2015-05-24 20:45 | 158
2015-05-24 21:00 | 152
2015-05-24 21:15 | 144
2015-05-24 21:30 | 150
2015-05-24 21:45 | 149
2015-05-24 22:00 | 144
2015-05-24 22:15 | 144
2015-05-24 22:30 | 141
2015-05-24 22:45 | 155
2015-05-24 23:00 | 148
2015-05-24 23:15 | 140
2015-05-24 23:30 | 145
2015-05-24 23:45 | 154
2015-05-25 | 142
2015-05-25 00:15 | 140
2015-05-25 00:30 | 136
2015-05-25 00:45 | 151
2015-05-25 01:00 | 142
2015-05-25 01:15 | 136
2015-05-25 01:30 | 138
2015-05-25 01:45 | 136
2015-05-25 02:00 | 152
2015-05-25 02:15 | 134
2015-05-25 02:30 | 136
2015-05-25 02:45 | 141
2015-05-25 03:00 | 135
2015-05-25 03:15 | 148
2015-05-25 03:30 | 139
2015-05-25 03:45 | 135
2015-05-25 04:00 | 135
2015-05-25 04:15 | 143
2015-05-25 04:30 | 146
2015-05-25 04:45 | 134
2015-05-25 05:00 | 147
2015-05-25 05:15 | 134
2015-05-25 05:30 | 135
2015-05-25 05:45 | 130
2015-05-25 06:00 | 141
2015-05-25 06:15 | 134
2015-05-25 06:30 | 130
2015-05-25 06:45 | 126
2015-05-25 07:00 | 121
2015-05-25 07:15 | 125
2015-05-25 07:30 | 118
2015-05-25 07:45 | 123
2015-05-25 08:00 | 131
2015-05-25 08:15 | 120
2015-05-25 08:30 | 120
2015-05-25 08:45 | 117
2015-05-25 09:00 | 126
2015-05-25 09:15 | 129
2015-05-25 09:30 | 123
2015-05-25 09:45 | 123
2015-05-25 10:00 | 128
2015-05-25 10:15 | 133
2015-05-25 10:30 | 143
2015-05-25 10:45 | 147
2015-05-25 11:00 | 159
2015-05-25 11:15 | 149
2015-05-25 11:30 | 158
2015-05-25 11:45 | 164
2015-05-25 12:00 | 168
2015-05-25 12:15 | 166
2015-05-25 12:30 | 160
2015-05-25 12:45 | 156
2015-05-25 13:00 | 166
2015-05-25 13:15 | 167
2015-05-25 13:30 | 159
2015-05-25 13:45 | 157
2015-05-25 14:00 | 158
2015-05-25 14:15 | 174
2015-05-25 14:30 | 161
2015-05-25 14:45 | 160
2015-05-25 15:00 | 168
2015-05-25 15:15 | 165
2015-05-25 15:30 | 184
2015-05-25 15:45 | 173
2015-05-25 16:00 | 178
2015-05-25 16:15 | 168
2015-05-25 16:30 | 175
2015-05-25 16:45 | 182
2015-05-25 17:00 | 173
2015-05-25 17:15 | 167
2015-05-25 17:30 | 172
2015-05-25 17:45 | 168
2015-05-25 18:00 | 189
2015-05-25 18:15 | 162
2015-05-25 18:30 | 174
2015-05-25 18:45 | 161
2015-05-25 19:00 | 175
2015-05-25 19:15 | 169
2015-05-25 19:30 | 155
2015-05-25 19:45 | 160
2015-05-25 20:00 | 149
2015-05-25 20:15 | 142
2015-05-25 20:30 | 154
2015-05-25 20:45 | 135
2015-05-25 21:00 | 137
2015-05-25 21:15 | 130
2015-05-25 21:30 | 139
2015-05-25 21:45 | 143
2015-05-25 22:00 | 130
2015-05-25 22:15 | 130
2015-05-25 22:30 | 129
2015-05-25 22:45 | 144
2015-05-25 23:00 | 130
2015-05-25 23:15 | 127
2015-05-25 23:30 | 128
2015-05-25 23:45 | 137
2015-05-26 | 145
2015-05-26 00:15 | 131
2015-05-26 00:30 | 142
2015-05-26 00:45 | 127
2015-05-26 01:00 | 130
2015-05-26 01:15 | 129
2015-05-26 01:30 | 147
2015-05-26 01:45 | 129
2015-05-26 02:00 | 131
2015-05-26 02:15 | 126
2015-05-26 02:30 | 130
2015-05-26 02:45 | 129
2015-05-26 03:00 | 129
2015-05-26 03:15 | 140
2015-05-26 03:30 | 126
2015-05-26 03:45 | 125
2015-05-26 04:00 | 125
2015-05-26 04:15 | 126
2015-05-26 04:30 | 126
2015-05-26 04:45 | 137
2015-05-26 05:00 | 127
2015-05-26 05:15 | 124
2015-05-26 05:30 | 125
2015-05-26 05:45 | 125
2015-05-26 06:00 | 138
2015-05-26 06:15 | 122
2015-05-26 06:30 | 126
2015-05-26 06:45 | 129
2015-05-26 07:00 | 140
2015-05-26 07:15 | 125
2015-05-26 07:30 | 131
2015-05-26 07:45 | 138
2015-05-26 08:00 | 156
2015-05-26 08:15 | 145
2015-05-26 08:30 | 145
2015-05-26 08:45 | 144
2015-05-26 09:00 | 162
2015-05-26 09:15 | 173
2015-05-26 09:30 | 174
2015-05-26 09:45 | 190
2015-05-26 10:00 | 196
2015-05-26 10:15 | 230
2015-05-26 10:30 | 221
2015-05-26 10:45 | 230
2015-05-26 11:00 | 215
2015-05-26 11:15 | 232
2015-05-26 11:30 | 238
2015-05-26 11:45 | 223
2015-05-26 12:00 | 243
2015-05-26 12:15 | 255
2015-05-26 12:30 | 232
2015-05-26 12:45 | 253
2015-05-26 13:00 | 253
2015-05-26 13:15 | 252
2015-05-26 13:30 | 272
2015-05-26 13:45 | 273
2015-05-26 14:00 | 283
2015-05-26 14:15 | 279
2015-05-26 14:30 | 271
2015-05-26 14:45 | 272
2015-05-26 15:00 | 275
2015-05-26 15:15 | 284
2015-05-26 15:30 | 271
2015-05-26 15:45 | 284
2015-05-26 16:00 | 284
2015-05-26 16:15 | 285
2015-05-26 16:30 | 278
2015-05-26 16:45 | 284
2015-05-26 17:00 | 272
2015-05-26 17:15 | 270
2015-05-26 17:30 | 283
2015-05-26 17:45 | 268
2015-05-26 18:00 | 275
2015-05-26 18:15 | 281
2015-05-26 18:30 | 256
2015-05-26 18:45 | 271
2015-05-26 19:00 | 240
2015-05-26 19:15 | 233
2015-05-26 19:30 | 230
2015-05-26 19:45 | 240
2015-05-26 20:00 | 220
2015-05-26 20:15 | 216
2015-05-26 20:30 | 203
2015-05-26 20:45 | 190
2015-05-26 21:00 | 194
2015-05-26 21:15 | 185
2015-05-26 21:30 | 162
2015-05-26 21:45 | 170
2015-05-26 22:00 | 164
2015-05-26 22:15 | 155
2015-05-26 22:30 | 164
2015-05-26 22:45 | 162
2015-05-26 23:00 | 177
2015-05-26 23:15 | 163
2015-05-26 23:30 | 161
2015-05-26 23:45 | 159
2015-05-27 | 166
2015-05-27 00:15 | 168
2015-05-27 00:30 | 158
2015-05-27 00:45 | 152
2015-05-27 01:00 | 160
2015-05-27 01:15 | 158
2015-05-27 01:30 | 149
2015-05-27 01:45 | 149
2015-05-27 02:00 | 149
2015-05-27 02:15 | 164
2015-05-27 02:30 | 146
2015-05-27 02:45 | 150
2015-05-27 03:00 | 145
2015-05-27 03:15 | 157
2015-05-27 03:30 | 155
2015-05-27 03:45 | 149
2015-05-27 04:00 | 148
2015-05-27 04:15 | 148
2015-05-27 04:30 | 158
2015-05-27 04:45 | 144
2015-05-27 05:00 | 142
2015-05-27 05:15 | 143
2015-05-27 05:30 | 148
2015-05-27 05:45 | 156
2015-05-27 06:00 | 142
2015-05-27 06:15 | 146
2015-05-27 06:30 | 147
2015-05-27 06:45 | 159
2015-05-27 07:00 | 146
2015-05-27 07:15 | 147
2015-05-27 07:30 | 146
2015-05-27 07:45 | 161
2015-05-27 08:00 | 154
2015-05-27 08:15 | 157
2015-05-27 08:30 | 165
2015-05-27 08:45 | 159
2015-05-27 09:00 | 183
2015-05-27 09:15 | 191
2015-05-27 09:30 | 191
2015-05-27 09:45 | 207
2015-05-27 10:00 | 225
2015-05-27 10:15 | 244
2015-05-27 10:30 | 237
2015-05-27 10:45 | 231
2015-05-27 11:00 | 248
2015-05-27 11:15 | 259
2015-05-27 11:30 | 259
2015-05-27 11:45 | 265
2015-05-27 12:00 | 261
2015-05-27 12:15 | 270
2015-05-27 12:30 | 281
2015-05-27 12:45 | 278
2015-05-27 13:00 | 278
2015-05-27 13:15 | 266
2015-05-27 13:30 | 275
2015-05-27 13:45 | 282
2015-05-27 14:00 | 279
2015-05-27 14:15 | 288
2015-05-27 14:30 | 273
2015-05-27 14:45 | 293
2015-05-27 15:00 | 278
2015-05-27 15:15 | 280
2015-05-27 15:30 | 295
2015-05-27 15:45 | 279
2015-05-27 16:00 | 281
2015-05-27 16:15 | 278
2015-05-27 16:30 | 293
2015-05-27 16:45 | 279
2015-05-27 17:00 | 276
2015-05-27 17:15 | 271
2015-05-27 17:30 | 270
2015-05-27 17:45 | 269
2015-05-27 18:00 | 269
2015-05-27 18:15 | 256
2015-05-27 18:30 | 243
2015-05-27 18:45 | 239
2015-05-27 19:00 | 241
2015-05-27 19:15 | 237
2015-05-27 19:30 | 232
2015-05-27 19:45 | 211
2015-05-27 20:00 | 221
2015-05-27 20:15 | 191
2015-05-27 20:30 | 187
2015-05-27 20:45 | 193
2015-05-27 21:00 | 180
2015-05-27 21:15 | 186
2015-05-27 21:30 | 183
2015-05-27 21:45 | 172
2015-05-27 22:00 | 176
2015-05-27 22:15 | 168
2015-05-27 22:30 | 175
2015-05-27 22:45 | 179
2015-05-27 23:00 | 186
2015-05-27 23:15 | 174
2015-05-27 23:30 | 167
2015-05-27 23:45 | 174
2015-05-28 | 163
2015-05-28 00:15 | 158
2015-05-28 00:30 | 158
2015-05-28 00:45 | 156
2015-05-28 01:00 | 166
2015-05-28 01:15 | 155
2015-05-28 01:30 | 156
2015-05-28 01:45 | 157
2015-05-28 02:00 | 158
2015-05-28 02:15 | 152
2015-05-28 02:30 | 160
2015-05-28 02:45 | 151
2015-05-28 03:00 | 147
2015-05-28 03:15 | 148
2015-05-28 03:30 | 152
2015-05-28 03:45 | 164
2015-05-28 04:00 | 146
2015-05-28 04:15 | 152
2015-05-28 04:30 | 149
2015-05-28 04:45 | 148
2015-05-28 05:00 | 157
2015-05-28 05:15 | 157
2015-05-28 05:30 | 145
2015-05-28 05:45 | 145
2015-05-28 06:00 | 148
2015-05-28 06:15 | 162
2015-05-28 06:30 | 146
2015-05-28 06:45 | 159
2015-05-28 07:00 | 149
2015-05-28 07:15 | 153
2015-05-28 07:30 | 143
2015-05-28 07:45 | 161
2015-05-28 08:00 | 168
2015-05-28 08:15 | 166
2015-05-28 08:30 | 163
2015-05-28 08:45 | 177
2015-05-28 09:00 | 195
2015-05-28 09:15 | 184
2015-05-28 09:30 | 188
2015-05-28 09:45 | 213
2015-05-28 10:00 | 225
2015-05-28 10:15 | 238
2015-05-28 10:30 | 219
2015-05-28 10:45 | 234
2015-05-28 11:00 | 235
2015-05-28 11:15 | 242
2015-05-28 11:30 | 239
2015-05-28 11:45 | 235
2015-05-28 12:00 | 249
2015-05-28 12:15 | 250
2015-05-28 12:30 | 262
2015-05-28 12:45 | 265
2015-05-28 13:00 | 252
2015-05-28 13:15 | 259
2015-05-28 13:30 | 261
2015-05-28 13:45 | 261
2015-05-28 14:00 | 270
2015-05-28 14:15 | 271
2015-05-28 14:30 | 272
2015-05-28 14:45 | 267
2015-05-28 15:00 | 263
2015-05-28 15:15 | 265
2015-05-28 15:30 | 278
2015-05-28 15:45 | 280
2015-05-28 16:00 | 277
2015-05-28 16:15 | 268
2015-05-28 16:30 | 287
2015-05-28 16:45 | 269
2015-05-28 17:00 | 291
2015-05-28 17:15 | 273
2015-05-28 17:30 | 273
2015-05-28 17:45 | 270
2015-05-28 18:00 | 277
2015-05-28 18:15 | 260
2015-05-28 18:30 | 255
2015-05-28 18:45 | 259
2015-05-28 19:00 | 238
2015-05-28 19:15 | 243
2015-05-28 19:30 | 238
2015-05-28 19:45 | 217
2015-05-28 20:00 | 221
2015-05-28 20:15 | 195
2015-05-28 20:30 | 186
2015-05-28 20:45 | 189
2015-05-28 21:00 | 190
2015-05-28 21:15 | 160
2015-05-28 21:30 | 163
2015-05-28 21:45 | 161
2015-05-28 22:00 | 166
2015-05-28 22:15 | 170
2015-05-28 22:30 | 158
2015-05-28 22:45 | 163
2015-05-28 23:00 | 166
2015-05-28 23:15 | 168
2015-05-28 23:30 | 165
2015-05-28 23:45 | 158
2015-05-29 | 158
2015-05-29 00:15 | 152
2015-05-29 00:30 | 160
2015-05-29 00:45 | 164
2015-05-29 01:00 | 153
2015-05-29 01:15 | 163
2015-05-29 01:30 | 157
2015-05-29 01:45 | 153
2015-05-29 02:00 | 159
2015-05-29 02:15 | 152
2015-05-29 02:30 | 155
2015-05-29 02:45 | 159
2015-05-29 03:00 | 148
2015-05-29 03:15 | 155
2015-05-29 03:30 | 151
2015-05-29 03:45 | 148
2015-05-29 04:00 | 148
2015-05-29 04:15 | 149
2015-05-29 04:30 | 155
2015-05-29 04:45 | 158
2015-05-29 05:00 | 144
2015-05-29 05:15 | 155
2015-05-29 05:30 | 150
2015-05-29 05:45 | 145
2015-05-29 06:00 | 143
2015-05-29 06:15 | 159
2015-05-29 06:30 | 146
2015-05-29 06:45 | 146
2015-05-29 07:00 | 149
2015-05-29 07:15 | 148
2015-05-29 07:30 | 158
2015-05-29 07:45 | 152
2015-05-29 08:00 | 154
2015-05-29 08:15 | 160
2015-05-29 08:30 | 159
2015-05-29 08:45 | 165
2015-05-29 09:00 | 180
2015-05-29 09:15 | 170
2015-05-29 09:30 | 169
2015-05-29 09:45 | 170
2015-05-29 10:00 | 194
2015-05-29 10:15 | 212
2015-05-29 10:30 | 218
2015-05-29 10:45 | 230
2015-05-29 11:00 | 239
2015-05-29 11:15 | 227
2015-05-29 11:30 | 234
2015-05-29 11:45 | 242
2015-05-29 12:00 | 263
2015-05-29 12:15 | 271
2015-05-29 12:30 | 246
2015-05-29 12:45 | 264
2015-05-29 13:00 | 263
2015-05-29 13:15 | 264
2015-05-29 13:30 | 260
2015-05-29 13:45 | 275
2015-05-29 14:00 | 278
2015-05-29 14:15 | 273
2015-05-29 14:30 | 270
2015-05-29 14:45 | 271
2015-05-29 15:00 | 270
2015-05-29 15:15 | 278
2015-05-29 15:30 | 282
2015-05-29 15:45 | 273
2015-05-29 16:00 | 279
2015-05-29 16:15 | 274
2015-05-29 16:30 | 273
2015-05-29 16:45 | 274
2015-05-29 17:00 | 283
2015-05-29 17:15 | 274
2015-05-29 17:30 | 269
2015-05-29 17:45 | 270
2015-05-29 18:00 | 267
2015-05-29 18:15 | 275
2015-05-29 18:30 | 273
2015-05-29 18:45 | 255
2015-05-29 19:00 | 247
2015-05-29 19:15 | 234
2015-05-29 19:30 | 228
2015-05-29 19:45 | 215
2015-05-29 20:00 | 207
2015-05-29 20:15 | 182
2015-05-29 20:30 | 183
2015-05-29 20:45 | 172
2015-05-29 21:00 | 178
2015-05-29 21:15 | 166
2015-05-29 21:30 | 163
2015-05-29 21:45 | 167
2015-05-29 22:00 | 153
2015-05-29 22:15 | 158
2015-05-29 22:30 | 160
2015-05-29 22:45 | 157
2015-05-29 23:00 | 156
2015-05-29 23:15 | 168
2015-05-29 23:30 | 155
2015-05-29 23:45 | 166
2015-05-30 | 164
2015-05-30 00:15 | 155
2015-05-30 00:30 | 159
2015-05-30 00:45 | 165
2015-05-30 01:00 | 153
2015-05-30 01:15 | 154
2015-05-30 01:30 | 153
2015-05-30 01:45 | 153
2015-05-30 02:00 | 166
2015-05-30 02:15 | 159
2015-05-30 02:30 | 157
2015-05-30 02:45 | 153
2015-05-30 03:00 | 163
2015-05-30 03:15 | 154
2015-05-30 03:30 | 150
2015-05-30 03:45 | 156
2015-05-30 04:00 | 156
2015-05-30 04:15 | 151
2015-05-30 04:30 | 154
2015-05-30 04:45 | 152
2015-05-30 05:00 | 171
2015-05-30 05:15 | 154
2015-05-30 05:30 | 152
2015-05-30 05:45 | 150
2015-05-30 06:00 | 154
2015-05-30 06:15 | 150
2015-05-30 06:30 | 160
2015-05-30 06:45 | 165
2015-05-30 07:00 | 154
2015-05-30 07:15 | 157
2015-05-30 07:30 | 156
2015-05-30 07:45 | 154
2015-05-30 08:00 | 146
2015-05-30 08:15 | 152
2015-05-30 08:30 | 146
2015-05-30 08:45 | 160
2015-05-30 09:00 | 159
2015-05-30 09:15 | 178
2015-05-30 09:30 | 193
2015-05-30 09:45 | 185
2015-05-30 10:00 | 186
2015-05-30 10:15 | 190
2015-05-30 10:30 | 203
2015-05-30 10:45 | 199
2015-05-30 11:00 | 212
2015-05-30 11:15 | 211
2015-05-30 11:30 | 213
2015-05-30 11:45 | 213
2015-05-30 12:00 | 221
2015-05-30 12:15 | 222
2015-05-30 12:30 | 224
2015-05-30 12:45 | 230
2015-05-30 13:00 | 234
2015-05-30 13:15 | 236
2015-05-30 13:30 | 250
2015-05-30 13:45 | 238
2015-05-30 14:00 | 248
2015-05-30 14:15 | 242
2015-05-30 14:30 | 244
2015-05-30 14:45 | 244
2015-05-30 15:00 | 242
2015-05-30 15:15 | 237
2015-05-30 15:30 | 175
2015-05-30 15:45 | 176
2015-05-30 16:00 | 171
2015-05-30 16:15 | 180
2015-05-30 16:30 | 183
2015-05-30 16:45 | 181
2015-05-30 17:00 | 192
2015-05-30 17:15 | 187
2015-05-30 17:30 | 186
2015-05-30 17:45 | 198
2015-05-30 18:00 | 185
2015-05-30 18:15 | 190
2015-05-30 18:30 | 192
2015-05-30 18:45 | 184
2015-05-30 19:00 | 188
2015-05-30 19:15 | 186
2015-05-30 19:30 | 186
2015-05-30 19:45 | 182
2015-05-30 20:00 | 172
2015-05-30 20:15 | 172
2015-05-30 20:30 | 159
2015-05-30 20:45 | 161
2015-05-30 21:00 | 164
2015-05-30 21:15 | 152
2015-05-30 21:30 | 159
2015-05-30 21:45 | 155
2015-05-30 22:00 | 152
2015-05-30 22:15 | 157
2015-05-30 22:30 | 158
2015-05-30 22:45 | 154
2015-05-30 23:00 | 154
2015-05-30 23:15 | 151
2015-05-30 23:30 | 146
2015-05-30 23:45 | 146
2015-05-31 | 145
2015-05-31 00:15 | 143
2015-05-31 00:30 | 151
2015-05-31 00:45 | 145
2015-05-31 01:00 | 144
2015-05-31 01:15 | 146
2015-05-31 01:30 | 145
2015-05-31 01:45 | 154
2015-05-31 02:00 | 148
2015-05-31 02:15 | 154
2015-05-31 02:30 | 148
2015-05-31 02:45 | 147
2015-05-31 03:00 | 147
2015-05-31 03:15 | 149
2015-05-31 03:30 | 145
2015-05-31 03:45 | 145
2015-05-31 04:00 | 144
2015-05-31 04:15 | 156
2015-05-31 04:30 | 154
2015-05-31 04:45 | 144
2015-05-31 05:00 | 152
2015-05-31 05:15 | 153
2015-05-31 05:30 | 147
2015-05-31 05:45 | 153
2015-05-31 06:00 | 150
2015-05-31 06:15 | 143
2015-05-31 06:30 | 151
2015-05-31 06:45 | 146
2015-05-31 07:00 | 160
2015-05-31 07:15 | 172
2015-05-31 07:30 | 157
2015-05-31 07:45 | 159
2015-05-31 08:00 | 155
2015-05-31 08:15 | 161
2015-05-31 08:30 | 164
2015-05-31 08:45 | 156
2015-05-31 09:00 | 171
2015-05-31 09:15 | 167
2015-05-31 09:30 | 170
2015-05-31 09:45 | 171
2015-05-31 10:00 | 168
2015-05-31 10:15 | 180
2015-05-31 10:30 | 167
2015-05-31 10:45 | 169
2015-05-31 11:00 | 174
2015-05-31 11:15 | 164
2015-05-31 11:30 | 180
2015-05-31 11:45 | 166
2015-05-31 12:00 | 170
2015-05-31 12:15 | 171
2015-05-31 12:30 | 166
2015-05-31 12:45 | 173
2015-05-31 13:00 | 167
2015-05-31 13:15 | 175
2015-05-31 13:30 | 170
2015-05-31 13:45 | 174
2015-05-31 14:00 | 178
2015-05-31 14:15 | 175
2015-05-31 14:30 | 174
2015-05-31 14:45 | 179
2015-05-31 15:00 | 176
2015-05-31 15:15 | 179
2015-05-31 15:30 | 182
2015-05-31 15:45 | 179
2015-05-31 16:00 | 184
2015-05-31 16:15 | 188
2015-05-31 16:30 | 183
2015-05-31 16:45 | 180
2015-05-31 17:00 | 190
2015-05-31 17:15 | 186
2015-05-31 17:30 | 185
2015-05-31 17:45 | 197
2015-05-31 18:00 | 185
2015-05-31 18:15 | 188
2015-05-31 18:30 | 189
2015-05-31 18:45 | 186
2015-05-31 19:00 | 186
2015-05-31 19:15 | 181
2015-05-31 19:30 | 182
2015-05-31 19:45 | 171
2015-05-31 20:00 | 176
2015-05-31 20:15 | 168
2015-05-31 20:30 | 174
2015-05-31 20:45 | 176
2015-05-31 21:00 | 164
2015-05-31 21:15 | 171
2015-05-31 21:30 | 150
2015-05-31 21:45 | 154
2015-05-31 22:00 | 140
2015-05-31 22:15 | 143
2015-05-31 22:30 | 143
2015-05-31 22:45 | 141
2015-05-31 23:00 | 137
2015-05-31 23:15 | 140
2015-05-31 23:30 | 141
2015-05-31 23:45 | 140
2015-06-01 | 136
2015-06-01 00:15 | 131
2015-06-01 00:30 | 136
2015-06-01 00:45 | 133
2015-06-01 01:00 | 133
2015-06-01 01:15 | 135
2015-06-01 01:30 | 135
2015-06-01 01:45 | 132
2015-06-01 02:00 | 137
2015-06-01 02:15 | 132
2015-06-01 02:30 | 133
2015-06-01 02:45 | 133
2015-06-01 03:00 | 137
2015-06-01 03:15 | 132
2015-06-01 03:30 | 133
2015-06-01 03:45 | 130
2015-06-01 04:00 | 132
2015-06-01 04:15 | 131
2015-06-01 04:30 | 130
2015-06-01 04:45 | 136
2015-06-01 05:00 | 130
2015-06-01 05:15 | 131
2015-06-01 05:30 | 131
2015-06-01 05:45 | 131
2015-06-01 06:00 | 132
2015-06-01 06:15 | 131
2015-06-01 06:30 | 131
2015-06-01 06:45 | 132
2015-06-01 07:00 | 132
2015-06-01 07:15 | 135
2015-06-01 07:30 | 127
2015-06-01 07:45 | 133
2015-06-01 08:00 | 137
2015-06-01 08:15 | 144
2015-06-01 08:30 | 151
2015-06-01 08:45 | 164
2015-06-01 09:00 | 190
2015-06-01 09:15 | 189
2015-06-01 09:30 | 191
2015-06-01 09:45 | 196
2015-06-01 10:00 | 188
2015-06-01 10:15 | 194
2015-06-01 10:30 | 195
2015-06-01 10:45 | 192
2015-06-01 11:00 | 202
2015-06-01 11:15 | 194
2015-06-01 11:30 | 197
2015-06-01 11:45 | 193
2015-06-01 12:00 | 206
2015-06-01 12:15 | 195
2015-06-01 12:30 | 197
2015-06-01 12:45 | 197
2015-06-01 13:00 | 199
2015-06-01 13:15 | 199
2015-06-01 13:30 | 205
2015-06-01 13:45 | 203
2015-06-01 14:00 | 204
2015-06-01 14:15 | 213
2015-06-01 14:30 | 210
2015-06-01 14:45 | 209
2015-06-01 15:00 | 208
2015-06-01 15:15 | 211
2015-06-01 15:30 | 207
2015-06-01 15:45 | 224
2015-06-01 16:00 | 213
2015-06-01 16:15 | 219
2015-06-01 16:30 | 216
2015-06-01 16:45 | 214
2015-06-01 17:00 | 220
2015-06-01 17:15 | 221
2015-06-01 17:30 | 215
2015-06-01 17:45 | 218
2015-06-01 18:00 | 223
2015-06-01 18:15 | 210
2015-06-01 18:30 | 218
2015-06-01 18:45 | 208
2015-06-01 19:00 | 217
2015-06-01 19:15 | 206
2015-06-01 19:30 | 209
2015-06-01 19:45 | 211
2015-06-01 20:00 | 203
2015-06-01 20:15 | 204
2015-06-01 20:30 | 193
2015-06-01 20:45 | 189
2015-06-01 21:00 | 186
2015-06-01 21:15 | 177
2015-06-01 21:30 | 176
2015-06-01 21:45 | 184
2015-06-01 22:00 | 183
2015-06-01 22:15 | 197
2015-06-01 22:30 | 186
2015-06-01 22:45 | 187
2015-06-01 23:00 | 180
2015-06-01 23:15 | 171
2015-06-01 23:30 | 166
2015-06-01 23:45 | 160
2015-06-02 | 163
2015-06-02 00:15 | 156
2015-06-02 00:30 | 163
2015-06-02 00:45 | 154
2015-06-02 01:00 | 152
2015-06-02 01:15 | 159
2015-06-02 01:30 | 139
2015-06-02 01:45 | 141
2015-06-02 02:00 | 138
2015-06-02 02:15 | 134
2015-06-02 02:30 | 133
2015-06-02 02:45 | 135
2015-06-02 03:00 | 136
2015-06-02 03:15 | 140
2015-06-02 03:30 | 133
2015-06-02 03:45 | 131
2015-06-02 04:00 | 132
2015-06-02 04:15 | 135
2015-06-02 04:30 | 132
2015-06-02 04:45 | 132
2015-06-02 05:00 | 138
2015-06-02 05:15 | 143
2015-06-02 05:30 | 133
2015-06-02 05:45 | 138
2015-06-02 06:00 | 139
2015-06-02 06:15 | 138
2015-06-02 06:30 | 145
2015-06-02 06:45 | 135
2015-06-02 07:00 | 141
2015-06-02 07:15 | 140
2015-06-02 07:30 | 145
2015-06-02 07:45 | 153
2015-06-02 08:00 | 149
2015-06-02 08:15 | 153
2015-06-02 08:30 | 155
2015-06-02 08:45 | 173
2015-06-02 09:00 | 169
2015-06-02 09:15 | 182
2015-06-02 09:30 | 192
2015-06-02 09:45 | 186
2015-06-02 10:00 | 190
2015-06-02 10:15 | 188
2015-06-02 10:30 | 189
2015-06-02 10:45 | 175
2015-06-02 11:00 | 181
2015-06-02 11:15 | 184
2015-06-02 11:30 | 190
2015-06-02 11:45 | 191
2015-06-02 12:00 | 197
2015-06-02 12:15 | 196
2015-06-02 12:30 | 196
2015-06-02 12:45 | 196
2015-06-02 13:00 | 199
2015-06-02 13:15 | 201
2015-06-02 13:30 | 202
2015-06-02 13:45 | 200
2015-06-02 14:00 | 199
2015-06-02 14:15 | 200
2015-06-02 14:30 | 203
2015-06-02 14:45 | 224
2015-06-02 15:00 | 267
2015-06-02 15:15 | 251
2015-06-02 15:30 | 260
2015-06-02 15:45 | 251
2015-06-02 16:00 | 243
2015-06-02 16:15 | 247
2015-06-02 16:30 | 236
2015-06-02 16:45 | 246
2015-06-02 17:00 | 235
2015-06-02 17:15 | 242
2015-06-02 17:30 | 239
2015-06-02 17:45 | 237
2015-06-02 18:00 | 235
2015-06-02 18:15 | 228
2015-06-02 18:30 | 236
2015-06-02 18:45 | 226
2015-06-02 19:00 | 217
2015-06-02 19:15 | 222
2015-06-02 19:30 | 220
2015-06-02 19:45 | 214
2015-06-02 20:00 | 210
2015-06-02 20:15 | 208
2015-06-02 20:30 | 203
2015-06-02 20:45 | 201
2015-06-02 21:00 | 203
2015-06-02 21:15 | 206
2015-06-02 21:30 | 198
2015-06-02 21:45 | 191
2015-06-02 22:00 | 185
2015-06-02 22:15 | 183
2015-06-02 22:30 | 183
2015-06-02 22:45 | 185
2015-06-02 23:00 | 190
2015-06-02 23:15 | 184
2015-06-02 23:30 | 167
2015-06-02 23:45 | 166
2015-06-03 | 157
2015-06-03 00:15 | 171
2015-06-03 00:30 | 152
2015-06-03 00:45 | 150
2015-06-03 01:00 | 153
2015-06-03 01:15 | 155
2015-06-03 01:30 | 149
2015-06-03 01:45 | 148
2015-06-03 02:00 | 149
2015-06-03 02:15 | 146
2015-06-03 02:30 | 164
2015-06-03 02:45 | 150
2015-06-03 03:00 | 153
2015-06-03 03:15 | 149
2015-06-03 03:30 | 145
2015-06-03 03:45 | 145
2015-06-03 04:00 | 146
2015-06-03 04:15 | 155
2015-06-03 04:30 | 144
2015-06-03 04:45 | 145
2015-06-03 05:00 | 143
2015-06-03 05:15 | 142
2015-06-03 05:30 | 154
2015-06-03 05:45 | 145
2015-06-03 06:00 | 141
2015-06-03 06:15 | 141
2015-06-03 06:30 | 153
2015-06-03 06:45 | 147
2015-06-03 07:00 | 149
2015-06-03 07:15 | 152
2015-06-03 07:30 | 146
2015-06-03 07:45 | 151
2015-06-03 08:00 | 159
2015-06-03 08:15 | 174
2015-06-03 08:30 | 177
2015-06-03 08:45 | 184
2015-06-03 09:00 | 194
2015-06-03 09:15 | 204
2015-06-03 09:30 | 203
2015-06-03 09:45 | 211
2015-06-03 10:00 | 206
2015-06-03 10:15 | 212
2015-06-03 10:30 | 232
2015-06-03 10:45 | 217
2015-06-03 11:00 | 218
2015-06-03 11:15 | 232
2015-06-03 11:30 | 219
2015-06-03 11:45 | 219
2015-06-03 12:00 | 241
2015-06-03 12:15 | 223
2015-06-03 12:30 | 225
2015-06-03 12:45 | 232
2015-06-03 13:00 | 224
2015-06-03 13:15 | 251
2015-06-03 13:30 | 238
2015-06-03 13:45 | 240
2015-06-03 14:00 | 257
2015-06-03 14:15 | 229
2015-06-03 14:30 | 229
2015-06-03 14:45 | 236
2015-06-03 15:00 | 230
2015-06-03 15:15 | 237
2015-06-03 15:30 | 234
2015-06-03 15:45 | 224
2015-06-03 16:00 | 241
2015-06-03 16:15 | 221
2015-06-03 16:30 | 229
2015-06-03 16:45 | 228
2015-06-03 17:00 | 220
2015-06-03 17:15 | 236
2015-06-03 17:30 | 225
2015-06-03 17:45 | 227
2015-06-03 18:00 | 225
2015-06-03 18:15 | 211
2015-06-03 18:30 | 218
2015-06-03 18:45 | 208
2015-06-03 19:00 | 208
2015-06-03 19:15 | 199
2015-06-03 19:30 | 194
2015-06-03 19:45 | 201
2015-06-03 20:00 | 199
2015-06-03 20:15 | 192
2015-06-03 20:30 | 181
2015-06-03 20:45 | 170
2015-06-03 21:00 | 179
2015-06-03 21:15 | 178
2015-06-03 21:30 | 157
2015-06-03 21:45 | 158
2015-06-03 22:00 | 153
2015-06-03 22:15 | 171
2015-06-03 22:30 | 154
2015-06-03 22:45 | 156
2015-06-03 23:00 | 158
2015-06-03 23:15 | 160
2015-06-03 23:30 | 168
2015-06-03 23:45 | 156
2015-06-04 | 156
2015-06-04 00:15 | 152
2015-06-04 00:30 | 163
2015-06-04 00:45 | 157
2015-06-04 01:00 | 155
2015-06-04 01:15 | 151
2015-06-04 01:30 | 153
2015-06-04 01:45 | 149
2015-06-04 02:00 | 151
2015-06-04 02:15 | 163
2015-06-04 02:30 | 149
2015-06-04 02:45 | 149
2015-06-04 03:00 | 150
2015-06-04 03:15 | 155
2015-06-04 03:30 | 151
2015-06-04 03:45 | 145
2015-06-04 04:00 | 144
2015-06-04 04:15 | 144
2015-06-04 04:30 | 152
2015-06-04 04:45 | 155
2015-06-04 05:00 | 148
2015-06-04 05:15 | 150
2015-06-04 05:30 | 143
2015-06-04 05:45 | 157
2015-06-04 06:00 | 151
2015-06-04 06:15 | 150
2015-06-04 06:30 | 144
2015-06-04 06:45 | 144
2015-06-04 07:00 | 148
2015-06-04 07:15 | 151
2015-06-04 07:30 | 160
2015-06-04 07:45 | 151
2015-06-04 08:00 | 170
2015-06-04 08:15 | 179
2015-06-04 08:30 | 173
2015-06-04 08:45 | 195
2015-06-04 09:00 | 184
2015-06-04 09:15 | 183
2015-06-04 09:30 | 194
2015-06-04 09:45 | 199
2015-06-04 10:00 | 211
2015-06-04 10:15 | 189
2015-06-04 10:30 | 220
2015-06-04 10:45 | 225
2015-06-04 11:00 | 218
2015-06-04 11:15 | 241
2015-06-04 11:30 | 228
2015-06-04 11:45 | 228
2015-06-04 12:00 | 229
2015-06-04 12:15 | 229
2015-06-04 12:30 | 249
2015-06-04 12:45 | 242
2015-06-04 13:00 | 238
2015-06-04 13:15 | 235
2015-06-04 13:30 | 238
2015-06-04 13:45 | 235
2015-06-04 14:00 | 240
2015-06-04 14:15 | 246
2015-06-04 14:30 | 243
2015-06-04 14:45 | 239
2015-06-04 15:00 | 251
2015-06-04 15:15 | 251
2015-06-04 15:30 | 243
2015-06-04 15:45 | 259
2015-06-04 16:00 | 249
2015-06-04 16:15 | 251
2015-06-04 16:30 | 251
2015-06-04 16:45 | 252
2015-06-04 17:00 | 259
2015-06-04 17:15 | 248
2015-06-04 17:30 | 255
2015-06-04 17:45 | 253
2015-06-04 18:00 | 245
2015-06-04 18:15 | 252
2015-06-04 18:30 | 250
2015-06-04 18:45 | 243
2015-06-04 19:00 | 253
2015-06-04 19:15 | 238
2015-06-04 19:30 | 232
2015-06-04 19:45 | 231
2015-06-04 20:00 | 225
2015-06-04 20:15 | 222
2015-06-04 20:30 | 214
2015-06-04 20:45 | 219
2015-06-04 21:00 | 213
2015-06-04 21:15 | 191
2015-06-04 21:30 | 198
2015-06-04 21:45 | 182
2015-06-04 22:00 | 197
2015-06-04 22:15 | 186
2015-06-04 22:30 | 185
2015-06-04 22:45 | 185
2015-06-04 23:00 | 191
2015-06-04 23:15 | 190
2015-06-04 23:30 | 196
2015-06-04 23:45 | 188
2015-06-05 | 181
2015-06-05 00:15 | 181
2015-06-05 00:30 | 178
2015-06-05 00:45 | 160
2015-06-05 01:00 | 160
2015-06-05 01:15 | 159
2015-06-05 01:30 | 153
2015-06-05 01:45 | 152
2015-06-05 02:00 | 150
2015-06-05 02:15 | 162
2015-06-05 02:30 | 155
2015-06-05 02:45 | 150
2015-06-05 03:00 | 157
2015-06-05 03:15 | 151
2015-06-05 03:30 | 147
2015-06-05 03:45 | 148
2015-06-05 04:00 | 147
2015-06-05 04:15 | 156
2015-06-05 04:30 | 159
2015-06-05 04:45 | 145
2015-06-05 05:00 | 146
2015-06-05 05:15 | 146
2015-06-05 05:30 | 163
2015-06-05 05:45 | 153
2015-06-05 06:00 | 146
2015-06-05 06:15 | 148
2015-06-05 06:30 | 144
2015-06-05 06:45 | 163
2015-06-05 07:00 | 152
2015-06-05 07:15 | 150
2015-06-05 07:30 | 148
2015-06-05 07:45 | 154
2015-06-05 08:00 | 172
2015-06-05 08:15 | 165
2015-06-05 08:30 | 176
2015-06-05 08:45 | 185
2015-06-05 09:00 | 192
2015-06-05 09:15 | 231
2015-06-05 09:30 | 216
2015-06-05 09:45 | 220
2015-06-05 10:00 | 218
2015-06-05 10:15 | 222
2015-06-05 10:30 | 242
2015-06-05 10:45 | 250
2015-06-05 11:00 | 235
2015-06-05 11:15 | 243
2015-06-05 11:30 | 240
2015-06-05 11:45 | 238
2015-06-05 12:00 | 237
2015-06-05 12:15 | 246
2015-06-05 12:30 | 252
2015-06-05 12:45 | 248
2015-06-05 13:00 | 235
2015-06-05 13:15 | 246
2015-06-05 13:30 | 256
2015-06-05 13:45 | 254
2015-06-05 14:00 | 259
2015-06-05 14:15 | 262
2015-06-05 14:30 | 256
2015-06-05 14:45 | 259
2015-06-05 15:00 | 258
2015-06-05 15:15 | 264
2015-06-05 15:30 | 264
2015-06-05 15:45 | 268
2015-06-05 16:00 | 279
2015-06-05 16:15 | 269
2015-06-05 16:30 | 267
2015-06-05 16:45 | 269
2015-06-05 17:00 | 271
2015-06-05 17:15 | 278
2015-06-05 17:30 | 260
2015-06-05 17:45 | 256
2015-06-05 18:00 | 254
2015-06-05 18:15 | 251
2015-06-05 18:30 | 253
2015-06-05 18:45 | 248
2015-06-05 19:00 | 252
2015-06-05 19:15 | 243
2015-06-05 19:30 | 232
2015-06-05 19:45 | 239
2015-06-05 20:00 | 229
2015-06-05 20:15 | 224
2015-06-05 20:30 | 231
2015-06-05 20:45 | 222
2015-06-05 21:00 | 216
2015-06-05 21:15 | 205
2015-06-05 21:30 | 190
2015-06-05 21:45 | 190
2015-06-05 22:00 | 194
2015-06-05 22:15 | 189
2015-06-05 22:30 | 194
2015-06-05 22:45 | 181
2015-06-05 23:00 | 188
2015-06-05 23:15 | 184
2015-06-05 23:30 | 180
2015-06-05 23:45 | 187
2015-06-06 | 183
2015-06-06 00:15 | 187
2015-06-06 00:30 | 191
2015-06-06 00:45 | 184
2015-06-06 01:00 | 181
2015-06-06 01:15 | 182
2015-06-06 01:30 | 178
2015-06-06 01:45 | 178
2015-06-06 02:00 | 173
2015-06-06 02:15 | 188
2015-06-06 02:30 | 174
2015-06-06 02:45 | 170
2015-06-06 03:00 | 160
2015-06-06 03:15 | 162
2015-06-06 03:30 | 158
2015-06-06 03:45 | 153
2015-06-06 04:00 | 166
2015-06-06 04:15 | 160
2015-06-06 04:30 | 150
2015-06-06 04:45 | 151
2015-06-06 05:00 | 151
2015-06-06 05:15 | 156
2015-06-06 05:30 | 158
2015-06-06 05:45 | 150
2015-06-06 06:00 | 149
2015-06-06 06:15 | 149
2015-06-06 06:30 | 150
2015-06-06 06:45 | 154
2015-06-06 07:00 | 159
2015-06-06 07:15 | 154
2015-06-06 07:30 | 148
2015-06-06 07:45 | 155
2015-06-06 08:00 | 150
2015-06-06 08:15 | 175
2015-06-06 08:30 | 176
2015-06-06 08:45 | 169
2015-06-06 09:00 | 181
2015-06-06 09:15 | 179
2015-06-06 09:30 | 192
2015-06-06 09:45 | 184
2015-06-06 10:00 | 183
2015-06-06 10:15 | 189
2015-06-06 10:30 | 184
2015-06-06 10:45 | 190
2015-06-06 11:00 | 187
2015-06-06 11:15 | 190
2015-06-06 11:30 | 201
2015-06-06 11:45 | 210
2015-06-06 12:00 | 206
2015-06-06 12:15 | 202
2015-06-06 12:30 | 199
2015-06-06 12:45 | 198
2015-06-06 13:00 | 213
2015-06-06 13:15 | 211
2015-06-06 13:30 | 202
2015-06-06 13:45 | 211
2015-06-06 14:00 | 213
2015-06-06 14:15 | 219
2015-06-06 14:30 | 207
2015-06-06 14:45 | 223
2015-06-06 15:00 | 214
2015-06-06 15:15 | 222
2015-06-06 15:30 | 213
2015-06-06 15:45 | 226
2015-06-06 16:00 | 216
2015-06-06 16:15 | 223
2015-06-06 16:30 | 222
2015-06-06 16:45 | 227
2015-06-06 17:00 | 222
2015-06-06 17:15 | 227
2015-06-06 17:30 | 224
2015-06-06 17:45 | 227
2015-06-06 18:00 | 223
2015-06-06 18:15 | 214
2015-06-06 18:30 | 219
2015-06-06 18:45 | 225
2015-06-06 19:00 | 215
2015-06-06 19:15 | 215
2015-06-06 19:30 | 210
2015-06-06 19:45 | 218
2015-06-06 20:00 | 206
2015-06-06 20:15 | 210
2015-06-06 20:30 | 207
2015-06-06 20:45 | 210
2015-06-06 21:00 | 191
2015-06-06 21:15 | 196
2015-06-06 21:30 | 190
2015-06-06 21:45 | 199
2015-06-06 22:00 | 185
2015-06-06 22:15 | 190
2015-06-06 22:30 | 189
2015-06-06 22:45 | 185
2015-06-06 23:00 | 190
2015-06-06 23:15 | 189
2015-06-06 23:30 | 179
2015-06-06 23:45 | 181
2015-06-07 | 194
2015-06-07 00:15 | 179
2015-06-07 00:30 | 188
2015-06-07 00:45 | 192
2015-06-07 01:00 | 175
2015-06-07 01:15 | 187
2015-06-07 01:30 | 182
2015-06-07 01:45 | 179
2015-06-07 02:00 | 181
2015-06-07 02:15 | 176
2015-06-07 02:30 | 186
2015-06-07 02:45 | 172
2015-06-07 03:00 | 180
2015-06-07 03:15 | 182
2015-06-07 03:30 | 178
2015-06-07 03:45 | 181
2015-06-07 04:00 | 175
2015-06-07 04:15 | 187
2015-06-07 04:30 | 176
2015-06-07 04:45 | 183
2015-06-07 05:00 | 179
2015-06-07 05:15 | 185
2015-06-07 05:30 | 176
2015-06-07 05:45 | 178
2015-06-07 06:00 | 181
2015-06-07 06:15 | 177
2015-06-07 06:30 | 178
2015-06-07 06:45 | 179
2015-06-07 07:00 | 192
2015-06-07 07:15 | 190
2015-06-07 07:30 | 194
2015-06-07 07:45 | 189
2015-06-07 08:00 | 200
2015-06-07 08:15 | 186
2015-06-07 08:30 | 196
2015-06-07 08:45 | 191
2015-06-07 09:00 | 196
2015-06-07 09:15 | 194
2015-06-07 09:30 | 192
2015-06-07 09:45 | 200
2015-06-07 10:00 | 203
2015-06-07 10:15 | 212
2015-06-07 10:30 | 203
2015-06-07 10:45 | 201
2015-06-07 11:00 | 208
2015-06-07 11:15 | 210
2015-06-07 11:30 | 214
2015-06-07 11:45 | 209
2015-06-07 12:00 | 210
2015-06-07 12:15 | 211
2015-06-07 12:30 | 214
2015-06-07 12:45 | 215
2015-06-07 13:00 | 223
2015-06-07 13:15 | 217
2015-06-07 13:30 | 229
2015-06-07 13:45 | 219
2015-06-07 14:00 | 235
2015-06-07 14:15 | 224
2015-06-07 14:30 | 243
2015-06-07 14:45 | 234
2015-06-07 15:00 | 249
2015-06-07 15:15 | 236
2015-06-07 15:30 | 255
2015-06-07 15:45 | 251
2015-06-07 16:00 | 256
2015-06-07 16:15 | 259
2015-06-07 16:30 | 259
2015-06-07 16:45 | 256
2015-06-07 17:00 | 269
2015-06-07 17:15 | 257
2015-06-07 17:30 | 258
2015-06-07 17:45 | 254
2015-06-07 18:00 | 243
2015-06-07 18:15 | 255
2015-06-07 18:30 | 244
2015-06-07 18:45 | 257
2015-06-07 19:00 | 234
2015-06-07 19:15 | 240
2015-06-07 19:30 | 233
2015-06-07 19:45 | 239
2015-06-07 20:00 | 230
2015-06-07 20:15 | 243
2015-06-07 20:30 | 224
2015-06-07 20:45 | 219
2015-06-07 21:00 | 217
2015-06-07 21:15 | 213
2015-06-07 21:30 | 198
2015-06-07 21:45 | 203
2015-06-07 22:00 | 205
2015-06-07 22:15 | 206
2015-06-07 22:30 | 200
2015-06-07 22:45 | 203
2015-06-07 23:00 | 197
2015-06-07 23:15 | 199
2015-06-07 23:30 | 204
2015-06-07 23:45 | 210
2015-06-08 | 195
2015-06-08 00:15 | 196
2015-06-08 00:30 | 193
2015-06-08 00:45 | 195
2015-06-08 01:00 | 195
2015-06-08 01:15 | 190
2015-06-08 01:30 | 199
2015-06-08 01:45 | 200
2015-06-08 02:00 | 187
2015-06-08 02:15 | 189
2015-06-08 02:30 | 199
2015-06-08 02:45 | 182
2015-06-08 03:00 | 194
2015-06-08 03:15 | 187
2015-06-08 03:30 | 194
2015-06-08 03:45 | 199
2015-06-08 04:00 | 185
2015-06-08 04:15 | 180
2015-06-08 04:30 | 186
2015-06-08 04:45 | 191
2015-06-08 05:00 | 182
2015-06-08 05:15 | 179
2015-06-08 05:30 | 188
2015-06-08 05:45 | 187
2015-06-08 06:00 | 181
2015-06-08 06:15 | 189
2015-06-08 06:30 | 192
2015-06-08 06:45 | 183
2015-06-08 07:00 | 188
2015-06-08 07:15 | 195
2015-06-08 07:30 | 193
2015-06-08 07:45 | 199
2015-06-08 08:00 | 195
2015-06-08 08:15 | 205
2015-06-08 08:30 | 204
2015-06-08 08:45 | 213
2015-06-08 09:00 | 224
2015-06-08 09:15 | 224
2015-06-08 09:30 | 230
2015-06-08 09:45 | 234
2015-06-08 10:00 | 241
2015-06-08 10:15 | 247
2015-06-08 10:30 | 259
2015-06-08 10:45 | 254
2015-06-08 11:00 | 275
2015-06-08 11:15 | 263
2015-06-08 11:30 | 284
2015-06-08 11:45 | 277
2015-06-08 12:00 | 287
2015-06-08 12:15 | 286
2015-06-08 12:30 | 296
2015-06-08 12:45 | 294
2015-06-08 13:00 | 294
2015-06-08 13:15 | 299
2015-06-08 13:30 | 291
2015-06-08 13:45 | 302
2015-06-08 14:00 | 298
2015-06-08 14:15 | 294
2015-06-08 14:30 | 303
2015-06-08 14:45 | 298
2015-06-08 15:00 | 307
2015-06-08 15:15 | 315
2015-06-08 15:30 | 321
2015-06-08 15:45 | 322
2015-06-08 16:00 | 320
2015-06-08 16:15 | 321
2015-06-08 16:30 | 318
2015-06-08 16:45 | 315
2015-06-08 17:00 | 316
2015-06-08 17:15 | 316
2015-06-08 17:30 | 314
2015-06-08 17:45 | 318
2015-06-08 18:00 | 316
2015-06-08 18:15 | 317
2015-06-08 18:30 | 316
2015-06-08 18:45 | 310
2015-06-08 19:00 | 305
2015-06-08 19:15 | 289
2015-06-08 19:30 | 286
2015-06-08 19:45 | 280
2015-06-08 20:00 | 282
2015-06-08 20:15 | 279
2015-06-08 20:30 | 264
2015-06-08 20:45 | 272
2015-06-08 21:00 | 259
2015-06-08 21:15 | 253
2015-06-08 21:30 | 239
2015-06-08 21:45 | 231
2015-06-08 22:00 | 236
2015-06-08 22:15 | 227
2015-06-08 22:30 | 234
2015-06-08 22:45 | 217
2015-06-08 23:00 | 234
2015-06-08 23:15 | 219
2015-06-08 23:30 | 217
2015-06-08 23:45 | 206
2015-06-09 | 207
2015-06-09 00:15 | 209
2015-06-09 00:30 | 204
2015-06-09 00:45 | 210
2015-06-09 01:00 | 203
2015-06-09 01:15 | 204
2015-06-09 01:30 | 202
2015-06-09 01:45 | 202
2015-06-09 02:00 | 209
2015-06-09 02:15 | 194
2015-06-09 02:30 | 199
2015-06-09 02:45 | 197
2015-06-09 03:00 | 195
2015-06-09 03:15 | 194
2015-06-09 03:30 | 194
2015-06-09 03:45 | 187
2015-06-09 04:00 | 194
2015-06-09 04:15 | 189
2015-06-09 04:30 | 185
2015-06-09 04:45 | 183
2015-06-09 05:00 | 188
2015-06-09 05:15 | 189
2015-06-09 05:30 | 180
2015-06-09 05:45 | 187
2015-06-09 06:00 | 188
2015-06-09 06:15 | 179
2015-06-09 06:30 | 188
2015-06-09 06:45 | 190
2015-06-09 07:00 | 191
2015-06-09 07:15 | 190
2015-06-09 07:30 | 195
2015-06-09 07:45 | 192
2015-06-09 08:00 | 211
2015-06-09 08:15 | 196
2015-06-09 08:30 | 208
2015-06-09 08:45 | 223
2015-06-09 09:00 | 218
2015-06-09 09:15 | 232
2015-06-09 09:30 | 242
2015-06-09 09:45 | 250
2015-06-09 10:00 | 245
2015-06-09 10:15 | 248
2015-06-09 10:30 | 255
2015-06-09 10:45 | 257
2015-06-09 11:00 | 250
2015-06-09 11:15 | 250
2015-06-09 11:30 | 248
2015-06-09 11:45 | 250
2015-06-09 12:00 | 258
2015-06-09 12:15 | 250
2015-06-09 12:30 | 261
2015-06-09 12:45 | 253
2015-06-09 13:00 | 266
2015-06-09 13:15 | 261
2015-06-09 13:30 | 270
2015-06-09 13:45 | 263
2015-06-09 14:00 | 277
2015-06-09 14:15 | 269
2015-06-09 14:30 | 285
2015-06-09 14:45 | 279
2015-06-09 15:00 | 267
2015-06-09 15:15 | 278
2015-06-09 15:30 | 284
2015-06-09 15:45 | 293
2015-06-09 16:00 | 277
2015-06-09 16:15 | 284
2015-06-09 16:30 | 292
2015-06-09 16:45 | 278
2015-06-09 17:00 | 267
2015-06-09 17:15 | 265
2015-06-09 17:30 | 262
2015-06-09 17:45 | 258
2015-06-09 18:00 | 253
2015-06-09 18:15 | 245
2015-06-09 18:30 | 238
2015-06-09 18:45 | 249
2015-06-09 19:00 | 233
2015-06-09 19:15 | 232
2015-06-09 19:30 | 234
2015-06-09 19:45 | 226
2015-06-09 20:00 | 227
2015-06-09 20:15 | 228
2015-06-09 20:30 | 232
2015-06-09 20:45 | 232
2015-06-09 21:00 | 220
2015-06-09 21:15 | 215
2015-06-09 21:30 | 211
2015-06-09 21:45 | 215
2015-06-09 22:00 | 214
2015-06-09 22:15 | 210
2015-06-09 22:30 | 211
2015-06-09 22:45 | 215
2015-06-09 23:00 | 214
2015-06-09 23:15 | 221
2015-06-09 23:30 | 210
2015-06-09 23:45 | 209
2015-06-10 | 219
2015-06-10 00:15 | 200
2015-06-10 00:30 | 208
2015-06-10 00:45 | 203
2015-06-10 01:00 | 202
2015-06-10 01:15 | 202
2015-06-10 01:30 | 201
2015-06-10 01:45 | 203
2015-06-10 02:00 | 202
2015-06-10 02:15 | 197
2015-06-10 02:30 | 205
2015-06-10 02:45 | 199
2015-06-10 03:00 | 205
2015-06-10 03:15 | 202
2015-06-10 03:30 | 196
2015-06-10 03:45 | 206
2015-06-10 04:00 | 192
2015-06-10 04:15 | 202
2015-06-10 04:30 | 203
2015-06-10 04:45 | 204
2015-06-10 05:00 | 198
2015-06-10 05:15 | 194
2015-06-10 05:30 | 198
2015-06-10 05:45 | 190
2015-06-10 06:00 | 197
2015-06-10 06:15 | 188
2015-06-10 06:30 | 192
2015-06-10 06:45 | 195
2015-06-10 07:00 | 187
2015-06-10 07:15 | 188
2015-06-10 07:30 | 190
2015-06-10 07:45 | 188
2015-06-10 08:00 | 196
2015-06-10 08:15 | 205
2015-06-10 08:30 | 197
2015-06-10 08:45 | 199
2015-06-10 09:00 | 214
2015-06-10 09:15 | 216
2015-06-10 09:30 | 223
2015-06-10 09:45 | 222
2015-06-10 10:00 | 225
2015-06-10 10:15 | 223
2015-06-10 10:30 | 223
2015-06-10 10:45 | 219
2015-06-10 11:00 | 222
2015-06-10 11:15 | 228
2015-06-10 11:30 | 229
2015-06-10 11:45 | 227
2015-06-10 12:00 | 231
2015-06-10 12:15 | 220
2015-06-10 12:30 | 221
2015-06-10 12:45 | 225
2015-06-10 13:00 | 218
2015-06-10 13:15 | 229
2015-06-10 13:30 | 222
2015-06-10 13:45 | 223
2015-06-10 14:00 | 225
2015-06-10 14:15 | 225
2015-06-10 14:30 | 223
2015-06-10 14:45 | 223
2015-06-10 15:00 | 228
2015-06-10 15:15 | 226
2015-06-10 15:30 | 222
2015-06-10 15:45 | 219
2015-06-10 16:00 | 228
2015-06-10 16:15 | 230
2015-06-10 16:30 | 229
2015-06-10 16:45 | 238
2015-06-10 17:00 | 229
2015-06-10 17:15 | 231
2015-06-10 17:30 | 222
2015-06-10 17:45 | 221
2015-06-10 18:00 | 222
2015-06-10 18:15 | 215
2015-06-10 18:30 | 210
2015-06-10 18:45 | 203
2015-06-10 19:00 | 211
2015-06-10 19:15 | 203
2015-06-10 19:30 | 200
2015-06-10 19:45 | 203
2015-06-10 20:00 | 199
2015-06-10 20:15 | 201
2015-06-10 20:30 | 195
2015-06-10 20:45 | 196
2015-06-10 21:00 | 197
2015-06-10 21:15 | 185
2015-06-10 21:30 | 185
2015-06-10 21:45 | 187
2015-06-10 22:00 | 178
2015-06-10 22:15 | 189
2015-06-10 22:30 | 186
2015-06-10 22:45 | 179
2015-06-10 23:00 | 184
2015-06-10 23:15 | 183
2015-06-10 23:30 | 177
2015-06-10 23:45 | 177
2015-06-11 | 170
2015-06-11 00:15 | 181
2015-06-11 00:30 | 169
2015-06-11 00:45 | 172
2015-06-11 01:00 | 168
2015-06-11 01:15 | 165
2015-06-11 01:30 | 164
2015-06-11 01:45 | 164
2015-06-11 02:00 | 167
2015-06-11 02:15 | 167
2015-06-11 02:30 | 166
2015-06-11 02:45 | 160
2015-06-11 03:00 | 167
2015-06-11 03:15 | 164
2015-06-11 03:30 | 163
2015-06-11 03:45 | 159
2015-06-11 04:00 | 163
2015-06-11 04:15 | 163
2015-06-11 04:30 | 163
2015-06-11 04:45 | 164
2015-06-11 05:00 | 163
2015-06-11 05:15 | 164
2015-06-11 05:30 | 162
2015-06-11 05:45 | 161
2015-06-11 06:00 | 165
2015-06-11 06:15 | 170
2015-06-11 06:30 | 166
2015-06-11 06:45 | 168
2015-06-11 07:00 | 166
2015-06-11 07:15 | 169
2015-06-11 07:30 | 167
2015-06-11 07:45 | 163
2015-06-11 08:00 | 170
2015-06-11 08:15 | 179
2015-06-11 08:30 | 183
2015-06-11 08:45 | 183
2015-06-11 09:00 | 186
2015-06-11 09:15 | 200
2015-06-11 09:30 | 203
2015-06-11 09:45 | 207
2015-06-11 10:00 | 216
2015-06-11 10:15 | 218
2015-06-11 10:30 | 224
2015-06-11 10:45 | 220
2015-06-11 11:00 | 226
2015-06-11 11:15 | 225
2015-06-11 11:30 | 225
2015-06-11 11:45 | 214
2015-06-11 12:00 | 228
2015-06-11 12:15 | 224
2015-06-11 12:30 | 235
2015-06-11 12:45 | 213
2015-06-11 13:00 | 232
2015-06-11 13:15 | 219
2015-06-11 13:30 | 232
2015-06-11 13:45 | 232
2015-06-11 14:00 | 233
2015-06-11 14:15 | 234
2015-06-11 14:30 | 246
2015-06-11 14:45 | 236
2015-06-11 15:00 | 248
2015-06-11 15:15 | 239
2015-06-11 15:30 | 247
2015-06-11 15:45 | 255
2015-06-11 16:00 | 249
2015-06-11 16:15 | 253
2015-06-11 16:30 | 249
2015-06-11 16:45 | 244
2015-06-11 17:00 | 252
2015-06-11 17:15 | 250
2015-06-11 17:30 | 249
2015-06-11 17:45 | 239
2015-06-11 18:00 | 243
2015-06-11 18:15 | 242
2015-06-11 18:30 | 242
2015-06-11 18:45 | 233
2015-06-11 19:00 | 230
2015-06-11 19:15 | 234
2015-06-11 19:30 | 222
2015-06-11 19:45 | 229
2015-06-11 20:00 | 225
2015-06-11 20:15 | 230
2015-06-11 20:30 | 211
2015-06-11 20:45 | 214
2015-06-11 21:00 | 209
2015-06-11 21:15 | 201
2015-06-11 21:30 | 205
2015-06-11 21:45 | 198
2015-06-11 22:00 | 190
2015-06-11 22:15 | 195
2015-06-11 22:30 | 190
2015-06-11 22:45 | 191
2015-06-11 23:00 | 191
2015-06-11 23:15 | 188
2015-06-11 23:30 | 183
2015-06-11 23:45 | 185
2015-06-12 | 175
2015-06-12 00:15 | 181
2015-06-12 00:30 | 176
2015-06-12 00:45 | 176
2015-06-12 01:00 | 172
2015-06-12 01:15 | 170
2015-06-12 01:30 | 176
2015-06-12 01:45 | 175
2015-06-12 02:00 | 166
2015-06-12 02:15 | 167
2015-06-12 02:30 | 174
2015-06-12 02:45 | 169
2015-06-12 03:00 | 162
2015-06-12 03:15 | 169
2015-06-12 03:30 | 168
2015-06-12 03:45 | 164
2015-06-12 04:00 | 167
2015-06-12 04:15 | 167
2015-06-12 04:30 | 165
2015-06-12 04:45 | 163
2015-06-12 05:00 | 170
2015-06-12 05:15 | 168
2015-06-12 05:30 | 162
2015-06-12 05:45 | 164
2015-06-12 06:00 | 166
2015-06-12 06:15 | 165
2015-06-12 06:30 | 162
2015-06-12 06:45 | 170
2015-06-12 07:00 | 167
2015-06-12 07:15 | 169
2015-06-12 07:30 | 171
2015-06-12 07:45 | 177
2015-06-12 08:00 | 179
2015-06-12 08:15 | 185
2015-06-12 08:30 | 197
2015-06-12 08:45 | 194
2015-06-12 09:00 | 205
2015-06-12 09:15 | 202
2015-06-12 09:30 | 216
2015-06-12 09:45 | 216
2015-06-12 10:00 | 218
2015-06-12 10:15 | 242
2015-06-12 10:30 | 231
2015-06-12 10:45 | 227
2015-06-12 11:00 | 234
2015-06-12 11:15 | 238
2015-06-12 11:30 | 254
2015-06-12 11:45 | 244
2015-06-12 12:00 | 261
2015-06-12 12:15 | 242
2015-06-12 12:30 | 253
2015-06-12 12:45 | 254
2015-06-12 13:00 | 267
2015-06-12 13:15 | 249
2015-06-12 13:30 | 264
2015-06-12 13:45 | 265
2015-06-12 14:00 | 260
2015-06-12 14:15 | 276
2015-06-12 14:30 | 265
2015-06-12 14:45 | 273
2015-06-12 15:00 | 271
2015-06-12 15:15 | 280
2015-06-12 15:30 | 269
2015-06-12 15:45 | 273
2015-06-12 16:00 | 277
2015-06-12 16:15 | 273
2015-06-12 16:30 | 269
2015-06-12 16:45 | 275
2015-06-12 17:00 | 278
2015-06-12 17:15 | 277
2015-06-12 17:30 | 267
2015-06-12 17:45 | 271
2015-06-12 18:00 | 267
2015-06-12 18:15 | 266
2015-06-12 18:30 | 255
2015-06-12 18:45 | 266
2015-06-12 19:00 | 250
2015-06-12 19:15 | 261
2015-06-12 19:30 | 248
2015-06-12 19:45 | 246
2015-06-12 20:00 | 234
2015-06-12 20:15 | 242
2015-06-12 20:30 | 223
2015-06-12 20:45 | 226
2015-06-12 21:00 | 228
2015-06-12 21:15 | 204
2015-06-12 21:30 | 204
2015-06-12 21:45 | 198
2015-06-12 22:00 | 204
2015-06-12 22:15 | 204
2015-06-12 22:30 | 194
2015-06-12 22:45 | 194
2015-06-12 23:00 | 192
2015-06-12 23:15 | 189
2015-06-12 23:30 | 190
2015-06-12 23:45 | 200
2015-06-13 | 183
2015-06-13 00:15 | 193
2015-06-13 00:30 | 196
2015-06-13 00:45 | 189
2015-06-13 01:00 | 197
2015-06-13 01:15 | 192
2015-06-13 01:30 | 182
2015-06-13 01:45 | 181
2015-06-13 02:00 | 179
2015-06-13 02:15 | 189
2015-06-13 02:30 | 185
2015-06-13 02:45 | 172
2015-06-13 03:00 | 172
2015-06-13 03:15 | 186
2015-06-13 03:30 | 184
2015-06-13 03:45 | 174
2015-06-13 04:00 | 176
2015-06-13 04:15 | 170
2015-06-13 04:30 | 174
2015-06-13 04:45 | 186
2015-06-13 05:00 | 183
2015-06-13 05:15 | 170
2015-06-13 05:30 | 167
2015-06-13 05:45 | 180
2015-06-13 06:00 | 188
2015-06-13 06:15 | 167
2015-06-13 06:30 | 173
2015-06-13 06:45 | 190
2015-06-13 07:00 | 176
2015-06-13 07:15 | 173
2015-06-13 07:30 | 177
2015-06-13 07:45 | 189
2015-06-13 08:00 | 170
2015-06-13 08:15 | 171
2015-06-13 08:30 | 174
2015-06-13 08:45 | 178
2015-06-13 09:00 | 186
2015-06-13 09:15 | 178
2015-06-13 09:30 | 176
2015-06-13 09:45 | 189
2015-06-13 10:00 | 191
2015-06-13 10:15 | 181
2015-06-13 10:30 | 190
2015-06-13 10:45 | 203
2015-06-13 11:00 | 201
2015-06-13 11:15 | 190
2015-06-13 11:30 | 191
2015-06-13 11:45 | 190
2015-06-13 12:00 | 214
2015-06-13 12:15 | 204
2015-06-13 12:30 | 196
2015-06-13 12:45 | 209
2015-06-13 13:00 | 199
2015-06-13 13:15 | 219
2015-06-13 13:30 | 217
2015-06-13 13:45 | 226
2015-06-13 14:00 | 214
2015-06-13 14:15 | 227
2015-06-13 14:30 | 215
2015-06-13 14:45 | 237
2015-06-13 15:00 | 225
2015-06-13 15:15 | 237
2015-06-13 15:30 | 228
2015-06-13 15:45 | 236
2015-06-13 16:00 | 228
2015-06-13 16:15 | 231
2015-06-13 16:30 | 235
2015-06-13 16:45 | 229
2015-06-13 17:00 | 250
2015-06-13 17:15 | 226
2015-06-13 17:30 | 241
2015-06-13 17:45 | 223
2015-06-13 18:00 | 232
2015-06-13 18:15 | 215
2015-06-13 18:30 | 227
2015-06-13 18:45 | 234
2015-06-13 19:00 | 239
2015-06-13 19:15 | 216
2015-06-13 19:30 | 235
2015-06-13 19:45 | 219
2015-06-13 20:00 | 208
2015-06-13 20:15 | 222
2015-06-13 20:30 | 199
2015-06-13 20:45 | 196
2015-06-13 21:00 | 203
2015-06-13 21:15 | 210
2015-06-13 21:30 | 192
2015-06-13 21:45 | 189
2015-06-13 22:00 | 182
2015-06-13 22:15 | 186
2015-06-13 22:30 | 194
2015-06-13 22:45 | 185
2015-06-13 23:00 | 180
2015-06-13 23:15 | 180
2015-06-13 23:30 | 192
2015-06-13 23:45 | 177
2015-06-14 | 176
2015-06-14 00:15 | 170
2015-06-14 00:30 | 171
2015-06-14 00:45 | 185
2015-06-14 01:00 | 172
2015-06-14 01:15 | 167
2015-06-14 01:30 | 159
2015-06-14 01:45 | 189
2015-06-14 02:00 | 168
2015-06-14 02:15 | 156
2015-06-14 02:30 | 160
2015-06-14 02:45 | 152
2015-06-14 03:00 | 166
2015-06-14 03:15 | 158
2015-06-14 03:30 | 153
2015-06-14 03:45 | 154
2015-06-14 04:00 | 167
2015-06-14 04:15 | 159
2015-06-14 04:30 | 170
2015-06-14 04:45 | 163
2015-06-14 05:00 | 173
2015-06-14 05:15 | 172
2015-06-14 05:30 | 161
2015-06-14 05:45 | 159
2015-06-14 06:00 | 157
2015-06-14 06:15 | 173
2015-06-14 06:30 | 185
2015-06-14 06:45 | 172
2015-06-14 07:00 | 172
2015-06-14 07:15 | 180
2015-06-14 07:30 | 186
2015-06-14 07:45 | 176
2015-06-14 08:00 | 175
2015-06-14 08:15 | 174
2015-06-14 08:30 | 183
2015-06-14 08:45 | 204
2015-06-14 09:00 | 199
2015-06-14 09:15 | 193
2015-06-14 09:30 | 189
2015-06-14 09:45 | 204
2015-06-14 10:00 | 199
2015-06-14 10:15 | 198
2015-06-14 10:30 | 198
2015-06-14 10:45 | 200
2015-06-14 11:00 | 216
2015-06-14 11:15 | 207
2015-06-14 11:30 | 204
2015-06-14 11:45 | 207
2015-06-14 12:00 | 209
2015-06-14 12:15 | 229
2015-06-14 12:30 | 212
2015-06-14 12:45 | 215
2015-06-14 13:00 | 215
2015-06-14 13:15 | 221
2015-06-14 13:30 | 232
2015-06-14 13:45 | 229
2015-06-14 14:00 | 213
2015-06-14 14:15 | 225
2015-06-14 14:30 | 230
2015-06-14 14:45 | 231
2015-06-14 15:00 | 226
2015-06-14 15:15 | 222
2015-06-14 15:30 | 232
2015-06-14 15:45 | 238
2015-06-14 16:00 | 248
2015-06-14 16:15 | 226
2015-06-14 16:30 | 240
2015-06-14 16:45 | 228
2015-06-14 17:00 | 252
2015-06-14 17:15 | 236
2015-06-14 17:30 | 238
2015-06-14 17:45 | 237
2015-06-14 18:00 | 238
2015-06-14 18:15 | 246
2015-06-14 18:30 | 237
2015-06-14 18:45 | 223
2015-06-14 19:00 | 235
2015-06-14 19:15 | 220
2015-06-14 19:30 | 228
2015-06-14 19:45 | 226
2015-06-14 20:00 | 212
2015-06-14 20:15 | 210
2015-06-14 20:30 | 199
2015-06-14 20:45 | 217
2015-06-14 21:00 | 198
2015-06-14 21:15 | 185
2015-06-14 21:30 | 193
2015-06-14 21:45 | 178
2015-06-14 22:00 | 171
2015-06-14 22:15 | 163
2015-06-14 22:30 | 186
2015-06-14 22:45 | 172
2015-06-14 23:00 | 168
2015-06-14 23:15 | 164
2015-06-14 23:30 | 164
2015-06-14 23:45 | 180
2015-06-15 | 169
2015-06-15 00:15 | 161
2015-06-15 00:30 | 161
2015-06-15 00:45 | 163
2015-06-15 01:00 | 179
2015-06-15 01:15 | 163
2015-06-15 01:30 | 163
2015-06-15 01:45 | 164
2015-06-15 02:00 | 162
2015-06-15 02:15 | 178
2015-06-15 02:30 | 157
2015-06-15 02:45 | 166
2015-06-15 03:00 | 159
2015-06-15 03:15 | 157
2015-06-15 03:30 | 174
2015-06-15 03:45 | 161
2015-06-15 04:00 | 162
2015-06-15 04:15 | 159
2015-06-15 04:30 | 163
2015-06-15 04:45 | 175
2015-06-15 05:00 | 160
2015-06-15 05:15 | 157
2015-06-15 05:30 | 157
2015-06-15 05:45 | 168
2015-06-15 06:00 | 169
2015-06-15 06:15 | 157
2015-06-15 06:30 | 159
2015-06-15 06:45 | 154
2015-06-15 07:00 | 159
2015-06-15 07:15 | 171
2015-06-15 07:30 | 157
2015-06-15 07:45 | 169
2015-06-15 08:00 | 166
2015-06-15 08:15 | 183
2015-06-15 08:30 | 187
2015-06-15 08:45 | 177
2015-06-15 09:00 | 182
2015-06-15 09:15 | 187
2015-06-15 09:30 | 204
2015-06-15 09:45 | 242
2015-06-15 10:00 | 219
2015-06-15 10:15 | 223
2015-06-15 10:30 | 222
2015-06-15 10:45 | 223
2015-06-15 11:00 | 238
2015-06-15 11:15 | 227
2015-06-15 11:30 | 226
2015-06-15 11:45 | 241
2015-06-15 12:00 | 228
2015-06-15 12:15 | 250
2015-06-15 12:30 | 238
2015-06-15 12:45 | 229
2015-06-15 13:00 | 225
2015-06-15 13:15 | 233
2015-06-15 13:30 | 241
2015-06-15 13:45 | 236
2015-06-15 14:00 | 235
2015-06-15 14:15 | 244
2015-06-15 14:30 | 254
2015-06-15 14:45 | 235
2015-06-15 15:00 | 235
2015-06-15 15:15 | 243
2015-06-15 15:30 | 248
2015-06-15 15:45 | 247
2015-06-15 16:00 | 250
2015-06-15 16:15 | 239
2015-06-15 16:30 | 249
2015-06-15 16:45 | 247
2015-06-15 17:00 | 259
2015-06-15 17:15 | 251
2015-06-15 17:30 | 243
2015-06-15 17:45 | 239
2015-06-15 18:00 | 257
2015-06-15 18:15 | 241
2015-06-15 18:30 | 235
2015-06-15 18:45 | 234
2015-06-15 19:00 | 238
2015-06-15 19:15 | 238
2015-06-15 19:30 | 220
2015-06-15 19:45 | 220
2015-06-15 20:00 | 212
2015-06-15 20:15 | 223
2015-06-15 20:30 | 210
2015-06-15 20:45 | 197
2015-06-15 21:00 | 198
2015-06-15 21:15 | 196
2015-06-15 21:30 | 195
2015-06-15 21:45 | 180
2015-06-15 22:00 | 185
2015-06-15 22:15 | 180
2015-06-15 22:30 | 192
2015-06-15 22:45 | 189
2015-06-15 23:00 | 180
2015-06-15 23:15 | 174
2015-06-15 23:30 | 168
2015-06-15 23:45 | 174
2015-06-16 | 175
2015-06-16 00:15 | 161
2015-06-16 00:30 | 161
2015-06-16 00:45 | 158
2015-06-16 01:00 | 161
2015-06-16 01:15 | 169
2015-06-16 01:30 | 166
2015-06-16 01:45 | 154
2015-06-16 02:00 | 151
2015-06-16 02:15 | 154
2015-06-16 02:30 | 153
2015-06-16 02:45 | 159
2015-06-16 03:00 | 138
2015-06-16 03:15 | 150
2015-06-16 03:30 | 155
2015-06-16 03:45 | 167
2015-06-16 04:00 | 137
2015-06-16 04:15 | 143
2015-06-16 04:30 | 136
2015-06-16 04:45 | 139
2015-06-16 05:00 | 148
2015-06-16 05:15 | 143
2015-06-16 05:30 | 137
2015-06-16 05:45 | 137
2015-06-16 06:00 | 139
2015-06-16 06:15 | 152
2015-06-16 06:30 | 149
2015-06-16 06:45 | 154
2015-06-16 07:00 | 139
2015-06-16 07:15 | 155
2015-06-16 07:30 | 158
2015-06-16 07:45 | 170
2015-06-16 08:00 | 174
2015-06-16 08:15 | 174
2015-06-16 08:30 | 174
2015-06-16 08:45 | 187
2015-06-16 09:00 | 201
2015-06-16 09:15 | 189
2015-06-16 09:30 | 213
2015-06-16 09:45 | 203
2015-06-16 10:00 | 214
2015-06-16 10:15 | 234
2015-06-16 10:30 | 218
2015-06-16 10:45 | 214
2015-06-16 11:00 | 176
2015-06-16 11:15 | 188
2015-06-16 11:30 | 200
2015-06-16 11:45 | 208
2015-06-16 12:00 | 200
2015-06-16 12:15 | 195
2015-06-16 12:30 | 194
2015-06-16 12:45 | 219
2015-06-16 13:00 | 245
2015-06-16 13:15 | 228
2015-06-16 13:30 | 240
2015-06-16 13:45 | 226
2015-06-16 14:00 | 243
2015-06-16 14:15 | 235
2015-06-16 14:30 | 229
2015-06-16 14:45 | 227
2015-06-16 15:00 | 228
2015-06-16 15:15 | 237
2015-06-16 15:30 | 246
2015-06-16 15:45 | 233
2015-06-16 16:00 | 237
2015-06-16 16:15 | 242
2015-06-16 16:30 | 240
2015-06-16 16:45 | 245
2015-06-16 17:00 | 250
2015-06-16 17:15 | 243
2015-06-16 17:30 | 237
2015-06-16 17:45 | 231
2015-06-16 18:00 | 248
2015-06-16 18:15 | 228
2015-06-16 18:30 | 247
2015-06-16 18:45 | 230
2015-06-16 19:00 | 231
2015-06-16 19:15 | 225
2015-06-16 19:30 | 218
2015-06-16 19:45 | 224
2015-06-16 20:00 | 208
2015-06-16 20:15 | 212
2015-06-16 20:30 | 218
2015-06-16 20:45 | 206
2015-06-16 21:00 | 200
2015-06-16 21:15 | 191
2015-06-16 21:30 | 189
2015-06-16 21:45 | 191
2015-06-16 22:00 | 202
2015-06-16 22:15 | 184
2015-06-16 22:30 | 176
2015-06-16 22:45 | 179
2015-06-16 23:00 | 188
2015-06-16 23:15 | 174
2015-06-16 23:30 | 164
2015-06-16 23:45 | 160
2015-06-17 | 161
2015-06-17 00:15 | 176
2015-06-17 00:30 | 163
2015-06-17 00:45 | 157
2015-06-17 01:00 | 162
2015-06-17 01:15 | 167
2015-06-17 01:30 | 167
2015-06-17 01:45 | 155
2015-06-17 02:00 | 154
2015-06-17 02:15 | 154
2015-06-17 02:30 | 166
2015-06-17 02:45 | 154
2015-06-17 03:00 | 147
2015-06-17 03:15 | 153
2015-06-17 03:30 | 151
2015-06-17 03:45 | 166
2015-06-17 04:00 | 143
2015-06-17 04:15 | 135
2015-06-17 04:30 | 131
2015-06-17 04:45 | 149
2015-06-17 05:00 | 134
2015-06-17 05:15 | 131
2015-06-17 05:30 | 132
2015-06-17 05:45 | 131
2015-06-17 06:00 | 148
2015-06-17 06:15 | 137
2015-06-17 06:30 | 153
2015-06-17 06:45 | 152
2015-06-17 07:00 | 152
2015-06-17 07:15 | 165
2015-06-17 07:30 | 148
2015-06-17 07:45 | 151
2015-06-17 08:00 | 163
2015-06-17 08:15 | 175
2015-06-17 08:30 | 191
2015-06-17 08:45 | 210
2015-06-17 09:00 | 207
2015-06-17 09:15 | 210
2015-06-17 09:30 | 213
2015-06-17 09:45 | 227
2015-06-17 10:00 | 233
2015-06-17 10:15 | 234
2015-06-17 10:30 | 237
2015-06-17 10:45 | 231
2015-06-17 11:00 | 244
2015-06-17 11:15 | 240
2015-06-17 11:30 | 235
2015-06-17 11:45 | 242
2015-06-17 12:00 | 228
2015-06-17 12:15 | 241
2015-06-17 12:30 | 239
2015-06-17 12:45 | 254
2015-06-17 13:00 | 243
2015-06-17 13:15 | 246
2015-06-17 13:30 | 251
2015-06-17 13:45 | 259
2015-06-17 14:00 | 260
2015-06-17 14:15 | 284
2015-06-17 14:30 | 261
2015-06-17 14:45 | 277
2015-06-17 15:00 | 273
2015-06-17 15:15 | 261
2015-06-17 15:30 | 259
2015-06-17 15:45 | 274
2015-06-17 16:00 | 262
2015-06-17 16:15 | 259
2015-06-17 16:30 | 265
2015-06-17 16:45 | 255
2015-06-17 17:00 | 259
2015-06-17 17:15 | 258
2015-06-17 17:30 | 268
2015-06-17 17:45 | 252
2015-06-17 18:00 | 254
2015-06-17 18:15 | 243
2015-06-17 18:30 | 252
2015-06-17 18:45 | 259
2015-06-17 19:00 | 244
2015-06-17 19:15 | 249
2015-06-17 19:30 | 243
2015-06-17 19:45 | 233
2015-06-17 20:00 | 224
2015-06-17 20:15 | 222
2015-06-17 20:30 | 232
2015-06-17 20:45 | 214
2015-06-17 21:00 | 213
2015-06-17 21:15 | 201
2015-06-17 21:30 | 209
2015-06-17 21:45 | 199
2015-06-17 22:00 | 191
2015-06-17 22:15 | 200
2015-06-17 22:30 | 203
2015-06-17 22:45 | 210
2015-06-17 23:00 | 190
2015-06-17 23:15 | 188
2015-06-17 23:30 | 176
2015-06-17 23:45 | 182
2015-06-18 | 172
2015-06-18 00:15 | 163
2015-06-18 00:30 | 158
2015-06-18 00:45 | 178
2015-06-18 01:00 | 167
2015-06-18 01:15 | 169
2015-06-18 01:30 | 158
2015-06-18 01:45 | 158
2015-06-18 02:00 | 173
2015-06-18 02:15 | 151
2015-06-18 02:30 | 151
2015-06-18 02:45 | 159
2015-06-18 03:00 | 163
2015-06-18 03:15 | 150
2015-06-18 03:30 | 148
2015-06-18 03:45 | 149
2015-06-18 04:00 | 165
2015-06-18 04:15 | 145
2015-06-18 04:30 | 141
2015-06-18 04:45 | 130
2015-06-18 05:00 | 141
2015-06-18 05:15 | 141
2015-06-18 05:30 | 134
2015-06-18 05:45 | 140
2015-06-18 06:00 | 130
2015-06-18 06:15 | 130
2015-06-18 06:30 | 152
2015-06-18 06:45 | 147
2015-06-18 07:00 | 158
2015-06-18 07:15 | 163
2015-06-18 07:30 | 167
2015-06-18 07:45 | 177
2015-06-18 08:00 | 185
2015-06-18 08:15 | 187
2015-06-18 08:30 | 183
2015-06-18 08:45 | 182
2015-06-18 09:00 | 202
2015-06-18 09:15 | 201
2015-06-18 09:30 | 204
2015-06-18 09:45 | 223
2015-06-18 10:00 | 215
2015-06-18 10:15 | 241
2015-06-18 10:30 | 216
2015-06-18 10:45 | 221
2015-06-18 11:00 | 236
2015-06-18 11:15 | 230
2015-06-18 11:30 | 247
2015-06-18 11:45 | 240
2015-06-18 12:00 | 232
2015-06-18 12:15 | 246
2015-06-18 12:30 | 240
2015-06-18 12:45 | 246
2015-06-18 13:00 | 234
2015-06-18 13:15 | 242
2015-06-18 13:30 | 250
2015-06-18 13:45 | 254
2015-06-18 14:00 | 256
2015-06-18 14:15 | 243
2015-06-18 14:30 | 254
2015-06-18 14:45 | 239
2015-06-18 15:00 | 259
2015-06-18 15:15 | 246
2015-06-18 15:30 | 250
2015-06-18 15:45 | 249
2015-06-18 16:00 | 257
2015-06-18 16:15 | 248
2015-06-18 16:30 | 237
2015-06-18 16:45 | 247
2015-06-18 17:00 | 241
2015-06-18 17:15 | 259
2015-06-18 17:30 | 240
2015-06-18 17:45 | 245
2015-06-18 18:00 | 235
2015-06-18 18:15 | 240
2015-06-18 18:30 | 233
2015-06-18 18:45 | 230
2015-06-18 19:00 | 247
2015-06-18 19:15 | 226
2015-06-18 19:30 | 221
2015-06-18 19:45 | 223
2015-06-18 20:00 | 230
2015-06-18 20:15 | 216
2015-06-18 20:30 | 219
2015-06-18 20:45 | 202
2015-06-18 21:00 | 205
2015-06-18 21:15 | 189
2015-06-18 21:30 | 199
2015-06-18 21:45 | 177
2015-06-18 22:00 | 188
2015-06-18 22:15 | 172
2015-06-18 22:30 | 188
2015-06-18 22:45 | 186
2015-06-18 23:00 | 184
2015-06-18 23:15 | 175
2015-06-18 23:30 | 174
2015-06-18 23:45 | 173
2015-06-19 | 180
2015-06-19 00:15 | 169
2015-06-19 00:30 | 171
2015-06-19 00:45 | 167
2015-06-19 01:00 | 176
2015-06-19 01:15 | 180
2015-06-19 01:30 | 177
2015-06-19 01:45 | 165
2015-06-19 02:00 | 159
2015-06-19 02:15 | 158
2015-06-19 02:30 | 156
2015-06-19 02:45 | 164
2015-06-19 03:00 | 156
2015-06-19 03:15 | 159
2015-06-19 03:30 | 154
2015-06-19 03:45 | 158
2015-06-19 04:00 | 156
2015-06-19 04:15 | 168
2015-06-19 04:30 | 146
2015-06-19 04:45 | 146
2015-06-19 05:00 | 144
2015-06-19 05:15 | 147
2015-06-19 05:30 | 145
2015-06-19 05:45 | 143
2015-06-19 06:00 | 148
2015-06-19 06:15 | 140
2015-06-19 06:30 | 146
2015-06-19 06:45 | 156
2015-06-19 07:00 | 166
2015-06-19 07:15 | 170
2015-06-19 07:30 | 164
2015-06-19 07:45 | 167
2015-06-19 08:00 | 170
2015-06-19 08:15 | 175
2015-06-19 08:30 | 181
2015-06-19 08:45 | 191
2015-06-19 09:00 | 204
2015-06-19 09:15 | 194
2015-06-19 09:30 | 196
2015-06-19 09:45 | 210
2015-06-19 10:00 | 207
2015-06-19 10:15 | 210
2015-06-19 10:30 | 206
2015-06-19 10:45 | 213
2015-06-19 11:00 | 225
2015-06-19 11:15 | 207
2015-06-19 11:30 | 216
2015-06-19 11:45 | 217
2015-06-19 12:00 | 218
2015-06-19 12:15 | 238
2015-06-19 12:30 | 227
2015-06-19 12:45 | 223
2015-06-19 13:00 | 235
2015-06-19 13:15 | 226
2015-06-19 13:30 | 242
2015-06-19 13:45 | 237
2015-06-19 14:00 | 239
2015-06-19 14:15 | 237
2015-06-19 14:30 | 247
2015-06-19 14:45 | 241
2015-06-19 15:00 | 246
2015-06-19 15:15 | 238
2015-06-19 15:30 | 246
2015-06-19 15:45 | 244
2015-06-19 16:00 | 248
2015-06-19 16:15 | 243
2015-06-19 16:30 | 247
2015-06-19 16:45 | 234
2015-06-19 17:00 | 236
2015-06-19 17:15 | 244
2015-06-19 17:30 | 259
2015-06-19 17:45 | 240
2015-06-19 18:00 | 246
2015-06-19 18:15 | 230
2015-06-19 18:30 | 244
2015-06-19 18:45 | 240
2015-06-19 19:00 | 230
2015-06-19 19:15 | 227
2015-06-19 19:30 | 224
2015-06-19 19:45 | 218
2015-06-19 20:00 | 211
2015-06-19 20:15 | 223
2015-06-19 20:30 | 216
2015-06-19 20:45 | 209
2015-06-19 21:00 | 205
2015-06-19 21:15 | 194
2015-06-19 21:30 | 186
2015-06-19 21:45 | 197
2015-06-19 22:00 | 178
2015-06-19 22:15 | 178
2015-06-19 22:30 | 173
2015-06-19 22:45 | 186
2015-06-19 23:00 | 176
2015-06-19 23:15 | 179
2015-06-19 23:30 | 163
2015-06-19 23:45 | 175
2015-06-20 | 170
2015-06-20 00:15 | 183
2015-06-20 00:30 | 164
2015-06-20 00:45 | 166
2015-06-20 01:00 | 156
2015-06-20 01:15 | 160
2015-06-20 01:30 | 174
2015-06-20 01:45 | 157
2015-06-20 02:00 | 163
2015-06-20 02:15 | 153
2015-06-20 02:30 | 169
2015-06-20 02:45 | 150
2015-06-20 03:00 | 152
2015-06-20 03:15 | 148
2015-06-20 03:30 | 150
2015-06-20 03:45 | 162
2015-06-20 04:00 | 152
2015-06-20 04:15 | 148
2015-06-20 04:30 | 146
2015-06-20 04:45 | 146
2015-06-20 05:00 | 145
2015-06-20 05:15 | 159
2015-06-20 05:30 | 147
2015-06-20 05:45 | 144
2015-06-20 06:00 | 143
2015-06-20 06:15 | 144
2015-06-20 06:30 | 148
2015-06-20 06:45 | 149
2015-06-20 07:00 | 141
2015-06-20 07:15 | 142
2015-06-20 07:30 | 142
2015-06-20 07:45 | 143
2015-06-20 08:00 | 145
2015-06-20 08:15 | 147
2015-06-20 08:30 | 161
2015-06-20 08:45 | 156
2015-06-20 09:00 | 150
2015-06-20 09:15 | 154
2015-06-20 09:30 | 165
2015-06-20 09:45 | 159
2015-06-20 10:00 | 164
2015-06-20 10:15 | 164
2015-06-20 10:30 | 160
2015-06-20 10:45 | 177
2015-06-20 11:00 | 180
2015-06-20 11:15 | 176
2015-06-20 11:30 | 169
2015-06-20 11:45 | 190
2015-06-20 12:00 | 192
2015-06-20 12:15 | 172
2015-06-20 12:30 | 198
2015-06-20 12:45 | 174
2015-06-20 13:00 | 195
2015-06-20 13:15 | 188
2015-06-20 13:30 | 180
2015-06-20 13:45 | 184
2015-06-20 14:00 | 184
2015-06-20 14:15 | 212
2015-06-20 14:30 | 195
2015-06-20 14:45 | 202
2015-06-20 15:00 | 187
2015-06-20 15:15 | 195
2015-06-20 15:30 | 216
2015-06-20 15:45 | 200
2015-06-20 16:00 | 205
2015-06-20 16:15 | 193
2015-06-20 16:30 | 194
2015-06-20 16:45 | 216
2015-06-20 17:00 | 196
2015-06-20 17:15 | 200
2015-06-20 17:30 | 195
2015-06-20 17:45 | 209
2015-06-20 18:00 | 211
2015-06-20 18:15 | 201
2015-06-20 18:30 | 204
2015-06-20 18:45 | 201
2015-06-20 19:00 | 211
2015-06-20 19:15 | 198
2015-06-20 19:30 | 194
2015-06-20 19:45 | 196
2015-06-20 20:00 | 191
2015-06-20 20:15 | 201
2015-06-20 20:30 | 192
2015-06-20 20:45 | 184
2015-06-20 21:00 | 175
2015-06-20 21:15 | 188
2015-06-20 21:30 | 191
2015-06-20 21:45 | 176
2015-06-20 22:00 | 175
2015-06-20 22:15 | 167
2015-06-20 22:30 | 188
2015-06-20 22:45 | 172
2015-06-20 23:00 | 178
2015-06-20 23:15 | 179
2015-06-20 23:30 | 178
2015-06-20 23:45 | 183
2015-06-21 | 175
2015-06-21 00:15 | 161
2015-06-21 00:30 | 172
2015-06-21 00:45 | 180
2015-06-21 01:00 | 167
2015-06-21 01:15 | 161
2015-06-21 01:30 | 164
2015-06-21 01:45 | 163
2015-06-21 02:00 | 174
2015-06-21 02:15 | 164
2015-06-21 02:30 | 160
2015-06-21 02:45 | 161
2015-06-21 03:00 | 173
2015-06-21 03:15 | 165
2015-06-21 03:30 | 156
2015-06-21 03:45 | 159
2015-06-21 04:00 | 160
2015-06-21 04:15 | 170
2015-06-21 04:30 | 154
2015-06-21 04:45 | 151
2015-06-21 05:00 | 149
2015-06-21 05:15 | 152
2015-06-21 05:30 | 155
2015-06-21 05:45 | 160
2015-06-21 06:00 | 152
2015-06-21 06:15 | 148
2015-06-21 06:30 | 158
2015-06-21 06:45 | 177
2015-06-21 07:00 | 166
2015-06-21 07:15 | 163
2015-06-21 07:30 | 158
2015-06-21 07:45 | 156
2015-06-21 08:00 | 171
2015-06-21 08:15 | 166
2015-06-21 08:30 | 181
2015-06-21 08:45 | 169
2015-06-21 09:00 | 167
2015-06-21 09:15 | 179
2015-06-21 09:30 | 176
2015-06-21 09:45 | 175
2015-06-21 10:00 | 172
2015-06-21 10:15 | 173
2015-06-21 10:30 | 191
2015-06-21 10:45 | 181
2015-06-21 11:00 | 185
2015-06-21 11:15 | 179
2015-06-21 11:30 | 190
2015-06-21 11:45 | 207
2015-06-21 12:00 | 191
2015-06-21 12:15 | 187
2015-06-21 12:30 | 189
2015-06-21 12:45 | 189
2015-06-21 13:00 | 203
2015-06-21 13:15 | 191
2015-06-21 13:30 | 190
2015-06-21 13:45 | 187
2015-06-21 14:00 | 203
2015-06-21 14:15 | 193
2015-06-21 14:30 | 187
2015-06-21 14:45 | 192
2015-06-21 15:00 | 194
2015-06-21 15:15 | 209
2015-06-21 15:30 | 201
2015-06-21 15:45 | 204
2015-06-21 16:00 | 194
2015-06-21 16:15 | 199
2015-06-21 16:30 | 216
2015-06-21 16:45 | 203
2015-06-21 17:00 | 207
2015-06-21 17:15 | 211
2015-06-21 17:30 | 213
2015-06-21 17:45 | 220
2015-06-21 18:00 | 204
2015-06-21 18:15 | 199
2015-06-21 18:30 | 204
2015-06-21 18:45 | 201
2015-06-21 19:00 | 213
2015-06-21 19:15 | 199
2015-06-21 19:30 | 197
2015-06-21 19:45 | 197
2015-06-21 20:00 | 200
2015-06-21 20:15 | 200
2015-06-21 20:30 | 194
2015-06-21 20:45 | 178
2015-06-21 21:00 | 188
2015-06-21 21:15 | 188
2015-06-21 21:30 | 174
2015-06-21 21:45 | 163
2015-06-21 22:00 | 157
2015-06-21 22:15 | 170
2015-06-21 22:30 | 165
2015-06-21 22:45 | 157
2015-06-21 23:00 | 159
2015-06-21 23:15 | 160
2015-06-21 23:30 | 164
2015-06-21 23:45 | 171
2015-06-22 | 168
2015-06-22 00:15 | 159
2015-06-22 00:30 | 158
2015-06-22 00:45 | 159
2015-06-22 01:00 | 164
2015-06-22 01:15 | 166
2015-06-22 01:30 | 155
2015-06-22 01:45 | 149
2015-06-22 02:00 | 149
2015-06-22 02:15 | 143
2015-06-22 02:30 | 150
2015-06-22 02:45 | 136
2015-06-22 03:00 | 145
2015-06-22 03:15 | 134
2015-06-22 03:30 | 137
2015-06-22 03:45 | 138
2015-06-22 04:00 | 144
2015-06-22 04:15 | 136
2015-06-22 04:30 | 138
2015-06-22 04:45 | 134
2015-06-22 05:00 | 135
2015-06-22 05:15 | 142
2015-06-22 05:30 | 153
2015-06-22 05:45 | 148
2015-06-22 06:00 | 152
2015-06-22 06:15 | 150
2015-06-22 06:30 | 149
2015-06-22 06:45 | 151
2015-06-22 07:00 | 156
2015-06-22 07:15 | 160
2015-06-22 07:30 | 165
2015-06-22 07:45 | 156
2015-06-22 08:00 | 156
2015-06-22 08:15 | 167
2015-06-22 08:30 | 176
2015-06-22 08:45 | 186
2015-06-22 09:00 | 183
2015-06-22 09:15 | 200
2015-06-22 09:30 | 190
2015-06-22 09:45 | 211
2015-06-22 10:00 | 210
2015-06-22 10:15 | 217
2015-06-22 10:30 | 211
2015-06-22 10:45 | 202
2015-06-22 11:00 | 199
2015-06-22 11:15 | 208
2015-06-22 11:30 | 221
2015-06-22 11:45 | 213
2015-06-22 12:00 | 217
2015-06-22 12:15 | 213
2015-06-22 12:30 | 232
2015-06-22 12:45 | 211
2015-06-22 13:00 | 218
2015-06-22 13:15 | 219
2015-06-22 13:30 | 225
2015-06-22 13:45 | 225
2015-06-22 14:00 | 220
2015-06-22 14:15 | 219
2015-06-22 14:30 | 220
2015-06-22 14:45 | 219
2015-06-22 15:00 | 225
2015-06-22 15:15 | 229
2015-06-22 15:30 | 216
2015-06-22 15:45 | 219
2015-06-22 16:00 | 216
2015-06-22 16:15 | 235
2015-06-22 16:30 | 234
2015-06-22 16:45 | 220
2015-06-22 17:00 | 221
2015-06-22 17:15 | 228
2015-06-22 17:30 | 237
2015-06-22 17:45 | 217
2015-06-22 18:00 | 226
2015-06-22 18:15 | 217
2015-06-22 18:30 | 227
2015-06-22 18:45 | 226
2015-06-22 19:00 | 211
2015-06-22 19:15 | 217
2015-06-22 19:30 | 215
2015-06-22 19:45 | 209
2015-06-22 20:00 | 223
2015-06-22 20:15 | 200
2015-06-22 20:30 | 202
2015-06-22 20:45 | 196
2015-06-22 21:00 | 209
2015-06-22 21:15 | 182
2015-06-22 21:30 | 177
2015-06-22 21:45 | 190
2015-06-22 22:00 | 194
2015-06-22 22:15 | 185
2015-06-22 22:30 | 181
2015-06-22 22:45 | 174
2015-06-22 23:00 | 182
2015-06-22 23:15 | 177
2015-06-22 23:30 | 177
2015-06-22 23:45 | 172
2015-06-23 | 162
2015-06-23 00:15 | 177
2015-06-23 00:30 | 173
2015-06-23 00:45 | 162
2015-06-23 01:00 | 160
2015-06-23 01:15 | 160
2015-06-23 01:30 | 162
2015-06-23 01:45 | 166
2015-06-23 02:00 | 155
2015-06-23 02:15 | 150
2015-06-23 02:30 | 159
2015-06-23 02:45 | 157
2015-06-23 03:00 | 149
2015-06-23 03:15 | 150
2015-06-23 03:30 | 148
2015-06-23 03:45 | 148
2015-06-23 04:00 | 158
2015-06-23 04:15 | 155
2015-06-23 04:30 | 146
2015-06-23 04:45 | 141
2015-06-23 05:00 | 135
2015-06-23 05:15 | 133
2015-06-23 05:30 | 145
2015-06-23 05:45 | 138
2015-06-23 06:00 | 136
2015-06-23 06:15 | 129
2015-06-23 06:30 | 143
2015-06-23 06:45 | 152
2015-06-23 07:00 | 164
2015-06-23 07:15 | 155
2015-06-23 07:30 | 158
2015-06-23 07:45 | 156
2015-06-23 08:00 | 177
2015-06-23 08:15 | 178
2015-06-23 08:30 | 187
2015-06-23 08:45 | 190
2015-06-23 09:00 | 188
2015-06-23 09:15 | 186
2015-06-23 09:30 | 210
2015-06-23 09:45 | 205
2015-06-23 10:00 | 200
2015-06-23 10:15 | 209
2015-06-23 10:30 | 219
2015-06-23 10:45 | 215
2015-06-23 11:00 | 215
2015-06-23 11:15 | 209
2015-06-23 11:30 | 215
2015-06-23 11:45 | 226
2015-06-23 12:00 | 224
2015-06-23 12:15 | 220
2015-06-23 12:30 | 218
2015-06-23 12:45 | 217
2015-06-23 13:00 | 231
2015-06-23 13:15 | 234
2015-06-23 13:30 | 232
2015-06-23 13:45 | 231
2015-06-23 14:00 | 231
2015-06-23 14:15 | 249
2015-06-23 14:30 | 245
2015-06-23 14:45 | 233
2015-06-23 15:00 | 233
2015-06-23 15:15 | 239
2015-06-23 15:30 | 256
2015-06-23 15:45 | 253
2015-06-23 16:00 | 251
2015-06-23 16:15 | 254
2015-06-23 16:30 | 251
2015-06-23 16:45 | 268
2015-06-23 17:00 | 254
2015-06-23 17:15 | 261
2015-06-23 17:30 | 245
2015-06-23 17:45 | 244
2015-06-23 18:00 | 250
2015-06-23 18:15 | 249
2015-06-23 18:30 | 230
2015-06-23 18:45 | 237
2015-06-23 19:00 | 231
2015-06-23 19:15 | 236
2015-06-23 19:30 | 229
2015-06-23 19:45 | 221
2015-06-23 20:00 | 218
2015-06-23 20:15 | 216
2015-06-23 20:30 | 226
2015-06-23 20:45 | 205
2015-06-23 21:00 | 206
2015-06-23 21:15 | 195
2015-06-23 21:30 | 198
2015-06-23 21:45 | 202
2015-06-23 22:00 | 183
2015-06-23 22:15 | 184
2015-06-23 22:30 | 190
2015-06-23 22:45 | 189
2015-06-23 23:00 | 184
2015-06-23 23:15 | 165
2015-06-23 23:30 | 170
2015-06-23 23:45 | 165
2015-06-24 | 184
2015-06-24 00:15 | 164
2015-06-24 00:30 | 163
2015-06-24 00:45 | 170
2015-06-24 01:00 | 171
2015-06-24 01:15 | 163
2015-06-24 01:30 | 164
2015-06-24 01:45 | 158
2015-06-24 02:00 | 157
2015-06-24 02:15 | 163
2015-06-24 02:30 | 157
2015-06-24 02:45 | 150
2015-06-24 03:00 | 151
2015-06-24 03:15 | 151
2015-06-24 03:30 | 150
2015-06-24 03:45 | 165
2015-06-24 04:00 | 149
2015-06-24 04:15 | 148
2015-06-24 04:30 | 143
2015-06-24 04:45 | 149
2015-06-24 05:00 | 147
2015-06-24 05:15 | 153
2015-06-24 05:30 | 149
2015-06-24 05:45 | 145
2015-06-24 06:00 | 138
2015-06-24 06:15 | 142
2015-06-24 06:30 | 150
2015-06-24 06:45 | 159
2015-06-24 07:00 | 152
2015-06-24 07:15 | 154
2015-06-24 07:30 | 151
2015-06-24 07:45 | 154
2015-06-24 08:00 | 163
2015-06-24 08:15 | 167
2015-06-24 08:30 | 168
2015-06-24 08:45 | 176
2015-06-24 09:00 | 190
2015-06-24 09:15 | 179
2015-06-24 09:30 | 199
2015-06-24 09:45 | 199
2015-06-24 10:00 | 192
2015-06-24 10:15 | 202
2015-06-24 10:30 | 203
2015-06-24 10:45 | 209
2015-06-24 11:00 | 226
2015-06-24 11:15 | 207
2015-06-24 11:30 | 216
2015-06-24 11:45 | 218
2015-06-24 12:00 | 219
2015-06-24 12:15 | 240
2015-06-24 12:30 | 223
2015-06-24 12:45 | 222
2015-06-24 13:00 | 225
2015-06-24 13:15 | 235
2015-06-24 13:30 | 244
2015-06-24 13:45 | 248
2015-06-24 14:00 | 238
2015-06-24 14:15 | 250
2015-06-24 14:30 | 259
2015-06-24 14:45 | 272
2015-06-24 15:00 | 254
2015-06-24 15:15 | 262
2015-06-24 15:30 | 257
2015-06-24 15:45 | 285
2015-06-24 16:00 | 272
2015-06-24 16:15 | 269
2015-06-24 16:30 | 259
2015-06-24 16:45 | 263
2015-06-24 17:00 | 263
2015-06-24 17:15 | 285
2015-06-24 17:30 | 262
2015-06-24 17:45 | 264
2015-06-24 18:00 | 245
2015-06-24 18:15 | 265
2015-06-24 18:30 | 251
2015-06-24 18:45 | 253
2015-06-24 19:00 | 245
2015-06-24 19:15 | 239
2015-06-24 19:30 | 243
2015-06-24 19:45 | 253
2015-06-24 20:00 | 229
2015-06-24 20:15 | 228
2015-06-24 20:30 | 222
2015-06-24 20:45 | 227
2015-06-24 21:00 | 216
2015-06-24 21:15 | 201
2015-06-24 21:30 | 198
2015-06-24 21:45 | 200
2015-06-24 22:00 | 207
2015-06-24 22:15 | 198
2015-06-24 22:30 | 192
2015-06-24 22:45 | 200
2015-06-24 23:00 | 200
2015-06-24 23:15 | 204
2015-06-24 23:30 | 191
2015-06-24 23:45 | 183
2015-06-25 | 190
2015-06-25 00:15 | 200
2015-06-25 00:30 | 182
2015-06-25 00:45 | 180
2015-06-25 01:00 | 176
2015-06-25 01:15 | 173
2015-06-25 01:30 | 193
2015-06-25 01:45 | 178
2015-06-25 02:00 | 183
2015-06-25 02:15 | 172
2015-06-25 02:30 | 188
2015-06-25 02:45 | 177
2015-06-25 03:00 | 170
2015-06-25 03:15 | 163
2015-06-25 03:30 | 177
2015-06-25 03:45 | 186
2015-06-25 04:00 | 170
2015-06-25 04:15 | 174
2015-06-25 04:30 | 164
2015-06-25 04:45 | 181
2015-06-25 05:00 | 172
2015-06-25 05:15 | 172
2015-06-25 05:30 | 160
2015-06-25 05:45 | 164
2015-06-25 06:00 | 179
2015-06-25 06:15 | 170
2015-06-25 06:30 | 166
2015-06-25 06:45 | 176
2015-06-25 07:00 | 171
2015-06-25 07:15 | 196
2015-06-25 07:30 | 184
2015-06-25 07:45 | 179
2015-06-25 08:00 | 182
2015-06-25 08:15 | 191
2015-06-25 08:30 | 213
2015-06-25 08:45 | 198
2015-06-25 09:00 | 201
2015-06-25 09:15 | 201
2015-06-25 09:30 | 202
2015-06-25 09:45 | 227
2015-06-25 10:00 | 217
2015-06-25 10:15 | 221
2015-06-25 10:30 | 223
2015-06-25 10:45 | 239
2015-06-25 11:00 | 236
2015-06-25 11:15 | 230
2015-06-25 11:30 | 248
2015-06-25 11:45 | 238
2015-06-25 12:00 | 263
2015-06-25 12:15 | 259
2015-06-25 12:30 | 258
2015-06-25 12:45 | 252
2015-06-25 13:00 | 267
2015-06-25 13:15 | 270
2015-06-25 13:30 | 290
2015-06-25 13:45 | 263
2015-06-25 14:00 | 275
2015-06-25 14:15 | 263
2015-06-25 14:30 | 279
2015-06-25 14:45 | 298
2015-06-25 15:00 | 287
2015-06-25 15:15 | 292
2015-06-25 15:30 | 285
2015-06-25 15:45 | 284
2015-06-25 16:00 | 302
2015-06-25 16:15 | 280
2015-06-25 16:30 | 289
2015-06-25 16:45 | 270
2015-06-25 17:00 | 278
2015-06-25 17:15 | 287
2015-06-25 17:30 | 286
2015-06-25 17:45 | 278
2015-06-25 18:00 | 280
2015-06-25 18:15 | 270
2015-06-25 18:30 | 276
2015-06-25 18:45 | 283
2015-06-25 19:00 | 269
2015-06-25 19:15 | 264
2015-06-25 19:30 | 261
2015-06-25 19:45 | 257
2015-06-25 20:00 | 256
2015-06-25 20:15 | 262
2015-06-25 20:30 | 237
2015-06-25 20:45 | 237
2015-06-25 21:00 | 238
2015-06-25 21:15 | 213
2015-06-25 21:30 | 231
2015-06-25 21:45 | 206
2015-06-25 22:00 | 213
2015-06-25 22:15 | 209
2015-06-25 22:30 | 226
2015-06-25 22:45 | 218
2015-06-25 23:00 | 212
2015-06-25 23:15 | 208
2015-06-25 23:30 | 208
2015-06-25 23:45 | 219
2015-06-26 | 205
2015-06-26 00:15 | 202
2015-06-26 00:30 | 198
2015-06-26 00:45 | 211
2015-06-26 01:00 | 200
2015-06-26 01:15 | 192
2015-06-26 01:30 | 194
2015-06-26 01:45 | 189
2015-06-26 02:00 | 208
2015-06-26 02:15 | 185
2015-06-26 02:30 | 184
2015-06-26 02:45 | 182
2015-06-26 03:00 | 187
2015-06-26 03:15 | 193
2015-06-26 03:30 | 185
2015-06-26 03:45 | 177
2015-06-26 04:00 | 175
2015-06-26 04:15 | 193
2015-06-26 04:30 | 185
2015-06-26 04:45 | 175
2015-06-26 05:00 | 177
2015-06-26 05:15 | 180
2015-06-26 05:30 | 186
2015-06-26 05:45 | 176
2015-06-26 06:00 | 182
2015-06-26 06:15 | 171
2015-06-26 06:30 | 186
2015-06-26 06:45 | 186
2015-06-26 07:00 | 179
2015-06-26 07:15 | 179
2015-06-26 07:30 | 176
2015-06-26 07:45 | 192
2015-06-26 08:00 | 202
2015-06-26 08:15 | 190
2015-06-26 08:30 | 201
2015-06-26 08:45 | 200
2015-06-26 09:00 | 211
2015-06-26 09:15 | 212
2015-06-26 09:30 | 207
2015-06-26 09:45 | 217
2015-06-26 10:00 | 225
2015-06-26 10:15 | 237
2015-06-26 10:30 | 229
2015-06-26 10:45 | 237
2015-06-26 11:00 | 246
2015-06-26 11:15 | 244
2015-06-26 11:30 | 275
2015-06-26 11:45 | 258
2015-06-26 12:00 | 258
2015-06-26 12:15 | 253
2015-06-26 12:30 | 256
2015-06-26 12:45 | 273
2015-06-26 13:00 | 271
2015-06-26 13:15 | 274
2015-06-26 13:30 | 270
2015-06-26 13:45 | 261
2015-06-26 14:00 | 275
2015-06-26 14:15 | 289
2015-06-26 14:30 | 289
2015-06-26 14:45 | 271
2015-06-26 15:00 | 268
2015-06-26 15:15 | 271
2015-06-26 15:30 | 277
2015-06-26 15:45 | 269
2015-06-26 16:00 | 270
2015-06-26 16:15 | 275
2015-06-26 16:30 | 277
2015-06-26 16:45 | 270
2015-06-26 17:00 | 276
2015-06-26 17:15 | 271
2015-06-26 17:30 | 270
2015-06-26 17:45 | 261
2015-06-26 18:00 | 265
2015-06-26 18:15 | 265
2015-06-26 18:30 | 263
2015-06-26 18:45 | 265
2015-06-26 19:00 | 255
2015-06-26 19:15 | 257
2015-06-26 19:30 | 252
2015-06-26 19:45 | 245
2015-06-26 20:00 | 254
2015-06-26 20:15 | 241
2015-06-26 20:30 | 229
2015-06-26 20:45 | 225
2015-06-26 21:00 | 218
2015-06-26 21:15 | 209
2015-06-26 21:30 | 200
2015-06-26 21:45 | 200
2015-06-26 22:00 | 198
2015-06-26 22:15 | 195
2015-06-26 22:30 | 196
2015-06-26 22:45 | 192
2015-06-26 23:00 | 192
2015-06-26 23:15 | 191
2015-06-26 23:30 | 186
2015-06-26 23:45 | 193
2015-06-27 | 183
2015-06-27 00:15 | 181
2015-06-27 00:30 | 181
2015-06-27 00:45 | 195
2015-06-27 01:00 | 178
2015-06-27 01:15 | 179
2015-06-27 01:30 | 177
2015-06-27 01:45 | 175
2015-06-27 02:00 | 185
2015-06-27 02:15 | 173
2015-06-27 02:30 | 175
2015-06-27 02:45 | 178
2015-06-27 03:00 | 174
2015-06-27 03:15 | 179
2015-06-27 03:30 | 175
2015-06-27 03:45 | 170
2015-06-27 04:00 | 160
2015-06-27 04:15 | 168
2015-06-27 04:30 | 170
2015-06-27 04:45 | 173
2015-06-27 05:00 | 161
2015-06-27 05:15 | 165
2015-06-27 05:30 | 172
2015-06-27 05:45 | 166
2015-06-27 06:00 | 171
2015-06-27 06:15 | 154
2015-06-27 06:30 | 165
2015-06-27 06:45 | 169
2015-06-27 07:00 | 178
2015-06-27 07:15 | 165
2015-06-27 07:30 | 166
2015-06-27 07:45 | 172
2015-06-27 08:00 | 170
2015-06-27 08:15 | 170
2015-06-27 08:30 | 177
2015-06-27 08:45 | 181
2015-06-27 09:00 | 167
2015-06-27 09:15 | 176
2015-06-27 09:30 | 169
2015-06-27 09:45 | 192
2015-06-27 10:00 | 190
2015-06-27 10:15 | 188
2015-06-27 10:30 | 192
2015-06-27 10:45 | 205
2015-06-27 11:00 | 208
2015-06-27 11:15 | 211
2015-06-27 11:30 | 212
2015-06-27 11:45 | 227
2015-06-27 12:00 | 228
2015-06-27 12:15 | 226
2015-06-27 12:30 | 236
2015-06-27 12:45 | 233
2015-06-27 13:00 | 238
2015-06-27 13:15 | 262
2015-06-27 13:30 | 245
2015-06-27 13:45 | 249
2015-06-27 14:00 | 249
2015-06-27 14:15 | 248
2015-06-27 14:30 | 247
2015-06-27 14:45 | 254
2015-06-27 15:00 | 248
2015-06-27 15:15 | 260
2015-06-27 15:30 | 260
2015-06-27 15:45 | 269
2015-06-27 16:00 | 259
2015-06-27 16:15 | 270
2015-06-27 16:30 | 265
2015-06-27 16:45 | 258
2015-06-27 17:00 | 274
2015-06-27 17:15 | 258
2015-06-27 17:30 | 270
2015-06-27 17:45 | 259
2015-06-27 18:00 | 269
2015-06-27 18:15 | 249
2015-06-27 18:30 | 263
2015-06-27 18:45 | 247
2015-06-27 19:00 | 257
2015-06-27 19:15 | 238
2015-06-27 19:30 | 245
2015-06-27 19:45 | 247
2015-06-27 20:00 | 236
2015-06-27 20:15 | 240
2015-06-27 20:30 | 237
2015-06-27 20:45 | 228
2015-06-27 21:00 | 229
2015-06-27 21:15 | 212
2015-06-27 21:30 | 209
2015-06-27 21:45 | 203
2015-06-27 22:00 | 202
2015-06-27 22:15 | 199
2015-06-27 22:30 | 197
2015-06-27 22:45 | 203
2015-06-27 23:00 | 201
2015-06-27 23:15 | 197
2015-06-27 23:30 | 197
2015-06-27 23:45 | 195
2015-06-28 | 192
2015-06-28 00:15 | 196
2015-06-28 00:30 | 191
2015-06-28 00:45 | 196
2015-06-28 01:00 | 195
2015-06-28 01:15 | 189
2015-06-28 01:30 | 203
2015-06-28 01:45 | 188
2015-06-28 02:00 | 190
2015-06-28 02:15 | 188
2015-06-28 02:30 | 193
2015-06-28 02:45 | 193
2015-06-28 03:00 | 190
2015-06-28 03:15 | 190
2015-06-28 03:30 | 187
2015-06-28 03:45 | 192
2015-06-28 04:00 | 189
2015-06-28 04:15 | 190
2015-06-28 04:30 | 187
2015-06-28 04:45 | 187
2015-06-28 05:00 | 182
2015-06-28 05:15 | 184
2015-06-28 05:30 | 191
2015-06-28 05:45 | 183
2015-06-28 06:00 | 189
2015-06-28 06:15 | 183
2015-06-28 06:30 | 201
2015-06-28 06:45 | 200
2015-06-28 07:00 | 200
2015-06-28 07:15 | 203
2015-06-28 07:30 | 199
2015-06-28 07:45 | 203
2015-06-28 08:00 | 199
2015-06-28 08:15 | 202
2015-06-28 08:30 | 197
2015-06-28 08:45 | 208
2015-06-28 09:00 | 197
2015-06-28 09:15 | 208
2015-06-28 09:30 | 209
2015-06-28 09:45 | 206
2015-06-28 10:00 | 201
2015-06-28 10:15 | 215
2015-06-28 10:30 | 218
2015-06-28 10:45 | 213
2015-06-28 11:00 | 214
2015-06-28 11:15 | 221
2015-06-28 11:30 | 221
2015-06-28 11:45 | 233
2015-06-28 12:00 | 231
2015-06-28 12:15 | 219
2015-06-28 12:30 | 237
2015-06-28 12:45 | 225
2015-06-28 13:00 | 223
2015-06-28 13:15 | 222
2015-06-28 13:30 | 227
2015-06-28 13:45 | 224
2015-06-28 14:00 | 233
2015-06-28 14:15 | 226
2015-06-28 14:30 | 235
2015-06-28 14:45 | 221
2015-06-28 15:00 | 238
2015-06-28 15:15 | 222
2015-06-28 15:30 | 231
2015-06-28 15:45 | 233
2015-06-28 16:00 | 225
2015-06-28 16:15 | 240
2015-06-28 16:30 | 233
2015-06-28 16:45 | 236
2015-06-28 17:00 | 237
2015-06-28 17:15 | 254
2015-06-28 17:30 | 243
2015-06-28 17:45 | 243
2015-06-28 18:00 | 243
2015-06-28 18:15 | 243
2015-06-28 18:30 | 241
2015-06-28 18:45 | 249
2015-06-28 19:00 | 238
2015-06-28 19:15 | 240
2015-06-28 19:30 | 234
2015-06-28 19:45 | 233
2015-06-28 20:00 | 223
2015-06-28 20:15 | 215
2015-06-28 20:30 | 221
2015-06-28 20:45 | 212
2015-06-28 21:00 | 210
2015-06-28 21:15 | 204
2015-06-28 21:30 | 194
2015-06-28 21:45 | 193
2015-06-28 22:00 | 196
2015-06-28 22:15 | 193
2015-06-28 22:30 | 193
2015-06-28 22:45 | 192
2015-06-28 23:00 | 191
2015-06-28 23:15 | 188
2015-06-28 23:30 | 185
2015-06-28 23:45 | 191
2015-06-29 | 181
2015-06-29 00:15 | 184
2015-06-29 00:30 | 192
2015-06-29 00:45 | 175
2015-06-29 01:00 | 174
2015-06-29 01:15 | 181
2015-06-29 01:30 | 185
2015-06-29 01:45 | 170
2015-06-29 02:00 | 178
2015-06-29 02:15 | 176
2015-06-29 02:30 | 179
2015-06-29 02:45 | 170
2015-06-29 03:00 | 174
2015-06-29 03:15 | 177
2015-06-29 03:30 | 178
2015-06-29 03:45 | 175
2015-06-29 04:00 | 168
2015-06-29 04:15 | 172
2015-06-29 04:30 | 174
2015-06-29 04:45 | 171
2015-06-29 05:00 | 165
2015-06-29 05:15 | 171
2015-06-29 05:30 | 170
2015-06-29 05:45 | 170
2015-06-29 06:00 | 164
2015-06-29 06:15 | 167
2015-06-29 06:30 | 168
2015-06-29 06:45 | 161
2015-06-29 07:00 | 173
2015-06-29 07:15 | 173
2015-06-29 07:30 | 156
2015-06-29 07:45 | 169
2015-06-29 08:00 | 172
2015-06-29 08:15 | 177
2015-06-29 08:30 | 192
2015-06-29 08:45 | 193
2015-06-29 09:00 | 187
2015-06-29 09:15 | 197
2015-06-29 09:30 | 211
2015-06-29 09:45 | 205
2015-06-29 10:00 | 208
2015-06-29 10:15 | 219
2015-06-29 10:30 | 218
2015-06-29 10:45 | 227
2015-06-29 11:00 | 223
2015-06-29 11:15 | 223
2015-06-29 11:30 | 221
2015-06-29 11:45 | 230
2015-06-29 12:00 | 233
2015-06-29 12:15 | 236
2015-06-29 12:30 | 241
2015-06-29 12:45 | 250
2015-06-29 13:00 | 237
2015-06-29 13:15 | 244
2015-06-29 13:30 | 242
2015-06-29 13:45 | 258
2015-06-29 14:00 | 253
2015-06-29 14:15 | 254
2015-06-29 14:30 | 254
2015-06-29 14:45 | 261
2015-06-29 15:00 | 250
2015-06-29 15:15 | 259
2015-06-29 15:30 | 267
2015-06-29 15:45 | 279
2015-06-29 16:00 | 264
2015-06-29 16:15 | 274
2015-06-29 16:30 | 270
2015-06-29 16:45 | 274
2015-06-29 17:00 | 285
2015-06-29 17:15 | 274
2015-06-29 17:30 | 271
2015-06-29 17:45 | 263
2015-06-29 18:00 | 274
2015-06-29 18:15 | 259
2015-06-29 18:30 | 276
2015-06-29 18:45 | 255
2015-06-29 19:00 | 255
2015-06-29 19:15 | 249
2015-06-29 19:30 | 255
2015-06-29 19:45 | 248
2015-06-29 20:00 | 245
2015-06-29 20:15 | 248
2015-06-29 20:30 | 247
2015-06-29 20:45 | 233
2015-06-29 21:00 | 233
2015-06-29 21:15 | 215
2015-06-29 21:30 | 209
2015-06-29 21:45 | 209
2015-06-29 22:00 | 202
2015-06-29 22:15 | 201
2015-06-29 22:30 | 201
2015-06-29 22:45 | 200
2015-06-29 23:00 | 211
2015-06-29 23:15 | 191
2015-06-29 23:30 | 192
2015-06-29 23:45 | 191
2015-06-30 | 186
2015-06-30 00:15 | 195
2015-06-30 00:30 | 189
2015-06-30 00:45 | 183
2015-06-30 01:00 | 186
2015-06-30 01:15 | 183
2015-06-30 01:30 | 182
2015-06-30 01:45 | 192
2015-06-30 02:00 | 185
2015-06-30 02:15 | 179
2015-06-30 02:30 | 178
2015-06-30 02:45 | 186
2015-06-30 03:00 | 175
2015-06-30 03:15 | 173
2015-06-30 03:30 | 172
2015-06-30 03:45 | 191
2015-06-30 04:00 | 181
2015-06-30 04:15 | 176
2015-06-30 04:30 | 178
2015-06-30 04:45 | 178
2015-06-30 05:00 | 185
2015-06-30 05:15 | 170
2015-06-30 05:30 | 179
2015-06-30 05:45 | 173
2015-06-30 06:00 | 180
2015-06-30 06:15 | 172
2015-06-30 06:30 | 178
2015-06-30 06:45 | 180
2015-06-30 07:00 | 182
2015-06-30 07:15 | 189
2015-06-30 07:30 | 179
2015-06-30 07:45 | 186
2015-06-30 08:00 | 192
2015-06-30 08:15 | 207
2015-06-30 08:30 | 199
2015-06-30 08:45 | 202
2015-06-30 09:00 | 211
2015-06-30 09:15 | 213
2015-06-30 09:30 | 223
2015-06-30 09:45 | 224
2015-06-30 10:00 | 233
2015-06-30 10:15 | 240
2015-06-30 10:30 | 249
2015-06-30 10:45 | 257
2015-06-30 11:00 | 246
2015-06-30 11:15 | 272
2015-06-30 11:30 | 259
2015-06-30 11:45 | 276
2015-06-30 12:00 | 274
2015-06-30 12:15 | 274
2015-06-30 12:30 | 268
2015-06-30 12:45 | 282
2015-06-30 13:00 | 279
2015-06-30 13:15 | 276
2015-06-30 13:30 | 279
2015-06-30 13:45 | 286
2015-06-30 14:00 | 284
2015-06-30 14:15 | 280
2015-06-30 14:30 | 285
2015-06-30 14:45 | 288
2015-06-30 15:00 | 293
2015-06-30 15:15 | 293
2015-06-30 15:30 | 290
2015-06-30 15:45 | 299
2015-06-30 16:00 | 312
2015-06-30 16:15 | 310
2015-06-30 16:30 | 315
2015-06-30 16:45 | 308
2015-06-30 17:00 | 314
2015-06-30 17:15 | 310
2015-06-30 17:30 | 311
2015-06-30 17:45 | 305
2015-06-30 18:00 | 298
2015-06-30 18:15 | 282
2015-06-30 18:30 | 290
2015-06-30 18:45 | 291
2015-06-30 19:00 | 285
2015-06-30 19:15 | 277
2015-06-30 19:30 | 268
2015-06-30 19:45 | 270
2015-06-30 20:00 | 276
2015-06-30 20:15 | 265
2015-06-30 20:30 | 250
2015-06-30 20:45 | 250
2015-06-30 21:00 | 246
2015-06-30 21:15 | 232
2015-06-30 21:30 | 230
2015-06-30 21:45 | 243
2015-06-30 22:00 | 222
2015-06-30 22:15 | 216
2015-06-30 22:30 | 221
2015-06-30 22:45 | 221
2015-06-30 23:00 | 232
2015-06-30 23:15 | 221
2015-06-30 23:30 | 213
2015-06-30 23:45 | 212
2015-07-01 | 204
2015-07-01 00:15 | 216
2015-07-01 00:30 | 210
2015-07-01 00:45 | 205
2015-07-01 01:00 | 209
2015-07-01 01:15 | 206
2015-07-01 01:30 | 194
2015-07-01 01:45 | 198
2015-07-01 02:00 | 190
2015-07-01 02:15 | 201
2015-07-01 02:30 | 202
2015-07-01 02:45 | 207
2015-07-01 03:00 | 190
2015-07-01 03:15 | 196
2015-07-01 03:30 | 193
2015-07-01 03:45 | 192
2015-07-01 04:00 | 200
2015-07-01 04:15 | 193
2015-07-01 04:30 | 193
2015-07-01 04:45 | 184
2015-07-01 05:00 | 195
2015-07-01 05:15 | 190
2015-07-01 05:30 | 186
2015-07-01 05:45 | 194
2015-07-01 06:00 | 187
2015-07-01 06:15 | 184
2015-07-01 06:30 | 186
2015-07-01 06:45 | 181
2015-07-01 07:00 | 198
2015-07-01 07:15 | 190
2015-07-01 07:30 | 190
2015-07-01 07:45 | 193
2015-07-01 08:00 | 199
2015-07-01 08:15 | 205
2015-07-01 08:30 | 208
2015-07-01 08:45 | 220
2015-07-01 09:00 | 225
2015-07-01 09:15 | 228
2015-07-01 09:30 | 237
2015-07-01 09:45 | 235
2015-07-01 10:00 | 238
2015-07-01 10:15 | 265
2015-07-01 10:30 | 245
2015-07-01 10:45 | 263
2015-07-01 11:00 | 264
2015-07-01 11:15 | 282
2015-07-01 11:30 | 278
2015-07-01 11:45 | 285
2015-07-01 12:00 | 286
2015-07-01 12:15 | 295
2015-07-01 12:30 | 300
2015-07-01 12:45 | 295
2015-07-01 13:00 | 298
2015-07-01 13:15 | 295
2015-07-01 13:30 | 297
2015-07-01 13:45 | 296
2015-07-01 14:00 | 294
2015-07-01 14:15 | 292
2015-07-01 14:30 | 292
2015-07-01 14:45 | 294
2015-07-01 15:00 | 293
2015-07-01 15:15 | 303
2015-07-01 15:30 | 300
2015-07-01 15:45 | 294
2015-07-01 16:00 | 299
2015-07-01 16:15 | 300
2015-07-01 16:30 | 309
2015-07-01 16:45 | 313
2015-07-01 17:00 | 304
2015-07-01 17:15 | 301
2015-07-01 17:30 | 286
2015-07-01 17:45 | 290
2015-07-01 18:00 | 276
2015-07-01 18:15 | 280
2015-07-01 18:30 | 265
2015-07-01 18:45 | 259
2015-07-01 19:00 | 254
2015-07-01 19:15 | 262
2015-07-01 19:30 | 248
2015-07-01 19:45 | 249
2015-07-01 20:00 | 246
2015-07-01 20:15 | 247
2015-07-01 20:30 | 249
2015-07-01 20:45 | 231
2015-07-01 21:00 | 242
2015-07-01 21:15 | 238
2015-07-01 21:30 | 218
2015-07-01 21:45 | 217
2015-07-01 22:00 | 215
2015-07-01 22:15 | 210
2015-07-01 22:30 | 217
2015-07-01 22:45 | 220
2015-07-01 23:00 | 226
2015-07-01 23:15 | 205
2015-07-01 23:30 | 206
2015-07-01 23:45 | 208
2015-07-02 | 207
2015-07-02 00:15 | 219
2015-07-02 00:30 | 219
2015-07-02 00:45 | 220
2015-07-02 01:00 | 210
2015-07-02 01:15 | 210
2015-07-02 01:30 | 210
2015-07-02 01:45 | 205
2015-07-02 02:00 | 215
2015-07-02 02:15 | 201
2015-07-02 02:30 | 220
2015-07-02 02:45 | 207
2015-07-02 03:00 | 207
2015-07-02 03:15 | 196
2015-07-02 03:30 | 208
2015-07-02 03:45 | 199
2015-07-02 04:00 | 202
2015-07-02 04:15 | 202
2015-07-02 04:30 | 200
2015-07-02 04:45 | 201
2015-07-02 05:00 | 191
2015-07-02 05:15 | 198
2015-07-02 05:30 | 201
2015-07-02 05:45 | 190
2015-07-02 06:00 | 197
2015-07-02 06:15 | 194
2015-07-02 06:30 | 191
2015-07-02 06:45 | 193
2015-07-02 07:00 | 194
2015-07-02 07:15 | 189
2015-07-02 07:30 | 186
2015-07-02 07:45 | 190
2015-07-02 08:00 | 199
2015-07-02 08:15 | 195
2015-07-02 08:30 | 197
2015-07-02 08:45 | 206
2015-07-02 09:00 | 221
2015-07-02 09:15 | 216
2015-07-02 09:30 | 220
2015-07-02 09:45 | 230
2015-07-02 10:00 | 231
2015-07-02 10:15 | 232
2015-07-02 10:30 | 243
2015-07-02 10:45 | 253
2015-07-02 11:00 | 248
2015-07-02 11:15 | 259
2015-07-02 11:30 | 251
2015-07-02 11:45 | 268
2015-07-02 12:00 | 259
2015-07-02 12:15 | 272
2015-07-02 12:30 | 264
2015-07-02 12:45 | 267
2015-07-02 13:00 | 258
2015-07-02 13:15 | 269
2015-07-02 13:30 | 263
2015-07-02 13:45 | 272
2015-07-02 14:00 | 268
2015-07-02 14:15 | 275
2015-07-02 14:30 | 271
2015-07-02 14:45 | 274
2015-07-02 15:00 | 277
2015-07-02 15:15 | 263
2015-07-02 15:30 | 280
2015-07-02 15:45 | 281
2015-07-02 16:00 | 273
2015-07-02 16:15 | 273
2015-07-02 16:30 | 274
2015-07-02 16:45 | 271
2015-07-02 17:00 | 263
2015-07-02 17:15 | 271
2015-07-02 17:30 | 262
2015-07-02 17:45 | 258
2015-07-02 18:00 | 240
2015-07-02 18:15 | 257
2015-07-02 18:30 | 242
2015-07-02 18:45 | 249
2015-07-02 19:00 | 241
2015-07-02 19:15 | 239
2015-07-02 19:30 | 252
2015-07-02 19:45 | 244
2015-07-02 20:00 | 242
2015-07-02 20:15 | 233
2015-07-02 20:30 | 235
2015-07-02 20:45 | 230
2015-07-02 21:00 | 221
2015-07-02 21:15 | 210
2015-07-02 21:30 | 205
2015-07-02 21:45 | 202
2015-07-02 22:00 | 193
2015-07-02 22:15 | 208
2015-07-02 22:30 | 195
2015-07-02 22:45 | 198
2015-07-02 23:00 | 196
2015-07-02 23:15 | 194
2015-07-02 23:30 | 200
2015-07-02 23:45 | 197
2015-07-03 | 189
2015-07-03 00:15 | 192
2015-07-03 00:30 | 189
2015-07-03 00:45 | 188
2015-07-03 01:00 | 188
2015-07-03 01:15 | 191
2015-07-03 01:30 | 184
2015-07-03 01:45 | 183
2015-07-03 02:00 | 190
2015-07-03 02:15 | 185
2015-07-03 02:30 | 186
2015-07-03 02:45 | 183
2015-07-03 03:00 | 185
2015-07-03 03:15 | 186
2015-07-03 03:30 | 184
2015-07-03 03:45 | 181
2015-07-03 04:00 | 185
2015-07-03 04:15 | 191
2015-07-03 04:30 | 182
2015-07-03 04:45 | 182
2015-07-03 05:00 | 185
2015-07-03 05:15 | 189
2015-07-03 05:30 | 182
2015-07-03 05:45 | 183
2015-07-03 06:00 | 183
2015-07-03 06:15 | 182
2015-07-03 06:30 | 183
2015-07-03 06:45 | 188
2015-07-03 07:00 | 182
2015-07-03 07:15 | 180
2015-07-03 07:30 | 186
2015-07-03 07:45 | 180
2015-07-03 08:00 | 183
2015-07-03 08:15 | 191
2015-07-03 08:30 | 183
2015-07-03 08:45 | 185
2015-07-03 09:00 | 189
2015-07-03 09:15 | 190
2015-07-03 09:30 | 196
2015-07-03 09:45 | 198
2015-07-03 10:00 | 200
2015-07-03 10:15 | 204
2015-07-03 10:30 | 214
2015-07-03 10:45 | 217
2015-07-03 11:00 | 208
2015-07-03 11:15 | 211
2015-07-03 11:30 | 223
2015-07-03 11:45 | 219
2015-07-03 12:00 | 218
2015-07-03 12:15 | 233
2015-07-03 12:30 | 221
2015-07-03 12:45 | 241
2015-07-03 13:00 | 227
2015-07-03 13:15 | 233
2015-07-03 13:30 | 233
2015-07-03 13:45 | 238
2015-07-03 14:00 | 232
2015-07-03 14:15 | 236
2015-07-03 14:30 | 234
2015-07-03 14:45 | 246
2015-07-03 15:00 | 236
2015-07-03 15:15 | 246
2015-07-03 15:30 | 248
2015-07-03 15:45 | 249
2015-07-03 16:00 | 240
2015-07-03 16:15 | 252
2015-07-03 16:30 | 239
2015-07-03 16:45 | 245
2015-07-03 17:00 | 254
2015-07-03 17:15 | 253
2015-07-03 17:30 | 247
2015-07-03 17:45 | 243
2015-07-03 18:00 | 246
2015-07-03 18:15 | 245
2015-07-03 18:30 | 249
2015-07-03 18:45 | 242
2015-07-03 19:00 | 230
2015-07-03 19:15 | 243
2015-07-03 19:30 | 234
2015-07-03 19:45 | 239
2015-07-03 20:00 | 233
2015-07-03 20:15 | 236
2015-07-03 20:30 | 221
2015-07-03 20:45 | 213
2015-07-03 21:00 | 210
2015-07-03 21:15 | 207
2015-07-03 21:30 | 215
2015-07-03 21:45 | 200
2015-07-03 22:00 | 195
2015-07-03 22:15 | 201
2015-07-03 22:30 | 199
2015-07-03 22:45 | 201
2015-07-03 23:00 | 203
2015-07-03 23:15 | 189
2015-07-03 23:30 | 201
2015-07-03 23:45 | 190
2015-07-04 | 191
2015-07-04 00:15 | 196
2015-07-04 00:30 | 197
2015-07-04 00:45 | 188
2015-07-04 01:00 | 190
2015-07-04 01:15 | 185
2015-07-04 01:30 | 183
2015-07-04 01:45 | 189
2015-07-04 02:00 | 184
2015-07-04 02:15 | 184
2015-07-04 02:30 | 182
2015-07-04 02:45 | 189
2015-07-04 03:00 | 187
2015-07-04 03:15 | 179
2015-07-04 03:30 | 186
2015-07-04 03:45 | 185
2015-07-04 04:00 | 183
2015-07-04 04:15 | 185
2015-07-04 04:30 | 180
2015-07-04 04:45 | 187
2015-07-04 05:00 | 184
2015-07-04 05:15 | 183
2015-07-04 05:30 | 183
2015-07-04 05:45 | 185
2015-07-04 06:00 | 189
2015-07-04 06:15 | 181
2015-07-04 06:30 | 181
2015-07-04 06:45 | 178
2015-07-04 07:00 | 181
2015-07-04 07:15 | 183
2015-07-04 07:30 | 182
2015-07-04 07:45 | 180
2015-07-04 08:00 | 176
2015-07-04 08:15 | 183
2015-07-04 08:30 | 181
2015-07-04 08:45 | 179
2015-07-04 09:00 | 185
2015-07-04 09:15 | 190
2015-07-04 09:30 | 187
2015-07-04 09:45 | 190
2015-07-04 10:00 | 205
2015-07-04 10:15 | 204
2015-07-04 10:30 | 208
2015-07-04 10:45 | 208
2015-07-04 11:00 | 211
2015-07-04 11:15 | 218
2015-07-04 11:30 | 222
2015-07-04 11:45 | 219
2015-07-04 12:00 | 222
2015-07-04 12:15 | 233
2015-07-04 12:30 | 223
2015-07-04 12:45 | 224
2015-07-04 13:00 | 232
2015-07-04 13:15 | 227
2015-07-04 13:30 | 227
2015-07-04 13:45 | 236
2015-07-04 14:00 | 229
2015-07-04 14:15 | 236
2015-07-04 14:30 | 224
2015-07-04 14:45 | 236
2015-07-04 15:00 | 229
2015-07-04 15:15 | 242
2015-07-04 15:30 | 233
2015-07-04 15:45 | 245
2015-07-04 16:00 | 238
2015-07-04 16:15 | 245
2015-07-04 16:30 | 234
2015-07-04 16:45 | 243
2015-07-04 17:00 | 238
2015-07-04 17:15 | 245
2015-07-04 17:30 | 239
2015-07-04 17:45 | 242
2015-07-04 18:00 | 228
2015-07-04 18:15 | 236
2015-07-04 18:30 | 236
2015-07-04 18:45 | 241
2015-07-04 19:00 | 226
2015-07-04 19:15 | 236
2015-07-04 19:30 | 232
2015-07-04 19:45 | 231
2015-07-04 20:00 | 219
2015-07-04 20:15 | 223
2015-07-04 20:30 | 205
2015-07-04 20:45 | 202
2015-07-04 21:00 | 204
2015-07-04 21:15 | 203
2015-07-04 21:30 | 207
2015-07-04 21:45 | 195
2015-07-04 22:00 | 199
2015-07-04 22:15 | 194
2015-07-04 22:30 | 202
2015-07-04 22:45 | 194
2015-07-04 23:00 | 188
2015-07-04 23:15 | 203
2015-07-04 23:30 | 187
2015-07-04 23:45 | 192
2015-07-05 | 194
2015-07-05 00:15 | 185
2015-07-05 00:30 | 190
2015-07-05 00:45 | 193
2015-07-05 01:00 | 186
2015-07-05 01:15 | 188
2015-07-05 01:30 | 193
2015-07-05 01:45 | 185
2015-07-05 02:00 | 181
2015-07-05 02:15 | 198
2015-07-05 02:30 | 192
2015-07-05 02:45 | 183
2015-07-05 03:00 | 184
2015-07-05 03:15 | 182
2015-07-05 03:30 | 174
2015-07-05 03:45 | 177
2015-07-05 04:00 | 176
2015-07-05 04:15 | 179
2015-07-05 04:30 | 174
2015-07-05 04:45 | 170
2015-07-05 05:00 | 179
2015-07-05 05:15 | 173
2015-07-05 05:30 | 177
2015-07-05 05:45 | 171
2015-07-05 06:00 | 177
2015-07-05 06:15 | 178
2015-07-05 06:30 | 175
2015-07-05 06:45 | 178
2015-07-05 07:00 | 168
2015-07-05 07:15 | 169
2015-07-05 07:30 | 172
2015-07-05 07:45 | 166
2015-07-05 08:00 | 171
2015-07-05 08:15 | 167
2015-07-05 08:30 | 175
2015-07-05 08:45 | 172
2015-07-05 09:00 | 172
2015-07-05 09:15 | 172
2015-07-05 09:30 | 177
2015-07-05 09:45 | 175
2015-07-05 10:00 | 180
2015-07-05 10:15 | 188
2015-07-05 10:30 | 197
2015-07-05 10:45 | 193
2015-07-05 11:00 | 191
2015-07-05 11:15 | 205
2015-07-05 11:30 | 202
2015-07-05 11:45 | 209
2015-07-05 12:00 | 217
2015-07-05 12:15 | 216
2015-07-05 12:30 | 215
2015-07-05 12:45 | 209
2015-07-05 13:00 | 215
2015-07-05 13:15 | 222
2015-07-05 13:30 | 226
2015-07-05 13:45 | 213
2015-07-05 14:00 | 225
2015-07-05 14:15 | 222
2015-07-05 14:30 | 228
2015-07-05 14:45 | 232
2015-07-05 15:00 | 228
2015-07-05 15:15 | 229
2015-07-05 15:30 | 232
2015-07-05 15:45 | 235
2015-07-05 16:00 | 228
2015-07-05 16:15 | 237
2015-07-05 16:30 | 231
2015-07-05 16:45 | 239
2015-07-05 17:00 | 238
2015-07-05 17:15 | 251
2015-07-05 17:30 | 236
2015-07-05 17:45 | 249
2015-07-05 18:00 | 234
2015-07-05 18:15 | 237
2015-07-05 18:30 | 235
2015-07-05 18:45 | 232
2015-07-05 19:00 | 232
2015-07-05 19:15 | 237
2015-07-05 19:30 | 229
2015-07-05 19:45 | 224
2015-07-05 20:00 | 217
2015-07-05 20:15 | 206
2015-07-05 20:30 | 210
2015-07-05 20:45 | 204
2015-07-05 21:00 | 200
2015-07-05 21:15 | 189
2015-07-05 21:30 | 193
2015-07-05 21:45 | 186
2015-07-05 22:00 | 192
2015-07-05 22:15 | 184
2015-07-05 22:30 | 179
2015-07-05 22:45 | 189
2015-07-05 23:00 | 177
2015-07-05 23:15 | 185
2015-07-05 23:30 | 180
2015-07-05 23:45 | 176
2015-07-06 | 186
2015-07-06 00:15 | 172
2015-07-06 00:30 | 178
2015-07-06 00:45 | 172
2015-07-06 01:00 | 182
2015-07-06 01:15 | 172
2015-07-06 01:30 | 176
2015-07-06 01:45 | 181
2015-07-06 02:00 | 168
2015-07-06 02:15 | 179
2015-07-06 02:30 | 174
2015-07-06 02:45 | 180
2015-07-06 03:00 | 173
2015-07-06 03:15 | 177
2015-07-06 03:30 | 175
2015-07-06 03:45 | 175
2015-07-06 04:00 | 169
2015-07-06 04:15 | 172
2015-07-06 04:30 | 176
2015-07-06 04:45 | 177
2015-07-06 05:00 | 175
2015-07-06 05:15 | 165
2015-07-06 05:30 | 177
2015-07-06 05:45 | 167
2015-07-06 06:00 | 178
2015-07-06 06:15 | 164
2015-07-06 06:30 | 177
2015-07-06 06:45 | 176
2015-07-06 07:00 | 171
2015-07-06 07:15 | 172
2015-07-06 07:30 | 167
2015-07-06 07:45 | 175
2015-07-06 08:00 | 181
2015-07-06 08:15 | 187
2015-07-06 08:30 | 193
2015-07-06 08:45 | 195
2015-07-06 09:00 | 203
2015-07-06 09:15 | 212
2015-07-06 09:30 | 218
2015-07-06 09:45 | 215
2015-07-06 10:00 | 225
2015-07-06 10:15 | 218
2015-07-06 10:30 | 221
2015-07-06 10:45 | 225
2015-07-06 11:00 | 238
2015-07-06 11:15 | 244
2015-07-06 11:30 | 239
2015-07-06 11:45 | 238
2015-07-06 12:00 | 241
2015-07-06 12:15 | 250
2015-07-06 12:30 | 251
2015-07-06 12:45 | 246
2015-07-06 13:00 | 244
2015-07-06 13:15 | 253
2015-07-06 13:30 | 252
2015-07-06 13:45 | 250
2015-07-06 14:00 | 250
2015-07-06 14:15 | 256
2015-07-06 14:30 | 261
2015-07-06 14:45 | 258
2015-07-06 15:00 | 253
2015-07-06 15:15 | 257
2015-07-06 15:30 | 270
2015-07-06 15:45 | 264
2015-07-06 16:00 | 259
2015-07-06 16:15 | 263
2015-07-06 16:30 | 258
2015-07-06 16:45 | 278
2015-07-06 17:00 | 271
2015-07-06 17:15 | 276
2015-07-06 17:30 | 265
2015-07-06 17:45 | 278
2015-07-06 18:00 | 260
2015-07-06 18:15 | 275
2015-07-06 18:30 | 262
2015-07-06 18:45 | 269
2015-07-06 19:00 | 251
2015-07-06 19:15 | 256
2015-07-06 19:30 | 257
2015-07-06 19:45 | 256
2015-07-06 20:00 | 248
2015-07-06 20:15 | 251
2015-07-06 20:30 | 241
2015-07-06 20:45 | 238
2015-07-06 21:00 | 225
2015-07-06 21:15 | 213
2015-07-06 21:30 | 219
2015-07-06 21:45 | 217
2015-07-06 22:00 | 204
2015-07-06 22:15 | 206
2015-07-06 22:30 | 200
2015-07-06 22:45 | 200
2015-07-06 23:00 | 207
2015-07-06 23:15 | 198
2015-07-06 23:30 | 208
2015-07-06 23:45 | 196
2015-07-07 | 194
2015-07-07 00:15 | 193
2015-07-07 00:30 | 191
2015-07-07 00:45 | 193
2015-07-07 01:00 | 191
2015-07-07 01:15 | 185
2015-07-07 01:30 | 182
2015-07-07 01:45 | 190
2015-07-07 02:00 | 177
2015-07-07 02:15 | 184
2015-07-07 02:30 | 188
2015-07-07 02:45 | 185
2015-07-07 03:00 | 174
2015-07-07 03:15 | 170
2015-07-07 03:30 | 176
2015-07-07 03:45 | 181
2015-07-07 04:00 | 176
2015-07-07 04:15 | 182
2015-07-07 04:30 | 183
2015-07-07 04:45 | 180
2015-07-07 05:00 | 176
2015-07-07 05:15 | 176
2015-07-07 05:30 | 177
2015-07-07 05:45 | 180
2015-07-07 06:00 | 180
2015-07-07 06:15 | 172
2015-07-07 06:30 | 186
2015-07-07 06:45 | 181
2015-07-07 07:00 | 183
2015-07-07 07:15 | 187
2015-07-07 07:30 | 178
2015-07-07 07:45 | 195
2015-07-07 08:00 | 191
2015-07-07 08:15 | 195
2015-07-07 08:30 | 188
2015-07-07 08:45 | 205
2015-07-07 09:00 | 204
2015-07-07 09:15 | 202
2015-07-07 09:30 | 213
2015-07-07 09:45 | 215
2015-07-07 10:00 | 215
2015-07-07 10:15 | 219
2015-07-07 10:30 | 224
2015-07-07 10:45 | 225
2015-07-07 11:00 | 225
2015-07-07 11:15 | 229
2015-07-07 11:30 | 228
2015-07-07 11:45 | 235
2015-07-07 12:00 | 232
2015-07-07 12:15 | 239
2015-07-07 12:30 | 246
2015-07-07 12:45 | 242
2015-07-07 13:00 | 260
2015-07-07 13:15 | 241
2015-07-07 13:30 | 258
2015-07-07 13:45 | 252
2015-07-07 14:00 | 263
2015-07-07 14:15 | 261
2015-07-07 14:30 | 268
2015-07-07 14:45 | 262
2015-07-07 15:00 | 274
2015-07-07 15:15 | 263
2015-07-07 15:30 | 273
2015-07-07 15:45 | 267
2015-07-07 16:00 | 279
2015-07-07 16:15 | 266
2015-07-07 16:30 | 267
2015-07-07 16:45 | 253
2015-07-07 17:00 | 276
2015-07-07 17:15 | 268
2015-07-07 17:30 | 270
2015-07-07 17:45 | 260
2015-07-07 18:00 | 271
2015-07-07 18:15 | 257
2015-07-07 18:30 | 264
2015-07-07 18:45 | 256
2015-07-07 19:00 | 264
2015-07-07 19:15 | 252
2015-07-07 19:30 | 238
2015-07-07 19:45 | 238
2015-07-07 20:00 | 238
2015-07-07 20:15 | 241
2015-07-07 20:30 | 230
2015-07-07 20:45 | 221
2015-07-07 21:00 | 221
2015-07-07 21:15 | 212
2015-07-07 21:30 | 210
2015-07-07 21:45 | 210
2015-07-07 22:00 | 193
2015-07-07 22:15 | 199
2015-07-07 22:30 | 191
2015-07-07 22:45 | 189
2015-07-07 23:00 | 192
2015-07-07 23:15 | 181
2015-07-07 23:30 | 178
2015-07-07 23:45 | 178
2015-07-08 | 174
2015-07-08 00:15 | 165
2015-07-08 00:30 | 188
2015-07-08 00:45 | 180
2015-07-08 01:00 | 177
2015-07-08 01:15 | 175
2015-07-08 01:30 | 175
2015-07-08 01:45 | 181
2015-07-08 02:00 | 176
2015-07-08 02:15 | 173
2015-07-08 02:30 | 177
2015-07-08 02:45 | 170
2015-07-08 03:00 | 167
2015-07-08 03:15 | 170
2015-07-08 03:30 | 176
2015-07-08 03:45 | 168
2015-07-08 04:00 | 166
2015-07-08 04:15 | 161
2015-07-08 04:30 | 170
2015-07-08 04:45 | 159
2015-07-08 05:00 | 180
2015-07-08 05:15 | 160
2015-07-08 05:30 | 162
2015-07-08 05:45 | 160
2015-07-08 06:00 | 166
2015-07-08 06:15 | 167
2015-07-08 06:30 | 166
2015-07-08 06:45 | 162
2015-07-08 07:00 | 164
2015-07-08 07:15 | 172
2015-07-08 07:30 | 182
2015-07-08 07:45 | 167
2015-07-08 08:00 | 168
2015-07-08 08:15 | 190
2015-07-08 08:30 | 189
2015-07-08 08:45 | 204
2015-07-08 09:00 | 196
2015-07-08 09:15 | 201
2015-07-08 09:30 | 215
2015-07-08 09:45 | 209
2015-07-08 10:00 | 208
2015-07-08 10:15 | 206
2015-07-08 10:30 | 202
2015-07-08 10:45 | 219
2015-07-08 11:00 | 221
2015-07-08 11:15 | 212
2015-07-08 11:30 | 229
2015-07-08 11:45 | 218
2015-07-08 12:00 | 225
2015-07-08 12:15 | 223
2015-07-08 12:30 | 229
2015-07-08 12:45 | 227
2015-07-08 13:00 | 236
2015-07-08 13:15 | 231
2015-07-08 13:30 | 233
2015-07-08 13:45 | 236
2015-07-08 14:00 | 238
2015-07-08 14:15 | 240
2015-07-08 14:30 | 253
2015-07-08 14:45 | 242
2015-07-08 15:00 | 245
2015-07-08 15:15 | 240
2015-07-08 15:30 | 245
2015-07-08 15:45 | 248
2015-07-08 16:00 | 241
2015-07-08 16:15 | 238
2015-07-08 16:30 | 247
2015-07-08 16:45 | 240
2015-07-08 17:00 | 249
2015-07-08 17:15 | 260
2015-07-08 17:30 | 246
2015-07-08 17:45 | 245
2015-07-08 18:00 | 242
2015-07-08 18:15 | 227
2015-07-08 18:30 | 233
2015-07-08 18:45 | 228
2015-07-08 19:00 | 223
2015-07-08 19:15 | 223
2015-07-08 19:30 | 227
2015-07-08 19:45 | 227
2015-07-08 20:00 | 216
2015-07-08 20:15 | 206
2015-07-08 20:30 | 211
2015-07-08 20:45 | 209
2015-07-08 21:00 | 209
2015-07-08 21:15 | 179
2015-07-08 21:30 | 178
2015-07-08 21:45 | 189
2015-07-08 22:00 | 185
2015-07-08 22:15 | 187
2015-07-08 22:30 | 198
2015-07-08 22:45 | 192
2015-07-08 23:00 | 191
2015-07-08 23:15 | 191
2015-07-08 23:30 | 190
2015-07-08 23:45 | 189
2015-07-09 | 182
2015-07-09 00:15 | 177
2015-07-09 00:30 | 185
2015-07-09 00:45 | 167
2015-07-09 01:00 | 171
2015-07-09 01:15 | 173
2015-07-09 01:30 | 174
2015-07-09 01:45 | 181
2015-07-09 02:00 | 173
2015-07-09 02:15 | 168
2015-07-09 02:30 | 165
2015-07-09 02:45 | 171
2015-07-09 03:00 | 165
2015-07-09 03:15 | 177
2015-07-09 03:30 | 172
2015-07-09 03:45 | 165
2015-07-09 04:00 | 167
2015-07-09 04:15 | 174
2015-07-09 04:30 | 170
2015-07-09 04:45 | 165
2015-07-09 05:00 | 174
2015-07-09 05:15 | 165
2015-07-09 05:30 | 172
2015-07-09 05:45 | 168
2015-07-09 06:00 | 164
2015-07-09 06:15 | 171
2015-07-09 06:30 | 162
2015-07-09 06:45 | 180
2015-07-09 07:00 | 179
2015-07-09 07:15 | 177
2015-07-09 07:30 | 171
2015-07-09 07:45 | 178
2015-07-09 08:00 | 192
2015-07-09 08:15 | 186
2015-07-09 08:30 | 189
2015-07-09 08:45 | 193
2015-07-09 09:00 | 203
2015-07-09 09:15 | 199
2015-07-09 09:30 | 195
2015-07-09 09:45 | 203
2015-07-09 10:00 | 200
2015-07-09 10:15 | 213
2015-07-09 10:30 | 214
2015-07-09 10:45 | 208
2015-07-09 11:00 | 213
2015-07-09 11:15 | 214
2015-07-09 11:30 | 207
2015-07-09 11:45 | 217
2015-07-09 12:00 | 207
2015-07-09 12:15 | 232
2015-07-09 12:30 | 219
2015-07-09 12:45 | 220
2015-07-09 13:00 | 224
2015-07-09 13:15 | 226
2015-07-09 13:30 | 230
2015-07-09 13:45 | 234
2015-07-09 14:00 | 229
2015-07-09 14:15 | 235
2015-07-09 14:30 | 238
2015-07-09 14:45 | 232
2015-07-09 15:00 | 241
2015-07-09 15:15 | 242
2015-07-09 15:30 | 248
2015-07-09 15:45 | 227
2015-07-09 16:00 | 233
2015-07-09 16:15 | 231
2015-07-09 16:30 | 238
2015-07-09 16:45 | 237
2015-07-09 17:00 | 226
2015-07-09 17:15 | 223
2015-07-09 17:30 | 226
2015-07-09 17:45 | 216
2015-07-09 18:00 | 226
2015-07-09 18:15 | 217
2015-07-09 18:30 | 225
2015-07-09 18:45 | 217
2015-07-09 19:00 | 210
2015-07-09 19:15 | 208
2015-07-09 19:30 | 206
2015-07-09 19:45 | 211
2015-07-09 20:00 | 214
2015-07-09 20:15 | 204
2015-07-09 20:30 | 210
2015-07-09 20:45 | 210
2015-07-09 21:00 | 201
2015-07-09 21:15 | 187
2015-07-09 21:30 | 189
2015-07-09 21:45 | 200
2015-07-09 22:00 | 201
2015-07-09 22:15 | 190
2015-07-09 22:30 | 196
2015-07-09 22:45 | 194
2015-07-09 23:00 | 193
2015-07-09 23:15 | 183
2015-07-09 23:30 | 188
2015-07-09 23:45 | 187
2015-07-10 | 188
2015-07-10 00:15 | 197
2015-07-10 00:30 | 189
2015-07-10 00:45 | 189
2015-07-10 01:00 | 184
2015-07-10 01:15 | 194
2015-07-10 01:30 | 194
2015-07-10 01:45 | 177
2015-07-10 02:00 | 179
2015-07-10 02:15 | 186
2015-07-10 02:30 | 174
2015-07-10 02:45 | 181
2015-07-10 03:00 | 175
2015-07-10 03:15 | 178
2015-07-10 03:30 | 183
2015-07-10 03:45 | 170
2015-07-10 04:00 | 167
2015-07-10 04:15 | 176
2015-07-10 04:30 | 186
2015-07-10 04:45 | 170
2015-07-10 05:00 | 174
2015-07-10 05:15 | 177
2015-07-10 05:30 | 180
2015-07-10 05:45 | 177
2015-07-10 06:00 | 167
2015-07-10 06:15 | 173
2015-07-10 06:30 | 172
2015-07-10 06:45 | 188
2015-07-10 07:00 | 183
2015-07-10 07:15 | 186
2015-07-10 07:30 | 182
2015-07-10 07:45 | 180
2015-07-10 08:00 | 192
2015-07-10 08:15 | 194
2015-07-10 08:30 | 192
2015-07-10 08:45 | 195
2015-07-10 09:00 | 199
2015-07-10 09:15 | 204
2015-07-10 09:30 | 212
2015-07-10 09:45 | 205
2015-07-10 10:00 | 206
2015-07-10 10:15 | 207
2015-07-10 10:30 | 212
2015-07-10 10:45 | 224
2015-07-10 11:00 | 211
2015-07-10 11:15 | 214
2015-07-10 11:30 | 218
2015-07-10 11:45 | 223
2015-07-10 12:00 | 224
2015-07-10 12:15 | 217
2015-07-10 12:30 | 234
2015-07-10 12:45 | 220
2015-07-10 13:00 | 217
2015-07-10 13:15 | 235
2015-07-10 13:30 | 226
2015-07-10 13:45 | 237
2015-07-10 14:00 | 234
2015-07-10 14:15 | 229
2015-07-10 14:30 | 227
2015-07-10 14:45 | 231
2015-07-10 15:00 | 240
2015-07-10 15:15 | 243
2015-07-10 15:30 | 249
2015-07-10 15:45 | 232
2015-07-10 16:00 | 238
2015-07-10 16:15 | 232
2015-07-10 16:30 | 235
2015-07-10 16:45 | 238
2015-07-10 17:00 | 235
2015-07-10 17:15 | 237
2015-07-10 17:30 | 227
2015-07-10 17:45 | 230
2015-07-10 18:00 | 228
2015-07-10 18:15 | 216
2015-07-10 18:30 | 229
2015-07-10 18:45 | 223
2015-07-10 19:00 | 213
2015-07-10 19:15 | 213
2015-07-10 19:30 | 215
2015-07-10 19:45 | 215
2015-07-10 20:00 | 209
2015-07-10 20:15 | 220
2015-07-10 20:30 | 205
2015-07-10 20:45 | 203
2015-07-10 21:00 | 199
2015-07-10 21:15 | 190
2015-07-10 21:30 | 197
2015-07-10 21:45 | 175
2015-07-10 22:00 | 179
2015-07-10 22:15 | 181
2015-07-10 22:30 | 185
2015-07-10 22:45 | 177
2015-07-10 23:00 | 172
2015-07-10 23:15 | 177
2015-07-10 23:30 | 178
2015-07-10 23:45 | 171
2015-07-11 | 179
2015-07-11 00:15 | 168
2015-07-11 00:30 | 164
2015-07-11 00:45 | 168
2015-07-11 01:00 | 181
2015-07-11 01:15 | 168
2015-07-11 01:30 | 168
2015-07-11 01:45 | 170
2015-07-11 02:00 | 175
2015-07-11 02:15 | 171
2015-07-11 02:30 | 161
2015-07-11 02:45 | 166
2015-07-11 03:00 | 158
2015-07-11 03:15 | 179
2015-07-11 03:30 | 169
2015-07-11 03:45 | 159
2015-07-11 04:00 | 164
2015-07-11 04:15 | 174
2015-07-11 04:30 | 184
2015-07-11 04:45 | 164
2015-07-11 05:00 | 170
2015-07-11 05:15 | 169
2015-07-11 05:30 | 173
2015-07-11 05:45 | 185
2015-07-11 06:00 | 162
2015-07-11 06:15 | 159
2015-07-11 06:30 | 158
2015-07-11 06:45 | 169
2015-07-11 07:00 | 170
2015-07-11 07:15 | 161
2015-07-11 07:30 | 174
2015-07-11 07:45 | 159
2015-07-11 08:00 | 157
2015-07-11 08:15 | 171
2015-07-11 08:30 | 185
2015-07-11 08:45 | 177
2015-07-11 09:00 | 171
2015-07-11 09:15 | 170
2015-07-11 09:30 | 172
2015-07-11 09:45 | 175
2015-07-11 10:00 | 195
2015-07-11 10:15 | 181
2015-07-11 10:30 | 179
2015-07-11 10:45 | 184
2015-07-11 11:00 | 193
2015-07-11 11:15 | 193
2015-07-11 11:30 | 185
2015-07-11 11:45 | 193
2015-07-11 12:00 | 200
2015-07-11 12:15 | 191
2015-07-11 12:30 | 194
2015-07-11 12:45 | 201
2015-07-11 13:00 | 209
2015-07-11 13:15 | 204
2015-07-11 13:30 | 209
2015-07-11 13:45 | 199
2015-07-11 14:00 | 202
2015-07-11 14:15 | 212
2015-07-11 14:30 | 219
2015-07-11 14:45 | 210
2015-07-11 15:00 | 219
2015-07-11 15:15 | 214
2015-07-11 15:30 | 227
2015-07-11 15:45 | 225
2015-07-11 16:00 | 232
2015-07-11 16:15 | 224
2015-07-11 16:30 | 226
2015-07-11 16:45 | 234
2015-07-11 17:00 | 234
2015-07-11 17:15 | 240
2015-07-11 17:30 | 234
2015-07-11 17:45 | 224
2015-07-11 18:00 | 224
2015-07-11 18:15 | 226
2015-07-11 18:30 | 216
2015-07-11 18:45 | 222
2015-07-11 19:00 | 225
2015-07-11 19:15 | 212
2015-07-11 19:30 | 210
2015-07-11 19:45 | 209
2015-07-11 20:00 | 223
2015-07-11 20:15 | 203
2015-07-11 20:30 | 199
2015-07-11 20:45 | 199
2015-07-11 21:00 | 204
2015-07-11 21:15 | 193
2015-07-11 21:30 | 184
2015-07-11 21:45 | 195
2015-07-11 22:00 | 180
2015-07-11 22:15 | 176
2015-07-11 22:30 | 177
2015-07-11 22:45 | 183
2015-07-11 23:00 | 187
2015-07-11 23:15 | 183
2015-07-11 23:30 | 177
2015-07-11 23:45 | 172
2015-07-12 | 179
2015-07-12 00:15 | 178
2015-07-12 00:30 | 162
2015-07-12 00:45 | 170
2015-07-12 01:00 | 174
2015-07-12 01:15 | 160
2015-07-12 01:30 | 159
2015-07-12 01:45 | 161
2015-07-12 02:00 | 175
2015-07-12 02:15 | 164
2015-07-12 02:30 | 156
2015-07-12 02:45 | 162
2015-07-12 03:00 | 160
2015-07-12 03:15 | 178
2015-07-12 03:30 | 173
2015-07-12 03:45 | 174
2015-07-12 04:00 | 173
2015-07-12 04:15 | 180
2015-07-12 04:30 | 187
2015-07-12 04:45 | 167
2015-07-12 05:00 | 177
2015-07-12 05:15 | 168
2015-07-12 05:30 | 175
2015-07-12 05:45 | 173
2015-07-12 06:00 | 160
2015-07-12 06:15 | 161
2015-07-12 06:30 | 159
2015-07-12 06:45 | 181
2015-07-12 07:00 | 179
2015-07-12 07:15 | 171
2015-07-12 07:30 | 166
2015-07-12 07:45 | 172
2015-07-12 08:00 | 185
2015-07-12 08:15 | 185
2015-07-12 08:30 | 176
2015-07-12 08:45 | 177
2015-07-12 09:00 | 187
2015-07-12 09:15 | 195
2015-07-12 09:30 | 180
2015-07-12 09:45 | 182
2015-07-12 10:00 | 184
2015-07-12 10:15 | 191
2015-07-12 10:30 | 199
2015-07-12 10:45 | 191
2015-07-12 11:00 | 191
2015-07-12 11:15 | 199
2015-07-12 11:30 | 202
2015-07-12 11:45 | 212
2015-07-12 12:00 | 207
2015-07-12 12:15 | 208
2015-07-12 12:30 | 211
2015-07-12 12:45 | 208
2015-07-12 13:00 | 207
2015-07-12 13:15 | 209
2015-07-12 13:30 | 212
2015-07-12 13:45 | 223
2015-07-12 14:00 | 217
2015-07-12 14:15 | 209
2015-07-12 14:30 | 217
2015-07-12 14:45 | 226
2015-07-12 15:00 | 217
2015-07-12 15:15 | 234
2015-07-12 15:30 | 239
2015-07-12 15:45 | 220
2015-07-12 16:00 | 246
2015-07-12 16:15 | 242
2015-07-12 16:30 | 231
2015-07-12 16:45 | 234
2015-07-12 17:00 | 245
2015-07-12 17:15 | 226
2015-07-12 17:30 | 240
2015-07-12 17:45 | 230
2015-07-12 18:00 | 238
2015-07-12 18:15 | 228
2015-07-12 18:30 | 231
2015-07-12 18:45 | 215
2015-07-12 19:00 | 220
2015-07-12 19:15 | 226
2015-07-12 19:30 | 220
2015-07-12 19:45 | 224
2015-07-12 20:00 | 211
2015-07-12 20:15 | 209
2015-07-12 20:30 | 207
2015-07-12 20:45 | 211
2015-07-12 21:00 | 205
2015-07-12 21:15 | 190
2015-07-12 21:30 | 196
2015-07-12 21:45 | 187
2015-07-12 22:00 | 191
2015-07-12 22:15 | 188
2015-07-12 22:30 | 184
2015-07-12 22:45 | 177
2015-07-12 23:00 | 179
2015-07-12 23:15 | 174
2015-07-12 23:30 | 185
2015-07-12 23:45 | 183
2015-07-13 | 171
2015-07-13 00:15 | 179
2015-07-13 00:30 | 177
2015-07-13 00:45 | 176
2015-07-13 01:00 | 171
2015-07-13 01:15 | 183
2015-07-13 01:30 | 168
2015-07-13 01:45 | 167
2015-07-13 02:00 | 166
2015-07-13 02:15 | 168
2015-07-13 02:30 | 175
2015-07-13 02:45 | 164
2015-07-13 03:00 | 157
2015-07-13 03:15 | 158
2015-07-13 03:30 | 169
2015-07-13 03:45 | 163
2015-07-13 04:00 | 163
2015-07-13 04:15 | 157
2015-07-13 04:30 | 156
2015-07-13 04:45 | 163
2015-07-13 05:00 | 170
2015-07-13 05:15 | 158
2015-07-13 05:30 | 159
2015-07-13 05:45 | 162
2015-07-13 06:00 | 163
2015-07-13 06:15 | 158
2015-07-13 06:30 | 154
2015-07-13 06:45 | 153
2015-07-13 07:00 | 166
2015-07-13 07:15 | 191
2015-07-13 07:30 | 172
2015-07-13 07:45 | 171
2015-07-13 08:00 | 188
2015-07-13 08:15 | 195
2015-07-13 08:30 | 208
2015-07-13 08:45 | 197
2015-07-13 09:00 | 207
2015-07-13 09:15 | 202
2015-07-13 09:30 | 215
2015-07-13 09:45 | 212
2015-07-13 10:00 | 209
2015-07-13 10:15 | 219
2015-07-13 10:30 | 229
2015-07-13 10:45 | 228
2015-07-13 11:00 | 219
2015-07-13 11:15 | 226
2015-07-13 11:30 | 224
2015-07-13 11:45 | 235
2015-07-13 12:00 | 251
2015-07-13 12:15 | 234
2015-07-13 12:30 | 235
2015-07-13 12:45 | 240
2015-07-13 13:00 | 249
2015-07-13 13:15 | 251
2015-07-13 13:30 | 246
2015-07-13 13:45 | 249
2015-07-13 14:00 | 258
2015-07-13 14:15 | 268
2015-07-13 14:30 | 259
2015-07-13 14:45 | 266
2015-07-13 15:00 | 264
2015-07-13 15:15 | 261
2015-07-13 15:30 | 267
2015-07-13 15:45 | 263
2015-07-13 16:00 | 277
2015-07-13 16:15 | 259
2015-07-13 16:30 | 267
2015-07-13 16:45 | 257
2015-07-13 17:00 | 267
2015-07-13 17:15 | 264
2015-07-13 17:30 | 282
2015-07-13 17:45 | 251
2015-07-13 18:00 | 258
2015-07-13 18:15 | 234
2015-07-13 18:30 | 259
2015-07-13 18:45 | 247
2015-07-13 19:00 | 239
2015-07-13 19:15 | 232
2015-07-13 19:30 | 238
2015-07-13 19:45 | 232
2015-07-13 20:00 | 242
2015-07-13 20:15 | 220
2015-07-13 20:30 | 217
2015-07-13 20:45 | 217
2015-07-13 21:00 | 229
2015-07-13 21:15 | 207
2015-07-13 21:30 | 203
2015-07-13 21:45 | 197
2015-07-13 22:00 | 205
2015-07-13 22:15 | 207
2015-07-13 22:30 | 195
2015-07-13 22:45 | 196
2015-07-13 23:00 | 200
2015-07-13 23:15 | 202
2015-07-13 23:30 | 181
2015-07-13 23:45 | 183
2015-07-14 | 183
2015-07-14 00:15 | 189
2015-07-14 00:30 | 178
2015-07-14 00:45 | 179
2015-07-14 01:00 | 170
2015-07-14 01:15 | 185
2015-07-14 01:30 | 188
2015-07-14 01:45 | 167
2015-07-14 02:00 | 172
2015-07-14 02:15 | 170
2015-07-14 02:30 | 190
2015-07-14 02:45 | 168
2015-07-14 03:00 | 169
2015-07-14 03:15 | 170
2015-07-14 03:30 | 178
2015-07-14 03:45 | 180
2015-07-14 04:00 | 164
2015-07-14 04:15 | 169
2015-07-14 04:30 | 163
2015-07-14 04:45 | 180
2015-07-14 05:00 | 168
2015-07-14 05:15 | 169
2015-07-14 05:30 | 165
2015-07-14 05:45 | 165
2015-07-14 06:00 | 179
2015-07-14 06:15 | 162
2015-07-14 06:30 | 161
2015-07-14 06:45 | 160
2015-07-14 07:00 | 171
2015-07-14 07:15 | 171
2015-07-14 07:30 | 160
2015-07-14 07:45 | 163
2015-07-14 08:00 | 172
2015-07-14 08:15 | 192
2015-07-14 08:30 | 201
2015-07-14 08:45 | 191
2015-07-14 09:00 | 198
2015-07-14 09:15 | 194
2015-07-14 09:30 | 215
2015-07-14 09:45 | 198
2015-07-14 10:00 | 205
2015-07-14 10:15 | 203
2015-07-14 10:30 | 217
2015-07-14 10:45 | 229
2015-07-14 11:00 | 209
2015-07-14 11:15 | 219
2015-07-14 11:30 | 224
2015-07-14 11:45 | 219
2015-07-14 12:00 | 239
2015-07-14 12:15 | 219
2015-07-14 12:30 | 217
2015-07-14 12:45 | 210
2015-07-14 13:00 | 229
2015-07-14 13:15 | 225
2015-07-14 13:30 | 220
2015-07-14 13:45 | 216
2015-07-14 14:00 | 236
2015-07-14 14:15 | 215
2015-07-14 14:30 | 233
2015-07-14 14:45 | 221
2015-07-14 15:00 | 249
2015-07-14 15:15 | 230
2015-07-14 15:30 | 238
2015-07-14 15:45 | 224
2015-07-14 16:00 | 241
2015-07-14 16:15 | 236
2015-07-14 16:30 | 250
2015-07-14 16:45 | 241
2015-07-14 17:00 | 243
2015-07-14 17:15 | 240
2015-07-14 17:30 | 232
2015-07-14 17:45 | 261
2015-07-14 18:00 | 231
2015-07-14 18:15 | 234
2015-07-14 18:30 | 239
2015-07-14 18:45 | 240
2015-07-14 19:00 | 221
2015-07-14 19:15 | 223
2015-07-14 19:30 | 221
2015-07-14 19:45 | 223
2015-07-14 20:00 | 210
2015-07-14 20:15 | 209
2015-07-14 20:30 | 208
2015-07-14 20:45 | 221
2015-07-14 21:00 | 205
2015-07-14 21:15 | 187
2015-07-14 21:30 | 196
2015-07-14 21:45 | 192
2015-07-14 22:00 | 205
2015-07-14 22:15 | 178
2015-07-14 22:30 | 185
2015-07-14 22:45 | 184
2015-07-14 23:00 | 184
2015-07-14 23:15 | 187
2015-07-14 23:30 | 174
2015-07-14 23:45 | 168
2015-07-15 | 171
2015-07-15 00:15 | 196
2015-07-15 00:30 | 167
2015-07-15 00:45 | 174
2015-07-15 01:00 | 170
2015-07-15 01:15 | 185
2015-07-15 01:30 | 174
2015-07-15 01:45 | 164
2015-07-15 02:00 | 167
2015-07-15 02:15 | 174
2015-07-15 02:30 | 171
2015-07-15 02:45 | 166
2015-07-15 03:00 | 171
2015-07-15 03:15 | 161
2015-07-15 03:30 | 179
2015-07-15 03:45 | 163
2015-07-15 04:00 | 158
2015-07-15 04:15 | 159
2015-07-15 04:30 | 161
2015-07-15 04:45 | 175
2015-07-15 05:00 | 150
2015-07-15 05:15 | 150
2015-07-15 05:30 | 146
2015-07-15 05:45 | 159
2015-07-15 06:00 | 156
2015-07-15 06:15 | 155
2015-07-15 06:30 | 149
2015-07-15 06:45 | 159
2015-07-15 07:00 | 172
2015-07-15 07:15 | 160
2015-07-15 07:30 | 163
2015-07-15 07:45 | 165
2015-07-15 08:00 | 173
2015-07-15 08:15 | 197
2015-07-15 08:30 | 194
2015-07-15 08:45 | 196
2015-07-15 09:00 | 192
2015-07-15 09:15 | 207
2015-07-15 09:30 | 210
2015-07-15 09:45 | 204
2015-07-15 10:00 | 203
2015-07-15 10:15 | 207
2015-07-15 10:30 | 228
2015-07-15 10:45 | 222
2015-07-15 11:00 | 216
2015-07-15 11:15 | 221
2015-07-15 11:30 | 221
2015-07-15 11:45 | 236
2015-07-15 12:00 | 230
2015-07-15 12:15 | 240
2015-07-15 12:30 | 231
2015-07-15 12:45 | 241
2015-07-15 13:00 | 251
2015-07-15 13:15 | 245
2015-07-15 13:30 | 250
2015-07-15 13:45 | 253
2015-07-15 14:00 | 256
2015-07-15 14:15 | 268
2015-07-15 14:30 | 249
2015-07-15 14:45 | 254
2015-07-15 15:00 | 262
2015-07-15 15:15 | 268
2015-07-15 15:30 | 266
2015-07-15 15:45 | 267
2015-07-15 16:00 | 262
2015-07-15 16:15 | 269
2015-07-15 16:30 | 275
2015-07-15 16:45 | 270
2015-07-15 17:00 | 276
2015-07-15 17:15 | 272
2015-07-15 17:30 | 262
2015-07-15 17:45 | 257
2015-07-15 18:00 | 260
2015-07-15 18:15 | 269
2015-07-15 18:30 | 265
2015-07-15 18:45 | 259
2015-07-15 19:00 | 255
2015-07-15 19:15 | 248
2015-07-15 19:30 | 249
2015-07-15 19:45 | 238
2015-07-15 20:00 | 234
2015-07-15 20:15 | 251
2015-07-15 20:30 | 240
2015-07-15 20:45 | 220
2015-07-15 21:00 | 231
2015-07-15 21:15 | 220
2015-07-15 21:30 | 225
2015-07-15 21:45 | 219
2015-07-15 22:00 | 231
2015-07-15 22:15 | 216
2015-07-15 22:30 | 214
2015-07-15 22:45 | 213
2015-07-15 23:00 | 216
2015-07-15 23:15 | 223
2015-07-15 23:30 | 199
2015-07-15 23:45 | 198
2015-07-16 | 190
2015-07-16 00:15 | 194
2015-07-16 00:30 | 191
2015-07-16 00:45 | 200
2015-07-16 01:00 | 189
2015-07-16 01:15 | 178
2015-07-16 01:30 | 174
2015-07-16 01:45 | 187
2015-07-16 02:00 | 186
2015-07-16 02:15 | 170
2015-07-16 02:30 | 175
2015-07-16 02:45 | 173
2015-07-16 03:00 | 179
2015-07-16 03:15 | 172
2015-07-16 03:30 | 168
2015-07-16 03:45 | 173
2015-07-16 04:00 | 181
2015-07-16 04:15 | 172
2015-07-16 04:30 | 167
2015-07-16 04:45 | 170
2015-07-16 05:00 | 165
2015-07-16 05:15 | 180
2015-07-16 05:30 | 165
2015-07-16 05:45 | 165
2015-07-16 06:00 | 165
2015-07-16 06:15 | 180
2015-07-16 06:30 | 173
2015-07-16 06:45 | 169
2015-07-16 07:00 | 172
2015-07-16 07:15 | 174
2015-07-16 07:30 | 191
2015-07-16 07:45 | 170
2015-07-16 08:00 | 178
2015-07-16 08:15 | 188
2015-07-16 08:30 | 197
2015-07-16 08:45 | 198
2015-07-16 09:00 | 196
2015-07-16 09:15 | 212
2015-07-16 09:30 | 205
2015-07-16 09:45 | 222
2015-07-16 10:00 | 214
2015-07-16 10:15 | 216
2015-07-16 10:30 | 222
2015-07-16 10:45 | 227
2015-07-16 11:00 | 245
2015-07-16 11:15 | 231
2015-07-16 11:30 | 245
2015-07-16 11:45 | 245
2015-07-16 12:00 | 237
2015-07-16 12:15 | 247
2015-07-16 12:30 | 245
2015-07-16 12:45 | 254
2015-07-16 13:00 | 253
2015-07-16 13:15 | 267
2015-07-16 13:30 | 250
2015-07-16 13:45 | 266
2015-07-16 14:00 | 252
2015-07-16 14:15 | 282
2015-07-16 14:30 | 276
2015-07-16 14:45 | 262
2015-07-16 15:00 | 273
2015-07-16 15:15 | 277
2015-07-16 15:30 | 278
2015-07-16 15:45 | 280
2015-07-16 16:00 | 272
2015-07-16 16:15 | 275
2015-07-16 16:30 | 269
2015-07-16 16:45 | 258
2015-07-16 17:00 | 279
2015-07-16 17:15 | 275
2015-07-16 17:30 | 261
2015-07-16 17:45 | 273
2015-07-16 18:00 | 263
2015-07-16 18:15 | 264
2015-07-16 18:30 | 260
2015-07-16 18:45 | 263
2015-07-16 19:00 | 246
2015-07-16 19:15 | 255
2015-07-16 19:30 | 238
2015-07-16 19:45 | 249
2015-07-16 20:00 | 253
2015-07-16 20:15 | 237
2015-07-16 20:30 | 234
2015-07-16 20:45 | 225
2015-07-16 21:00 | 219
2015-07-16 21:15 | 216
2015-07-16 21:30 | 218
2015-07-16 21:45 | 210
2015-07-16 22:00 | 220
2015-07-16 22:15 | 208
2015-07-16 22:30 | 208
2015-07-16 22:45 | 222
2015-07-16 23:00 | 203
2015-07-16 23:15 | 200
2015-07-16 23:30 | 195
2015-07-16 23:45 | 197
2015-07-17 | 206
2015-07-17 00:15 | 185
2015-07-17 00:30 | 186
2015-07-17 00:45 | 189
2015-07-17 01:00 | 192
2015-07-17 01:15 | 194
2015-07-17 01:30 | 187
2015-07-17 01:45 | 179
2015-07-17 02:00 | 182
2015-07-17 02:15 | 190
2015-07-17 02:30 | 187
2015-07-17 02:45 | 180
2015-07-17 03:00 | 178
2015-07-17 03:15 | 184
2015-07-17 03:30 | 191
2015-07-17 03:45 | 187
2015-07-17 04:00 | 168
2015-07-17 04:15 | 176
2015-07-17 04:30 | 178
2015-07-17 04:45 | 189
2015-07-17 05:00 | 172
2015-07-17 05:15 | 176
2015-07-17 05:30 | 178
2015-07-17 05:45 | 186
2015-07-17 06:00 | 174
2015-07-17 06:15 | 169
2015-07-17 06:30 | 179
2015-07-17 06:45 | 181
2015-07-17 07:00 | 190
2015-07-17 07:15 | 172
2015-07-17 07:30 | 174
2015-07-17 07:45 | 172
2015-07-17 08:00 | 181
2015-07-17 08:15 | 194
2015-07-17 08:30 | 186
2015-07-17 08:45 | 196
2015-07-17 09:00 | 198
2015-07-17 09:15 | 212
2015-07-17 09:30 | 200
2015-07-17 09:45 | 202
2015-07-17 10:00 | 210
2015-07-17 10:15 | 222
2015-07-17 10:30 | 232
2015-07-17 10:45 | 217
2015-07-17 11:00 | 221
2015-07-17 11:15 | 220
2015-07-17 11:30 | 231
2015-07-17 11:45 | 241
2015-07-17 12:00 | 236
2015-07-17 12:15 | 232
2015-07-17 12:30 | 244
2015-07-17 12:45 | 253
2015-07-17 13:00 | 238
2015-07-17 13:15 | 246
2015-07-17 13:30 | 258
2015-07-17 13:45 | 268
2015-07-17 14:00 | 266
2015-07-17 14:15 | 258
2015-07-17 14:30 | 266
2015-07-17 14:45 | 272
2015-07-17 15:00 | 268
2015-07-17 15:15 | 275
2015-07-17 15:30 | 267
2015-07-17 15:45 | 261
2015-07-17 16:00 | 251
2015-07-17 16:15 | 265
2015-07-17 16:30 | 267
2015-07-17 16:45 | 254
2015-07-17 17:00 | 261
2015-07-17 17:15 | 264
2015-07-17 17:30 | 269
2015-07-17 17:45 | 264
2015-07-17 18:00 | 262
2015-07-17 18:15 | 257
2015-07-17 18:30 | 266
2015-07-17 18:45 | 254
2015-07-17 19:00 | 249
2015-07-17 19:15 | 246
2015-07-17 19:30 | 236
2015-07-17 19:45 | 247
2015-07-17 20:00 | 249
2015-07-17 20:15 | 223
2015-07-17 20:30 | 234
2015-07-17 20:45 | 215
2015-07-17 21:00 | 226
2015-07-17 21:15 | 201
2015-07-17 21:30 | 193
2015-07-17 21:45 | 196
2015-07-17 22:00 | 191
2015-07-17 22:15 | 182
2015-07-17 22:30 | 187
2015-07-17 22:45 | 192
2015-07-17 23:00 | 193
2015-07-17 23:15 | 182
2015-07-17 23:30 | 178
2015-07-17 23:45 | 182
2015-07-18 | 190
2015-07-18 00:15 | 175
2015-07-18 00:30 | 178
2015-07-18 00:45 | 172
2015-07-18 01:00 | 178
2015-07-18 01:15 | 181
2015-07-18 01:30 | 170
2015-07-18 01:45 | 172
2015-07-18 02:00 | 164
2015-07-18 02:15 | 182
2015-07-18 02:30 | 173
2015-07-18 02:45 | 167
2015-07-18 03:00 | 164
2015-07-18 03:15 | 170
2015-07-18 03:30 | 185
2015-07-18 03:45 | 162
2015-07-18 04:00 | 172
2015-07-18 04:15 | 165
2015-07-18 04:30 | 179
2015-07-18 04:45 | 176
2015-07-18 05:00 | 162
2015-07-18 05:15 | 164
2015-07-18 05:30 | 175
2015-07-18 05:45 | 178
2015-07-18 06:00 | 158
2015-07-18 06:15 | 161
2015-07-18 06:30 | 164
2015-07-18 06:45 | 177
2015-07-18 07:00 | 163
2015-07-18 07:15 | 166
2015-07-18 07:30 | 158
2015-07-18 07:45 | 169
2015-07-18 08:00 | 175
2015-07-18 08:15 | 167
2015-07-18 08:30 | 167
2015-07-18 08:45 | 164
2015-07-18 09:00 | 174
2015-07-18 09:15 | 191
2015-07-18 09:30 | 177
2015-07-18 09:45 | 182
2015-07-18 10:00 | 179
2015-07-18 10:15 | 187
2015-07-18 10:30 | 187
2015-07-18 10:45 | 185
2015-07-18 11:00 | 182
2015-07-18 11:15 | 186
2015-07-18 11:30 | 203
2015-07-18 11:45 | 193
2015-07-18 12:00 | 193
2015-07-18 12:15 | 187
2015-07-18 12:30 | 198
2015-07-18 12:45 | 203
2015-07-18 13:00 | 192
2015-07-18 13:15 | 197
2015-07-18 13:30 | 197
2015-07-18 13:45 | 214
2015-07-18 14:00 | 210
2015-07-18 14:15 | 205
2015-07-18 14:30 | 203
2015-07-18 14:45 | 209
2015-07-18 15:00 | 226
2015-07-18 15:15 | 227
2015-07-18 15:30 | 227
2015-07-18 15:45 | 220
2015-07-18 16:00 | 226
2015-07-18 16:15 | 224
2015-07-18 16:30 | 236
2015-07-18 16:45 | 215
2015-07-18 17:00 | 232
2015-07-18 17:15 | 223
2015-07-18 17:30 | 235
2015-07-18 17:45 | 231
2015-07-18 18:00 | 229
2015-07-18 18:15 | 214
2015-07-18 18:30 | 219
2015-07-18 18:45 | 230
2015-07-18 19:00 | 228
2015-07-18 19:15 | 221
2015-07-18 19:30 | 217
2015-07-18 19:45 | 208
2015-07-18 20:00 | 220
2015-07-18 20:15 | 218
2015-07-18 20:30 | 204
2015-07-18 20:45 | 210
2015-07-18 21:00 | 200
2015-07-18 21:15 | 198
2015-07-18 21:30 | 189
2015-07-18 21:45 | 197
2015-07-18 22:00 | 192
2015-07-18 22:15 | 183
2015-07-18 22:30 | 185
2015-07-18 22:45 | 179
2015-07-18 23:00 | 201
2015-07-18 23:15 | 182
2015-07-18 23:30 | 179
2015-07-18 23:45 | 182
2015-07-19 | 192
2015-07-19 00:15 | 181
2015-07-19 00:30 | 175
2015-07-19 00:45 | 176
2015-07-19 01:00 | 175
2015-07-19 01:15 | 186
2015-07-19 01:30 | 171
2015-07-19 01:45 | 167
2015-07-19 02:00 | 174
2015-07-19 02:15 | 182
2015-07-19 02:30 | 176
2015-07-19 02:45 | 172
2015-07-19 03:00 | 176
2015-07-19 03:15 | 171
2015-07-19 03:30 | 180
2015-07-19 03:45 | 180
2015-07-19 04:00 | 170
2015-07-19 04:15 | 162
2015-07-19 04:30 | 165
2015-07-19 04:45 | 185
2015-07-19 05:00 | 174
2015-07-19 05:15 | 165
2015-07-19 05:30 | 169
2015-07-19 05:45 | 173
2015-07-19 06:00 | 184
2015-07-19 06:15 | 171
2015-07-19 06:30 | 171
2015-07-19 06:45 | 176
2015-07-19 07:00 | 189
2015-07-19 07:15 | 181
2015-07-19 07:30 | 171
2015-07-19 07:45 | 180
2015-07-19 08:00 | 174
2015-07-19 08:15 | 193
2015-07-19 08:30 | 187
2015-07-19 08:45 | 182
2015-07-19 09:00 | 182
2015-07-19 09:15 | 184
2015-07-19 09:30 | 193
2015-07-19 09:45 | 194
2015-07-19 10:00 | 182
2015-07-19 10:15 | 191
2015-07-19 10:30 | 197
2015-07-19 10:45 | 195
2015-07-19 11:00 | 206
2015-07-19 11:15 | 189
2015-07-19 11:30 | 190
2015-07-19 11:45 | 189
2015-07-19 12:00 | 201
2015-07-19 12:15 | 212
2015-07-19 12:30 | 194
2015-07-19 12:45 | 198
2015-07-19 13:00 | 199
2015-07-19 13:15 | 212
2015-07-19 13:30 | 217
2015-07-19 13:45 | 219
2015-07-19 14:00 | 215
2015-07-19 14:15 | 229
2015-07-19 14:30 | 245
2015-07-19 14:45 | 229
2015-07-19 15:00 | 235
2015-07-19 15:15 | 239
2015-07-19 15:30 | 243
2015-07-19 15:45 | 258
2015-07-19 16:00 | 246
2015-07-19 16:15 | 232
2015-07-19 16:30 | 242
2015-07-19 16:45 | 255
2015-07-19 17:00 | 255
2015-07-19 17:15 | 238
2015-07-19 17:30 | 237
2015-07-19 17:45 | 240
2015-07-19 18:00 | 240
2015-07-19 18:15 | 245
2015-07-19 18:30 | 223
2015-07-19 18:45 | 228
2015-07-19 19:00 | 221
2015-07-19 19:15 | 243
2015-07-19 19:30 | 216
2015-07-19 19:45 | 216
2015-07-19 20:00 | 233
2015-07-19 20:15 | 211
2015-07-19 20:30 | 205
2015-07-19 20:45 | 211
2015-07-19 21:00 | 206
2015-07-19 21:15 | 211
2015-07-19 21:30 | 189
2015-07-19 21:45 | 190
2015-07-19 22:00 | 186
2015-07-19 22:15 | 190
2015-07-19 22:30 | 192
2015-07-19 22:45 | 182
2015-07-19 23:00 | 175
2015-07-19 23:15 | 186
2015-07-19 23:30 | 192
2015-07-19 23:45 | 179
2015-07-20 | 178
2015-07-20 00:15 | 175
2015-07-20 00:30 | 197
2015-07-20 00:45 | 205
2015-07-20 01:00 | 188
2015-07-20 01:15 | 184
2015-07-20 01:30 | 177
2015-07-20 01:45 | 196
2015-07-20 02:00 | 194
2015-07-20 02:15 | 175
2015-07-20 02:30 | 184
2015-07-20 02:45 | 182
2015-07-20 03:00 | 193
2015-07-20 03:15 | 186
2015-07-20 03:30 | 179
2015-07-20 03:45 | 177
2015-07-20 04:00 | 191
2015-07-20 04:15 | 188
2015-07-20 04:30 | 179
2015-07-20 04:45 | 176
2015-07-20 05:00 | 177
2015-07-20 05:15 | 199
2015-07-20 05:30 | 182
2015-07-20 05:45 | 175
2015-07-20 06:00 | 176
2015-07-20 06:15 | 183
2015-07-20 06:30 | 194
2015-07-20 06:45 | 189
2015-07-20 07:00 | 180
2015-07-20 07:15 | 185
2015-07-20 07:30 | 190
2015-07-20 07:45 | 204
2015-07-20 08:00 | 195
2015-07-20 08:15 | 194
2015-07-20 08:30 | 208
2015-07-20 08:45 | 219
2015-07-20 09:00 | 225
2015-07-20 09:15 | 207
2015-07-20 09:30 | 212
2015-07-20 09:45 | 213
2015-07-20 10:00 | 231
2015-07-20 10:15 | 232
2015-07-20 10:30 | 224
2015-07-20 10:45 | 234
2015-07-20 11:00 | 248
2015-07-20 11:15 | 250
2015-07-20 11:30 | 242
2015-07-20 11:45 | 250
2015-07-20 12:00 | 258
2015-07-20 12:15 | 253
2015-07-20 12:30 | 273
2015-07-20 12:45 | 247
2015-07-20 13:00 | 257
2015-07-20 13:15 | 245
2015-07-20 13:30 | 267
2015-07-20 13:45 | 267
2015-07-20 14:00 | 249
2015-07-20 14:15 | 263
2015-07-20 14:30 | 263
2015-07-20 14:45 | 264
2015-07-20 15:00 | 265
2015-07-20 15:15 | 273
2015-07-20 15:30 | 258
2015-07-20 15:45 | 266
2015-07-20 16:00 | 261
2015-07-20 16:15 | 265
2015-07-20 16:30 | 280
2015-07-20 16:45 | 271
2015-07-20 17:00 | 267
2015-07-20 17:15 | 280
2015-07-20 17:30 | 265
2015-07-20 17:45 | 263
2015-07-20 18:00 | 257
2015-07-20 18:15 | 256
2015-07-20 18:30 | 261
2015-07-20 18:45 | 266
2015-07-20 19:00 | 240
2015-07-20 19:15 | 255
2015-07-20 19:30 | 234
2015-07-20 19:45 | 236
2015-07-20 20:00 | 237
2015-07-20 20:15 | 241
2015-07-20 20:30 | 228
2015-07-20 20:45 | 226
2015-07-20 21:00 | 215
2015-07-20 21:15 | 212
2015-07-20 21:30 | 206
2015-07-20 21:45 | 198
2015-07-20 22:00 | 201
2015-07-20 22:15 | 222
2015-07-20 22:30 | 203
2015-07-20 22:45 | 199
2015-07-20 23:00 | 200
2015-07-20 23:15 | 189
2015-07-20 23:30 | 205
2015-07-20 23:45 | 187
2015-07-21 | 187
2015-07-21 00:15 | 177
2015-07-21 00:30 | 181
2015-07-21 00:45 | 191
2015-07-21 01:00 | 173
2015-07-21 01:15 | 180
2015-07-21 01:30 | 178
2015-07-21 01:45 | 175
2015-07-21 02:00 | 190
2015-07-21 02:15 | 170
2015-07-21 02:30 | 166
2015-07-21 02:45 | 169
2015-07-21 03:00 | 179
2015-07-21 03:15 | 176
2015-07-21 03:30 | 164
2015-07-21 03:45 | 173
2015-07-21 04:00 | 165
2015-07-21 04:15 | 181
2015-07-21 04:30 | 174
2015-07-21 04:45 | 163
2015-07-21 05:00 | 166
2015-07-21 05:15 | 165
2015-07-21 05:30 | 184
2015-07-21 05:45 | 164
2015-07-21 06:00 | 166
2015-07-21 06:15 | 161
2015-07-21 06:30 | 178
2015-07-21 06:45 | 180
2015-07-21 07:00 | 167
2015-07-21 07:15 | 169
2015-07-21 07:30 | 169
2015-07-21 07:45 | 185
2015-07-21 08:00 | 172
2015-07-21 08:15 | 175
2015-07-21 08:30 | 187
2015-07-21 08:45 | 200
2015-07-21 09:00 | 202
2015-07-21 09:15 | 192
2015-07-21 09:30 | 192
2015-07-21 09:45 | 192
2015-07-21 10:00 | 209
2015-07-21 10:15 | 204
2015-07-21 10:30 | 203
2015-07-21 10:45 | 206
2015-07-21 11:00 | 208
2015-07-21 11:15 | 213
2015-07-21 11:30 | 233
2015-07-21 11:45 | 214
2015-07-21 12:00 | 231
2015-07-21 12:15 | 208
2015-07-21 12:30 | 236
2015-07-21 12:45 | 226
2015-07-21 13:00 | 230
2015-07-21 13:15 | 219
2015-07-21 13:30 | 227
2015-07-21 13:45 | 223
2015-07-21 14:00 | 243
2015-07-21 14:15 | 234
2015-07-21 14:30 | 223
2015-07-21 14:45 | 235
2015-07-21 15:00 | 240
2015-07-21 15:15 | 243
2015-07-21 15:30 | 238
2015-07-21 15:45 | 247
2015-07-21 16:00 | 230
2015-07-21 16:15 | 234
2015-07-21 16:30 | 229
2015-07-21 16:45 | 251
2015-07-21 17:00 | 230
2015-07-21 17:15 | 238
2015-07-21 17:30 | 228
2015-07-21 17:45 | 234
2015-07-21 18:00 | 242
2015-07-21 18:15 | 232
2015-07-21 18:30 | 237
2015-07-21 18:45 | 235
2015-07-21 19:00 | 232
2015-07-21 19:15 | 232
2015-07-21 19:30 | 231
2015-07-21 19:45 | 212
2015-07-21 20:00 | 212
2015-07-21 20:15 | 206
2015-07-21 20:30 | 214
2015-07-21 20:45 | 209
2015-07-21 21:00 | 201
2015-07-21 21:15 | 192
2015-07-21 21:30 | 202
2015-07-21 21:45 | 190
2015-07-21 22:00 | 187
2015-07-21 22:15 | 184
2015-07-21 22:30 | 188
2015-07-21 22:45 | 202
2015-07-21 23:00 | 194
2015-07-21 23:15 | 185
2015-07-21 23:30 | 174
2015-07-21 23:45 | 184
2015-07-22 | 199
2015-07-22 00:15 | 176
2015-07-22 00:30 | 181
2015-07-22 00:45 | 185
2015-07-22 01:00 | 172
2015-07-22 01:15 | 173
2015-07-22 01:30 | 176
2015-07-22 01:45 | 189
2015-07-22 02:00 | 172
2015-07-22 02:15 | 172
2015-07-22 02:30 | 169
2015-07-22 02:45 | 172
2015-07-22 03:00 | 179
2015-07-22 03:15 | 169
2015-07-22 03:30 | 169
2015-07-22 03:45 | 161
2015-07-22 04:00 | 176
2015-07-22 04:15 | 175
2015-07-22 04:30 | 167
2015-07-22 04:45 | 163
2015-07-22 05:00 | 161
2015-07-22 05:15 | 177
2015-07-22 05:30 | 176
2015-07-22 05:45 | 157
2015-07-22 06:00 | 165
2015-07-22 06:15 | 166
2015-07-22 06:30 | 177
2015-07-22 06:45 | 165
2015-07-22 07:00 | 168
2015-07-22 07:15 | 169
2015-07-22 07:30 | 175
2015-07-22 07:45 | 182
2015-07-22 08:00 | 172
2015-07-22 08:15 | 179
2015-07-22 08:30 | 182
2015-07-22 08:45 | 196
2015-07-22 09:00 | 195
2015-07-22 09:15 | 198
2015-07-22 09:30 | 194
2015-07-22 09:45 | 196
2015-07-22 10:00 | 219
2015-07-22 10:15 | 197
2015-07-22 10:30 | 206
2015-07-22 10:45 | 199
2015-07-22 11:00 | 227
2015-07-22 11:15 | 218
2015-07-22 11:30 | 212
2015-07-22 11:45 | 222
2015-07-22 12:00 | 217
2015-07-22 12:15 | 228
2015-07-22 12:30 | 236
2015-07-22 12:45 | 216
2015-07-22 13:00 | 217
2015-07-22 13:15 | 226
2015-07-22 13:30 | 233
2015-07-22 13:45 | 236
2015-07-22 14:00 | 221
2015-07-22 14:15 | 228
2015-07-22 14:30 | 224
2015-07-22 14:45 | 238
2015-07-22 15:00 | 223
2015-07-22 15:15 | 225
2015-07-22 15:30 | 232
2015-07-22 15:45 | 227
2015-07-22 16:00 | 237
2015-07-22 16:15 | 225
2015-07-22 16:30 | 223
2015-07-22 16:45 | 232
2015-07-22 17:00 | 222
2015-07-22 17:15 | 248
2015-07-22 17:30 | 239
2015-07-22 17:45 | 225
2015-07-22 18:00 | 237
2015-07-22 18:15 | 218
2015-07-22 18:30 | 234
2015-07-22 18:45 | 237
2015-07-22 19:00 | 214
2015-07-22 19:15 | 215
2015-07-22 19:30 | 207
2015-07-22 19:45 | 223
2015-07-22 20:00 | 211
2015-07-22 20:15 | 206
2015-07-22 20:30 | 205
2015-07-22 20:45 | 209
2015-07-22 21:00 | 205
2015-07-22 21:15 | 189
2015-07-22 21:30 | 199
2015-07-22 21:45 | 184
2015-07-22 22:00 | 181
2015-07-22 22:15 | 184
2015-07-22 22:30 | 201
2015-07-22 22:45 | 176
2015-07-22 23:00 | 185
2015-07-22 23:15 | 176
2015-07-22 23:30 | 188
2015-07-22 23:45 | 182
2015-07-23 | 160
2015-07-23 00:15 | 167
2015-07-23 00:30 | 172
2015-07-23 00:45 | 177
2015-07-23 01:00 | 161
2015-07-23 01:15 | 167
2015-07-23 01:30 | 164
2015-07-23 01:45 | 168
2015-07-23 02:00 | 163
2015-07-23 02:15 | 159
2015-07-23 02:30 | 155
2015-07-23 02:45 | 157
2015-07-23 03:00 | 159
2015-07-23 03:15 | 171
2015-07-23 03:30 | 148
2015-07-23 03:45 | 148
2015-07-23 04:00 | 145
2015-07-23 04:15 | 148
2015-07-23 04:30 | 161
2015-07-23 04:45 | 149
2015-07-23 05:00 | 149
2015-07-23 05:15 | 142
2015-07-23 05:30 | 149
2015-07-23 05:45 | 162
2015-07-23 06:00 | 152
2015-07-23 06:15 | 130
2015-07-23 06:30 | 97
2015-07-23 06:45 | 95
2015-07-23 07:00 | 135
2015-07-23 07:15 | 152
2015-07-23 07:30 | 147
2015-07-23 07:45 | 165
2015-07-23 08:00 | 156
2015-07-23 08:15 | 167
2015-07-23 08:30 | 166
2015-07-23 08:45 | 168
2015-07-23 09:00 | 180
2015-07-23 09:15 | 177
2015-07-23 09:30 | 178
2015-07-23 09:45 | 180
2015-07-23 10:00 | 178
2015-07-23 10:15 | 182
2015-07-23 10:30 | 185
2015-07-23 10:45 | 182
2015-07-23 11:00 | 181
2015-07-23 11:15 | 208
2015-07-23 11:30 | 189
2015-07-23 11:45 | 188
2015-07-23 12:00 | 197
2015-07-23 12:15 | 195
2015-07-23 12:30 | 206
2015-07-23 12:45 | 212
2015-07-23 13:00 | 195
2015-07-23 13:15 | 210
2015-07-23 13:30 | 196
2015-07-23 13:45 | 199
2015-07-23 14:00 | 197
2015-07-23 14:15 | 212
2015-07-23 14:30 | 206
2015-07-23 14:45 | 202
2015-07-23 15:00 | 205
2015-07-23 15:15 | 202
2015-07-23 15:30 | 206
2015-07-23 15:45 | 203
2015-07-23 16:00 | 217
2015-07-23 16:15 | 215
2015-07-23 16:30 | 224
2015-07-23 16:45 | 217
2015-07-23 17:00 | 211
2015-07-23 17:15 | 226
2015-07-23 17:30 | 212
2015-07-23 17:45 | 224
2015-07-23 18:00 | 211
2015-07-23 18:15 | 213
2015-07-23 18:30 | 220
2015-07-23 18:45 | 229
2015-07-23 19:00 | 212
2015-07-23 19:15 | 212
2015-07-23 19:30 | 211
2015-07-23 19:45 | 212
2015-07-23 20:00 | 201
2015-07-23 20:15 | 212
2015-07-23 20:30 | 196
2015-07-23 20:45 | 191
2015-07-23 21:00 | 199
2015-07-23 21:15 | 179
2015-07-23 21:30 | 189
2015-07-23 21:45 | 183
2015-07-23 22:00 | 167
2015-07-23 22:15 | 176
2015-07-23 22:30 | 169
2015-07-23 22:45 | 190
2015-07-23 23:00 | 170
2015-07-23 23:15 | 170
2015-07-23 23:30 | 161
2015-07-23 23:45 | 169
2015-07-24 | 175
2015-07-24 00:15 | 163
2015-07-24 00:30 | 165
2015-07-24 00:45 | 151
2015-07-24 01:00 | 169
2015-07-24 01:15 | 169
2015-07-24 01:30 | 157
2015-07-24 01:45 | 166
2015-07-24 02:00 | 152
2015-07-24 02:15 | 170
2015-07-24 02:30 | 153
2015-07-24 02:45 | 155
2015-07-24 03:00 | 143
2015-07-24 03:15 | 145
2015-07-24 03:30 | 154
2015-07-24 03:45 | 158
2015-07-24 04:00 | 148
2015-07-24 04:15 | 151
2015-07-24 04:30 | 152
2015-07-24 04:45 | 159
2015-07-24 05:00 | 148
2015-07-24 05:15 | 146
2015-07-24 05:30 | 143
2015-07-24 05:45 | 144
2015-07-24 06:00 | 151
2015-07-24 06:15 | 151
2015-07-24 06:30 | 150
2015-07-24 06:45 | 145
2015-07-24 07:00 | 164
2015-07-24 07:15 | 154
2015-07-24 07:30 | 153
2015-07-24 07:45 | 151
2015-07-24 08:00 | 154
2015-07-24 08:15 | 165
2015-07-24 08:30 | 171
2015-07-24 08:45 | 188
2015-07-24 09:00 | 174
2015-07-24 09:15 | 180
2015-07-24 09:30 | 181
2015-07-24 09:45 | 195
2015-07-24 10:00 | 188
2015-07-24 10:15 | 181
2015-07-24 10:30 | 190
2015-07-24 10:45 | 206
2015-07-24 11:00 | 190
2015-07-24 11:15 | 197
2015-07-24 11:30 | 203
2015-07-24 11:45 | 193
2015-07-24 12:00 | 206
2015-07-24 12:15 | 201
2015-07-24 12:30 | 201
2015-07-24 12:45 | 201
2015-07-24 13:00 | 204
2015-07-24 13:15 | 216
2015-07-24 13:30 | 207
2015-07-24 13:45 | 208
2015-07-24 14:00 | 212
2015-07-24 14:15 | 209
2015-07-24 14:30 | 210
2015-07-24 14:45 | 221
2015-07-24 15:00 | 210
2015-07-24 15:15 | 210
2015-07-24 15:30 | 220
2015-07-24 15:45 | 210
2015-07-24 16:00 | 224
2015-07-24 16:15 | 225
2015-07-24 16:30 | 214
2015-07-24 16:45 | 220
2015-07-24 17:00 | 220
2015-07-24 17:15 | 216
2015-07-24 17:30 | 216
2015-07-24 17:45 | 227
2015-07-24 18:00 | 222
2015-07-24 18:15 | 215
2015-07-24 18:30 | 212
2015-07-24 18:45 | 223
2015-07-24 19:00 | 205
2015-07-24 19:15 | 210
2015-07-24 19:30 | 210
2015-07-24 19:45 | 222
2015-07-24 20:00 | 202
2015-07-24 20:15 | 199
2015-07-24 20:30 | 200
2015-07-24 20:45 | 187
2015-07-24 21:00 | 205
2015-07-24 21:15 | 184
2015-07-24 21:30 | 176
2015-07-24 21:45 | 170
2015-07-24 22:00 | 172
2015-07-24 22:15 | 182
2015-07-24 22:30 | 166
2015-07-24 22:45 | 170
2015-07-24 23:00 | 165
2015-07-24 23:15 | 171
2015-07-24 23:30 | 172
2015-07-24 23:45 | 157
2015-07-25 | 161
2015-07-25 00:15 | 161
2015-07-25 00:30 | 155
2015-07-25 00:45 | 168
2015-07-25 01:00 | 151
2015-07-25 01:15 | 157
2015-07-25 01:30 | 155
2015-07-25 01:45 | 169
2015-07-25 02:00 | 154
2015-07-25 02:15 | 153
2015-07-25 02:30 | 153
2015-07-25 02:45 | 146
2015-07-25 03:00 | 160
2015-07-25 03:15 | 157
2015-07-25 03:30 | 149
2015-07-25 03:45 | 149
2015-07-25 04:00 | 150
2015-07-25 04:15 | 150
2015-07-25 04:30 | 161
2015-07-25 04:45 | 151
2015-07-25 05:00 | 146
2015-07-25 05:15 | 142
2015-07-25 05:30 | 143
2015-07-25 05:45 | 145
2015-07-25 06:00 | 154
2015-07-25 06:15 | 144
2015-07-25 06:30 | 146
2015-07-25 06:45 | 145
2015-07-25 07:00 | 160
2015-07-25 07:15 | 152
2015-07-25 07:30 | 147
2015-07-25 07:45 | 144
2015-07-25 08:00 | 150
2015-07-25 08:15 | 168
2015-07-25 08:30 | 168
2015-07-25 08:45 | 158
2015-07-25 09:00 | 162
2015-07-25 09:15 | 161
2015-07-25 09:30 | 167
2015-07-25 09:45 | 170
2015-07-25 10:00 | 162
2015-07-25 10:15 | 163
2015-07-25 10:30 | 161
2015-07-25 10:45 | 170
2015-07-25 11:00 | 183
2015-07-25 11:15 | 165
2015-07-25 11:30 | 174
2015-07-25 11:45 | 173
2015-07-25 12:00 | 185
2015-07-25 12:15 | 182
2015-07-25 12:30 | 180
2015-07-25 12:45 | 175
2015-07-25 13:00 | 184
2015-07-25 13:15 | 194
2015-07-25 13:30 | 187
2015-07-25 13:45 | 185
2015-07-25 14:00 | 183
2015-07-25 14:15 | 186
2015-07-25 14:30 | 187
2015-07-25 14:45 | 191
2015-07-25 15:00 | 185
2015-07-25 15:15 | 188
2015-07-25 15:30 | 192
2015-07-25 15:45 | 214
2015-07-25 16:00 | 202
2015-07-25 16:15 | 200
2015-07-25 16:30 | 203
2015-07-25 16:45 | 198
2015-07-25 17:00 | 200
2015-07-25 17:15 | 219
2015-07-25 17:30 | 202
2015-07-25 17:45 | 198
2015-07-25 18:00 | 210
2015-07-25 18:15 | 207
2015-07-25 18:30 | 210
2015-07-25 18:45 | 200
2015-07-25 19:00 | 201
2015-07-25 19:15 | 195
2015-07-25 19:30 | 192
2015-07-25 19:45 | 193
2015-07-25 20:00 | 202
2015-07-25 20:15 | 189
2015-07-25 20:30 | 185
2015-07-25 20:45 | 175
2015-07-25 21:00 | 192
2015-07-25 21:15 | 182
2015-07-25 21:30 | 171
2015-07-25 21:45 | 183
2015-07-25 22:00 | 170
2015-07-25 22:15 | 161
2015-07-25 22:30 | 176
2015-07-25 22:45 | 181
2015-07-25 23:00 | 160
2015-07-25 23:15 | 173
2015-07-25 23:30 | 161
2015-07-25 23:45 | 169
2015-07-26 | 182
2015-07-26 00:15 | 169
2015-07-26 00:30 | 164
2015-07-26 00:45 | 162
2015-07-26 01:00 | 178
2015-07-26 01:15 | 164
2015-07-26 01:30 | 158
2015-07-26 01:45 | 164
2015-07-26 02:00 | 172
2015-07-26 02:15 | 167
2015-07-26 02:30 | 160
2015-07-26 02:45 | 158
2015-07-26 03:00 | 170
2015-07-26 03:15 | 163
2015-07-26 03:30 | 159
2015-07-26 03:45 | 158
2015-07-26 04:00 | 152
2015-07-26 04:15 | 175
2015-07-26 04:30 | 166
2015-07-26 04:45 | 157
2015-07-26 05:00 | 158
2015-07-26 05:15 | 170
2015-07-26 05:30 | 161
2015-07-26 05:45 | 156
2015-07-26 06:00 | 154
2015-07-26 06:15 | 151
2015-07-26 06:30 | 172
2015-07-26 06:45 | 158
2015-07-26 07:00 | 164
2015-07-26 07:15 | 165
2015-07-26 07:30 | 176
2015-07-26 07:45 | 174
2015-07-26 08:00 | 168
2015-07-26 08:15 | 173
2015-07-26 08:30 | 170
2015-07-26 08:45 | 187
2015-07-26 09:00 | 179
2015-07-26 09:15 | 171
2015-07-26 09:30 | 169
2015-07-26 09:45 | 178
2015-07-26 10:00 | 190
2015-07-26 10:15 | 176
2015-07-26 10:30 | 186
2015-07-26 10:45 | 181
2015-07-26 11:00 | 196
2015-07-26 11:15 | 197
2015-07-26 11:30 | 190
2015-07-26 11:45 | 192
2015-07-26 12:00 | 189
2015-07-26 12:15 | 207
2015-07-26 12:30 | 202
2015-07-26 12:45 | 198
2015-07-26 13:00 | 199
2015-07-26 13:15 | 204
2015-07-26 13:30 | 199
2015-07-26 13:45 | 217
2015-07-26 14:00 | 192
2015-07-26 14:15 | 211
2015-07-26 14:30 | 196
2015-07-26 14:45 | 227
2015-07-26 15:00 | 201
2015-07-26 15:15 | 207
2015-07-26 15:30 | 209
2015-07-26 15:45 | 208
2015-07-26 16:00 | 204
2015-07-26 16:15 | 223
2015-07-26 16:30 | 205
2015-07-26 16:45 | 208
2015-07-26 17:00 | 206
2015-07-26 17:15 | 214
2015-07-26 17:30 | 227
2015-07-26 17:45 | 213
2015-07-26 18:00 | 213
2015-07-26 18:15 | 213
2015-07-26 18:30 | 211
2015-07-26 18:45 | 202
2015-07-26 19:00 | 212
2015-07-26 19:15 | 219
2015-07-26 19:30 | 198
2015-07-26 19:45 | 199
2015-07-26 20:00 | 198
2015-07-26 20:15 | 194
2015-07-26 20:30 | 206
2015-07-26 20:45 | 192
2015-07-26 21:00 | 190
2015-07-26 21:15 | 180
2015-07-26 21:30 | 185
2015-07-26 21:45 | 182
2015-07-26 22:00 | 174
2015-07-26 22:15 | 170
2015-07-26 22:30 | 175
2015-07-26 22:45 | 185
2015-07-26 23:00 | 165
2015-07-26 23:15 | 174
2015-07-26 23:30 | 167
2015-07-26 23:45 | 179
2015-07-27 | 162
2015-07-27 00:15 | 159
2015-07-27 00:30 | 159
2015-07-27 00:45 | 171
2015-07-27 01:00 | 158
2015-07-27 01:15 | 154
2015-07-27 01:30 | 162
2015-07-27 01:45 | 153
2015-07-27 02:00 | 179
2015-07-27 02:15 | 149
2015-07-27 02:30 | 157
2015-07-27 02:45 | 151
2015-07-27 03:00 | 171
2015-07-27 03:15 | 150
2015-07-27 03:30 | 155
2015-07-27 03:45 | 147
2015-07-27 04:00 | 147
2015-07-27 04:15 | 159
2015-07-27 04:30 | 152
2015-07-27 04:45 | 154
2015-07-27 05:00 | 150
2015-07-27 05:15 | 145
2015-07-27 05:30 | 155
2015-07-27 05:45 | 153
2015-07-27 06:00 | 147
2015-07-27 06:15 | 143
2015-07-27 06:30 | 145
2015-07-27 06:45 | 153
2015-07-27 07:00 | 165
2015-07-27 07:15 | 159
2015-07-27 07:30 | 158
2015-07-27 07:45 | 157
2015-07-27 08:00 | 162
2015-07-27 08:15 | 176
2015-07-27 08:30 | 177
2015-07-27 08:45 | 166
2015-07-27 09:00 | 176
2015-07-27 09:15 | 179
2015-07-27 09:30 | 188
2015-07-27 09:45 | 196
2015-07-27 10:00 | 197
2015-07-27 10:15 | 195
2015-07-27 10:30 | 197
2015-07-27 10:45 | 215
2015-07-27 11:00 | 201
2015-07-27 11:15 | 209
2015-07-27 11:30 | 203
2015-07-27 11:45 | 209
2015-07-27 12:00 | 219
2015-07-27 12:15 | 208
2015-07-27 12:30 | 213
2015-07-27 12:45 | 221
2015-07-27 13:00 | 216
2015-07-27 13:15 | 236
2015-07-27 13:30 | 214
2015-07-27 13:45 | 225
2015-07-27 14:00 | 226
2015-07-27 14:15 | 231
2015-07-27 14:30 | 237
2015-07-27 14:45 | 234
2015-07-27 15:00 | 238
2015-07-27 15:15 | 240
2015-07-27 15:30 | 248
2015-07-27 15:45 | 242
2015-07-27 16:00 | 251
2015-07-27 16:15 | 237
2015-07-27 16:30 | 255
2015-07-27 16:45 | 264
2015-07-27 17:00 | 246
2015-07-27 17:15 | 248
2015-07-27 17:30 | 246
2015-07-27 17:45 | 251
2015-07-27 18:00 | 260
2015-07-27 18:15 | 229
2015-07-27 18:30 | 240
2015-07-27 18:45 | 233
2015-07-27 19:00 | 244
2015-07-27 19:15 | 238
2015-07-27 19:30 | 226
2015-07-27 19:45 | 216
2015-07-27 20:00 | 222
2015-07-27 20:15 | 208
2015-07-27 20:30 | 216
2015-07-27 20:45 | 215
2015-07-27 21:00 | 203
2015-07-27 21:15 | 191
2015-07-27 21:30 | 190
2015-07-27 21:45 | 199
2015-07-27 22:00 | 189
2015-07-27 22:15 | 188
2015-07-27 22:30 | 193
2015-07-27 22:45 | 193
2015-07-27 23:00 | 203
2015-07-27 23:15 | 182
2015-07-27 23:30 | 181
2015-07-27 23:45 | 181
2015-07-28 | 194
2015-07-28 00:15 | 173
2015-07-28 00:30 | 176
2015-07-28 00:45 | 169
2015-07-28 01:00 | 174
2015-07-28 01:15 | 172
2015-07-28 01:30 | 161
2015-07-28 01:45 | 159
2015-07-28 02:00 | 165
2015-07-28 02:15 | 171
2015-07-28 02:30 | 161
2015-07-28 02:45 | 152
2015-07-28 03:00 | 158
2015-07-28 03:15 | 170
2015-07-28 03:30 | 157
2015-07-28 03:45 | 152
2015-07-28 04:00 | 157
2015-07-28 04:15 | 149
2015-07-28 04:30 | 169
2015-07-28 04:45 | 154
2015-07-28 05:00 | 159
2015-07-28 05:15 | 151
2015-07-28 05:30 | 170
2015-07-28 05:45 | 154
2015-07-28 06:00 | 163
2015-07-28 06:15 | 151
2015-07-28 06:30 | 151
2015-07-28 06:45 | 158
2015-07-28 07:00 | 170
2015-07-28 07:15 | 167
2015-07-28 07:30 | 162
2015-07-28 07:45 | 167
2015-07-28 08:00 | 166
2015-07-28 08:15 | 176
2015-07-28 08:30 | 180
2015-07-28 08:45 | 188
2015-07-28 09:00 | 172
2015-07-28 09:15 | 186
2015-07-28 09:30 | 187
2015-07-28 09:45 | 201
2015-07-28 10:00 | 194
2015-07-28 10:15 | 195
2015-07-28 10:30 | 200
2015-07-28 10:45 | 221
2015-07-28 11:00 | 206
2015-07-28 11:15 | 210
2015-07-28 11:30 | 225
2015-07-28 11:45 | 224
2015-07-28 12:00 | 238
2015-07-28 12:15 | 230
2015-07-28 12:30 | 236
2015-07-28 12:45 | 245
2015-07-28 13:00 | 250
2015-07-28 13:15 | 259
2015-07-28 13:30 | 247
2015-07-28 13:45 | 249
2015-07-28 14:00 | 247
2015-07-28 14:15 | 267
2015-07-28 14:30 | 253
2015-07-28 14:45 | 256
2015-07-28 15:00 | 257
2015-07-28 15:15 | 261
2015-07-28 15:30 | 258
2015-07-28 15:45 | 278
2015-07-28 16:00 | 267
2015-07-28 16:15 | 274
2015-07-28 16:30 | 270
2015-07-28 16:45 | 268
2015-07-28 17:00 | 285
2015-07-28 17:15 | 278
2015-07-28 17:30 | 268
2015-07-28 17:45 | 273
2015-07-28 18:00 | 285
2015-07-28 18:15 | 266
2015-07-28 18:30 | 263
2015-07-28 18:45 | 263
2015-07-28 19:00 | 256
2015-07-28 19:15 | 258
2015-07-28 19:30 | 254
2015-07-28 19:45 | 247
2015-07-28 20:00 | 247
2015-07-28 20:15 | 234
2015-07-28 20:30 | 239
2015-07-28 20:45 | 234
2015-07-28 21:00 | 227
2015-07-28 21:15 | 218
2015-07-28 21:30 | 202
2015-07-28 21:45 | 209
2015-07-28 22:00 | 210
2015-07-28 22:15 | 197
2015-07-28 22:30 | 202
2015-07-28 22:45 | 206
2015-07-28 23:00 | 208
2015-07-28 23:15 | 191
2015-07-28 23:30 | 188
2015-07-28 23:45 | 190
2015-07-29 | 200
2015-07-29 00:15 | 181
2015-07-29 00:30 | 185
2015-07-29 00:45 | 175
2015-07-29 01:00 | 192
2015-07-29 01:15 | 184
2015-07-29 01:30 | 174
2015-07-29 01:45 | 170
2015-07-29 02:00 | 175
2015-07-29 02:15 | 181
2015-07-29 02:30 | 169
2015-07-29 02:45 | 166
2015-07-29 03:00 | 175
2015-07-29 03:15 | 173
2015-07-29 03:30 | 165
2015-07-29 03:45 | 160
2015-07-29 04:00 | 163
2015-07-29 04:15 | 175
2015-07-29 04:30 | 156
2015-07-29 04:45 | 164
2015-07-29 05:00 | 163
2015-07-29 05:15 | 168
2015-07-29 05:30 | 161
2015-07-29 05:45 | 155
2015-07-29 06:00 | 163
2015-07-29 06:15 | 158
2015-07-29 06:30 | 168
2015-07-29 06:45 | 178
2015-07-29 07:00 | 176
2015-07-29 07:15 | 181
2015-07-29 07:30 | 171
2015-07-29 07:45 | 170
2015-07-29 08:00 | 195
2015-07-29 08:15 | 177
2015-07-29 08:30 | 180
2015-07-29 08:45 | 196
2015-07-29 09:00 | 203
2015-07-29 09:15 | 180
2015-07-29 09:30 | 194
2015-07-29 09:45 | 194
2015-07-29 10:00 | 203
2015-07-29 10:15 | 222
2015-07-29 10:30 | 208
2015-07-29 10:45 | 212
2015-07-29 11:00 | 216
2015-07-29 11:15 | 236
2015-07-29 11:30 | 226
2015-07-29 11:45 | 236
2015-07-29 12:00 | 229
2015-07-29 12:15 | 245
2015-07-29 12:30 | 243
2015-07-29 12:45 | 239
2015-07-29 13:00 | 230
2015-07-29 13:15 | 238
2015-07-29 13:30 | 230
2015-07-29 13:45 | 268
2015-07-29 14:00 | 234
2015-07-29 14:15 | 248
2015-07-29 14:30 | 242
2015-07-29 14:45 | 252
2015-07-29 15:00 | 272
2015-07-29 15:15 | 259
2015-07-29 15:30 | 249
2015-07-29 15:45 | 255
2015-07-29 16:00 | 258
2015-07-29 16:15 | 271
2015-07-29 16:30 | 248
2015-07-29 16:45 | 253
2015-07-29 17:00 | 260
2015-07-29 17:15 | 251
2015-07-29 17:30 | 252
2015-07-29 17:45 | 250
2015-07-29 18:00 | 245
2015-07-29 18:15 | 253
2015-07-29 18:30 | 251
2015-07-29 18:45 | 243
2015-07-29 19:00 | 236
2015-07-29 19:15 | 238
2015-07-29 19:30 | 233
2015-07-29 19:45 | 229
2015-07-29 20:00 | 231
2015-07-29 20:15 | 224
2015-07-29 20:30 | 215
2015-07-29 20:45 | 222
2015-07-29 21:00 | 218
2015-07-29 21:15 | 218
2015-07-29 21:30 | 204
2015-07-29 21:45 | 200
2015-07-29 22:00 | 199
2015-07-29 22:15 | 210
2015-07-29 22:30 | 198
2015-07-29 22:45 | 194
2015-07-29 23:00 | 185
2015-07-29 23:15 | 188
2015-07-29 23:30 | 193
2015-07-29 23:45 | 179
2015-07-30 | 183
2015-07-30 00:15 | 176
2015-07-30 00:30 | 196
2015-07-30 00:45 | 186
2015-07-30 01:00 | 183
2015-07-30 01:15 | 187
2015-07-30 01:30 | 175
2015-07-30 01:45 | 191
2015-07-30 02:00 | 179
2015-07-30 02:15 | 169
2015-07-30 02:30 | 176
2015-07-30 02:45 | 177
2015-07-30 03:00 | 186
2015-07-30 03:15 | 170
2015-07-30 03:30 | 177
2015-07-30 03:45 | 175
2015-07-30 04:00 | 172
2015-07-30 04:15 | 184
2015-07-30 04:30 | 173
2015-07-30 04:45 | 171
2015-07-30 05:00 | 171
2015-07-30 05:15 | 191
2015-07-30 05:30 | 172
2015-07-30 05:45 | 169
2015-07-30 06:00 | 172
2015-07-30 06:15 | 174
2015-07-30 06:30 | 186
2015-07-30 06:45 | 174
2015-07-30 07:00 | 178
2015-07-30 07:15 | 182
2015-07-30 07:30 | 181
2015-07-30 07:45 | 180
2015-07-30 08:00 | 179
2015-07-30 08:15 | 182
2015-07-30 08:30 | 183
2015-07-30 08:45 | 194
2015-07-30 09:00 | 191
2015-07-30 09:15 | 184
2015-07-30 09:30 | 196
2015-07-30 09:45 | 201
2015-07-30 10:00 | 220
2015-07-30 10:15 | 200
2015-07-30 10:30 | 214
2015-07-30 10:45 | 207
2015-07-30 11:00 | 206
2015-07-30 11:15 | 226
2015-07-30 11:30 | 222
2015-07-30 11:45 | 223
2015-07-30 12:00 | 215
2015-07-30 12:15 | 221
2015-07-30 12:30 | 242
2015-07-30 12:45 | 215
2015-07-30 13:00 | 235
2015-07-30 13:15 | 232
2015-07-30 13:30 | 227
2015-07-30 13:45 | 229
2015-07-30 14:00 | 238
2015-07-30 14:15 | 239
2015-07-30 14:30 | 264
2015-07-30 14:45 | 233
2015-07-30 15:00 | 246
2015-07-30 15:15 | 244
2015-07-30 15:30 | 256
2015-07-30 15:45 | 250
2015-07-30 16:00 | 252
2015-07-30 16:15 | 263
2015-07-30 16:30 | 254
2015-07-30 16:45 | 238
2015-07-30 17:00 | 251
2015-07-30 17:15 | 257
2015-07-30 17:30 | 243
2015-07-30 17:45 | 272
2015-07-30 18:00 | 251
2015-07-30 18:15 | 254
2015-07-30 18:30 | 249
2015-07-30 18:45 | 254
2015-07-30 19:00 | 241
2015-07-30 19:15 | 235
2015-07-30 19:30 | 223
2015-07-30 19:45 | 226
2015-07-30 20:00 | 219
2015-07-30 20:15 | 231
2015-07-30 20:30 | 216
2015-07-30 20:45 | 209
2015-07-30 21:00 | 219
2015-07-30 21:15 | 211
2015-07-30 21:30 | 202
2015-07-30 21:45 | 194
2015-07-30 22:00 | 193
2015-07-30 22:15 | 192
2015-07-30 22:30 | 193
2015-07-30 22:45 | 203
2015-07-30 23:00 | 186
2015-07-30 23:15 | 192
2015-07-30 23:30 | 192
2015-07-30 23:45 | 199
2015-07-31 | 187
2015-07-31 00:15 | 185
2015-07-31 00:30 | 187
2015-07-31 00:45 | 191
2015-07-31 01:00 | 198
2015-07-31 01:15 | 185
2015-07-31 01:30 | 184
2015-07-31 01:45 | 180
2015-07-31 02:00 | 199
2015-07-31 02:15 | 183
2015-07-31 02:30 | 185
2015-07-31 02:45 | 187
2015-07-31 03:00 | 174
2015-07-31 03:15 | 176
2015-07-31 03:30 | 182
2015-07-31 03:45 | 190
2015-07-31 04:00 | 174
2015-07-31 04:15 | 173
2015-07-31 04:30 | 166
2015-07-31 04:45 | 187
2015-07-31 05:00 | 180
2015-07-31 05:15 | 162
2015-07-31 05:30 | 167
2015-07-31 05:45 | 168
2015-07-31 06:00 | 183
2015-07-31 06:15 | 170
2015-07-31 06:30 | 183
2015-07-31 06:45 | 178
2015-07-31 07:00 | 178
2015-07-31 07:15 | 195
2015-07-31 07:30 | 180
2015-07-31 07:45 | 181
2015-07-31 08:00 | 184
2015-07-31 08:15 | 198
2015-07-31 08:30 | 183
2015-07-31 08:45 | 178
2015-07-31 09:00 | 173
2015-07-31 09:15 | 186
2015-07-31 09:30 | 202
2015-07-31 09:45 | 197
2015-07-31 10:00 | 215
2015-07-31 10:15 | 204
2015-07-31 10:30 | 194
2015-07-31 10:45 | 197
2015-07-31 11:00 | 216
2015-07-31 11:15 | 211
2015-07-31 11:30 | 205
2015-07-31 11:45 | 207
2015-07-31 12:00 | 207
2015-07-31 12:15 | 223
2015-07-31 12:30 | 229
2015-07-31 12:45 | 215
2015-07-31 13:00 | 206
2015-07-31 13:15 | 213
2015-07-31 13:30 | 227
2015-07-31 13:45 | 232
2015-07-31 14:00 | 223
2015-07-31 14:15 | 229
2015-07-31 14:30 | 228
2015-07-31 14:45 | 222
2015-07-31 15:00 | 229
2015-07-31 15:15 | 231
2015-07-31 15:30 | 251
2015-07-31 15:45 | 216
2015-07-31 16:00 | 231
2015-07-31 16:15 | 224
2015-07-31 16:30 | 240
2015-07-31 16:45 | 232
2015-07-31 17:00 | 226
2015-07-31 17:15 | 239
2015-07-31 17:30 | 231
2015-07-31 17:45 | 243
2015-07-31 18:00 | 222
2015-07-31 18:15 | 229
2015-07-31 18:30 | 219
2015-07-31 18:45 | 219
2015-07-31 19:00 | 236
2015-07-31 19:15 | 228
2015-07-31 19:30 | 216
2015-07-31 19:45 | 218
2015-07-31 20:00 | 229
2015-07-31 20:15 | 211
2015-07-31 20:30 | 206
2015-07-31 20:45 | 207
2015-07-31 21:00 | 204
2015-07-31 21:15 | 194
2015-07-31 21:30 | 198
2015-07-31 21:45 | 178
2015-07-31 22:00 | 188
2015-07-31 22:15 | 180
2015-07-31 22:30 | 190
2015-07-31 22:45 | 196
2015-07-31 23:00 | 182
2015-07-31 23:15 | 200
2015-07-31 23:30 | 180
2015-07-31 23:45 | 176
2015-08-01 | 173
2015-08-01 00:15 | 179
2015-08-01 00:30 | 170
2015-08-01 00:45 | 162
2015-08-01 01:00 | 164
2015-08-01 01:15 | 152
2015-08-01 01:30 | 174
2015-08-01 01:45 | 168
2015-08-01 02:00 | 156
2015-08-01 02:15 | 156
2015-08-01 02:30 | 172
2015-08-01 02:45 | 167
2015-08-01 03:00 | 159
2015-08-01 03:15 | 158
2015-08-01 03:30 | 157
2015-08-01 03:45 | 173
2015-08-01 04:00 | 158
2015-08-01 04:15 | 157
2015-08-01 04:30 | 156
2015-08-01 04:45 | 166
2015-08-01 05:00 | 165
2015-08-01 05:15 | 158
2015-08-01 05:30 | 154
2015-08-01 05:45 | 148
2015-08-01 06:00 | 167
2015-08-01 06:15 | 157
2015-08-01 06:30 | 151
2015-08-01 06:45 | 148
2015-08-01 07:00 | 167
2015-08-01 07:15 | 164
2015-08-01 07:30 | 154
2015-08-01 07:45 | 157
2015-08-01 08:00 | 154
2015-08-01 08:15 | 169
2015-08-01 08:30 | 158
2015-08-01 08:45 | 154
2015-08-01 09:00 | 155
2015-08-01 09:15 | 162
2015-08-01 09:30 | 167
2015-08-01 09:45 | 157
2015-08-01 10:00 | 160
2015-08-01 10:15 | 161
2015-08-01 10:30 | 169
2015-08-01 10:45 | 179
2015-08-01 11:00 | 163
2015-08-01 11:15 | 173
2015-08-01 11:30 | 172
2015-08-01 11:45 | 196
2015-08-01 12:00 | 178
2015-08-01 12:15 | 180
2015-08-01 12:30 | 176
2015-08-01 12:45 | 179
2015-08-01 13:00 | 195
2015-08-01 13:15 | 177
2015-08-01 13:30 | 182
2015-08-01 13:45 | 177
2015-08-01 14:00 | 191
2015-08-01 14:15 | 191
2015-08-01 14:30 | 188
2015-08-01 14:45 | 188
2015-08-01 15:00 | 186
2015-08-01 15:15 | 185
2015-08-01 15:30 | 207
2015-08-01 15:45 | 193
2015-08-01 16:00 | 198
2015-08-01 16:15 | 188
2015-08-01 16:30 | 189
2015-08-01 16:45 | 210
2015-08-01 17:00 | 196
2015-08-01 17:15 | 209
2015-08-01 17:30 | 202
2015-08-01 17:45 | 203
2015-08-01 18:00 | 194
2015-08-01 18:15 | 194
2015-08-01 18:30 | 214
2015-08-01 18:45 | 201
2015-08-01 19:00 | 193
2015-08-01 19:15 | 195
2015-08-01 19:30 | 190
2015-08-01 19:45 | 203
2015-08-01 20:00 | 179
2015-08-01 20:15 | 185
2015-08-01 20:30 | 178
2015-08-01 20:45 | 194
2015-08-01 21:00 | 181
2015-08-01 21:15 | 183
2015-08-01 21:30 | 173
2015-08-01 21:45 | 175
2015-08-01 22:00 | 182
2015-08-01 22:15 | 179
2015-08-01 22:30 | 168
2015-08-01 22:45 | 165
2015-08-01 23:00 | 177
2015-08-01 23:15 | 181
2015-08-01 23:30 | 163
2015-08-01 23:45 | 177
2015-08-02 | 169
2015-08-02 00:15 | 170
2015-08-02 00:30 | 170
2015-08-02 00:45 | 166
2015-08-02 01:00 | 163
2015-08-02 01:15 | 167
2015-08-02 01:30 | 175
2015-08-02 01:45 | 166
2015-08-02 02:00 | 160
2015-08-02 02:15 | 162
2015-08-02 02:30 | 177
2015-08-02 02:45 | 164
2015-08-02 03:00 | 158
2015-08-02 03:15 | 159
2015-08-02 03:30 | 163
2015-08-02 03:45 | 171
2015-08-02 04:00 | 157
2015-08-02 04:15 | 162
2015-08-02 04:30 | 159
2015-08-02 04:45 | 154
2015-08-02 05:00 | 173
2015-08-02 05:15 | 158
2015-08-02 05:30 | 156
2015-08-02 05:45 | 153
2015-08-02 06:00 | 168
2015-08-02 06:15 | 172
2015-08-02 06:30 | 165
2015-08-02 06:45 | 164
2015-08-02 07:00 | 163
2015-08-02 07:15 | 182
2015-08-02 07:30 | 163
2015-08-02 07:45 | 162
2015-08-02 08:00 | 160
2015-08-02 08:15 | 160
2015-08-02 08:30 | 169
2015-08-02 08:45 | 157
2015-08-02 09:00 | 159
2015-08-02 09:15 | 156
2015-08-02 09:30 | 161
2015-08-02 09:45 | 173
2015-08-02 10:00 | 157
2015-08-02 10:15 | 155
2015-08-02 10:30 | 156
2015-08-02 10:45 | 177
2015-08-02 11:00 | 169
2015-08-02 11:15 | 173
2015-08-02 11:30 | 164
2015-08-02 11:45 | 187
2015-08-02 12:00 | 182
2015-08-02 12:15 | 175
2015-08-02 12:30 | 178
2015-08-02 12:45 | 181
2015-08-02 13:00 | 188
2015-08-02 13:15 | 178
2015-08-02 13:30 | 178
2015-08-02 13:45 | 174
2015-08-02 14:00 | 186
2015-08-02 14:15 | 198
2015-08-02 14:30 | 178
2015-08-02 14:45 | 189
2015-08-02 15:00 | 186
2015-08-02 15:15 | 206
2015-08-02 15:30 | 191
2015-08-02 15:45 | 188
2015-08-02 16:00 | 191
2015-08-02 16:15 | 185
2015-08-02 16:30 | 196
2015-08-02 16:45 | 203
2015-08-02 17:00 | 198
2015-08-02 17:15 | 191
2015-08-02 17:30 | 194
2015-08-02 17:45 | 200
2015-08-02 18:00 | 210
2015-08-02 18:15 | 196
2015-08-02 18:30 | 208
2015-08-02 18:45 | 200
2015-08-02 19:00 | 192
2015-08-02 19:15 | 198
2015-08-02 19:30 | 188
2015-08-02 19:45 | 208
2015-08-02 20:00 | 180
2015-08-02 20:15 | 185
2015-08-02 20:30 | 182
2015-08-02 20:45 | 175
2015-08-02 21:00 | 189
2015-08-02 21:15 | 179
2015-08-02 21:30 | 167
2015-08-02 21:45 | 173
2015-08-02 22:00 | 177
2015-08-02 22:15 | 175
2015-08-02 22:30 | 168
2015-08-02 22:45 | 163
2015-08-02 23:00 | 161
2015-08-02 23:15 | 182
2015-08-02 23:30 | 162
2015-08-02 23:45 | 161
2015-08-03 | 160
2015-08-03 00:15 | 173
2015-08-03 00:30 | 155
2015-08-03 00:45 | 159
2015-08-03 01:00 | 158
2015-08-03 01:15 | 159
2015-08-03 01:30 | 170
2015-08-03 01:45 | 153
2015-08-03 02:00 | 147
2015-08-03 02:15 | 152
2015-08-03 02:30 | 160
2015-08-03 02:45 | 164
2015-08-03 03:00 | 150
2015-08-03 03:15 | 153
2015-08-03 03:30 | 151
2015-08-03 03:45 | 162
2015-08-03 04:00 | 154
2015-08-03 04:15 | 149
2015-08-03 04:30 | 143
2015-08-03 04:45 | 153
2015-08-03 05:00 | 170
2015-08-03 05:15 | 146
2015-08-03 05:30 | 152
2015-08-03 05:45 | 152
2015-08-03 06:00 | 152
2015-08-03 06:15 | 170
2015-08-03 06:30 | 150
2015-08-03 06:45 | 152
2015-08-03 07:00 | 148
2015-08-03 07:15 | 161
2015-08-03 07:30 | 160
2015-08-03 07:45 | 154
2015-08-03 08:00 | 158
2015-08-03 08:15 | 159
2015-08-03 08:30 | 180
2015-08-03 08:45 | 181
2015-08-03 09:00 | 173
2015-08-03 09:15 | 170
2015-08-03 09:30 | 181
2015-08-03 09:45 | 192
2015-08-03 10:00 | 189
2015-08-03 10:15 | 188
2015-08-03 10:30 | 197
2015-08-03 10:45 | 191
2015-08-03 11:00 | 213
2015-08-03 11:15 | 196
2015-08-03 11:30 | 202
2015-08-03 11:45 | 204
2015-08-03 12:00 | 195
2015-08-03 12:15 | 218
2015-08-03 12:30 | 204
2015-08-03 12:45 | 196
2015-08-03 13:00 | 203
2015-08-03 13:15 | 206
2015-08-03 13:30 | 221
2015-08-03 13:45 | 202
2015-08-03 14:00 | 210
2015-08-03 14:15 | 212
2015-08-03 14:30 | 218
2015-08-03 14:45 | 226
2015-08-03 15:00 | 211
2015-08-03 15:15 | 218
2015-08-03 15:30 | 219
2015-08-03 15:45 | 221
2015-08-03 16:00 | 231
2015-08-03 16:15 | 239
2015-08-03 16:30 | 222
2015-08-03 16:45 | 218
2015-08-03 17:00 | 240
2015-08-03 17:15 | 240
2015-08-03 17:30 | 221
2015-08-03 17:45 | 228
2015-08-03 18:00 | 225
2015-08-03 18:15 | 228
2015-08-03 18:30 | 248
2015-08-03 18:45 | 216
2015-08-03 19:00 | 220
2015-08-03 19:15 | 218
2015-08-03 19:30 | 215
2015-08-03 19:45 | 229
2015-08-03 20:00 | 209
2015-08-03 20:15 | 217
2015-08-03 20:30 | 210
2015-08-03 20:45 | 201
2015-08-03 21:00 | 201
2015-08-03 21:15 | 199
2015-08-03 21:30 | 195
2015-08-03 21:45 | 189
2015-08-03 22:00 | 183
2015-08-03 22:15 | 185
2015-08-03 22:30 | 199
2015-08-03 22:45 | 173
2015-08-03 23:00 | 176
2015-08-03 23:15 | 171
2015-08-03 23:30 | 168
2015-08-03 23:45 | 171
2015-08-04 | 177
2015-08-04 00:15 | 166
2015-08-04 00:30 | 168
2015-08-04 00:45 | 160
2015-08-04 01:00 | 171
2015-08-04 01:15 | 166
2015-08-04 01:30 | 164
2015-08-04 01:45 | 158
2015-08-04 02:00 | 176
2015-08-04 02:15 | 160
2015-08-04 02:30 | 159
2015-08-04 02:45 | 155
2015-08-04 03:00 | 153
2015-08-04 03:15 | 162
2015-08-04 03:30 | 167
2015-08-04 03:45 | 154
2015-08-04 04:00 | 157
2015-08-04 04:15 | 154
2015-08-04 04:30 | 166
2015-08-04 04:45 | 158
2015-08-04 05:00 | 157
2015-08-04 05:15 | 154
2015-08-04 05:30 | 151
2015-08-04 05:45 | 170
2015-08-04 06:00 | 159
2015-08-04 06:15 | 153
2015-08-04 06:30 | 160
2015-08-04 06:45 | 155
2015-08-04 07:00 | 160
2015-08-04 07:15 | 179
2015-08-04 07:30 | 160
2015-08-04 07:45 | 161
2015-08-04 08:00 | 166
2015-08-04 08:15 | 173
2015-08-04 08:30 | 177
2015-08-04 08:45 | 183
2015-08-04 09:00 | 180
2015-08-04 09:15 | 182
2015-08-04 09:30 | 176
2015-08-04 09:45 | 191
2015-08-04 10:00 | 194
2015-08-04 10:15 | 181
2015-08-04 10:30 | 188
2015-08-04 10:45 | 189
2015-08-04 11:00 | 201
2015-08-04 11:15 | 192
2015-08-04 11:30 | 187
2015-08-04 11:45 | 195
2015-08-04 12:00 | 192
2015-08-04 12:15 | 216
2015-08-04 12:30 | 202
2015-08-04 12:45 | 198
2015-08-04 13:00 | 208
2015-08-04 13:15 | 201
2015-08-04 13:30 | 224
2015-08-04 13:45 | 216
2015-08-04 14:00 | 212
2015-08-04 14:15 | 213
2015-08-04 14:30 | 207
2015-08-04 14:45 | 217
2015-08-04 15:00 | 208
2015-08-04 15:15 | 203
2015-08-04 15:30 | 203
2015-08-04 15:45 | 214
2015-08-04 16:00 | 220
2015-08-04 16:15 | 209
2015-08-04 16:30 | 215
2015-08-04 16:45 | 206
2015-08-04 17:00 | 221
2015-08-04 17:15 | 236
2015-08-04 17:30 | 210
2015-08-04 17:45 | 229
2015-08-04 18:00 | 216
2015-08-04 18:15 | 214
2015-08-04 18:30 | 223
2015-08-04 18:45 | 221
2015-08-04 19:00 | 213
2015-08-04 19:15 | 209
2015-08-04 19:30 | 205
2015-08-04 19:45 | 213
2015-08-04 20:00 | 216
2015-08-04 20:15 | 201
2015-08-04 20:30 | 210
2015-08-04 20:45 | 197
2015-08-04 21:00 | 196
2015-08-04 21:15 | 185
2015-08-04 21:30 | 200
2015-08-04 21:45 | 189
2015-08-04 22:00 | 180
2015-08-04 22:15 | 181
2015-08-04 22:30 | 184
2015-08-04 22:45 | 194
2015-08-04 23:00 | 176
2015-08-04 23:15 | 181
2015-08-04 23:30 | 172
2015-08-04 23:45 | 185
2015-08-05 | 170
2015-08-05 00:15 | 168
2015-08-05 00:30 | 167
2015-08-05 00:45 | 169
2015-08-05 01:00 | 182
2015-08-05 01:15 | 162
2015-08-05 01:30 | 164
2015-08-05 01:45 | 156
2015-08-05 02:00 | 168
2015-08-05 02:15 | 174
2015-08-05 02:30 | 157
2015-08-05 02:45 | 157
2015-08-05 03:00 | 162
2015-08-05 03:15 | 158
2015-08-05 03:30 | 168
2015-08-05 03:45 | 160
2015-08-05 04:00 | 154
2015-08-05 04:15 | 150
2015-08-05 04:30 | 162
2015-08-05 04:45 | 169
2015-08-05 05:00 | 155
2015-08-05 05:15 | 158
2015-08-05 05:30 | 156
2015-08-05 05:45 | 165
2015-08-05 06:00 | 162
2015-08-05 06:15 | 156
2015-08-05 06:30 | 156
2015-08-05 06:45 | 150
2015-08-05 07:00 | 163
2015-08-05 07:15 | 174
2015-08-05 07:30 | 160
2015-08-05 07:45 | 160
2015-08-05 08:00 | 177
2015-08-05 08:15 | 168
2015-08-05 08:30 | 194
2015-08-05 08:45 | 179
2015-08-05 09:00 | 188
2015-08-05 09:15 | 186
2015-08-05 09:30 | 195
2015-08-05 09:45 | 212
2015-08-05 10:00 | 202
2015-08-05 10:15 | 198
2015-08-05 10:30 | 198
2015-08-05 10:45 | 212
2015-08-05 11:00 | 209
2015-08-05 11:15 | 210
2015-08-05 11:30 | 203
2015-08-05 11:45 | 212
2015-08-05 12:00 | 217
2015-08-05 12:15 | 206
2015-08-05 12:30 | 212
2015-08-05 12:45 | 212
2015-08-05 13:00 | 214
2015-08-05 13:15 | 230
2015-08-05 13:30 | 216
2015-08-05 13:45 | 218
2015-08-05 14:00 | 226
2015-08-05 14:15 | 231
2015-08-05 14:30 | 239
2015-08-05 14:45 | 222
2015-08-05 15:00 | 229
2015-08-05 15:15 | 233
2015-08-05 15:30 | 229
2015-08-05 15:45 | 238
2015-08-05 16:00 | 240
2015-08-05 16:15 | 237
2015-08-05 16:30 | 235
2015-08-05 16:45 | 235
2015-08-05 17:00 | 253
2015-08-05 17:15 | 242
2015-08-05 17:30 | 230
2015-08-05 17:45 | 235
2015-08-05 18:00 | 231
2015-08-05 18:15 | 237
2015-08-05 18:30 | 236
2015-08-05 18:45 | 226
2015-08-05 19:00 | 228
2015-08-05 19:15 | 241
2015-08-05 19:30 | 224
2015-08-05 19:45 | 214
2015-08-05 20:00 | 215
2015-08-05 20:15 | 207
2015-08-05 20:30 | 222
2015-08-05 20:45 | 218
2015-08-05 21:00 | 203
2015-08-05 21:15 | 200
2015-08-05 21:30 | 193
2015-08-05 21:45 | 213
2015-08-05 22:00 | 198
2015-08-05 22:15 | 212
2015-08-05 22:30 | 200
2015-08-05 22:45 | 197
2015-08-05 23:00 | 197
2015-08-05 23:15 | 205
2015-08-05 23:30 | 196
2015-08-05 23:45 | 189
2015-08-06 | 184
2015-08-06 00:15 | 185
2015-08-06 00:30 | 198
2015-08-06 00:45 | 182
2015-08-06 01:00 | 176
2015-08-06 01:15 | 173
2015-08-06 01:30 | 186
2015-08-06 01:45 | 181
2015-08-06 02:00 | 168
2015-08-06 02:15 | 176
2015-08-06 02:30 | 167
2015-08-06 02:45 | 181
2015-08-06 03:00 | 169
2015-08-06 03:15 | 172
2015-08-06 03:30 | 164
2015-08-06 03:45 | 170
2015-08-06 04:00 | 189
2015-08-06 04:15 | 169
2015-08-06 04:30 | 163
2015-08-06 04:45 | 167
2015-08-06 05:00 | 168
2015-08-06 05:15 | 172
2015-08-06 05:30 | 167
2015-08-06 05:45 | 159
2015-08-06 06:00 | 160
2015-08-06 06:15 | 158
2015-08-06 06:30 | 179
2015-08-06 06:45 | 161
2015-08-06 07:00 | 160
2015-08-06 07:15 | 171
2015-08-06 07:30 | 163
2015-08-06 07:45 | 182
2015-08-06 08:00 | 175
2015-08-06 08:15 | 174
2015-08-06 08:30 | 179
2015-08-06 08:45 | 200
2015-08-06 09:00 | 195
2015-08-06 09:15 | 189
2015-08-06 09:30 | 198
2015-08-06 09:45 | 193
2015-08-06 10:00 | 210
2015-08-06 10:15 | 205
2015-08-06 10:30 | 201
2015-08-06 10:45 | 200
2015-08-06 11:00 | 206
2015-08-06 11:15 | 207
2015-08-06 11:30 | 198
2015-08-06 11:45 | 209
2015-08-06 12:00 | 204
2015-08-06 12:15 | 214
2015-08-06 12:30 | 227
2015-08-06 12:45 | 214
2015-08-06 13:00 | 209
2015-08-06 13:15 | 207
2015-08-06 13:30 | 212
2015-08-06 13:45 | 207
2015-08-06 14:00 | 212
2015-08-06 14:15 | 211
2015-08-06 14:30 | 215
2015-08-06 14:45 | 226
2015-08-06 15:00 | 209
2015-08-06 15:15 | 220
2015-08-06 15:30 | 215
2015-08-06 15:45 | 232
2015-08-06 16:00 | 231
2015-08-06 16:15 | 220
2015-08-06 16:30 | 225
2015-08-06 16:45 | 234
2015-08-06 17:00 | 211
2015-08-06 17:15 | 225
2015-08-06 17:30 | 225
2015-08-06 17:45 | 249
2015-08-06 18:00 | 232
2015-08-06 18:15 | 231
2015-08-06 18:30 | 236
2015-08-06 18:45 | 219
2015-08-06 19:00 | 245
2015-08-06 19:15 | 224
2015-08-06 19:30 | 209
2015-08-06 19:45 | 208
2015-08-06 20:00 | 205
2015-08-06 20:15 | 217
2015-08-06 20:30 | 204
2015-08-06 20:45 | 193
2015-08-06 21:00 | 201
2015-08-06 21:15 | 196
2015-08-06 21:30 | 206
2015-08-06 21:45 | 191
2015-08-06 22:00 | 178
2015-08-06 22:15 | 184
2015-08-06 22:30 | 207
2015-08-06 22:45 | 188
2015-08-06 23:00 | 189
2015-08-06 23:15 | 197
2015-08-06 23:30 | 188
2015-08-06 23:45 | 192
2015-08-07 | 179
2015-08-07 00:15 | 171
2015-08-07 00:30 | 160
2015-08-07 00:45 | 167
2015-08-07 01:00 | 175
2015-08-07 01:15 | 162
2015-08-07 01:30 | 157
2015-08-07 01:45 | 155
2015-08-07 02:00 | 173
2015-08-07 02:15 | 170
2015-08-07 02:30 | 157
2015-08-07 02:45 | 155
2015-08-07 03:00 | 171
2015-08-07 03:15 | 169
2015-08-07 03:30 | 155
2015-08-07 03:45 | 162
2015-08-07 04:00 | 170
2015-08-07 04:15 | 150
2015-08-07 04:30 | 146
2015-08-07 04:45 | 151
2015-08-07 05:00 | 161
2015-08-07 05:15 | 159
2015-08-07 05:30 | 143
2015-08-07 05:45 | 147
2015-08-07 06:00 | 145
2015-08-07 06:15 | 164
2015-08-07 06:30 | 158
2015-08-07 06:45 | 150
2015-08-07 07:00 | 150
2015-08-07 07:15 | 166
2015-08-07 07:30 | 163
2015-08-07 07:45 | 153
2015-08-07 08:00 | 160
2015-08-07 08:15 | 162
2015-08-07 08:30 | 180
2015-08-07 08:45 | 178
2015-08-07 09:00 | 177
2015-08-07 09:15 | 180
2015-08-07 09:30 | 180
2015-08-07 09:45 | 199
2015-08-07 10:00 | 182
2015-08-07 10:15 | 181
2015-08-07 10:30 | 193
2015-08-07 10:45 | 200
2015-08-07 11:00 | 206
2015-08-07 11:15 | 203
2015-08-07 11:30 | 193
2015-08-07 11:45 | 200
2015-08-07 12:00 | 199
2015-08-07 12:15 | 216
2015-08-07 12:30 | 202
2015-08-07 12:45 | 205
2015-08-07 13:00 | 207
2015-08-07 13:15 | 204
2015-08-07 13:30 | 224
2015-08-07 13:45 | 213
2015-08-07 14:00 | 220
2015-08-07 14:15 | 216
2015-08-07 14:30 | 236
2015-08-07 14:45 | 235
2015-08-07 15:00 | 230
2015-08-07 15:15 | 237
2015-08-07 15:30 | 230
2015-08-07 15:45 | 245
2015-08-07 16:00 | 245
2015-08-07 16:15 | 231
2015-08-07 16:30 | 232
2015-08-07 16:45 | 234
2015-08-07 17:00 | 239
2015-08-07 17:15 | 247
2015-08-07 17:30 | 237
2015-08-07 17:45 | 232
2015-08-07 18:00 | 236
2015-08-07 18:15 | 229
2015-08-07 18:30 | 234
2015-08-07 18:45 | 222
2015-08-07 19:00 | 224
2015-08-07 19:15 | 211
2015-08-07 19:30 | 229
2015-08-07 19:45 | 222
2015-08-07 20:00 | 204
2015-08-07 20:15 | 223
2015-08-07 20:30 | 208
2015-08-07 20:45 | 206
2015-08-07 21:00 | 201
2015-08-07 21:15 | 200
2015-08-07 21:30 | 196
2015-08-07 21:45 | 196
2015-08-07 22:00 | 191
2015-08-07 22:15 | 188
2015-08-07 22:30 | 193
2015-08-07 22:45 | 198
2015-08-07 23:00 | 191
2015-08-07 23:15 | 183
2015-08-07 23:30 | 181
2015-08-07 23:45 | 194
2015-08-08 | 165
2015-08-08 00:15 | 168
2015-08-08 00:30 | 165
2015-08-08 00:45 | 163
2015-08-08 01:00 | 178
2015-08-08 01:15 | 163
2015-08-08 01:30 | 155
2015-08-08 01:45 | 165
2015-08-08 02:00 | 171
2015-08-08 02:15 | 163
2015-08-08 02:30 | 156
2015-08-08 02:45 | 154
2015-08-08 03:00 | 169
2015-08-08 03:15 | 166
2015-08-08 03:30 | 154
2015-08-08 03:45 | 154
2015-08-08 04:00 | 157
2015-08-08 04:15 | 161
2015-08-08 04:30 | 166
2015-08-08 04:45 | 154
2015-08-08 05:00 | 146
2015-08-08 05:15 | 162
2015-08-08 05:30 | 164
2015-08-08 05:45 | 148
2015-08-08 06:00 | 141
2015-08-08 06:15 | 147
2015-08-08 06:30 | 163
2015-08-08 06:45 | 150
2015-08-08 07:00 | 144
2015-08-08 07:15 | 150
2015-08-08 07:30 | 151
2015-08-08 07:45 | 157
2015-08-08 08:00 | 143
2015-08-08 08:15 | 145
2015-08-08 08:30 | 145
2015-08-08 08:45 | 159
2015-08-08 09:00 | 160
2015-08-08 09:15 | 152
2015-08-08 09:30 | 153
2015-08-08 09:45 | 149
2015-08-08 10:00 | 167
2015-08-08 10:15 | 158
2015-08-08 10:30 | 151
2015-08-08 10:45 | 158
2015-08-08 11:00 | 152
2015-08-08 11:15 | 163
2015-08-08 11:30 | 185
2015-08-08 11:45 | 166
2015-08-08 12:00 | 164
2015-08-08 12:15 | 166
2015-08-08 12:30 | 177
2015-08-08 12:45 | 183
2015-08-08 13:00 | 169
2015-08-08 13:15 | 169
2015-08-08 13:30 | 180
2015-08-08 13:45 | 185
2015-08-08 14:00 | 172
2015-08-08 14:15 | 170
2015-08-08 14:30 | 181
2015-08-08 14:45 | 178
2015-08-08 15:00 | 196
2015-08-08 15:15 | 177
2015-08-08 15:30 | 186
2015-08-08 15:45 | 177
2015-08-08 16:00 | 202
2015-08-08 16:15 | 189
2015-08-08 16:30 | 181
2015-08-08 16:45 | 189
2015-08-08 17:00 | 177
2015-08-08 17:15 | 198
2015-08-08 17:30 | 185
2015-08-08 17:45 | 180
2015-08-08 18:00 | 178
2015-08-08 18:15 | 177
2015-08-08 18:30 | 188
2015-08-08 18:45 | 190
2015-08-08 19:00 | 177
2015-08-08 19:15 | 177
2015-08-08 19:30 | 173
2015-08-08 19:45 | 186
2015-08-08 20:00 | 179
2015-08-08 20:15 | 169
2015-08-08 20:30 | 166
2015-08-08 20:45 | 170
2015-08-08 21:00 | 180
2015-08-08 21:15 | 162
2015-08-08 21:30 | 158
2015-08-08 21:45 | 154
2015-08-08 22:00 | 172
2015-08-08 22:15 | 161
2015-08-08 22:30 | 154
2015-08-08 22:45 | 154
2015-08-08 23:00 | 163
2015-08-08 23:15 | 159
2015-08-08 23:30 | 155
2015-08-08 23:45 | 147
2015-08-09 | 153
2015-08-09 00:15 | 163
2015-08-09 00:30 | 144
2015-08-09 00:45 | 149
2015-08-09 01:00 | 145
2015-08-09 01:15 | 160
2015-08-09 01:30 | 154
2015-08-09 01:45 | 145
2015-08-09 02:00 | 142
2015-08-09 02:15 | 143
2015-08-09 02:30 | 163
2015-08-09 02:45 | 134
2015-08-09 03:00 | 145
2015-08-09 03:15 | 137
2015-08-09 03:30 | 139
2015-08-09 03:45 | 158
2015-08-09 04:00 | 137
2015-08-09 04:15 | 143
2015-08-09 04:30 | 135
2015-08-09 04:45 | 155
2015-08-09 05:00 | 142
2015-08-09 05:15 | 144
2015-08-09 05:30 | 138
2015-08-09 05:45 | 133
2015-08-09 06:00 | 150
2015-08-09 06:15 | 143
2015-08-09 06:30 | 149
2015-08-09 06:45 | 149
2015-08-09 07:00 | 150
2015-08-09 07:15 | 174
2015-08-09 07:30 | 151
2015-08-09 07:45 | 160
2015-08-09 08:00 | 157
2015-08-09 08:15 | 159
2015-08-09 08:30 | 166
2015-08-09 08:45 | 158
2015-08-09 09:00 | 165
2015-08-09 09:15 | 150
2015-08-09 09:30 | 163
2015-08-09 09:45 | 163
2015-08-09 10:00 | 176
2015-08-09 10:15 | 168
2015-08-09 10:30 | 161
2015-08-09 10:45 | 161
2015-08-09 11:00 | 175
2015-08-09 11:15 | 178
2015-08-09 11:30 | 195
2015-08-09 11:45 | 182
2015-08-09 12:00 | 177
2015-08-09 12:15 | 182
2015-08-09 12:30 | 189
2015-08-09 12:45 | 197
2015-08-09 13:00 | 183
2015-08-09 13:15 | 186
2015-08-09 13:30 | 190
2015-08-09 13:45 | 206
2015-08-09 14:00 | 183
2015-08-09 14:15 | 188
2015-08-09 14:30 | 192
2015-08-09 14:45 | 195
2015-08-09 15:00 | 210
2015-08-09 15:15 | 193
2015-08-09 15:30 | 203
2015-08-09 15:45 | 197
2015-08-09 16:00 | 223
2015-08-09 16:15 | 209
2015-08-09 16:30 | 210
2015-08-09 16:45 | 206
2015-08-09 17:00 | 213
2015-08-09 17:15 | 206
2015-08-09 17:30 | 232
2015-08-09 17:45 | 214
2015-08-09 18:00 | 209
2015-08-09 18:15 | 211
2015-08-09 18:30 | 215
2015-08-09 18:45 | 217
2015-08-09 19:00 | 197
2015-08-09 19:15 | 197
2015-08-09 19:30 | 194
2015-08-09 19:45 | 195
2015-08-09 20:00 | 202
2015-08-09 20:15 | 189
2015-08-09 20:30 | 191
2015-08-09 20:45 | 184
2015-08-09 21:00 | 201
2015-08-09 21:15 | 173
2015-08-09 21:30 | 183
2015-08-09 21:45 | 188
2015-08-09 22:00 | 172
2015-08-09 22:15 | 178
2015-08-09 22:30 | 175
2015-08-09 22:45 | 188
2015-08-09 23:00 | 170
2015-08-09 23:15 | 166
2015-08-09 23:30 | 167
2015-08-09 23:45 | 176
2015-08-10 | 181
2015-08-10 00:15 | 163
2015-08-10 00:30 | 167
2015-08-10 00:45 | 163
2015-08-10 01:00 | 174
2015-08-10 01:15 | 176
2015-08-10 01:30 | 160
2015-08-10 01:45 | 161
2015-08-10 02:00 | 162
2015-08-10 02:15 | 185
2015-08-10 02:30 | 158
2015-08-10 02:45 | 159
2015-08-10 03:00 | 158
2015-08-10 03:15 | 156
2015-08-10 03:30 | 168
2015-08-10 03:45 | 155
2015-08-10 04:00 | 152
2015-08-10 04:15 | 146
2015-08-10 04:30 | 167
2015-08-10 04:45 | 161
2015-08-10 05:00 | 147
2015-08-10 05:15 | 150
2015-08-10 05:30 | 152
2015-08-10 05:45 | 161
2015-08-10 06:00 | 156
2015-08-10 06:15 | 148
2015-08-10 06:30 | 149
2015-08-10 06:45 | 154
2015-08-10 07:00 | 165
2015-08-10 07:15 | 159
2015-08-10 07:30 | 157
2015-08-10 07:45 | 158
2015-08-10 08:00 | 167
2015-08-10 08:15 | 183
2015-08-10 08:30 | 170
2015-08-10 08:45 | 173
2015-08-10 09:00 | 184
2015-08-10 09:15 | 189
2015-08-10 09:30 | 193
2015-08-10 09:45 | 193
2015-08-10 10:00 | 201
2015-08-10 10:15 | 194
2015-08-10 10:30 | 200
2015-08-10 10:45 | 205
2015-08-10 11:00 | 195
2015-08-10 11:15 | 207
2015-08-10 11:30 | 201
2015-08-10 11:45 | 217
2015-08-10 12:00 | 216
2015-08-10 12:15 | 207
2015-08-10 12:30 | 206
2015-08-10 12:45 | 207
2015-08-10 13:00 | 231
2015-08-10 13:15 | 219
2015-08-10 13:30 | 231
2015-08-10 13:45 | 219
2015-08-10 14:00 | 234
2015-08-10 14:15 | 241
2015-08-10 14:30 | 239
2015-08-10 14:45 | 236
2015-08-10 15:00 | 225
2015-08-10 15:15 | 236
2015-08-10 15:30 | 227
2015-08-10 15:45 | 245
2015-08-10 16:00 | 227
2015-08-10 16:15 | 239
2015-08-10 16:30 | 227
2015-08-10 16:45 | 230
2015-08-10 17:00 | 247
2015-08-10 17:15 | 237
2015-08-10 17:30 | 230
2015-08-10 17:45 | 226
2015-08-10 18:00 | 229
2015-08-10 18:15 | 242
2015-08-10 18:30 | 219
2015-08-10 18:45 | 231
2015-08-10 19:00 | 218
2015-08-10 19:15 | 212
2015-08-10 19:30 | 203
2015-08-10 19:45 | 222
2015-08-10 20:00 | 210
2015-08-10 20:15 | 200
2015-08-10 20:30 | 204
2015-08-10 20:45 | 201
2015-08-10 21:00 | 209
2015-08-10 21:15 | 190
2015-08-10 21:30 | 183
2015-08-10 21:45 | 188
2015-08-10 22:00 | 200
2015-08-10 22:15 | 190
2015-08-10 22:30 | 182
2015-08-10 22:45 | 184
2015-08-10 23:00 | 177
2015-08-10 23:15 | 191
2015-08-10 23:30 | 176
2015-08-10 23:45 | 159
2015-08-11 | 167
2015-08-11 00:15 | 177
2015-08-11 00:30 | 163
2015-08-11 00:45 | 162
2015-08-11 01:00 | 159
2015-08-11 01:15 | 160
2015-08-11 01:30 | 176
2015-08-11 01:45 | 158
2015-08-11 02:00 | 154
2015-08-11 02:15 | 158
2015-08-11 02:30 | 164
2015-08-11 02:45 | 166
2015-08-11 03:00 | 155
2015-08-11 03:15 | 162
2015-08-11 03:30 | 149
2015-08-11 03:45 | 171
2015-08-11 04:00 | 161
2015-08-11 04:15 | 151
2015-08-11 04:30 | 156
2015-08-11 04:45 | 172
2015-08-11 05:00 | 159
2015-08-11 05:15 | 158
2015-08-11 05:30 | 156
2015-08-11 05:45 | 154
2015-08-11 06:00 | 174
2015-08-11 06:15 | 155
2015-08-11 06:30 | 150
2015-08-11 06:45 | 160
2015-08-11 07:00 | 165
2015-08-11 07:15 | 177
2015-08-11 07:30 | 162
2015-08-11 07:45 | 164
2015-08-11 08:00 | 171
2015-08-11 08:15 | 179
2015-08-11 08:30 | 193
2015-08-11 08:45 | 175
2015-08-11 09:00 | 183
2015-08-11 09:15 | 178
2015-08-11 09:30 | 177
2015-08-11 09:45 | 192
2015-08-11 10:00 | 197
2015-08-11 10:15 | 191
2015-08-11 10:30 | 194
2015-08-11 10:45 | 199
2015-08-11 11:00 | 204
2015-08-11 11:15 | 210
2015-08-11 11:30 | 200
2015-08-11 11:45 | 210
2015-08-11 12:00 | 212
2015-08-11 12:15 | 207
2015-08-11 12:30 | 203
2015-08-11 12:45 | 217
2015-08-11 13:00 | 222
2015-08-11 13:15 | 210
2015-08-11 13:30 | 214
2015-08-11 13:45 | 216
2015-08-11 14:00 | 229
2015-08-11 14:15 | 235
2015-08-11 14:30 | 226
2015-08-11 14:45 | 224
2015-08-11 15:00 | 234
2015-08-11 15:15 | 228
2015-08-11 15:30 | 229
2015-08-11 15:45 | 221
2015-08-11 16:00 | 227
2015-08-11 16:15 | 230
2015-08-11 16:30 | 235
2015-08-11 16:45 | 225
2015-08-11 17:00 | 232
2015-08-11 17:15 | 236
2015-08-11 17:30 | 226
2015-08-11 17:45 | 240
2015-08-11 18:00 | 230
2015-08-11 18:15 | 227
2015-08-11 18:30 | 214
2015-08-11 18:45 | 227
2015-08-11 19:00 | 233
2015-08-11 19:15 | 209
2015-08-11 19:30 | 215
2015-08-11 19:45 | 208
2015-08-11 20:00 | 210
2015-08-11 20:15 | 219
2015-08-11 20:30 | 206
2015-08-11 20:45 | 190
2015-08-11 21:00 | 197
2015-08-11 21:15 | 199
2015-08-11 21:30 | 197
2015-08-11 21:45 | 183
2015-08-11 22:00 | 191
2015-08-11 22:15 | 185
2015-08-11 22:30 | 179
2015-08-11 22:45 | 179
2015-08-11 23:00 | 194
2015-08-11 23:15 | 167
2015-08-11 23:30 | 178
2015-08-11 23:45 | 168
2015-08-12 | 170
2015-08-12 00:15 | 186
2015-08-12 00:30 | 163
2015-08-12 00:45 | 166
2015-08-12 01:00 | 164
2015-08-12 01:15 | 176
2015-08-12 01:30 | 168
2015-08-12 01:45 | 159
2015-08-12 02:00 | 160
2015-08-12 02:15 | 150
2015-08-12 02:30 | 171
2015-08-12 02:45 | 161
2015-08-12 03:00 | 157
2015-08-12 03:15 | 160
2015-08-12 03:30 | 151
2015-08-12 03:45 | 177
2015-08-12 04:00 | 154
2015-08-12 04:15 | 156
2015-08-12 04:30 | 160
2015-08-12 04:45 | 155
2015-08-12 05:00 | 172
2015-08-12 05:15 | 148
2015-08-12 05:30 | 159
2015-08-12 05:45 | 145
2015-08-12 06:00 | 155
2015-08-12 06:15 | 166
2015-08-12 06:30 | 158
2015-08-12 06:45 | 151
2015-08-12 07:00 | 158
2015-08-12 07:15 | 150
2015-08-12 07:30 | 163
2015-08-12 07:45 | 167
2015-08-12 08:00 | 162
2015-08-12 08:15 | 162
2015-08-12 08:30 | 165
2015-08-12 08:45 | 179
2015-08-12 09:00 | 180
2015-08-12 09:15 | 175
2015-08-12 09:30 | 184
2015-08-12 09:45 | 182
2015-08-12 10:00 | 197
2015-08-12 10:15 | 206
2015-08-12 10:30 | 192
2015-08-12 10:45 | 186
2015-08-12 11:00 | 197
2015-08-12 11:15 | 204
2015-08-12 11:30 | 214
2015-08-12 11:45 | 203
2015-08-12 12:00 | 201
2015-08-12 12:15 | 202
2015-08-12 12:30 | 216
2015-08-12 12:45 | 213
2015-08-12 13:00 | 211
2015-08-12 13:15 | 202
2015-08-12 13:30 | 210
2015-08-12 13:45 | 223
2015-08-12 14:00 | 205
2015-08-12 14:15 | 214
2015-08-12 14:30 | 225
2015-08-12 14:45 | 207
2015-08-12 15:00 | 227
2015-08-12 15:15 | 230
2015-08-12 15:30 | 216
2015-08-12 15:45 | 225
2015-08-12 16:00 | 213
2015-08-12 16:15 | 249
2015-08-12 16:30 | 224
2015-08-12 16:45 | 236
2015-08-12 17:00 | 227
2015-08-12 17:15 | 239
2015-08-12 17:30 | 228
2015-08-12 17:45 | 252
2015-08-12 18:00 | 222
2015-08-12 18:15 | 232
2015-08-12 18:30 | 220
2015-08-12 18:45 | 236
2015-08-12 19:00 | 228
2015-08-12 19:15 | 228
2015-08-12 19:30 | 215
2015-08-12 19:45 | 206
2015-08-12 20:00 | 207
2015-08-12 20:15 | 199
2015-08-12 20:30 | 210
2015-08-12 20:45 | 212
2015-08-12 21:00 | 200
2015-08-12 21:15 | 193
2015-08-12 21:30 | 196
2015-08-12 21:45 | 197
2015-08-12 22:00 | 209
2015-08-12 22:15 | 184
2015-08-12 22:30 | 198
2015-08-12 22:45 | 208
2015-08-12 23:00 | 213
2015-08-12 23:15 | 194
2015-08-12 23:30 | 191
2015-08-12 23:45 | 184
2015-08-13 | 199
2015-08-13 00:15 | 185
2015-08-13 00:30 | 172
2015-08-13 00:45 | 175
2015-08-13 01:00 | 191
2015-08-13 01:15 | 184
2015-08-13 01:30 | 179
2015-08-13 01:45 | 180
2015-08-13 02:00 | 177
2015-08-13 02:15 | 195
2015-08-13 02:30 | 188
2015-08-13 02:45 | 175
2015-08-13 03:00 | 173
2015-08-13 03:15 | 168
2015-08-13 03:30 | 180
2015-08-13 03:45 | 174
2015-08-13 04:00 | 171
2015-08-13 04:15 | 164
2015-08-13 04:30 | 169
2015-08-13 04:45 | 180
2015-08-13 05:00 | 171
2015-08-13 05:15 | 160
2015-08-13 05:30 | 163
2015-08-13 05:45 | 177
2015-08-13 06:00 | 168
2015-08-13 06:15 | 161
2015-08-13 06:30 | 167
2015-08-13 06:45 | 167
2015-08-13 07:00 | 183
2015-08-13 07:15 | 173
2015-08-13 07:30 | 162
2015-08-13 07:45 | 166
2015-08-13 08:00 | 181
2015-08-13 08:15 | 189
2015-08-13 08:30 | 177
2015-08-13 08:45 | 185
2015-08-13 09:00 | 183
2015-08-13 09:15 | 198
2015-08-13 09:30 | 190
2015-08-13 09:45 | 186
2015-08-13 10:00 | 195
2015-08-13 10:15 | 189
2015-08-13 10:30 | 211
2015-08-13 10:45 | 198
2015-08-13 11:00 | 205
2015-08-13 11:15 | 200
2015-08-13 11:30 | 208
2015-08-13 11:45 | 225
2015-08-13 12:00 | 221
2015-08-13 12:15 | 211
2015-08-13 12:30 | 217
2015-08-13 12:45 | 229
2015-08-13 13:00 | 221
2015-08-13 13:15 | 221
2015-08-13 13:30 | 218
2015-08-13 13:45 | 216
2015-08-13 14:00 | 234
2015-08-13 14:15 | 226
2015-08-13 14:30 | 216
2015-08-13 14:45 | 225
2015-08-13 15:00 | 214
2015-08-13 15:15 | 226
2015-08-13 15:30 | 226
2015-08-13 15:45 | 243
2015-08-13 16:00 | 229
2015-08-13 16:15 | 225
2015-08-13 16:30 | 231
2015-08-13 16:45 | 231
2015-08-13 17:00 | 234
2015-08-13 17:15 | 250
2015-08-13 17:30 | 235
2015-08-13 17:45 | 225
2015-08-13 18:00 | 229
2015-08-13 18:15 | 220
2015-08-13 18:30 | 243
2015-08-13 18:45 | 220
2015-08-13 19:00 | 236
2015-08-13 19:15 | 224
2015-08-13 19:30 | 208
2015-08-13 19:45 | 206
2015-08-13 20:00 | 218
2015-08-13 20:15 | 202
2015-08-13 20:30 | 197
2015-08-13 20:45 | 199
2015-08-13 21:00 | 191
2015-08-13 21:15 | 204
2015-08-13 21:30 | 186
2015-08-13 21:45 | 192
2015-08-13 22:00 | 183
2015-08-13 22:15 | 200
2015-08-13 22:30 | 193
2015-08-13 22:45 | 186
2015-08-13 23:00 | 192
2015-08-13 23:15 | 187
2015-08-13 23:30 | 189
2015-08-13 23:45 | 179
2015-08-14 | 173
2015-08-14 00:15 | 180
2015-08-14 00:30 | 186
2015-08-14 00:45 | 166
2015-08-14 01:00 | 172
2015-08-14 01:15 | 171
2015-08-14 01:30 | 174
2015-08-14 01:45 | 176
2015-08-14 02:00 | 163
2015-08-14 02:15 | 160
2015-08-14 02:30 | 169
2015-08-14 02:45 | 178
2015-08-14 03:00 | 160
2015-08-14 03:15 | 173
2015-08-14 03:30 | 163
2015-08-14 03:45 | 171
2015-08-14 04:00 | 177
2015-08-14 04:15 | 162
2015-08-14 04:30 | 162
2015-08-14 04:45 | 168
2015-08-14 05:00 | 180
2015-08-14 05:15 | 156
2015-08-14 05:30 | 161
2015-08-14 05:45 | 163
2015-08-14 06:00 | 173
2015-08-14 06:15 | 176
2015-08-14 06:30 | 165
2015-08-14 06:45 | 158
2015-08-14 07:00 | 164
2015-08-14 07:15 | 183
2015-08-14 07:30 | 163
2015-08-14 07:45 | 162
2015-08-14 08:00 | 173
2015-08-14 08:15 | 181
2015-08-14 08:30 | 185
2015-08-14 08:45 | 174
2015-08-14 09:00 | 170
2015-08-14 09:15 | 184
2015-08-14 09:30 | 198
2015-08-14 09:45 | 194
2015-08-14 10:00 | 184
2015-08-14 10:15 | 189
2015-08-14 10:30 | 191
2015-08-14 10:45 | 203
2015-08-14 11:00 | 200
2015-08-14 11:15 | 196
2015-08-14 11:30 | 190
2015-08-14 11:45 | 200
2015-08-14 12:00 | 208
2015-08-14 12:15 | 198
2015-08-14 12:30 | 201
2015-08-14 12:45 | 200
2015-08-14 13:00 | 219
2015-08-14 13:15 | 203
2015-08-14 13:30 | 211
2015-08-14 13:45 | 201
2015-08-14 14:00 | 210
2015-08-14 14:15 | 216
2015-08-14 14:30 | 231
2015-08-14 14:45 | 212
2015-08-14 15:00 | 226
2015-08-14 15:15 | 216
2015-08-14 15:30 | 236
2015-08-14 15:45 | 236
2015-08-14 16:00 | 240
2015-08-14 16:15 | 225
2015-08-14 16:30 | 241
2015-08-14 16:45 | 237
2015-08-14 17:00 | 238
2015-08-14 17:15 | 228
2015-08-14 17:30 | 228
2015-08-14 17:45 | 232
2015-08-14 18:00 | 226
2015-08-14 18:15 | 216
2015-08-14 18:30 | 220
2015-08-14 18:45 | 219
2015-08-14 19:00 | 231
2015-08-14 19:15 | 225
2015-08-14 19:30 | 205
2015-08-14 19:45 | 201
2015-08-14 20:00 | 202
2015-08-14 20:15 | 208
2015-08-14 20:30 | 206
2015-08-14 20:45 | 196
2015-08-14 21:00 | 194
2015-08-14 21:15 | 180
2015-08-14 21:30 | 192
2015-08-14 21:45 | 181
2015-08-14 22:00 | 181
2015-08-14 22:15 | 178
2015-08-14 22:30 | 184
2015-08-14 22:45 | 191
2015-08-14 23:00 | 179
2015-08-14 23:15 | 174
2015-08-14 23:30 | 174
2015-08-14 23:45 | 190
2015-08-15 | 168
2015-08-15 00:15 | 161
2015-08-15 00:30 | 168
2015-08-15 00:45 | 179
2015-08-15 01:00 | 160
2015-08-15 01:15 | 159
2015-08-15 01:30 | 156
2015-08-15 01:45 | 171
2015-08-15 02:00 | 162
2015-08-15 02:15 | 157
2015-08-15 02:30 | 151
2015-08-15 02:45 | 165
2015-08-15 03:00 | 173
2015-08-15 03:15 | 149
2015-08-15 03:30 | 153
2015-08-15 03:45 | 157
2015-08-15 04:00 | 161
2015-08-15 04:15 | 153
2015-08-15 04:30 | 153
2015-08-15 04:45 | 148
2015-08-15 05:00 | 167
2015-08-15 05:15 | 143
2015-08-15 05:30 | 154
2015-08-15 05:45 | 143
2015-08-15 06:00 | 146
2015-08-15 06:15 | 161
2015-08-15 06:30 | 149
2015-08-15 06:45 | 146
2015-08-15 07:00 | 144
2015-08-15 07:15 | 156
2015-08-15 07:30 | 142
2015-08-15 07:45 | 170
2015-08-15 08:00 | 156
2015-08-15 08:15 | 163
2015-08-15 08:30 | 153
2015-08-15 08:45 | 151
2015-08-15 09:00 | 155
2015-08-15 09:15 | 180
2015-08-15 09:30 | 164
2015-08-15 09:45 | 158
2015-08-15 10:00 | 181
2015-08-15 10:15 | 170
2015-08-15 10:30 | 169
2015-08-15 10:45 | 175
2015-08-15 11:00 | 173
2015-08-15 11:15 | 181
2015-08-15 11:30 | 194
2015-08-15 11:45 | 180
2015-08-15 12:00 | 182
2015-08-15 12:15 | 193
2015-08-15 12:30 | 187
2015-08-15 12:45 | 215
2015-08-15 13:00 | 192
2015-08-15 13:15 | 203
2015-08-15 13:30 | 208
2015-08-15 13:45 | 217
2015-08-15 14:00 | 207
2015-08-15 14:15 | 211
2015-08-15 14:30 | 213
2015-08-15 14:45 | 216
2015-08-15 15:00 | 232
2015-08-15 15:15 | 217
2015-08-15 15:30 | 228
2015-08-15 15:45 | 209
2015-08-15 16:00 | 227
2015-08-15 16:15 | 239
2015-08-15 16:30 | 221
2015-08-15 16:45 | 228
2015-08-15 17:00 | 226
2015-08-15 17:15 | 235
2015-08-15 17:30 | 247
2015-08-15 17:45 | 224
2015-08-15 18:00 | 228
2015-08-15 18:15 | 216
2015-08-15 18:30 | 226
2015-08-15 18:45 | 234
2015-08-15 19:00 | 223
2015-08-15 19:15 | 218
2015-08-15 19:30 | 207
2015-08-15 19:45 | 220
2015-08-15 20:00 | 196
2015-08-15 20:15 | 208
2015-08-15 20:30 | 192
2015-08-15 20:45 | 188
2015-08-15 21:00 | 201
2015-08-15 21:15 | 192
2015-08-15 21:30 | 187
2015-08-15 21:45 | 180
2015-08-15 22:00 | 194
2015-08-15 22:15 | 192
2015-08-15 22:30 | 180
2015-08-15 22:45 | 180
2015-08-15 23:00 | 177
2015-08-15 23:15 | 187
2015-08-15 23:30 | 176
2015-08-15 23:45 | 172
2015-08-16 | 174
2015-08-16 00:15 | 167
2015-08-16 00:30 | 196
2015-08-16 00:45 | 166
2015-08-16 01:00 | 173
2015-08-16 01:15 | 161
2015-08-16 01:30 | 165
2015-08-16 01:45 | 178
2015-08-16 02:00 | 167
2015-08-16 02:15 | 174
2015-08-16 02:30 | 160
2015-08-16 02:45 | 158
2015-08-16 03:00 | 167
2015-08-16 03:15 | 170
2015-08-16 03:30 | 158
2015-08-16 03:45 | 161
2015-08-16 04:00 | 159
2015-08-16 04:15 | 163
2015-08-16 04:30 | 170
2015-08-16 04:45 | 157
2015-08-16 05:00 | 155
2015-08-16 05:15 | 156
2015-08-16 05:30 | 150
2015-08-16 05:45 | 177
2015-08-16 06:00 | 158
2015-08-16 06:15 | 158
2015-08-16 06:30 | 171
2015-08-16 06:45 | 172
2015-08-16 07:00 | 178
2015-08-16 07:15 | 195
2015-08-16 07:30 | 169
2015-08-16 07:45 | 170
2015-08-16 08:00 | 168
2015-08-16 08:15 | 172
2015-08-16 08:30 | 176
2015-08-16 08:45 | 170
2015-08-16 09:00 | 174
2015-08-16 09:15 | 184
2015-08-16 09:30 | 191
2015-08-16 09:45 | 176
2015-08-16 10:00 | 184
2015-08-16 10:15 | 186
2015-08-16 10:30 | 207
2015-08-16 10:45 | 204
2015-08-16 11:00 | 199
2015-08-16 11:15 | 198
2015-08-16 11:30 | 200
2015-08-16 11:45 | 225
2015-08-16 12:00 | 212
2015-08-16 12:15 | 219
2015-08-16 12:30 | 216
2015-08-16 12:45 | 229
2015-08-16 13:00 | 236
2015-08-16 13:15 | 241
2015-08-16 13:30 | 230
2015-08-16 13:45 | 233
2015-08-16 14:00 | 247
2015-08-16 14:15 | 261
2015-08-16 14:30 | 244
2015-08-16 14:45 | 244
2015-08-16 15:00 | 252
2015-08-16 15:15 | 249
2015-08-16 15:30 | 267
2015-08-16 15:45 | 261
2015-08-16 16:00 | 253
2015-08-16 16:15 | 251
2015-08-16 16:30 | 265
2015-08-16 16:45 | 259
2015-08-16 17:00 | 259
2015-08-16 17:15 | 256
2015-08-16 17:30 | 250
2015-08-16 17:45 | 269
2015-08-16 18:00 | 245
2015-08-16 18:15 | 248
2015-08-16 18:30 | 252
2015-08-16 18:45 | 255
2015-08-16 19:00 | 258
2015-08-16 19:15 | 240
2015-08-16 19:30 | 236
2015-08-16 19:45 | 225
2015-08-16 20:00 | 223
2015-08-16 20:15 | 231
2015-08-16 20:30 | 216
2015-08-16 20:45 | 211
2015-08-16 21:00 | 206
2015-08-16 21:15 | 210
2015-08-16 21:30 | 207
2015-08-16 21:45 | 192
2015-08-16 22:00 | 191
2015-08-16 22:15 | 185
2015-08-16 22:30 | 211
2015-08-16 22:45 | 188
2015-08-16 23:00 | 199
2015-08-16 23:15 | 181
2015-08-16 23:30 | 197
2015-08-16 23:45 | 191
2015-08-17 | 183
2015-08-17 00:15 | 187
2015-08-17 00:30 | 183
2015-08-17 00:45 | 196
2015-08-17 01:00 | 174
2015-08-17 01:15 | 178
2015-08-17 01:30 | 166
2015-08-17 01:45 | 180
2015-08-17 02:00 | 186
2015-08-17 02:15 | 174
2015-08-17 02:30 | 180
2015-08-17 02:45 | 170
2015-08-17 03:00 | 192
2015-08-17 03:15 | 188
2015-08-17 03:30 | 173
2015-08-17 03:45 | 182
2015-08-17 04:00 | 173
2015-08-17 04:15 | 184
2015-08-17 04:30 | 188
2015-08-17 04:45 | 175
2015-08-17 05:00 | 178
2015-08-17 05:15 | 164
2015-08-17 05:30 | 176
2015-08-17 05:45 | 168
2015-08-17 06:00 | 159
2015-08-17 06:15 | 160
2015-08-17 06:30 | 160
2015-08-17 06:45 | 185
2015-08-17 07:00 | 160
2015-08-17 07:15 | 167
2015-08-17 07:30 | 169
2015-08-17 07:45 | 174
2015-08-17 08:00 | 183
2015-08-17 08:15 | 186
2015-08-17 08:30 | 180
2015-08-17 08:45 | 185
2015-08-17 09:00 | 208
2015-08-17 09:15 | 200
2015-08-17 09:30 | 198
2015-08-17 09:45 | 201
2015-08-17 10:00 | 207
2015-08-17 10:15 | 216
2015-08-17 10:30 | 226
2015-08-17 10:45 | 219
2015-08-17 11:00 | 231
2015-08-17 11:15 | 231
2015-08-17 11:30 | 253
2015-08-17 11:45 | 233
2015-08-17 12:00 | 258
2015-08-17 12:15 | 246
2015-08-17 12:30 | 251
2015-08-17 12:45 | 239
2015-08-17 13:00 | 261
2015-08-17 13:15 | 259
2015-08-17 13:30 | 254
2015-08-17 13:45 | 248
2015-08-17 14:00 | 257
2015-08-17 14:15 | 261
2015-08-17 14:30 | 280
2015-08-17 14:45 | 266
2015-08-17 15:00 | 263
2015-08-17 15:15 | 257
2015-08-17 15:30 | 262
2015-08-17 15:45 | 275
2015-08-17 16:00 | 267
2015-08-17 16:15 | 263
2015-08-17 16:30 | 264
2015-08-17 16:45 | 262
2015-08-17 17:00 | 254
2015-08-17 17:15 | 269
2015-08-17 17:30 | 281
2015-08-17 17:45 | 263
2015-08-17 18:00 | 248
2015-08-17 18:15 | 259
2015-08-17 18:30 | 250
2015-08-17 18:45 | 252
2015-08-17 19:00 | 255
2015-08-17 19:15 | 239
2015-08-17 19:30 | 249
2015-08-17 19:45 | 231
2015-08-17 20:00 | 235
2015-08-17 20:15 | 219
2015-08-17 20:30 | 228
2015-08-17 20:45 | 207
2015-08-17 21:00 | 235
2015-08-17 21:15 | 222
2015-08-17 21:30 | 200
2015-08-17 21:45 | 199
2015-08-17 22:00 | 210
2015-08-17 22:15 | 209
2015-08-17 22:30 | 207
2015-08-17 22:45 | 202
2015-08-17 23:00 | 201
2015-08-17 23:15 | 198
2015-08-17 23:30 | 197
2015-08-17 23:45 | 184
2015-08-18 | 184
2015-08-18 00:15 | 177
2015-08-18 00:30 | 191
2015-08-18 00:45 | 183
2015-08-18 01:00 | 176
2015-08-18 01:15 | 181
2015-08-18 01:30 | 181
2015-08-18 01:45 | 190
2015-08-18 02:00 | 183
2015-08-18 02:15 | 175
2015-08-18 02:30 | 174
2015-08-18 02:45 | 170
2015-08-18 03:00 | 178
2015-08-18 03:15 | 185
2015-08-18 03:30 | 161
2015-08-18 03:45 | 166
2015-08-18 04:00 | 160
2015-08-18 04:15 | 172
2015-08-18 04:30 | 173
2015-08-18 04:45 | 151
2015-08-18 05:00 | 166
2015-08-18 05:15 | 166
2015-08-18 05:30 | 170
2015-08-18 05:45 | 157
2015-08-18 06:00 | 161
2015-08-18 06:15 | 158
2015-08-18 06:30 | 171
2015-08-18 06:45 | 161
2015-08-18 07:00 | 157
2015-08-18 07:15 | 160
2015-08-18 07:30 | 160
2015-08-18 07:45 | 176
2015-08-18 08:00 | 168
2015-08-18 08:15 | 168
2015-08-18 08:30 | 171
2015-08-18 08:45 | 188
2015-08-18 09:00 | 190
2015-08-18 09:15 | 177
2015-08-18 09:30 | 177
2015-08-18 09:45 | 180
2015-08-18 10:00 | 203
2015-08-18 10:15 | 191
2015-08-18 10:30 | 203
2015-08-18 10:45 | 199
2015-08-18 11:00 | 208
2015-08-18 11:15 | 223
2015-08-18 11:30 | 212
2015-08-18 11:45 | 205
2015-08-18 12:00 | 212
2015-08-18 12:15 | 223
2015-08-18 12:30 | 220
2015-08-18 12:45 | 212
2015-08-18 13:00 | 225
2015-08-18 13:15 | 219
2015-08-18 13:30 | 237
2015-08-18 13:45 | 234
2015-08-18 14:00 | 235
2015-08-18 14:15 | 227
2015-08-18 14:30 | 248
2015-08-18 14:45 | 243
2015-08-18 15:00 | 263
2015-08-18 15:15 | 248
2015-08-18 15:30 | 261
2015-08-18 15:45 | 258
2015-08-18 16:00 | 263
2015-08-18 16:15 | 250
2015-08-18 16:30 | 255
2015-08-18 16:45 | 254
2015-08-18 17:00 | 257
2015-08-18 17:15 | 264
2015-08-18 17:30 | 248
2015-08-18 17:45 | 253
2015-08-18 18:00 | 240
2015-08-18 18:15 | 243
2015-08-18 18:30 | 254
2015-08-18 18:45 | 251
2015-08-18 19:00 | 232
2015-08-18 19:15 | 228
2015-08-18 19:30 | 230
2015-08-18 19:45 | 241
2015-08-18 20:00 | 214
2015-08-18 20:15 | 222
2015-08-18 20:30 | 219
2015-08-18 20:45 | 210
2015-08-18 21:00 | 220
2015-08-18 21:15 | 214
2015-08-18 21:30 | 220
2015-08-18 21:45 | 206
2015-08-18 22:00 | 200
2015-08-18 22:15 | 192
2015-08-18 22:30 | 207
2015-08-18 22:45 | 204
2015-08-18 23:00 | 199
2015-08-18 23:15 | 195
2015-08-18 23:30 | 200
2015-08-18 23:45 | 205
2015-08-19 | 193
2015-08-19 00:15 | 191
2015-08-19 00:30 | 192
2015-08-19 00:45 | 196
2015-08-19 01:00 | 198
2015-08-19 01:15 | 188
2015-08-19 01:30 | 183
2015-08-19 01:45 | 190
2015-08-19 02:00 | 182
2015-08-19 02:15 | 174
2015-08-19 02:30 | 173
2015-08-19 02:45 | 179
2015-08-19 03:00 | 190
2015-08-19 03:15 | 170
2015-08-19 03:30 | 169
2015-08-19 03:45 | 178
2015-08-19 04:00 | 178
2015-08-19 04:15 | 185
2015-08-19 04:30 | 163
2015-08-19 04:45 | 171
2015-08-19 05:00 | 171
2015-08-19 05:15 | 174
2015-08-19 05:30 | 173
2015-08-19 05:45 | 162
2015-08-19 06:00 | 163
2015-08-19 06:15 | 158
2015-08-19 06:30 | 178
2015-08-19 06:45 | 174
2015-08-19 07:00 | 164
2015-08-19 07:15 | 163
2015-08-19 07:30 | 164
2015-08-19 07:45 | 183
2015-08-19 08:00 | 170
2015-08-19 08:15 | 168
2015-08-19 08:30 | 175
2015-08-19 08:45 | 184
2015-08-19 09:00 | 196
2015-08-19 09:15 | 186
2015-08-19 09:30 | 195
2015-08-19 09:45 | 192
2015-08-19 10:00 | 208
2015-08-19 10:15 | 219
2015-08-19 10:30 | 200
2015-08-19 10:45 | 207
2015-08-19 11:00 | 210
2015-08-19 11:15 | 230
2015-08-19 11:30 | 202
2015-08-19 11:45 | 212
2015-08-19 12:00 | 217
2015-08-19 12:15 | 216
2015-08-19 12:30 | 234
2015-08-19 12:45 | 225
2015-08-19 13:00 | 214
2015-08-19 13:15 | 226
2015-08-19 13:30 | 242
2015-08-19 13:45 | 231
2015-08-19 14:00 | 234
2015-08-19 14:15 | 232
2015-08-19 14:30 | 244
2015-08-19 14:45 | 245
2015-08-19 15:00 | 239
2015-08-19 15:15 | 227
2015-08-19 15:30 | 243
2015-08-19 15:45 | 230
2015-08-19 16:00 | 263
2015-08-19 16:15 | 234
2015-08-19 16:30 | 245
2015-08-19 16:45 | 238
2015-08-19 17:00 | 243
2015-08-19 17:15 | 252
2015-08-19 17:30 | 253
2015-08-19 17:45 | 236
2015-08-19 18:00 | 239
2015-08-19 18:15 | 235
2015-08-19 18:30 | 245
2015-08-19 18:45 | 239
2015-08-19 19:00 | 231
2015-08-19 19:15 | 239
2015-08-19 19:30 | 235
2015-08-19 19:45 | 221
2015-08-19 20:00 | 226
2015-08-19 20:15 | 206
2015-08-19 20:30 | 213
2015-08-19 20:45 | 221
2015-08-19 21:00 | 227
2015-08-19 21:15 | 207
2015-08-19 21:30 | 198
2015-08-19 21:45 | 196
2015-08-19 22:00 | 190
2015-08-19 22:15 | 208
2015-08-19 22:30 | 188
2015-08-19 22:45 | 194
2015-08-19 23:00 | 186
2015-08-19 23:15 | 188
2015-08-19 23:30 | 196
2015-08-19 23:45 | 174
2015-08-20 | 176
2015-08-20 00:15 | 184
2015-08-20 00:30 | 185
2015-08-20 00:45 | 201
2015-08-20 01:00 | 182
2015-08-20 01:15 | 185
2015-08-20 01:30 | 187
2015-08-20 01:45 | 198
2015-08-20 02:00 | 200
2015-08-20 02:15 | 175
2015-08-20 02:30 | 184
2015-08-20 02:45 | 181
2015-08-20 03:00 | 183
2015-08-20 03:15 | 176
2015-08-20 03:30 | 172
2015-08-20 03:45 | 168
2015-08-20 04:00 | 185
2015-08-20 04:15 | 175
2015-08-20 04:30 | 173
2015-08-20 04:45 | 174
2015-08-20 05:00 | 175
2015-08-20 05:15 | 195
2015-08-20 05:30 | 175
2015-08-20 05:45 | 175
2015-08-20 06:00 | 168
2015-08-20 06:15 | 183
2015-08-20 06:30 | 189
2015-08-20 06:45 | 169
2015-08-20 07:00 | 172
2015-08-20 07:15 | 177
2015-08-20 07:30 | 191
2015-08-20 07:45 | 179
2015-08-20 08:00 | 176
2015-08-20 08:15 | 184
2015-08-20 08:30 | 187
2015-08-20 08:45 | 204
2015-08-20 09:00 | 185
2015-08-20 09:15 | 192
2015-08-20 09:30 | 197
2015-08-20 09:45 | 192
2015-08-20 10:00 | 208
2015-08-20 10:15 | 211
2015-08-20 10:30 | 208
2015-08-20 10:45 | 217
2015-08-20 11:00 | 212
2015-08-20 11:15 | 230
2015-08-20 11:30 | 223
2015-08-20 11:45 | 223
2015-08-20 12:00 | 226
2015-08-20 12:15 | 220
2015-08-20 12:30 | 213
2015-08-20 12:45 | 219
2015-08-20 13:00 | 222
2015-08-20 13:15 | 221
2015-08-20 13:30 | 222
2015-08-20 13:45 | 229
2015-08-20 14:00 | 219
2015-08-20 14:15 | 225
2015-08-20 14:30 | 218
2015-08-20 14:45 | 212
2015-08-20 15:00 | 242
2015-08-20 15:15 | 227
2015-08-20 15:30 | 222
2015-08-20 15:45 | 239
2015-08-20 16:00 | 228
2015-08-20 16:15 | 224
2015-08-20 16:30 | 217
2015-08-20 16:45 | 231
2015-08-20 17:00 | 232
2015-08-20 17:15 | 239
2015-08-20 17:30 | 226
2015-08-20 17:45 | 222
2015-08-20 18:00 | 228
2015-08-20 18:15 | 225
2015-08-20 18:30 | 221
2015-08-20 18:45 | 226
2015-08-20 19:00 | 215
2015-08-20 19:15 | 220
2015-08-20 19:30 | 228
2015-08-20 19:45 | 214
2015-08-20 20:00 | 206
2015-08-20 20:15 | 208
2015-08-20 20:30 | 212
2015-08-20 20:45 | 190
2015-08-20 21:00 | 197
2015-08-20 21:15 | 190
2015-08-20 21:30 | 207
2015-08-20 21:45 | 184
2015-08-20 22:00 | 185
2015-08-20 22:15 | 198
2015-08-20 22:30 | 185
2015-08-20 22:45 | 186
2015-08-20 23:00 | 184
2015-08-20 23:15 | 185
2015-08-20 23:30 | 181
2015-08-20 23:45 | 176
2015-08-21 | 171
2015-08-21 00:15 | 171
2015-08-21 00:30 | 188
2015-08-21 00:45 | 175
2015-08-21 01:00 | 166
2015-08-21 01:15 | 172
2015-08-21 01:30 | 167
2015-08-21 01:45 | 183
2015-08-21 02:00 | 177
2015-08-21 02:15 | 166
2015-08-21 02:30 | 168
2015-08-21 02:45 | 165
2015-08-21 03:00 | 182
2015-08-21 03:15 | 166
2015-08-21 03:30 | 161
2015-08-21 03:45 | 165
2015-08-21 04:00 | 160
2015-08-21 04:15 | 169
2015-08-21 04:30 | 156
2015-08-21 04:45 | 157
2015-08-21 05:00 | 152
2015-08-21 05:15 | 174
2015-08-21 05:30 | 160
2015-08-21 05:45 | 155
2015-08-21 06:00 | 154
2015-08-21 06:15 | 153
2015-08-21 06:30 | 165
2015-08-21 06:45 | 176
2015-08-21 07:00 | 158
2015-08-21 07:15 | 166
2015-08-21 07:30 | 166
2015-08-21 07:45 | 172
2015-08-21 08:00 | 183
2015-08-21 08:15 | 166
2015-08-21 08:30 | 170
2015-08-21 08:45 | 186
2015-08-21 09:00 | 186
2015-08-21 09:15 | 181
2015-08-21 09:30 | 186
2015-08-21 09:45 | 191
2015-08-21 10:00 | 202
2015-08-21 10:15 | 198
2015-08-21 10:30 | 199
2015-08-21 10:45 | 198
2015-08-21 11:00 | 204
2015-08-21 11:15 | 209
2015-08-21 11:30 | 224
2015-08-21 11:45 | 210
2015-08-21 12:00 | 208
2015-08-21 12:15 | 216
2015-08-21 12:30 | 215
2015-08-21 12:45 | 210
2015-08-21 13:00 | 209
2015-08-21 13:15 | 236
2015-08-21 13:30 | 221
2015-08-21 13:45 | 211
2015-08-21 14:00 | 220
2015-08-21 14:15 | 227
2015-08-21 14:30 | 217
2015-08-21 14:45 | 234
2015-08-21 15:00 | 230
2015-08-21 15:15 | 222
2015-08-21 15:30 | 243
2015-08-21 15:45 | 232
2015-08-21 16:00 | 227
2015-08-21 16:15 | 231
2015-08-21 16:30 | 223
2015-08-21 16:45 | 232
2015-08-21 17:00 | 235
2015-08-21 17:15 | 229
2015-08-21 17:30 | 213
2015-08-21 17:45 | 222
2015-08-21 18:00 | 227
2015-08-21 18:15 | 222
2015-08-21 18:30 | 232
2015-08-21 18:45 | 211
2015-08-21 19:00 | 225
2015-08-21 19:15 | 215
2015-08-21 19:30 | 217
2015-08-21 19:45 | 210
2015-08-21 20:00 | 221
2015-08-21 20:15 | 203
2015-08-21 20:30 | 202
2015-08-21 20:45 | 193
2015-08-21 21:00 | 200
2015-08-21 21:15 | 197
2015-08-21 21:30 | 175
2015-08-21 21:45 | 174
2015-08-21 22:00 | 188
2015-08-21 22:15 | 182
2015-08-21 22:30 | 171
2015-08-21 22:45 | 172
2015-08-21 23:00 | 188
2015-08-21 23:15 | 176
2015-08-21 23:30 | 163
2015-08-21 23:45 | 168
2015-08-22 | 164
2015-08-22 00:15 | 182
2015-08-22 00:30 | 173
2015-08-22 00:45 | 164
2015-08-22 01:00 | 161
2015-08-22 01:15 | 161
2015-08-22 01:30 | 181
2015-08-22 01:45 | 165
2015-08-22 02:00 | 156
2015-08-22 02:15 | 163
2015-08-22 02:30 | 171
2015-08-22 02:45 | 167
2015-08-22 03:00 | 153
2015-08-22 03:15 | 159
2015-08-22 03:30 | 154
2015-08-22 03:45 | 169
2015-08-22 04:00 | 162
2015-08-22 04:15 | 159
2015-08-22 04:30 | 155
2015-08-22 04:45 | 157
2015-08-22 05:00 | 173
2015-08-22 05:15 | 153
2015-08-22 05:30 | 157
2015-08-22 05:45 | 155
2015-08-22 06:00 | 157
2015-08-22 06:15 | 170
2015-08-22 06:30 | 151
2015-08-22 06:45 | 155
2015-08-22 07:00 | 153
2015-08-22 07:15 | 170
2015-08-22 07:30 | 159
2015-08-22 07:45 | 150
2015-08-22 08:00 | 153
2015-08-22 08:15 | 154
2015-08-22 08:30 | 154
2015-08-22 08:45 | 167
2015-08-22 09:00 | 148
2015-08-22 09:15 | 151
2015-08-22 09:30 | 154
2015-08-22 09:45 | 174
2015-08-22 10:00 | 165
2015-08-22 10:15 | 159
2015-08-22 10:30 | 167
2015-08-22 10:45 | 171
2015-08-22 11:00 | 175
2015-08-22 11:15 | 165
2015-08-22 11:30 | 168
2015-08-22 11:45 | 167
2015-08-22 12:00 | 183
2015-08-22 12:15 | 182
2015-08-22 12:30 | 175
2015-08-22 12:45 | 180
2015-08-22 13:00 | 181
2015-08-22 13:15 | 191
2015-08-22 13:30 | 190
2015-08-22 13:45 | 179
2015-08-22 14:00 | 180
2015-08-22 14:15 | 183
2015-08-22 14:30 | 198
2015-08-22 14:45 | 206
2015-08-22 15:00 | 194
2015-08-22 15:15 | 192
2015-08-22 15:30 | 205
2015-08-22 15:45 | 200
2015-08-22 16:00 | 221
2015-08-22 16:15 | 204
2015-08-22 16:30 | 203
2015-08-22 16:45 | 201
2015-08-22 17:00 | 205
2015-08-22 17:15 | 224
2015-08-22 17:30 | 198
2015-08-22 17:45 | 214
2015-08-22 18:00 | 205
2015-08-22 18:15 | 189
2015-08-22 18:30 | 199
2015-08-22 18:45 | 195
2015-08-22 19:00 | 205
2015-08-22 19:15 | 189
2015-08-22 19:30 | 192
2015-08-22 19:45 | 186
2015-08-22 20:00 | 185
2015-08-22 20:15 | 195
2015-08-22 20:30 | 191
2015-08-22 20:45 | 176
2015-08-22 21:00 | 179
2015-08-22 21:15 | 187
2015-08-22 21:30 | 185
2015-08-22 21:45 | 177
2015-08-22 22:00 | 178
2015-08-22 22:15 | 166
2015-08-22 22:30 | 184
2015-08-22 22:45 | 175
2015-08-22 23:00 | 163
2015-08-22 23:15 | 162
2015-08-22 23:30 | 174
2015-08-22 23:45 | 177
2015-08-23 | 158
2015-08-23 00:15 | 160
2015-08-23 00:30 | 158
2015-08-23 00:45 | 166
2015-08-23 01:00 | 161
2015-08-23 01:15 | 157
2015-08-23 01:30 | 157
2015-08-23 01:45 | 162
2015-08-23 02:00 | 164
2015-08-23 02:15 | 154
2015-08-23 02:30 | 148
2015-08-23 02:45 | 147
2015-08-23 03:00 | 164
2015-08-23 03:15 | 166
2015-08-23 03:30 | 146
2015-08-23 03:45 | 150
2015-08-23 04:00 | 163
2015-08-23 04:15 | 162
2015-08-23 04:30 | 149
2015-08-23 04:45 | 151
2015-08-23 05:00 | 151
2015-08-23 05:15 | 161
2015-08-23 05:30 | 165
2015-08-23 05:45 | 150
2015-08-23 06:00 | 145
2015-08-23 06:15 | 151
2015-08-23 06:30 | 170
2015-08-23 06:45 | 148
2015-08-23 07:00 | 153
2015-08-23 07:15 | 155
2015-08-23 07:30 | 161
2015-08-23 07:45 | 171
2015-08-23 08:00 | 156
2015-08-23 08:15 | 159
2015-08-23 08:30 | 158
2015-08-23 08:45 | 178
2015-08-23 09:00 | 171
2015-08-23 09:15 | 163
2015-08-23 09:30 | 166
2015-08-23 09:45 | 172
2015-08-23 10:00 | 182
2015-08-23 10:15 | 167
2015-08-23 10:30 | 170
2015-08-23 10:45 | 169
2015-08-23 11:00 | 171
2015-08-23 11:15 | 189
2015-08-23 11:30 | 178
2015-08-23 11:45 | 179
2015-08-23 12:00 | 183
2015-08-23 12:15 | 187
2015-08-23 12:30 | 199
2015-08-23 12:45 | 186
2015-08-23 13:00 | 182
2015-08-23 13:15 | 184
2015-08-23 13:30 | 189
2015-08-23 13:45 | 203
2015-08-23 14:00 | 186
2015-08-23 14:15 | 188
2015-08-23 14:30 | 204
2015-08-23 14:45 | 186
2015-08-23 15:00 | 184
2015-08-23 15:15 | 199
2015-08-23 15:30 | 207
2015-08-23 15:45 | 196
2015-08-23 16:00 | 185
2015-08-23 16:15 | 194
2015-08-23 16:30 | 193
2015-08-23 16:45 | 204
2015-08-23 17:00 | 198
2015-08-23 17:15 | 191
2015-08-23 17:30 | 193
2015-08-23 17:45 | 199
2015-08-23 18:00 | 200
2015-08-23 18:15 | 195
2015-08-23 18:30 | 188
2015-08-23 18:45 | 193
2015-08-23 19:00 | 193
2015-08-23 19:15 | 189
2015-08-23 19:30 | 199
2015-08-23 19:45 | 185
2015-08-23 20:00 | 187
2015-08-23 20:15 | 178
2015-08-23 20:30 | 180
2015-08-23 20:45 | 196
2015-08-23 21:00 | 177
2015-08-23 21:15 | 174
2015-08-23 21:30 | 171
2015-08-23 21:45 | 163
2015-08-23 22:00 | 159
2015-08-23 22:15 | 167
2015-08-23 22:30 | 176
2015-08-23 22:45 | 158
2015-08-23 23:00 | 162
2015-08-23 23:15 | 159
2015-08-23 23:30 | 172
2015-08-23 23:45 | 163
2015-08-24 | 159
2015-08-24 00:15 | 157
2015-08-24 00:30 | 167
2015-08-24 00:45 | 165
2015-08-24 01:00 | 157
2015-08-24 01:15 | 154
2015-08-24 01:30 | 156
2015-08-24 01:45 | 175
2015-08-24 02:00 | 161
2015-08-24 02:15 | 152
2015-08-24 02:30 | 153
2015-08-24 02:45 | 169
2015-08-24 03:00 | 158
2015-08-24 03:15 | 152
2015-08-24 03:30 | 157
2015-08-24 03:45 | 157
2015-08-24 04:00 | 167
2015-08-24 04:15 | 158
2015-08-24 04:30 | 156
2015-08-24 04:45 | 149
2015-08-24 05:00 | 158
2015-08-24 05:15 | 169
2015-08-24 05:30 | 149
2015-08-24 05:45 | 150
2015-08-24 06:00 | 150
2015-08-24 06:15 | 152
2015-08-24 06:30 | 164
2015-08-24 06:45 | 155
2015-08-24 07:00 | 156
2015-08-24 07:15 | 151
2015-08-24 07:30 | 170
2015-08-24 07:45 | 164
2015-08-24 08:00 | 155
2015-08-24 08:15 | 162
2015-08-24 08:30 | 165
2015-08-24 08:45 | 169
2015-08-24 09:00 | 177
2015-08-24 09:15 | 174
2015-08-24 09:30 | 177
2015-08-24 09:45 | 178
2015-08-24 10:00 | 195
2015-08-24 10:15 | 193
2015-08-24 10:30 | 189
2015-08-24 10:45 | 190
2015-08-24 11:00 | 208
2015-08-24 11:15 | 213
2015-08-24 11:30 | 203
2015-08-24 11:45 | 195
2015-08-24 12:00 | 203
2015-08-24 12:15 | 204
2015-08-24 12:30 | 215
2015-08-24 12:45 | 203
2015-08-24 13:00 | 202
2015-08-24 13:15 | 209
2015-08-24 13:30 | 223
2015-08-24 13:45 | 203
2015-08-24 14:00 | 208
2015-08-24 14:15 | 209
2015-08-24 14:30 | 221
2015-08-24 14:45 | 235
2015-08-24 15:00 | 218
2015-08-24 15:15 | 218
2015-08-24 15:30 | 221
2015-08-24 15:45 | 224
2015-08-24 16:00 | 247
2015-08-24 16:15 | 221
2015-08-24 16:30 | 220
2015-08-24 16:45 | 219
2015-08-24 17:00 | 233
2015-08-24 17:15 | 226
2015-08-24 17:30 | 215
2015-08-24 17:45 | 227
2015-08-24 18:00 | 210
2015-08-24 18:15 | 209
2015-08-24 18:30 | 225
2015-08-24 18:45 | 219
2015-08-24 19:00 | 200
2015-08-24 19:15 | 208
2015-08-24 19:30 | 203
2015-08-24 19:45 | 216
2015-08-24 20:00 | 200
2015-08-24 20:15 | 208
2015-08-24 20:30 | 202
2015-08-24 20:45 | 208
2015-08-24 21:00 | 195
2015-08-24 21:15 | 206
2015-08-24 21:30 | 205
2015-08-24 21:45 | 187
2015-08-24 22:00 | 194
2015-08-24 22:15 | 186
2015-08-24 22:30 | 198
2015-08-24 22:45 | 199
2015-08-24 23:00 | 178
2015-08-24 23:15 | 180
2015-08-24 23:30 | 184
2015-08-24 23:45 | 188
2015-08-25 | 191
2015-08-25 00:15 | 183
2015-08-25 00:30 | 176
2015-08-25 00:45 | 172
2015-08-25 01:00 | 182
2015-08-25 01:15 | 185
2015-08-25 01:30 | 159
2015-08-25 01:45 | 163
2015-08-25 02:00 | 162
2015-08-25 02:15 | 174
2015-08-25 02:30 | 160
2015-08-25 02:45 | 158
2015-08-25 03:00 | 165
2015-08-25 03:15 | 170
2015-08-25 03:30 | 162
2015-08-25 03:45 | 159
2015-08-25 04:00 | 156
2015-08-25 04:15 | 167
2015-08-25 04:30 | 177
2015-08-25 04:45 | 160
2015-08-25 05:00 | 160
2015-08-25 05:15 | 160
2015-08-25 05:30 | 170
2015-08-25 05:45 | 172
2015-08-25 06:00 | 156
2015-08-25 06:15 | 160
2015-08-25 06:30 | 158
2015-08-25 06:45 | 173
2015-08-25 07:00 | 162
2015-08-25 07:15 | 160
2015-08-25 07:30 | 162
2015-08-25 07:45 | 163
2015-08-25 08:00 | 188
2015-08-25 08:15 | 177
2015-08-25 08:30 | 185
2015-08-25 08:45 | 181
2015-08-25 09:00 | 186
2015-08-25 09:15 | 204
2015-08-25 09:30 | 192
2015-08-25 09:45 | 193
2015-08-25 10:00 | 205
2015-08-25 10:15 | 195
2015-08-25 10:30 | 197
2015-08-25 10:45 | 196
2015-08-25 11:00 | 217
2015-08-25 11:15 | 214
2015-08-25 11:30 | 199
2015-08-25 11:45 | 209
2015-08-25 12:00 | 201
2015-08-25 12:15 | 223
2015-08-25 12:30 | 211
2015-08-25 12:45 | 207
2015-08-25 13:00 | 210
2015-08-25 13:15 | 211
2015-08-25 13:30 | 223
2015-08-25 13:45 | 224
2015-08-25 14:00 | 224
2015-08-25 14:15 | 222
2015-08-25 14:30 | 224
2015-08-25 14:45 | 239
2015-08-25 15:00 | 239
2015-08-25 15:15 | 238
2015-08-25 15:30 | 233
2015-08-25 15:45 | 240
2015-08-25 16:00 | 242
2015-08-25 16:15 | 244
2015-08-25 16:30 | 239
2015-08-25 16:45 | 241
2015-08-25 17:00 | 232
2015-08-25 17:15 | 241
2015-08-25 17:30 | 253
2015-08-25 17:45 | 227
2015-08-25 18:00 | 229
2015-08-25 18:15 | 216
2015-08-25 18:30 | 217
2015-08-25 18:45 | 233
2015-08-25 19:00 | 210
2015-08-25 19:15 | 218
2015-08-25 19:30 | 213
2015-08-25 19:45 | 210
2015-08-25 20:00 | 205
2015-08-25 20:15 | 221
2015-08-25 20:30 | 206
2015-08-25 20:45 | 201
2015-08-25 21:00 | 205
2015-08-25 21:15 | 190
2015-08-25 21:30 | 208
2015-08-25 21:45 | 195
2015-08-25 22:00 | 186
2015-08-25 22:15 | 189
2015-08-25 22:30 | 189
2015-08-25 22:45 | 197
2015-08-25 23:00 | 185
2015-08-25 23:15 | 181
2015-08-25 23:30 | 169
2015-08-25 23:45 | 172
2015-08-26 | 186
2015-08-26 00:15 | 171
2015-08-26 00:30 | 167
2015-08-26 00:45 | 167
2015-08-26 01:00 | 185
2015-08-26 01:15 | 169
2015-08-26 01:30 | 164
2015-08-26 01:45 | 170
2015-08-26 02:00 | 162
2015-08-26 02:15 | 154
2015-08-26 02:30 | 158
2015-08-26 02:45 | 162
2015-08-26 03:00 | 171
2015-08-26 03:15 | 163
2015-08-26 03:30 | 158
2015-08-26 03:45 | 157
2015-08-26 04:00 | 169
2015-08-26 04:15 | 169
2015-08-26 04:30 | 153
2015-08-26 04:45 | 155
2015-08-26 05:00 | 165
2015-08-26 05:15 | 163
2015-08-26 05:30 | 158
2015-08-26 05:45 | 155
2015-08-26 06:00 | 167
2015-08-26 06:15 | 174
2015-08-26 06:30 | 176
2015-08-26 06:45 | 161
2015-08-26 07:00 | 167
2015-08-26 07:15 | 160
2015-08-26 07:30 | 175
2015-08-26 07:45 | 168
2015-08-26 08:00 | 169
2015-08-26 08:15 | 179
2015-08-26 08:30 | 184
2015-08-26 08:45 | 194
2015-08-26 09:00 | 182
2015-08-26 09:15 | 189
2015-08-26 09:30 | 193
2015-08-26 09:45 | 195
2015-08-26 10:00 | 200
2015-08-26 10:15 | 198
2015-08-26 10:30 | 203
2015-08-26 10:45 | 206
2015-08-26 11:00 | 210
2015-08-26 11:15 | 217
2015-08-26 11:30 | 229
2015-08-26 11:45 | 222
2015-08-26 12:00 | 219
2015-08-26 12:15 | 223
2015-08-26 12:30 | 229
2015-08-26 12:45 | 220
2015-08-26 13:00 | 222
2015-08-26 13:15 | 222
2015-08-26 13:30 | 211
2015-08-26 13:45 | 232
2015-08-26 14:00 | 212
2015-08-26 14:15 | 242
2015-08-26 14:30 | 229
2015-08-26 14:45 | 220
2015-08-26 15:00 | 218
2015-08-26 15:15 | 236
2015-08-26 15:30 | 228
2015-08-26 15:45 | 242
2015-08-26 16:00 | 240
2015-08-26 16:15 | 234
2015-08-26 16:30 | 224
2015-08-26 16:45 | 230
2015-08-26 17:00 | 233
2015-08-26 17:15 | 241
2015-08-26 17:30 | 226
2015-08-26 17:45 | 215
2015-08-26 18:00 | 222
2015-08-26 18:15 | 219
2015-08-26 18:30 | 222
2015-08-26 18:45 | 222
2015-08-26 19:00 | 226
2015-08-26 19:15 | 220
2015-08-26 19:30 | 214
2015-08-26 19:45 | 206
2015-08-26 20:00 | 214
2015-08-26 20:15 | 214
2015-08-26 20:30 | 200
2015-08-26 20:45 | 196
2015-08-26 21:00 | 203
2015-08-26 21:15 | 201
2015-08-26 21:30 | 189
2015-08-26 21:45 | 181
2015-08-26 22:00 | 184
2015-08-26 22:15 | 186
2015-08-26 22:30 | 193
2015-08-26 22:45 | 186
2015-08-26 23:00 | 191
2015-08-26 23:15 | 185
2015-08-26 23:30 | 210
2015-08-26 23:45 | 201
2015-08-27 | 192
2015-08-27 00:15 | 196
2015-08-27 00:30 | 189
2015-08-27 00:45 | 195
2015-08-27 01:00 | 188
2015-08-27 01:15 | 179
2015-08-27 01:30 | 177
2015-08-27 01:45 | 191
2015-08-27 02:00 | 179
2015-08-27 02:15 | 170
2015-08-27 02:30 | 172
2015-08-27 02:45 | 168
2015-08-27 03:00 | 177
2015-08-27 03:15 | 180
2015-08-27 03:30 | 164
2015-08-27 03:45 | 166
2015-08-27 04:00 | 176
2015-08-27 04:15 | 179
2015-08-27 04:30 | 166
2015-08-27 04:45 | 170
2015-08-27 05:00 | 166
2015-08-27 05:15 | 177
2015-08-27 05:30 | 176
2015-08-27 05:45 | 163
2015-08-27 06:00 | 164
2015-08-27 06:15 | 179
2015-08-27 06:30 | 184
2015-08-27 06:45 | 172
2015-08-27 07:00 | 173
2015-08-27 07:15 | 169
2015-08-27 07:30 | 185
2015-08-27 07:45 | 181
2015-08-27 08:00 | 173
2015-08-27 08:15 | 181
2015-08-27 08:30 | 177
2015-08-27 08:45 | 197
2015-08-27 09:00 | 190
2015-08-27 09:15 | 188
2015-08-27 09:30 | 192
2015-08-27 09:45 | 201
2015-08-27 10:00 | 214
2015-08-27 10:15 | 201
2015-08-27 10:30 | 211
2015-08-27 10:45 | 204
2015-08-27 11:00 | 218
2015-08-27 11:15 | 228
2015-08-27 11:30 | 218
2015-08-27 11:45 | 220
2015-08-27 12:00 | 217
2015-08-27 12:15 | 249
2015-08-27 12:30 | 226
2015-08-27 12:45 | 220
2015-08-27 13:00 | 235
2015-08-27 13:15 | 235
2015-08-27 13:30 | 257
2015-08-27 13:45 | 242
2015-08-27 14:00 | 247
2015-08-27 14:15 | 247
2015-08-27 14:30 | 255
2015-08-27 14:45 | 260
2015-08-27 15:00 | 254
2015-08-27 15:15 | 257
2015-08-27 15:30 | 254
2015-08-27 15:45 | 261
2015-08-27 16:00 | 263
2015-08-27 16:15 | 253
2015-08-27 16:30 | 258
2015-08-27 16:45 | 256
2015-08-27 17:00 | 254
2015-08-27 17:15 | 261
2015-08-27 17:30 | 251
2015-08-27 17:45 | 242
2015-08-27 18:00 | 248
2015-08-27 18:15 | 234
2015-08-27 18:30 | 257
2015-08-27 18:45 | 235
2015-08-27 19:00 | 243
2015-08-27 19:15 | 227
2015-08-27 19:30 | 224
2015-08-27 19:45 | 223
2015-08-27 20:00 | 234
2015-08-27 20:15 | 207
2015-08-27 20:30 | 228
2015-08-27 20:45 | 203
2015-08-27 21:00 | 224
2015-08-27 21:15 | 209
2015-08-27 21:30 | 185
2015-08-27 21:45 | 191
2015-08-27 22:00 | 193
2015-08-27 22:15 | 195
2015-08-27 22:30 | 190
2015-08-27 22:45 | 182
2015-08-27 23:00 | 177
2015-08-27 23:15 | 193
2015-08-27 23:30 | 181
2015-08-27 23:45 | 183
2015-08-28 | 176
2015-08-28 00:15 | 176
2015-08-28 00:30 | 194
2015-08-28 00:45 | 172
2015-08-28 01:00 | 180
2015-08-28 01:15 | 176
2015-08-28 01:30 | 169
2015-08-28 01:45 | 187
2015-08-28 02:00 | 180
2015-08-28 02:15 | 175
2015-08-28 02:30 | 172
2015-08-28 02:45 | 163
2015-08-28 03:00 | 183
2015-08-28 03:15 | 173
2015-08-28 03:30 | 172
2015-08-28 03:45 | 167
2015-08-28 04:00 | 168
2015-08-28 04:15 | 179
2015-08-28 04:30 | 168
2015-08-28 04:45 | 168
2015-08-28 05:00 | 157
2015-08-28 05:15 | 171
2015-08-28 05:30 | 178
2015-08-28 05:45 | 164
2015-08-28 06:00 | 170
2015-08-28 06:15 | 166
2015-08-28 06:30 | 178
2015-08-28 06:45 | 182
2015-08-28 07:00 | 169
2015-08-28 07:15 | 178
2015-08-28 07:30 | 171
2015-08-28 07:45 | 183
2015-08-28 08:00 | 183
2015-08-28 08:15 | 180
2015-08-28 08:30 | 184
2015-08-28 08:45 | 192
2015-08-28 09:00 | 205
2015-08-28 09:15 | 201
2015-08-28 09:30 | 209
2015-08-28 09:45 | 198
2015-08-28 10:00 | 218
2015-08-28 10:15 | 226
2015-08-28 10:30 | 221
2015-08-28 10:45 | 222
2015-08-28 11:00 | 233
2015-08-28 11:15 | 240
2015-08-28 11:30 | 250
2015-08-28 11:45 | 243
2015-08-28 12:00 | 246
2015-08-28 12:15 | 239
2015-08-28 12:30 | 247
2015-08-28 12:45 | 264
2015-08-28 13:00 | 246
2015-08-28 13:15 | 252
2015-08-28 13:30 | 258
2015-08-28 13:45 | 274
2015-08-28 14:00 | 269
2015-08-28 14:15 | 267
2015-08-28 14:30 | 266
2015-08-28 14:45 | 266
2015-08-28 15:00 | 290
2015-08-28 15:15 | 272
2015-08-28 15:30 | 268
2015-08-28 15:45 | 276
2015-08-28 16:00 | 272
2015-08-28 16:15 | 243
2015-08-28 16:30 | 250
2015-08-28 16:45 | 255
2015-08-28 17:00 | 257
2015-08-28 17:15 | 247
2015-08-28 17:30 | 256
2015-08-28 17:45 | 243
2015-08-28 18:00 | 242
2015-08-28 18:15 | 245
2015-08-28 18:30 | 246
2015-08-28 18:45 | 245
2015-08-28 19:00 | 233
2015-08-28 19:15 | 240
2015-08-28 19:30 | 224
2015-08-28 19:45 | 238
2015-08-28 20:00 | 220
2015-08-28 20:15 | 213
2015-08-28 20:30 | 215
2015-08-28 20:45 | 215
2015-08-28 21:00 | 220
2015-08-28 21:15 | 207
2015-08-28 21:30 | 209
2015-08-28 21:45 | 211
2015-08-28 22:00 | 196
2015-08-28 22:15 | 203
2015-08-28 22:30 | 200
2015-08-28 22:45 | 185
2015-08-28 23:00 | 192
2015-08-28 23:15 | 204
2015-08-28 23:30 | 221
2015-08-28 23:45 | 204
2015-08-29 | 200
2015-08-29 00:15 | 195
2015-08-29 00:30 | 180
2015-08-29 00:45 | 191
2015-08-29 01:00 | 190
2015-08-29 01:15 | 183
2015-08-29 01:30 | 177
2015-08-29 01:45 | 188
2015-08-29 02:00 | 187
2015-08-29 02:15 | 171
2015-08-29 02:30 | 182
2015-08-29 02:45 | 175
2015-08-29 03:00 | 184
2015-08-29 03:15 | 183
2015-08-29 03:30 | 177
2015-08-29 03:45 | 174
2015-08-29 04:00 | 171
2015-08-29 04:15 | 195
2015-08-29 04:30 | 174
2015-08-29 04:45 | 169
2015-08-29 05:00 | 176
2015-08-29 05:15 | 186
2015-08-29 05:30 | 188
2015-08-29 05:45 | 169
2015-08-29 06:00 | 171
2015-08-29 06:15 | 177
2015-08-29 06:30 | 194
2015-08-29 06:45 | 179
2015-08-29 07:00 | 173
2015-08-29 07:15 | 168
2015-08-29 07:30 | 179
2015-08-29 07:45 | 161
2015-08-29 08:00 | 169
2015-08-29 08:15 | 154
2015-08-29 08:30 | 152
2015-08-29 08:45 | 161
2015-08-29 09:00 | 169
2015-08-29 09:15 | 158
2015-08-29 09:30 | 162
2015-08-29 09:45 | 178
2015-08-29 10:00 | 170
2015-08-29 10:15 | 166
2015-08-29 10:30 | 169
2015-08-29 10:45 | 178
2015-08-29 11:00 | 168
2015-08-29 11:15 | 164
2015-08-29 11:30 | 167
2015-08-29 11:45 | 168
2015-08-29 12:00 | 187
2015-08-29 12:15 | 176
2015-08-29 12:30 | 179
2015-08-29 12:45 | 176
2015-08-29 13:00 | 184
2015-08-29 13:15 | 188
2015-08-29 13:30 | 179
2015-08-29 13:45 | 176
2015-08-29 14:00 | 175
2015-08-29 14:15 | 200
2015-08-29 14:30 | 194
2015-08-29 14:45 | 189
2015-08-29 15:00 | 190
2015-08-29 15:15 | 195
2015-08-29 15:30 | 202
2015-08-29 15:45 | 184
2015-08-29 16:00 | 198
2015-08-29 16:15 | 188
2015-08-29 16:30 | 181
2015-08-29 16:45 | 193
2015-08-29 17:00 | 202
2015-08-29 17:15 | 191
2015-08-29 17:30 | 188
2015-08-29 17:45 | 186
2015-08-29 18:00 | 182
2015-08-29 18:15 | 183
2015-08-29 18:30 | 198
2015-08-29 18:45 | 181
2015-08-29 19:00 | 186
2015-08-29 19:15 | 177
2015-08-29 19:30 | 174
2015-08-29 19:45 | 169
2015-08-29 20:00 | 171
2015-08-29 20:15 | 184
2015-08-29 20:30 | 161
2015-08-29 20:45 | 165
2015-08-29 21:00 | 164
2015-08-29 21:15 | 164
2015-08-29 21:30 | 176
2015-08-29 21:45 | 165
2015-08-29 22:00 | 156
2015-08-29 22:15 | 161
2015-08-29 22:30 | 179
2015-08-29 22:45 | 147
2015-08-29 23:00 | 157
2015-08-29 23:15 | 151
2015-08-29 23:30 | 159
2015-08-29 23:45 | 161
2015-08-30 | 144
2015-08-30 00:15 | 145
2015-08-30 00:30 | 159
2015-08-30 00:45 | 153
2015-08-30 01:00 | 140
2015-08-30 01:15 | 146
2015-08-30 01:30 | 144
2015-08-30 01:45 | 160
2015-08-30 02:00 | 137
2015-08-30 02:15 | 147
2015-08-30 02:30 | 135
2015-08-30 02:45 | 157
2015-08-30 03:00 | 146
2015-08-30 03:15 | 146
2015-08-30 03:30 | 136
2015-08-30 03:45 | 158
2015-08-30 04:00 | 147
2015-08-30 04:15 | 145
2015-08-30 04:30 | 138
2015-08-30 04:45 | 145
2015-08-30 05:00 | 152
2015-08-30 05:15 | 146
2015-08-30 05:30 | 142
2015-08-30 05:45 | 144
2015-08-30 06:00 | 149
2015-08-30 06:15 | 160
2015-08-30 06:30 | 138
2015-08-30 06:45 | 147
2015-08-30 07:00 | 150
2015-08-30 07:15 | 162
2015-08-30 07:30 | 162
2015-08-30 07:45 | 155
2015-08-30 08:00 | 157
2015-08-30 08:15 | 150
2015-08-30 08:30 | 163
2015-08-30 08:45 | 165
2015-08-30 09:00 | 171
2015-08-30 09:15 | 158
2015-08-30 09:30 | 158
2015-08-30 09:45 | 162
2015-08-30 10:00 | 162
2015-08-30 10:15 | 173
2015-08-30 10:30 | 168
2015-08-30 10:45 | 162
2015-08-30 11:00 | 163
2015-08-30 11:15 | 185
2015-08-30 11:30 | 183
2015-08-30 11:45 | 177
2015-08-30 12:00 | 174
2015-08-30 12:15 | 173
2015-08-30 12:30 | 189
2015-08-30 12:45 | 183
2015-08-30 13:00 | 174
2015-08-30 13:15 | 178
2015-08-30 13:30 | 175
2015-08-30 13:45 | 188
2015-08-30 14:00 | 194
2015-08-30 14:15 | 176
2015-08-30 14:30 | 179
2015-08-30 14:45 | 188
2015-08-30 15:00 | 201
2015-08-30 15:15 | 191
2015-08-30 15:30 | 190
2015-08-30 15:45 | 200
2015-08-30 16:00 | 202
2015-08-30 16:15 | 204
2015-08-30 16:30 | 204
2015-08-30 16:45 | 190
2015-08-30 17:00 | 198
2015-08-30 17:15 | 213
2015-08-30 17:30 | 205
2015-08-30 17:45 | 195
2015-08-30 18:00 | 210
2015-08-30 18:15 | 189
2015-08-30 18:30 | 193
2015-08-30 18:45 | 183
2015-08-30 19:00 | 202
2015-08-30 19:15 | 193
2015-08-30 19:30 | 180
2015-08-30 19:45 | 173
2015-08-30 20:00 | 172
2015-08-30 20:15 | 186
2015-08-30 20:30 | 179
2015-08-30 20:45 | 167
2015-08-30 21:00 | 174
2015-08-30 21:15 | 180
2015-08-30 21:30 | 169
2015-08-30 21:45 | 163
2015-08-30 22:00 | 167
2015-08-30 22:15 | 153
2015-08-30 22:30 | 166
2015-08-30 22:45 | 170
2015-08-30 23:00 | 151
2015-08-30 23:15 | 162
2015-08-30 23:30 | 172
2015-08-30 23:45 | 159
2015-08-31 | 155
2015-08-31 00:15 | 158
2015-08-31 00:30 | 161
2015-08-31 00:45 | 164
2015-08-31 01:00 | 155
2015-08-31 01:15 | 153
2015-08-31 01:30 | 147
2015-08-31 01:45 | 161
2015-08-31 02:00 | 167
2015-08-31 02:15 | 146
2015-08-31 02:30 | 149
2015-08-31 02:45 | 151
2015-08-31 03:00 | 150
2015-08-31 03:15 | 167
2015-08-31 03:30 | 143
2015-08-31 03:45 | 143
2015-08-31 04:00 | 147
2015-08-31 04:15 | 140
2015-08-31 04:30 | 166
2015-08-31 04:45 | 145
2015-08-31 05:00 | 147
2015-08-31 05:15 | 143
2015-08-31 05:30 | 144
2015-08-31 05:45 | 164
2015-08-31 06:00 | 145
2015-08-31 06:15 | 144
2015-08-31 06:30 | 142
2015-08-31 06:45 | 141
2015-08-31 07:00 | 158
2015-08-31 07:15 | 146
2015-08-31 07:30 | 141
2015-08-31 07:45 | 144
2015-08-31 08:00 | 154
2015-08-31 08:15 | 159
2015-08-31 08:30 | 179
2015-08-31 08:45 | 164
2015-08-31 09:00 | 171
2015-08-31 09:15 | 165
2015-08-31 09:30 | 178
2015-08-31 09:45 | 186
2015-08-31 10:00 | 191
2015-08-31 10:15 | 190
2015-08-31 10:30 | 197
2015-08-31 10:45 | 212
2015-08-31 11:00 | 199
2015-08-31 11:15 | 196
2015-08-31 11:30 | 198
2015-08-31 11:45 | 191
2015-08-31 12:00 | 218
2015-08-31 12:15 | 205
2015-08-31 12:30 | 203
2015-08-31 12:45 | 202
2015-08-31 13:00 | 201
2015-08-31 13:15 | 222
2015-08-31 13:30 | 218
2015-08-31 13:45 | 226
2015-08-31 14:00 | 214
2015-08-31 14:15 | 233
2015-08-31 14:30 | 238
2015-08-31 14:45 | 228
2015-08-31 15:00 | 226
2015-08-31 15:15 | 234
2015-08-31 15:30 | 238
2015-08-31 15:45 | 249
2015-08-31 16:00 | 231
2015-08-31 16:15 | 231
2015-08-31 16:30 | 240
2015-08-31 16:45 | 238
2015-08-31 17:00 | 262
2015-08-31 17:15 | 230
2015-08-31 17:30 | 234
2015-08-31 17:45 | 227
2015-08-31 18:00 | 229
2015-08-31 18:15 | 227
2015-08-31 18:30 | 231
2015-08-31 18:45 | 224
2015-08-31 19:00 | 218
2015-08-31 19:15 | 208
2015-08-31 19:30 | 220
2015-08-31 19:45 | 204
2015-08-31 20:00 | 202
2015-08-31 20:15 | 196
2015-08-31 20:30 | 210
2015-08-31 20:45 | 198
2015-08-31 21:00 | 195
2015-08-31 21:15 | 185
2015-08-31 21:30 | 204
2015-08-31 21:45 | 193
2015-08-31 22:00 | 196
2015-08-31 22:15 | 192
2015-08-31 22:30 | 185
2015-08-31 22:45 | 200
2015-08-31 23:00 | 195
2015-08-31 23:15 | 180
2015-08-31 23:30 | 178
2015-08-31 23:45 | 177
2015-09-01 | 184
2015-09-01 00:15 | 176
2015-09-01 00:30 | 168
2015-09-01 00:45 | 171
2015-09-01 01:00 | 170
2015-09-01 01:15 | 168
2015-09-01 01:30 | 164
2015-09-01 01:45 | 179
2015-09-01 02:00 | 166
2015-09-01 02:15 | 159
2015-09-01 02:30 | 160
2015-09-01 02:45 | 163
2015-09-01 03:00 | 173
2015-09-01 03:15 | 163
2015-09-01 03:30 | 161
2015-09-01 03:45 | 154
2015-09-01 04:00 | 173
2015-09-01 04:15 | 159
2015-09-01 04:30 | 154
2015-09-01 04:45 | 158
2015-09-01 05:00 | 157
2015-09-01 05:15 | 167
2015-09-01 05:30 | 151
2015-09-01 05:45 | 150
2015-09-01 06:00 | 150
2015-09-01 06:15 | 152
2015-09-01 06:30 | 162
2015-09-01 06:45 | 155
2015-09-01 07:00 | 159
2015-09-01 07:15 | 150
2015-09-01 07:30 | 156
2015-09-01 07:45 | 167
2015-09-01 08:00 | 152
2015-09-01 08:15 | 162
2015-09-01 08:30 | 166
2015-09-01 08:45 | 181
2015-09-01 09:00 | 187
2015-09-01 09:15 | 180
2015-09-01 09:30 | 188
2015-09-01 09:45 | 182
2015-09-01 10:00 | 198
2015-09-01 10:15 | 205
2015-09-01 10:30 | 185
2015-09-01 10:45 | 194
2015-09-01 11:00 | 194
2015-09-01 11:15 | 210
2015-09-01 11:30 | 205
2015-09-01 11:45 | 203
2015-09-01 12:00 | 209
2015-09-01 12:15 | 203
2015-09-01 12:30 | 219
2015-09-01 12:45 | 211
2015-09-01 13:00 | 212
2015-09-01 13:15 | 210
2015-09-01 13:30 | 214
2015-09-01 13:45 | 234
2015-09-01 14:00 | 231
2015-09-01 14:15 | 218
2015-09-01 14:30 | 231
2015-09-01 14:45 | 226
2015-09-01 15:00 | 242
2015-09-01 15:15 | 234
2015-09-01 15:30 | 240
2015-09-01 15:45 | 229
2015-09-01 16:00 | 235
2015-09-01 16:15 | 242
2015-09-01 16:30 | 250
2015-09-01 16:45 | 237
2015-09-01 17:00 | 250
2015-09-01 17:15 | 227
2015-09-01 17:30 | 248
2015-09-01 17:45 | 243
2015-09-01 18:00 | 228
2015-09-01 18:15 | 231
2015-09-01 18:30 | 219
2015-09-01 18:45 | 227
2015-09-01 19:00 | 238
2015-09-01 19:15 | 211
2015-09-01 19:30 | 210
2015-09-01 19:45 | 202
2015-09-01 20:00 | 203
2015-09-01 20:15 | 209
2015-09-01 20:30 | 201
2015-09-01 20:45 | 209
2015-09-01 21:00 | 207
2015-09-01 21:15 | 192
2015-09-01 21:30 | 198
2015-09-01 21:45 | 193
2015-09-01 22:00 | 192
2015-09-01 22:15 | 181
2015-09-01 22:30 | 192
2015-09-01 22:45 | 201
2015-09-01 23:00 | 181
2015-09-01 23:15 | 183
2015-09-01 23:30 | 177
2015-09-01 23:45 | 184
2015-09-02 | 183
2015-09-02 00:15 | 173
2015-09-02 00:30 | 163
2015-09-02 00:45 | 169
2015-09-02 01:00 | 172
2015-09-02 01:15 | 184
2015-09-02 01:30 | 168
2015-09-02 01:45 | 171
2015-09-02 02:00 | 167
2015-09-02 02:15 | 163
2015-09-02 02:30 | 181
2015-09-02 02:45 | 162
2015-09-02 03:00 | 155
2015-09-02 03:15 | 162
2015-09-02 03:30 | 170
2015-09-02 03:45 | 167
2015-09-02 04:00 | 158
2015-09-02 04:15 | 154
2015-09-02 04:30 | 164
2015-09-02 04:45 | 178
2015-09-02 05:00 | 163
2015-09-02 05:15 | 162
2015-09-02 05:30 | 153
2015-09-02 05:45 | 160
2015-09-02 06:00 | 174
2015-09-02 06:15 | 157
2015-09-02 06:30 | 166
2015-09-02 06:45 | 157
2015-09-02 07:00 | 172
2015-09-02 07:15 | 175
2015-09-02 07:30 | 160
2015-09-02 07:45 | 160
2015-09-02 08:00 | 165
2015-09-02 08:15 | 179
2015-09-02 08:30 | 180
2015-09-02 08:45 | 182
2015-09-02 09:00 | 173
2015-09-02 09:15 | 189
2015-09-02 09:30 | 198
2015-09-02 09:45 | 181
2015-09-02 10:00 | 185
2015-09-02 10:15 | 192
2015-09-02 10:30 | 211
2015-09-02 10:45 | 194
2015-09-02 11:00 | 201
2015-09-02 11:15 | 208
2015-09-02 11:30 | 205
2015-09-02 11:45 | 227
2015-09-02 12:00 | 213
2015-09-02 12:15 | 212
2015-09-02 12:30 | 205
2015-09-02 12:45 | 211
2015-09-02 13:00 | 217
2015-09-02 13:15 | 233
2015-09-02 13:30 | 221
2015-09-02 13:45 | 224
2015-09-02 14:00 | 227
2015-09-02 14:15 | 232
2015-09-02 14:30 | 225
2015-09-02 14:45 | 251
2015-09-02 15:00 | 221
2015-09-02 15:15 | 228
2015-09-02 15:30 | 229
2015-09-02 15:45 | 222
2015-09-02 16:00 | 235
2015-09-02 16:15 | 236
2015-09-02 16:30 | 223
2015-09-02 16:45 | 233
2015-09-02 17:00 | 229
2015-09-02 17:15 | 223
2015-09-02 17:30 | 225
2015-09-02 17:45 | 215
2015-09-02 18:00 | 217
2015-09-02 18:15 | 215
2015-09-02 18:30 | 215
2015-09-02 18:45 | 228
2015-09-02 19:00 | 212
2015-09-02 19:15 | 204
2015-09-02 19:30 | 197
2015-09-02 19:45 | 214
2015-09-02 20:00 | 204
2015-09-02 20:15 | 206
2015-09-02 20:30 | 192
2015-09-02 20:45 | 192
2015-09-02 21:00 | 205
2015-09-02 21:15 | 197
2015-09-02 21:30 | 185
2015-09-02 21:45 | 186
2015-09-02 22:00 | 186
2015-09-02 22:15 | 196
2015-09-02 22:30 | 182
2015-09-02 22:45 | 186
2015-09-02 23:00 | 184
2015-09-02 23:15 | 184
2015-09-02 23:30 | 188
2015-09-02 23:45 | 171
2015-09-03 | 177
2015-09-03 00:15 | 165
2015-09-03 00:30 | 182
2015-09-03 00:45 | 165
2015-09-03 01:00 | 161
2015-09-03 01:15 | 178
2015-09-03 01:30 | 163
2015-09-03 01:45 | 158
2015-09-03 02:00 | 158
2015-09-03 02:15 | 173
2015-09-03 02:30 | 160
2015-09-03 02:45 | 164
2015-09-03 03:00 | 156
2015-09-03 03:15 | 162
2015-09-03 03:30 | 177
2015-09-03 03:45 | 153
2015-09-03 04:00 | 162
2015-09-03 04:15 | 149
2015-09-03 04:30 | 166
2015-09-03 04:45 | 166
2015-09-03 05:00 | 154
2015-09-03 05:15 | 159
2015-09-03 05:30 | 152
2015-09-03 05:45 | 164
2015-09-03 06:00 | 168
2015-09-03 06:15 | 161
2015-09-03 06:30 | 158
2015-09-03 06:45 | 157
2015-09-03 07:00 | 174
2015-09-03 07:15 | 156
2015-09-03 07:30 | 162
2015-09-03 07:45 | 154
2015-09-03 08:00 | 164
2015-09-03 08:15 | 179
2015-09-03 08:30 | 167
2015-09-03 08:45 | 167
2015-09-03 09:00 | 167
2015-09-03 09:15 | 175
2015-09-03 09:30 | 189
2015-09-03 09:45 | 181
2015-09-03 10:00 | 188
2015-09-03 10:15 | 180
2015-09-03 10:30 | 186
2015-09-03 10:45 | 204
2015-09-03 11:00 | 192
2015-09-03 11:15 | 193
2015-09-03 11:30 | 195
2015-09-03 11:45 | 206
2015-09-03 12:00 | 212
2015-09-03 12:15 | 202
2015-09-03 12:30 | 198
2015-09-03 12:45 | 209
2015-09-03 13:00 | 205
2015-09-03 13:15 | 214
2015-09-03 13:30 | 198
2015-09-03 13:45 | 207
2015-09-03 14:00 | 204
2015-09-03 14:15 | 210
2015-09-03 14:30 | 209
2015-09-03 14:45 | 207
2015-09-03 15:00 | 212
2015-09-03 15:15 | 212
2015-09-03 15:30 | 207
2015-09-03 15:45 | 228
2015-09-03 16:00 | 224
2015-09-03 16:15 | 215
2015-09-03 16:30 | 203
2015-09-03 16:45 | 229
2015-09-03 17:00 | 216
2015-09-03 17:15 | 226
2015-09-03 17:30 | 215
2015-09-03 17:45 | 203
2015-09-03 18:00 | 212
2015-09-03 18:15 | 212
2015-09-03 18:30 | 204
2015-09-03 18:45 | 214
2015-09-03 19:00 | 193
2015-09-03 19:15 | 208
2015-09-03 19:30 | 202
2015-09-03 19:45 | 195
2015-09-03 20:00 | 192
2015-09-03 20:15 | 183
2015-09-03 20:30 | 184
2015-09-03 20:45 | 182
2015-09-03 21:00 | 183
2015-09-03 21:15 | 179
2015-09-03 21:30 | 165
2015-09-03 21:45 | 168
2015-09-03 22:00 | 162
2015-09-03 22:15 | 170
2015-09-03 22:30 | 165
2015-09-03 22:45 | 175
2015-09-03 23:00 | 164
2015-09-03 23:15 | 161
2015-09-03 23:30 | 161
2015-09-03 23:45 | 147
2015-09-04 | 154
2015-09-04 00:15 | 147
2015-09-04 00:30 | 147
2015-09-04 00:45 | 140
2015-09-04 01:00 | 143
2015-09-04 01:15 | 142
2015-09-04 01:30 | 148
2015-09-04 01:45 | 140
2015-09-04 02:00 | 140
2015-09-04 02:15 | 140
2015-09-04 02:30 | 140
2015-09-04 02:45 | 140
2015-09-04 03:00 | 141
2015-09-04 03:15 | 139
2015-09-04 03:30 | 140
2015-09-04 03:45 | 139
2015-09-04 04:00 | 133
2015-09-04 04:15 | 129
2015-09-04 04:30 | 125
2015-09-04 04:45 | 128
2015-09-04 05:00 | 125
2015-09-04 05:15 | 127
2015-09-04 05:30 | 126
2015-09-04 05:45 | 129
2015-09-04 06:00 | 129
2015-09-04 06:15 | 128
2015-09-04 06:30 | 130
2015-09-04 06:45 | 126
2015-09-04 07:00 | 128
2015-09-04 07:15 | 132
2015-09-04 07:30 | 131
2015-09-04 07:45 | 144
2015-09-04 08:00 | 147
2015-09-04 08:15 | 157
2015-09-04 08:30 | 157
2015-09-04 08:45 | 158
2015-09-04 09:00 | 157
2015-09-04 09:15 | 163
2015-09-04 09:30 | 174
2015-09-04 09:45 | 181
2015-09-04 10:00 | 174
2015-09-04 10:15 | 182
2015-09-04 10:30 | 181
2015-09-04 10:45 | 185
2015-09-04 11:00 | 189
2015-09-04 11:15 | 187
2015-09-04 11:30 | 184
2015-09-04 11:45 | 196
2015-09-04 12:00 | 185
2015-09-04 12:15 | 198
2015-09-04 12:30 | 196
2015-09-04 12:45 | 183
2015-09-04 13:00 | 196
2015-09-04 13:15 | 182
2015-09-04 13:30 | 194
2015-09-04 13:45 | 197
2015-09-04 14:00 | 190
2015-09-04 14:15 | 199
2015-09-04 14:30 | 200
2015-09-04 14:45 | 203
2015-09-04 15:00 | 211
2015-09-04 15:15 | 208
2015-09-04 15:30 | 200
2015-09-04 15:45 | 217
2015-09-04 16:00 | 217
2015-09-04 16:15 | 205
2015-09-04 16:30 | 221
2015-09-04 16:45 | 209
2015-09-04 17:00 | 203
2015-09-04 17:15 | 209
2015-09-04 17:30 | 200
2015-09-04 17:45 | 201
2015-09-04 18:00 | 199
2015-09-04 18:15 | 196
2015-09-04 18:30 | 188
2015-09-04 18:45 | 188
2015-09-04 19:00 | 181
2015-09-04 19:15 | 184
2015-09-04 19:30 | 179
2015-09-04 19:45 | 171
2015-09-04 20:00 | 179
2015-09-04 20:15 | 176
2015-09-04 20:30 | 176
2015-09-04 20:45 | 178
2015-09-04 21:00 | 170
2015-09-04 21:15 | 166
2015-09-04 21:30 | 158
2015-09-04 21:45 | 165
2015-09-04 22:00 | 163
2015-09-04 22:15 | 166
2015-09-04 22:30 | 162
2015-09-04 22:45 | 155
2015-09-04 23:00 | 163
2015-09-04 23:15 | 163
2015-09-04 23:30 | 157
2015-09-04 23:45 | 156
2015-09-05 | 146
2015-09-05 00:15 | 135
2015-09-05 00:30 | 139
2015-09-05 00:45 | 130
2015-09-05 01:00 | 131
2015-09-05 01:15 | 125
2015-09-05 01:30 | 125
2015-09-05 01:45 | 127
2015-09-05 02:00 | 128
2015-09-05 02:15 | 132
2015-09-05 02:30 | 119
2015-09-05 02:45 | 115
2015-09-05 03:00 | 120
2015-09-05 03:15 | 117
2015-09-05 03:30 | 115
2015-09-05 03:45 | 116
2015-09-05 04:00 | 110
2015-09-05 04:15 | 113
2015-09-05 04:30 | 113
2015-09-05 04:45 | 115
2015-09-05 05:00 | 118
2015-09-05 05:15 | 112
2015-09-05 05:30 | 111
2015-09-05 05:45 | 112
2015-09-05 06:00 | 113
2015-09-05 06:15 | 110
2015-09-05 06:30 | 118
2015-09-05 06:45 | 112
2015-09-05 07:00 | 111
2015-09-05 07:15 | 110
2015-09-05 07:30 | 118
2015-09-05 07:45 | 121
2015-09-05 08:00 | 132
2015-09-05 08:15 | 128
2015-09-05 08:30 | 120
2015-09-05 08:45 | 130
2015-09-05 09:00 | 138
2015-09-05 09:15 | 137
2015-09-05 09:30 | 139
2015-09-05 09:45 | 138
2015-09-05 10:00 | 139
2015-09-05 10:15 | 142
2015-09-05 10:30 | 138
2015-09-05 10:45 | 146
2015-09-05 11:00 | 149
2015-09-05 11:15 | 141
2015-09-05 11:30 | 147
2015-09-05 11:45 | 148
2015-09-05 12:00 | 140
2015-09-05 12:15 | 162
2015-09-05 12:30 | 153
2015-09-05 12:45 | 146
2015-09-05 13:00 | 152
2015-09-05 13:15 | 150
2015-09-05 13:30 | 149
2015-09-05 13:45 | 167
2015-09-05 14:00 | 146
2015-09-05 14:15 | 158
2015-09-05 14:30 | 161
2015-09-05 14:45 | 157
2015-09-05 15:00 | 164
2015-09-05 15:15 | 174
2015-09-05 15:30 | 161
2015-09-05 15:45 | 172
2015-09-05 16:00 | 168
2015-09-05 16:15 | 169
2015-09-05 16:30 | 174
2015-09-05 16:45 | 178
2015-09-05 17:00 | 163
2015-09-05 17:15 | 175
2015-09-05 17:30 | 178
2015-09-05 17:45 | 169
2015-09-05 18:00 | 174
2015-09-05 18:15 | 177
2015-09-05 18:30 | 165
2015-09-05 18:45 | 171
2015-09-05 19:00 | 170
2015-09-05 19:15 | 154
2015-09-05 19:30 | 160
2015-09-05 19:45 | 163
2015-09-05 20:00 | 153
2015-09-05 20:15 | 163
2015-09-05 20:30 | 152
2015-09-05 20:45 | 160
2015-09-05 21:00 | 148
2015-09-05 21:15 | 154
2015-09-05 21:30 | 143
2015-09-05 21:45 | 152
2015-09-05 22:00 | 145
2015-09-05 22:15 | 151
2015-09-05 22:30 | 140
2015-09-05 22:45 | 148
2015-09-05 23:00 | 142
2015-09-05 23:15 | 145
2015-09-05 23:30 | 143
2015-09-05 23:45 | 145
2015-09-06 | 144
2015-09-06 00:15 | 145
2015-09-06 00:30 | 140
2015-09-06 00:45 | 139
2015-09-06 01:00 | 140
2015-09-06 01:15 | 138
2015-09-06 01:30 | 137
2015-09-06 01:45 | 146
2015-09-06 02:00 | 133
2015-09-06 02:15 | 138
2015-09-06 02:30 | 130
2015-09-06 02:45 | 139
2015-09-06 03:00 | 133
2015-09-06 03:15 | 137
2015-09-06 03:30 | 130
2015-09-06 03:45 | 136
2015-09-06 04:00 | 132
2015-09-06 04:15 | 132
2015-09-06 04:30 | 134
2015-09-06 04:45 | 126
2015-09-06 05:00 | 129
2015-09-06 05:15 | 128
2015-09-06 05:30 | 129
2015-09-06 05:45 | 130
2015-09-06 06:00 | 126
2015-09-06 06:15 | 123
2015-09-06 06:30 | 131
2015-09-06 06:45 | 131
2015-09-06 07:00 | 138
2015-09-06 07:15 | 134
2015-09-06 07:30 | 139
2015-09-06 07:45 | 143
2015-09-06 08:00 | 139
2015-09-06 08:15 | 139
2015-09-06 08:30 | 144
2015-09-06 08:45 | 152
2015-09-06 09:00 | 144
2015-09-06 09:15 | 151
2015-09-06 09:30 | 150
2015-09-06 09:45 | 152
2015-09-06 10:00 | 157
2015-09-06 10:15 | 155
2015-09-06 10:30 | 151
2015-09-06 10:45 | 161
2015-09-06 11:00 | 160
2015-09-06 11:15 | 162
2015-09-06 11:30 | 156
2015-09-06 11:45 | 172
2015-09-06 12:00 | 169
2015-09-06 12:15 | 166
2015-09-06 12:30 | 171
2015-09-06 12:45 | 174
2015-09-06 13:00 | 174
2015-09-06 13:15 | 177
2015-09-06 13:30 | 180
2015-09-06 13:45 | 169
2015-09-06 14:00 | 174
2015-09-06 14:15 | 192
2015-09-06 14:30 | 180
2015-09-06 14:45 | 185
2015-09-06 15:00 | 195
2015-09-06 15:15 | 200
2015-09-06 15:30 | 183
2015-09-06 15:45 | 200
2015-09-06 16:00 | 189
2015-09-06 16:15 | 191
2015-09-06 16:30 | 200
2015-09-06 16:45 | 191
2015-09-06 17:00 | 188
2015-09-06 17:15 | 206
2015-09-06 17:30 | 193
2015-09-06 17:45 | 201
2015-09-06 18:00 | 194
2015-09-06 18:15 | 195
2015-09-06 18:30 | 187
2015-09-06 18:45 | 198
2015-09-06 19:00 | 197
2015-09-06 19:15 | 177
2015-09-06 19:30 | 178
2015-09-06 19:45 | 180
2015-09-06 20:00 | 172
2015-09-06 20:15 | 174
2015-09-06 20:30 | 177
2015-09-06 20:45 | 171
2015-09-06 21:00 | 177
2015-09-06 21:15 | 160
2015-09-06 21:30 | 161
2015-09-06 21:45 | 168
2015-09-06 22:00 | 152
2015-09-06 22:15 | 163
2015-09-06 22:30 | 152
2015-09-06 22:45 | 154
2015-09-06 23:00 | 160
2015-09-06 23:15 | 145
2015-09-06 23:30 | 152
2015-09-06 23:45 | 152
2015-09-07 | 147
2015-09-07 00:15 | 154
2015-09-07 00:30 | 144
2015-09-07 00:45 | 147
2015-09-07 01:00 | 146
2015-09-07 01:15 | 141
2015-09-07 01:30 | 148
2015-09-07 01:45 | 137
2015-09-07 02:00 | 143
2015-09-07 02:15 | 146
2015-09-07 02:30 | 141
2015-09-07 02:45 | 143
2015-09-07 03:00 | 139
2015-09-07 03:15 | 145
2015-09-07 03:30 | 137
2015-09-07 03:45 | 142
2015-09-07 04:00 | 131
2015-09-07 04:15 | 145
2015-09-07 04:30 | 138
2015-09-07 04:45 | 139
2015-09-07 05:00 | 139
2015-09-07 05:15 | 138
2015-09-07 05:30 | 134
2015-09-07 05:45 | 140
2015-09-07 06:00 | 134
2015-09-07 06:15 | 136
2015-09-07 06:30 | 139
2015-09-07 06:45 | 134
2015-09-07 07:00 | 134
2015-09-07 07:15 | 137
2015-09-07 07:30 | 137
2015-09-07 07:45 | 138
2015-09-07 08:00 | 147
2015-09-07 08:15 | 138
2015-09-07 08:30 | 149
2015-09-07 08:45 | 139
2015-09-07 09:00 | 147
2015-09-07 09:15 | 151
2015-09-07 09:30 | 146
2015-09-07 09:45 | 155
2015-09-07 10:00 | 152
2015-09-07 10:15 | 146
2015-09-07 10:30 | 155
2015-09-07 10:45 | 156
2015-09-07 11:00 | 159
2015-09-07 11:15 | 157
2015-09-07 11:30 | 174
2015-09-07 11:45 | 170
2015-09-07 12:00 | 167
2015-09-07 12:15 | 179
2015-09-07 12:30 | 167
2015-09-07 12:45 | 173
2015-09-07 13:00 | 175
2015-09-07 13:15 | 177
2015-09-07 13:30 | 178
2015-09-07 13:45 | 194
2015-09-07 14:00 | 185
2015-09-07 14:15 | 180
2015-09-07 14:30 | 217
2015-09-07 14:45 | 188
2015-09-07 15:00 | 204
2015-09-07 15:15 | 209
2015-09-07 15:30 | 207
2015-09-07 15:45 | 216
2015-09-07 16:00 | 209
2015-09-07 16:15 | 209
2015-09-07 16:30 | 209
2015-09-07 16:45 | 207
2015-09-07 17:00 | 216
2015-09-07 17:15 | 206
2015-09-07 17:30 | 217
2015-09-07 17:45 | 214
2015-09-07 18:00 | 201
2015-09-07 18:15 | 204
2015-09-07 18:30 | 198
2015-09-07 18:45 | 204
2015-09-07 19:00 | 202
2015-09-07 19:15 | 194
2015-09-07 19:30 | 186
2015-09-07 19:45 | 199
2015-09-07 20:00 | 174
2015-09-07 20:15 | 177
2015-09-07 20:30 | 180
2015-09-07 20:45 | 178
2015-09-07 21:00 | 165
2015-09-07 21:15 | 173
2015-09-07 21:30 | 171
2015-09-07 21:45 | 153
2015-09-07 22:00 | 167
2015-09-07 22:15 | 164
2015-09-07 22:30 | 159
2015-09-07 22:45 | 164
2015-09-07 23:00 | 160
2015-09-07 23:15 | 158
2015-09-07 23:30 | 157
2015-09-07 23:45 | 152
2015-09-08 | 158
2015-09-08 00:15 | 159
2015-09-08 00:30 | 145
2015-09-08 00:45 | 159
2015-09-08 01:00 | 149
2015-09-08 01:15 | 154
2015-09-08 01:30 | 157
2015-09-08 01:45 | 143
2015-09-08 02:00 | 153
2015-09-08 02:15 | 145
2015-09-08 02:30 | 152
2015-09-08 02:45 | 149
2015-09-08 03:00 | 143
2015-09-08 03:15 | 151
2015-09-08 03:30 | 141
2015-09-08 03:45 | 145
2015-09-08 04:00 | 144
2015-09-08 04:15 | 144
2015-09-08 04:30 | 138
2015-09-08 04:45 | 148
2015-09-08 05:00 | 135
2015-09-08 05:15 | 150
2015-09-08 05:30 | 136
2015-09-08 05:45 | 145
2015-09-08 06:00 | 138
2015-09-08 06:15 | 143
2015-09-08 06:30 | 138
2015-09-08 06:45 | 150
2015-09-08 07:00 | 135
2015-09-08 07:15 | 147
2015-09-08 07:30 | 143
2015-09-08 07:45 | 145
2015-09-08 08:00 | 157
2015-09-08 08:15 | 162
2015-09-08 08:30 | 159
2015-09-08 08:45 | 167
2015-09-08 09:00 | 163
2015-09-08 09:15 | 166
2015-09-08 09:30 | 171
2015-09-08 09:45 | 182
2015-09-08 10:00 | 189
2015-09-08 10:15 | 186
2015-09-08 10:30 | 202
2015-09-08 10:45 | 201
2015-09-08 11:00 | 195
2015-09-08 11:15 | 206
2015-09-08 11:30 | 213
2015-09-08 11:45 | 210
2015-09-08 12:00 | 220
2015-09-08 12:15 | 233
2015-09-08 12:30 | 214
2015-09-08 12:45 | 223
2015-09-08 13:00 | 235
2015-09-08 13:15 | 216
2015-09-08 13:30 | 250
2015-09-08 13:45 | 224
2015-09-08 14:00 | 250
2015-09-08 14:15 | 243
2015-09-08 14:30 | 240
2015-09-08 14:45 | 254
2015-09-08 15:00 | 243
2015-09-08 15:15 | 257
2015-09-08 15:30 | 248
2015-09-08 15:45 | 257
2015-09-08 16:00 | 257
2015-09-08 16:15 | 253
2015-09-08 16:30 | 257
2015-09-08 16:45 | 251
2015-09-08 17:00 | 251
2015-09-08 17:15 | 252
2015-09-08 17:30 | 249
2015-09-08 17:45 | 252
2015-09-08 18:00 | 239
2015-09-08 18:15 | 247
2015-09-08 18:30 | 245
2015-09-08 18:45 | 231
2015-09-08 19:00 | 234
2015-09-08 19:15 | 230
2015-09-08 19:30 | 221
2015-09-08 19:45 | 228
2015-09-08 20:00 | 215
2015-09-08 20:15 | 215
2015-09-08 20:30 | 212
2015-09-08 20:45 | 211
2015-09-08 21:00 | 201
2015-09-08 21:15 | 204
2015-09-08 21:30 | 191
2015-09-08 21:45 | 188
2015-09-08 22:00 | 195
2015-09-08 22:15 | 191
2015-09-08 22:30 | 182
2015-09-08 22:45 | 184
2015-09-08 23:00 | 192
2015-09-08 23:15 | 175
2015-09-08 23:30 | 178
2015-09-08 23:45 | 179
2015-09-09 | 169
2015-09-09 00:15 | 172
2015-09-09 00:30 | 173
2015-09-09 00:45 | 170
2015-09-09 01:00 | 172
2015-09-09 01:15 | 174
2015-09-09 01:30 | 164
2015-09-09 01:45 | 171
2015-09-09 02:00 | 170
2015-09-09 02:15 | 161
2015-09-09 02:30 | 177
2015-09-09 02:45 | 161
2015-09-09 03:00 | 160
2015-09-09 03:15 | 169
2015-09-09 03:30 | 159
2015-09-09 03:45 | 167
2015-09-09 04:00 | 165
2015-09-09 04:15 | 157
2015-09-09 04:30 | 166
2015-09-09 04:45 | 156
2015-09-09 05:00 | 169
2015-09-09 05:15 | 158
2015-09-09 05:30 | 163
2015-09-09 05:45 | 165
2015-09-09 06:00 | 160
2015-09-09 06:15 | 166
2015-09-09 06:30 | 156
2015-09-09 06:45 | 163
2015-09-09 07:00 | 155
2015-09-09 07:15 | 160
2015-09-09 07:30 | 152
2015-09-09 07:45 | 162
2015-09-09 08:00 | 162
2015-09-09 08:15 | 181
2015-09-09 08:30 | 181
2015-09-09 08:45 | 180
2015-09-09 09:00 | 181
2015-09-09 09:15 | 197
2015-09-09 09:30 | 184
2015-09-09 09:45 | 197
2015-09-09 10:00 | 210
2015-09-09 10:15 | 200
2015-09-09 10:30 | 216
2015-09-09 10:45 | 218
2015-09-09 11:00 | 218
2015-09-09 11:15 | 235
2015-09-09 11:30 | 239
2015-09-09 11:45 | 228
2015-09-09 12:00 | 247
2015-09-09 12:15 | 234
2015-09-09 12:30 | 253
2015-09-09 12:45 | 236
2015-09-09 13:00 | 252
2015-09-09 13:15 | 240
2015-09-09 13:30 | 248
2015-09-09 13:45 | 256
2015-09-09 14:00 | 258
2015-09-09 14:15 | 268
2015-09-09 14:30 | 263
2015-09-09 14:45 | 273
2015-09-09 15:00 | 267
2015-09-09 15:15 | 270
2015-09-09 15:30 | 273
2015-09-09 15:45 | 264
2015-09-09 16:00 | 270
2015-09-09 16:15 | 260
2015-09-09 16:30 | 274
2015-09-09 16:45 | 246
2015-09-09 17:00 | 270
2015-09-09 17:15 | 255
2015-09-09 17:30 | 258
2015-09-09 17:45 | 244
2015-09-09 18:00 | 248
2015-09-09 18:15 | 245
2015-09-09 18:30 | 239
2015-09-09 18:45 | 245
2015-09-09 19:00 | 235
2015-09-09 19:15 | 228
2015-09-09 19:30 | 233
2015-09-09 19:45 | 225
2015-09-09 20:00 | 224
2015-09-09 20:15 | 216
2015-09-09 20:30 | 208
2015-09-09 20:45 | 213
2015-09-09 21:00 | 203
2015-09-09 21:15 | 192
2015-09-09 21:30 | 206
2015-09-09 21:45 | 191
2015-09-09 22:00 | 202
2015-09-09 22:15 | 194
2015-09-09 22:30 | 184
2015-09-09 22:45 | 197
2015-09-09 23:00 | 192
2015-09-09 23:15 | 190
2015-09-09 23:30 | 191
2015-09-09 23:45 | 184
2015-09-10 | 179
2015-09-10 00:15 | 190
2015-09-10 00:30 | 175
2015-09-10 00:45 | 185
2015-09-10 01:00 | 176
2015-09-10 01:15 | 170
2015-09-10 01:30 | 175
2015-09-10 01:45 | 163
2015-09-10 02:00 | 171
2015-09-10 02:15 | 168
2015-09-10 02:30 | 162
2015-09-10 02:45 | 176
2015-09-10 03:00 | 164
2015-09-10 03:15 | 178
2015-09-10 03:30 | 163
2015-09-10 03:45 | 174
2015-09-10 04:00 | 162
2015-09-10 04:15 | 175
2015-09-10 04:30 | 170
2015-09-10 04:45 | 168
2015-09-10 05:00 | 168
2015-09-10 05:15 | 158
2015-09-10 05:30 | 168
2015-09-10 05:45 | 158
2015-09-10 06:00 | 171
2015-09-10 06:15 | 162
2015-09-10 06:30 | 170
2015-09-10 06:45 | 155
2015-09-10 07:00 | 169
2015-09-10 07:15 | 161
2015-09-10 07:30 | 167
2015-09-10 07:45 | 173
2015-09-10 08:00 | 177
2015-09-10 08:15 | 175
2015-09-10 08:30 | 180
2015-09-10 08:45 | 184
2015-09-10 09:00 | 199
2015-09-10 09:15 | 198
2015-09-10 09:30 | 194
2015-09-10 09:45 | 214
2015-09-10 10:00 | 210
2015-09-10 10:15 | 212
2015-09-10 10:30 | 230
2015-09-10 10:45 | 212
2015-09-10 11:00 | 235
2015-09-10 11:15 | 238
2015-09-10 11:30 | 256
2015-09-10 11:45 | 247
2015-09-10 12:00 | 236
2015-09-10 12:15 | 255
2015-09-10 12:30 | 250
2015-09-10 12:45 | 279
2015-09-10 13:00 | 261
2015-09-10 13:15 | 270
2015-09-10 13:30 | 257
2015-09-10 13:45 | 277
2015-09-10 14:00 | 276
2015-09-10 14:15 | 273
2015-09-10 14:30 | 269
2015-09-10 14:45 | 274
2015-09-10 15:00 | 276
2015-09-10 15:15 | 288
2015-09-10 15:30 | 275
2015-09-10 15:45 | 267
2015-09-10 16:00 | 246
2015-09-10 16:15 | 272
2015-09-10 16:30 | 274
2015-09-10 16:45 | 258
2015-09-10 17:00 | 253
2015-09-10 17:15 | 250
2015-09-10 17:30 | 248
2015-09-10 17:45 | 253
2015-09-10 18:00 | 252
2015-09-10 18:15 | 241
2015-09-10 18:30 | 246
2015-09-10 18:45 | 238
2015-09-10 19:00 | 248
2015-09-10 19:15 | 228
2015-09-10 19:30 | 224
2015-09-10 19:45 | 214
2015-09-10 20:00 | 220
2015-09-10 20:15 | 214
2015-09-10 20:30 | 214
2015-09-10 20:45 | 205
2015-09-10 21:00 | 203
2015-09-10 21:15 | 207
2015-09-10 21:30 | 202
2015-09-10 21:45 | 193
2015-09-10 22:00 | 202
2015-09-10 22:15 | 202
2015-09-10 22:30 | 195
2015-09-10 22:45 | 198
2015-09-10 23:00 | 184
2015-09-10 23:15 | 184
2015-09-10 23:30 | 185
2015-09-10 23:45 | 186
2015-09-11 | 184
2015-09-11 00:15 | 176
2015-09-11 00:30 | 174
2015-09-11 00:45 | 182
2015-09-11 01:00 | 176
2015-09-11 01:15 | 172
2015-09-11 01:30 | 170
2015-09-11 01:45 | 170
2015-09-11 02:00 | 183
2015-09-11 02:15 | 168
2015-09-11 02:30 | 169
2015-09-11 02:45 | 171
2015-09-11 03:00 | 169
2015-09-11 03:15 | 167
2015-09-11 03:30 | 179
2015-09-11 03:45 | 171
2015-09-11 04:00 | 158
2015-09-11 04:15 | 174
2015-09-11 04:30 | 166
2015-09-11 04:45 | 160
2015-09-11 05:00 | 181
2015-09-11 05:15 | 158
2015-09-11 05:30 | 170
2015-09-11 05:45 | 164
2015-09-11 06:00 | 167
2015-09-11 06:15 | 175
2015-09-11 06:30 | 166
2015-09-11 06:45 | 172
2015-09-11 07:00 | 173
2015-09-11 07:15 | 185
2015-09-11 07:30 | 181
2015-09-11 07:45 | 182
2015-09-11 08:00 | 192
2015-09-11 08:15 | 189
2015-09-11 08:30 | 197
2015-09-11 08:45 | 196
2015-09-11 09:00 | 191
2015-09-11 09:15 | 196
2015-09-11 09:30 | 217
2015-09-11 09:45 | 224
2015-09-11 10:00 | 225
2015-09-11 10:15 | 228
2015-09-11 10:30 | 241
2015-09-11 10:45 | 257
2015-09-11 11:00 | 245
2015-09-11 11:15 | 254
2015-09-11 11:30 | 254
2015-09-11 11:45 | 261
2015-09-11 12:00 | 262
2015-09-11 12:15 | 255
2015-09-11 12:30 | 262
2015-09-11 12:45 | 248
2015-09-11 13:00 | 275
2015-09-11 13:15 | 256
2015-09-11 13:30 | 263
2015-09-11 13:45 | 263
2015-09-11 14:00 | 265
2015-09-11 14:15 | 271
2015-09-11 14:30 | 276
2015-09-11 14:45 | 278
2015-09-11 15:00 | 263
2015-09-11 15:15 | 275
2015-09-11 15:30 | 273
2015-09-11 15:45 | 270
2015-09-11 16:00 | 278
2015-09-11 16:15 | 264
2015-09-11 16:30 | 261
2015-09-11 16:45 | 255
2015-09-11 17:00 | 266
2015-09-11 17:15 | 269
2015-09-11 17:30 | 262
2015-09-11 17:45 | 263
2015-09-11 18:00 | 261
2015-09-11 18:15 | 267
2015-09-11 18:30 | 249
2015-09-11 18:45 | 250
2015-09-11 19:00 | 242
2015-09-11 19:15 | 259
2015-09-11 19:30 | 226
2015-09-11 19:45 | 233
2015-09-11 20:00 | 228
2015-09-11 20:15 | 219
2015-09-11 20:30 | 226
2015-09-11 20:45 | 219
2015-09-11 21:00 | 211
2015-09-11 21:15 | 202
2015-09-11 21:30 | 205
2015-09-11 21:45 | 192
2015-09-11 22:00 | 187
2015-09-11 22:15 | 188
2015-09-11 22:30 | 191
2015-09-11 22:45 | 197
2015-09-11 23:00 | 188
2015-09-11 23:15 | 188
2015-09-11 23:30 | 197
2015-09-11 23:45 | 203
2015-09-12 | 185
2015-09-12 00:15 | 183
2015-09-12 00:30 | 183
2015-09-12 00:45 | 189
2015-09-12 01:00 | 186
2015-09-12 01:15 | 178
2015-09-12 01:30 | 180
2015-09-12 01:45 | 189
2015-09-12 02:00 | 178
2015-09-12 02:15 | 175
2015-09-12 02:30 | 171
2015-09-12 02:45 | 175
2015-09-12 03:00 | 191
2015-09-12 03:15 | 168
2015-09-12 03:30 | 168
2015-09-12 03:45 | 169
2015-09-12 04:00 | 186
2015-09-12 04:15 | 172
2015-09-12 04:30 | 165
2015-09-12 04:45 | 172
2015-09-12 05:00 | 169
2015-09-12 05:15 | 184
2015-09-12 05:30 | 165
2015-09-12 05:45 | 169
2015-09-12 06:00 | 168
2015-09-12 06:15 | 188
2015-09-12 06:30 | 175
2015-09-12 06:45 | 171
2015-09-12 07:00 | 177
2015-09-12 07:15 | 171
2015-09-12 07:30 | 185
2015-09-12 07:45 | 169
2015-09-12 08:00 | 168
2015-09-12 08:15 | 165
2015-09-12 08:30 | 186
2015-09-12 08:45 | 177
2015-09-12 09:00 | 169
2015-09-12 09:15 | 175
2015-09-12 09:30 | 174
2015-09-12 09:45 | 191
2015-09-12 10:00 | 182
2015-09-12 10:15 | 174
2015-09-12 10:30 | 175
2015-09-12 10:45 | 181
2015-09-12 11:00 | 196
2015-09-12 11:15 | 176
2015-09-12 11:30 | 178
2015-09-12 11:45 | 181
2015-09-12 12:00 | 176
2015-09-12 12:15 | 192
2015-09-12 12:30 | 186
2015-09-12 12:45 | 183
2015-09-12 13:00 | 181
2015-09-12 13:15 | 189
2015-09-12 13:30 | 197
2015-09-12 13:45 | 175
2015-09-12 14:00 | 174
2015-09-12 14:15 | 185
2015-09-12 14:30 | 197
2015-09-12 14:45 | 187
2015-09-12 15:00 | 182
2015-09-12 15:15 | 190
2015-09-12 15:30 | 189
2015-09-12 15:45 | 193
2015-09-12 16:00 | 199
2015-09-12 16:15 | 184
2015-09-12 16:30 | 186
2015-09-12 16:45 | 196
2015-09-12 17:00 | 200
2015-09-12 17:15 | 180
2015-09-12 17:30 | 187
2015-09-12 17:45 | 180
2015-09-12 18:00 | 199
2015-09-12 18:15 | 200
2015-09-12 18:30 | 185
2015-09-12 18:45 | 185
2015-09-12 19:00 | 179
2015-09-12 19:15 | 192
2015-09-12 19:30 | 195
2015-09-12 19:45 | 177
2015-09-12 20:00 | 176
2015-09-12 20:15 | 195
2015-09-12 20:30 | 181
2015-09-12 20:45 | 177
2015-09-12 21:00 | 179
2015-09-12 21:15 | 191
2015-09-12 21:30 | 171
2015-09-12 21:45 | 173
2015-09-12 22:00 | 174
2015-09-12 22:15 | 183
2015-09-12 22:30 | 172
2015-09-12 22:45 | 176
2015-09-12 23:00 | 171
2015-09-12 23:15 | 182
2015-09-12 23:30 | 174
2015-09-12 23:45 | 173
2015-09-13 | 171
2015-09-13 00:15 | 176
2015-09-13 00:30 | 188
2015-09-13 00:45 | 175
2015-09-13 01:00 | 172
2015-09-13 01:15 | 165
2015-09-13 01:30 | 172
2015-09-13 01:45 | 183
2015-09-13 02:00 | 169
2015-09-13 02:15 | 169
2015-09-13 02:30 | 168
2015-09-13 02:45 | 174
2015-09-13 03:00 | 183
2015-09-13 03:15 | 173
2015-09-13 03:30 | 169
2015-09-13 03:45 | 165
2015-09-13 04:00 | 167
2015-09-13 04:15 | 185
2015-09-13 04:30 | 168
2015-09-13 04:45 | 168
2015-09-13 05:00 | 177
2015-09-13 05:15 | 175
2015-09-13 05:30 | 163
2015-09-13 05:45 | 169
2015-09-13 06:00 | 161
2015-09-13 06:15 | 171
2015-09-13 06:30 | 184
2015-09-13 06:45 | 174
2015-09-13 07:00 | 172
2015-09-13 07:15 | 179
2015-09-13 07:30 | 189
2015-09-13 07:45 | 183
2015-09-13 08:00 | 183
2015-09-13 08:15 | 176
2015-09-13 08:30 | 175
2015-09-13 08:45 | 175
2015-09-13 09:00 | 195
2015-09-13 09:15 | 184
2015-09-13 09:30 | 178
2015-09-13 09:45 | 180
2015-09-13 10:00 | 183
2015-09-13 10:15 | 175
2015-09-13 10:30 | 170
2015-09-13 10:45 | 181
2015-09-13 11:00 | 184
2015-09-13 11:15 | 179
2015-09-13 11:30 | 172
2015-09-13 11:45 | 169
2015-09-13 12:00 | 184
2015-09-13 12:15 | 181
2015-09-13 12:30 | 171
2015-09-13 12:45 | 183
2015-09-13 13:00 | 187
2015-09-13 13:15 | 189
2015-09-13 13:30 | 179
2015-09-13 13:45 | 187
2015-09-13 14:00 | 188
2015-09-13 14:15 | 199
2015-09-13 14:30 | 191
2015-09-13 14:45 | 191
2015-09-13 15:00 | 191
2015-09-13 15:15 | 194
2015-09-13 15:30 | 221
2015-09-13 15:45 | 203
2015-09-13 16:00 | 201
2015-09-13 16:15 | 205
2015-09-13 16:30 | 203
2015-09-13 16:45 | 219
2015-09-13 17:00 | 203
2015-09-13 17:15 | 209
2015-09-13 17:30 | 196
2015-09-13 17:45 | 195
2015-09-13 18:00 | 203
2015-09-13 18:15 | 205
2015-09-13 18:30 | 184
2015-09-13 18:45 | 191
2015-09-13 19:00 | 182
2015-09-13 19:15 | 191
2015-09-13 19:30 | 200
2015-09-13 19:45 | 187
2015-09-13 20:00 | 187
2015-09-13 20:15 | 194
2015-09-13 20:30 | 180
2015-09-13 20:45 | 181
2015-09-13 21:00 | 189
2015-09-13 21:15 | 186
2015-09-13 21:30 | 168
2015-09-13 21:45 | 168
2015-09-13 22:00 | 168
2015-09-13 22:15 | 176
2015-09-13 22:30 | 168
2015-09-13 22:45 | 181
2015-09-13 23:00 | 177
2015-09-13 23:15 | 163
2015-09-13 23:30 | 173
2015-09-13 23:45 | 169
2015-09-14 | 185
2015-09-14 00:15 | 165
2015-09-14 00:30 | 163
2015-09-14 00:45 | 166
2015-09-14 01:00 | 174
2015-09-14 01:15 | 173
2015-09-14 01:30 | 163
2015-09-14 01:45 | 166
2015-09-14 02:00 | 161
2015-09-14 02:15 | 170
2015-09-14 02:30 | 176
2015-09-14 02:45 | 168
2015-09-14 03:00 | 158
2015-09-14 03:15 | 170
2015-09-14 03:30 | 176
2015-09-14 03:45 | 156
2015-09-14 04:00 | 156
2015-09-14 04:15 | 159
2015-09-14 04:30 | 163
2015-09-14 04:45 | 164
2015-09-14 05:00 | 160
2015-09-14 05:15 | 155
2015-09-14 05:30 | 157
2015-09-14 05:45 | 161
2015-09-14 06:00 | 172
2015-09-14 06:15 | 161
2015-09-14 06:30 | 159
2015-09-14 06:45 | 163
2015-09-14 07:00 | 171
2015-09-14 07:15 | 157
2015-09-14 07:30 | 152
2015-09-14 07:45 | 160
2015-09-14 08:00 | 186
2015-09-14 08:15 | 177
2015-09-14 08:30 | 175
2015-09-14 08:45 | 181
2015-09-14 09:00 | 177
2015-09-14 09:15 | 201
2015-09-14 09:30 | 202
2015-09-14 09:45 | 190
2015-09-14 10:00 | 188
2015-09-14 10:15 | 203
2015-09-14 10:30 | 201
2015-09-14 10:45 | 193
2015-09-14 11:00 | 196
2015-09-14 11:15 | 202
2015-09-14 11:30 | 216
2015-09-14 11:45 | 197
2015-09-14 12:00 | 200
2015-09-14 12:15 | 199
2015-09-14 12:30 | 208
2015-09-14 12:45 | 207
2015-09-14 13:00 | 202
2015-09-14 13:15 | 190
2015-09-14 13:30 | 202
2015-09-14 13:45 | 208
2015-09-14 14:00 | 192
2015-09-14 14:15 | 192
2015-09-14 14:30 | 199
2015-09-14 14:45 | 223
2015-09-14 15:00 | 194
2015-09-14 15:15 | 204
2015-09-14 15:30 | 206
2015-09-14 15:45 | 209
2015-09-14 16:00 | 197
2015-09-14 16:15 | 195
2015-09-14 16:30 | 199
2015-09-14 16:45 | 188
2015-09-14 17:00 | 211
2015-09-14 17:15 | 211
2015-09-14 17:30 | 199
2015-09-14 17:45 | 201
2015-09-14 18:00 | 192
2015-09-14 18:15 | 207
2015-09-14 18:30 | 204
2015-09-14 18:45 | 198
2015-09-14 19:00 | 201
2015-09-14 19:15 | 194
2015-09-14 19:30 | 199
2015-09-14 19:45 | 204
2015-09-14 20:00 | 191
2015-09-14 20:15 | 194
2015-09-14 20:30 | 188
2015-09-14 20:45 | 194
2015-09-14 21:00 | 203
2015-09-14 21:15 | 184
2015-09-14 21:30 | 184
2015-09-14 21:45 | 192
2015-09-14 22:00 | 186
2015-09-14 22:15 | 190
2015-09-14 22:30 | 186
2015-09-14 22:45 | 201
2015-09-14 23:00 | 184
2015-09-14 23:15 | 184
2015-09-14 23:30 | 171
2015-09-14 23:45 | 182
2015-09-15 | 175
2015-09-15 00:15 | 164
2015-09-15 00:30 | 164
2015-09-15 00:45 | 177
2015-09-15 01:00 | 170
2015-09-15 01:15 | 159
2015-09-15 01:30 | 166
2015-09-15 01:45 | 167
2015-09-15 02:00 | 171
2015-09-15 02:15 | 165
2015-09-15 02:30 | 161
2015-09-15 02:45 | 153
2015-09-15 03:00 | 165
2015-09-15 03:15 | 172
2015-09-15 03:30 | 152
2015-09-15 03:45 | 160
2015-09-15 04:00 | 154
2015-09-15 04:15 | 165
2015-09-15 04:30 | 166
2015-09-15 04:45 | 156
2015-09-15 05:00 | 154
2015-09-15 05:15 | 157
2015-09-15 05:30 | 160
2015-09-15 05:45 | 157
2015-09-15 06:00 | 151
2015-09-15 06:15 | 151
2015-09-15 06:30 | 156
2015-09-15 06:45 | 164
2015-09-15 07:00 | 145
2015-09-15 07:15 | 149
2015-09-15 07:30 | 140
2015-09-15 07:45 | 160
2015-09-15 08:00 | 166
2015-09-15 08:15 | 158
2015-09-15 08:30 | 158
2015-09-15 08:45 | 160
2015-09-15 09:00 | 189
2015-09-15 09:15 | 178
2015-09-15 09:30 | 180
2015-09-15 09:45 | 180
2015-09-15 10:00 | 189
2015-09-15 10:15 | 203
2015-09-15 10:30 | 189
2015-09-15 10:45 | 194
2015-09-15 11:00 | 194
2015-09-15 11:15 | 196
2015-09-15 11:30 | 204
2015-09-15 11:45 | 193
2015-09-15 12:00 | 184
2015-09-15 12:15 | 186
2015-09-15 12:30 | 208
2015-09-15 12:45 | 194
2015-09-15 13:00 | 191
2015-09-15 13:15 | 202
2015-09-15 13:30 | 187
2015-09-15 13:45 | 210
2015-09-15 14:00 | 201
2015-09-15 14:15 | 207
2015-09-15 14:30 | 194
2015-09-15 14:45 | 215
2015-09-15 15:00 | 210
2015-09-15 15:15 | 197
2015-09-15 15:30 | 210
2015-09-15 15:45 | 198
2015-09-15 16:00 | 212
2015-09-15 16:15 | 208
2015-09-15 16:30 | 196
2015-09-15 16:45 | 198
2015-09-15 17:00 | 221
2015-09-15 17:15 | 195
2015-09-15 17:30 | 203
2015-09-15 17:45 | 195
2015-09-15 18:00 | 186
2015-09-15 18:15 | 205
2015-09-15 18:30 | 191
2015-09-15 18:45 | 187
2015-09-15 19:00 | 178
2015-09-15 19:15 | 183
2015-09-15 19:30 | 178
2015-09-15 19:45 | 189
2015-09-15 20:00 | 189
2015-09-15 20:15 | 174
2015-09-15 20:30 | 181
2015-09-15 20:45 | 171
2015-09-15 21:00 | 180
2015-09-15 21:15 | 165
2015-09-15 21:30 | 178
2015-09-15 21:45 | 166
2015-09-15 22:00 | 164
2015-09-15 22:15 | 165
2015-09-15 22:30 | 161
2015-09-15 22:45 | 163
2015-09-15 23:00 | 160
2015-09-15 23:15 | 161
2015-09-15 23:30 | 150
2015-09-15 23:45 | 150
2015-09-16 | 141
2015-09-16 00:15 | 142
2015-09-16 00:30 | 136
2015-09-16 00:45 | 137
2015-09-16 01:00 | 139
2015-09-16 01:15 | 139
2015-09-16 01:30 | 142
2015-09-16 01:45 | 138
2015-09-16 02:00 | 137
2015-09-16 02:15 | 143
2015-09-16 02:30 | 142
2015-09-16 02:45 | 145
2015-09-16 03:00 | 147
2015-09-16 03:15 | 137
2015-09-16 03:30 | 133
2015-09-16 03:45 | 130
2015-09-16 04:00 | 131
2015-09-16 04:15 | 125
2015-09-16 04:30 | 129
2015-09-16 04:45 | 130
2015-09-16 05:00 | 130
2015-09-16 05:15 | 124
2015-09-16 05:30 | 124
2015-09-16 05:45 | 127
2015-09-16 06:00 | 128
2015-09-16 06:15 | 126
2015-09-16 06:30 | 127
2015-09-16 06:45 | 127
2015-09-16 07:00 | 139
2015-09-16 07:15 | 126
2015-09-16 07:30 | 127
2015-09-16 07:45 | 137
2015-09-16 08:00 | 144
2015-09-16 08:15 | 153
2015-09-16 08:30 | 151
2015-09-16 08:45 | 173
2015-09-16 09:00 | 164
2015-09-16 09:15 | 170
2015-09-16 09:30 | 170
2015-09-16 09:45 | 177
2015-09-16 10:00 | 169
2015-09-16 10:15 | 196
2015-09-16 10:30 | 175
2015-09-16 10:45 | 184
2015-09-16 11:00 | 184
2015-09-16 11:15 | 186
2015-09-16 11:30 | 191
2015-09-16 11:45 | 185
2015-09-16 12:00 | 181
2015-09-16 12:15 | 189
2015-09-16 12:30 | 194
2015-09-16 12:45 | 182
2015-09-16 13:00 | 188
2015-09-16 13:15 | 172
2015-09-16 13:30 | 182
2015-09-16 13:45 | 182
2015-09-16 14:00 | 185
2015-09-16 14:15 | 190
2015-09-16 14:30 | 191
2015-09-16 14:45 | 183
2015-09-16 15:00 | 185
2015-09-16 15:15 | 202
2015-09-16 15:30 | 194
2015-09-16 15:45 | 196
2015-09-16 16:00 | 192
2015-09-16 16:15 | 206
2015-09-16 16:30 | 201
2015-09-16 16:45 | 190
2015-09-16 17:00 | 197
2015-09-16 17:15 | 180
2015-09-16 17:30 | 188
2015-09-16 17:45 | 205
2015-09-16 18:00 | 179
2015-09-16 18:15 | 193
2015-09-16 18:30 | 187
2015-09-16 18:45 | 181
2015-09-16 19:00 | 195
2015-09-16 19:15 | 179
2015-09-16 19:30 | 180
2015-09-16 19:45 | 176
2015-09-16 20:00 | 184
2015-09-16 20:15 | 192
2015-09-16 20:30 | 177
2015-09-16 20:45 | 173
2015-09-16 21:00 | 184
2015-09-16 21:15 | 180
2015-09-16 21:30 | 175
2015-09-16 21:45 | 175
2015-09-16 22:00 | 168
2015-09-16 22:15 | 176
2015-09-16 22:30 | 179
2015-09-16 22:45 | 178
2015-09-16 23:00 | 167
2015-09-16 23:15 | 167
2015-09-16 23:30 | 158
2015-09-16 23:45 | 172
2015-09-17 | 160
2015-09-17 00:15 | 154
2015-09-17 00:30 | 155
2015-09-17 00:45 | 160
2015-09-17 01:00 | 166
2015-09-17 01:15 | 154
2015-09-17 01:30 | 157
2015-09-17 01:45 | 153
2015-09-17 02:00 | 157
2015-09-17 02:15 | 169
2015-09-17 02:30 | 155
2015-09-17 02:45 | 152
2015-09-17 03:00 | 159
2015-09-17 03:15 | 161
2015-09-17 03:30 | 158
2015-09-17 03:45 | 150
2015-09-17 04:00 | 150
2015-09-17 04:15 | 146
2015-09-17 04:30 | 160
2015-09-17 04:45 | 157
2015-09-17 05:00 | 145
2015-09-17 05:15 | 148
2015-09-17 05:30 | 146
2015-09-17 05:45 | 159
2015-09-17 06:00 | 149
2015-09-17 06:15 | 147
2015-09-17 06:30 | 144
2015-09-17 06:45 | 150
2015-09-17 07:00 | 165
2015-09-17 07:15 | 151
2015-09-17 07:30 | 146
2015-09-17 07:45 | 145
2015-09-17 08:00 | 152
2015-09-17 08:15 | 187
2015-09-17 08:30 | 161
2015-09-17 08:45 | 167
2015-09-17 09:00 | 168
2015-09-17 09:15 | 174
2015-09-17 09:30 | 184
2015-09-17 09:45 | 173
2015-09-17 10:00 | 179
2015-09-17 10:15 | 181
2015-09-17 10:30 | 200
2015-09-17 10:45 | 194
2015-09-17 11:00 | 184
2015-09-17 11:15 | 183
2015-09-17 11:30 | 184
2015-09-17 11:45 | 203
2015-09-17 12:00 | 189
2015-09-17 12:15 | 181
2015-09-17 12:30 | 181
2015-09-17 12:45 | 183
2015-09-17 13:00 | 200
2015-09-17 13:15 | 188
2015-09-17 13:30 | 189
2015-09-17 13:45 | 183
2015-09-17 14:00 | 189
2015-09-17 14:15 | 203
2015-09-17 14:30 | 192
2015-09-17 14:45 | 194
2015-09-17 15:00 | 202
2015-09-17 15:15 | 214
2015-09-17 15:30 | 202
2015-09-17 15:45 | 207
2015-09-17 16:00 | 194
2015-09-17 16:15 | 205
2015-09-17 16:30 | 215
2015-09-17 16:45 | 189
2015-09-17 17:00 | 205
2015-09-17 17:15 | 199
2015-09-17 17:30 | 204
2015-09-17 17:45 | 212
2015-09-17 18:00 | 187
2015-09-17 18:15 | 196
2015-09-17 18:30 | 191
2015-09-17 18:45 | 203
2015-09-17 19:00 | 195
2015-09-17 19:15 | 182
2015-09-17 19:30 | 194
2015-09-17 19:45 | 200
2015-09-17 20:00 | 179
2015-09-17 20:15 | 182
2015-09-17 20:30 | 185
2015-09-17 20:45 | 180
2015-09-17 21:00 | 195
2015-09-17 21:15 | 179
2015-09-17 21:30 | 167
2015-09-17 21:45 | 171
2015-09-17 22:00 | 185
2015-09-17 22:15 | 176
2015-09-17 22:30 | 165
2015-09-17 22:45 | 166
2015-09-17 23:00 | 168
2015-09-17 23:15 | 175
2015-09-17 23:30 | 157
2015-09-17 23:45 | 154
2015-09-18 | 145
2015-09-18 00:15 | 149
2015-09-18 00:30 | 169
2015-09-18 00:45 | 148
2015-09-18 01:00 | 152
2015-09-18 01:15 | 154
2015-09-18 01:30 | 153
2015-09-18 01:45 | 164
2015-09-18 02:00 | 145
2015-09-18 02:15 | 145
2015-09-18 02:30 | 144
2015-09-18 02:45 | 145
2015-09-18 03:00 | 159
2015-09-18 03:15 | 141
2015-09-18 03:30 | 145
2015-09-18 03:45 | 140
2015-09-18 04:00 | 143
2015-09-18 04:15 | 158
2015-09-18 04:30 | 139
2015-09-18 04:45 | 144
2015-09-18 05:00 | 133
2015-09-18 05:15 | 144
2015-09-18 05:30 | 148
2015-09-18 05:45 | 143
2015-09-18 06:00 | 142
2015-09-18 06:15 | 149
2015-09-18 06:30 | 145
2015-09-18 06:45 | 170
2015-09-18 07:00 | 145
2015-09-18 07:15 | 152
2015-09-18 07:30 | 137
2015-09-18 07:45 | 148
2015-09-18 08:00 | 159
2015-09-18 08:15 | 174
2015-09-18 08:30 | 165
2015-09-18 08:45 | 172
2015-09-18 09:00 | 173
2015-09-18 09:15 | 185
2015-09-18 09:30 | 173
2015-09-18 09:45 | 176
2015-09-18 10:00 | 174
2015-09-18 10:15 | 175
2015-09-18 10:30 | 199
2015-09-18 10:45 | 185
2015-09-18 11:00 | 186
2015-09-18 11:15 | 190
2015-09-18 11:30 | 207
2015-09-18 11:45 | 201
2015-09-18 12:00 | 198
2015-09-18 12:15 | 201
2015-09-18 12:30 | 205
2015-09-18 12:45 | 214
2015-09-18 13:00 | 206
2015-09-18 13:15 | 201
2015-09-18 13:30 | 198
2015-09-18 13:45 | 201
2015-09-18 14:00 | 216
2015-09-18 14:15 | 208
2015-09-18 14:30 | 205
2015-09-18 14:45 | 212
2015-09-18 15:00 | 243
2015-09-18 15:15 | 223
2015-09-18 15:30 | 227
2015-09-18 15:45 | 218
2015-09-18 16:00 | 212
2015-09-18 16:15 | 231
2015-09-18 16:30 | 225
2015-09-18 16:45 | 215
2015-09-18 17:00 | 212
2015-09-18 17:15 | 209
2015-09-18 17:30 | 220
2015-09-18 17:45 | 224
2015-09-18 18:00 | 209
2015-09-18 18:15 | 204
2015-09-18 18:30 | 217
2015-09-18 18:45 | 215
2015-09-18 19:00 | 199
2015-09-18 19:15 | 196
2015-09-18 19:30 | 193
2015-09-18 19:45 | 208
2015-09-18 20:00 | 194
2015-09-18 20:15 | 188
2015-09-18 20:30 | 190
2015-09-18 20:45 | 190
2015-09-18 21:00 | 199
2015-09-18 21:15 | 185
2015-09-18 21:30 | 169
2015-09-18 21:45 | 163
2015-09-18 22:00 | 175
2015-09-18 22:15 | 180
2015-09-18 22:30 | 159
2015-09-18 22:45 | 162
2015-09-18 23:00 | 163
2015-09-18 23:15 | 170
2015-09-18 23:30 | 165
2015-09-18 23:45 | 158
2015-09-19 | 161
2015-09-19 00:15 | 155
2015-09-19 00:30 | 174
2015-09-19 00:45 | 155
2015-09-19 01:00 | 152
2015-09-19 01:15 | 146
2015-09-19 01:30 | 159
2015-09-19 01:45 | 154
2015-09-19 02:00 | 143
2015-09-19 02:15 | 146
2015-09-19 02:30 | 135
2015-09-19 02:45 | 153
2015-09-19 03:00 | 142
2015-09-19 03:15 | 139
2015-09-19 03:30 | 138
2015-09-19 03:45 | 131
2015-09-19 04:00 | 143
2015-09-19 04:15 | 136
2015-09-19 04:30 | 135
2015-09-19 04:45 | 128
2015-09-19 05:00 | 136
2015-09-19 05:15 | 135
2015-09-19 05:30 | 137
2015-09-19 05:45 | 142
2015-09-19 06:00 | 130
2015-09-19 06:15 | 128
2015-09-19 06:30 | 131
2015-09-19 06:45 | 139
2015-09-19 07:00 | 140
2015-09-19 07:15 | 137
2015-09-19 07:30 | 129
2015-09-19 07:45 | 132
2015-09-19 08:00 | 127
2015-09-19 08:15 | 136
2015-09-19 08:30 | 134
2015-09-19 08:45 | 154
2015-09-19 09:00 | 141
2015-09-19 09:15 | 148
2015-09-19 09:30 | 141
2015-09-19 09:45 | 151
2015-09-19 10:00 | 148
2015-09-19 10:15 | 146
2015-09-19 10:30 | 152
2015-09-19 10:45 | 158
2015-09-19 11:00 | 163
2015-09-19 11:15 | 157
2015-09-19 11:30 | 163
2015-09-19 11:45 | 152
2015-09-19 12:00 | 156
2015-09-19 12:15 | 176
2015-09-19 12:30 | 167
2015-09-19 12:45 | 172
2015-09-19 13:00 | 168
2015-09-19 13:15 | 170
2015-09-19 13:30 | 174
2015-09-19 13:45 | 182
2015-09-19 14:00 | 173
2015-09-19 14:15 | 174
2015-09-19 14:30 | 184
2015-09-19 14:45 | 182
2015-09-19 15:00 | 190
2015-09-19 15:15 | 197
2015-09-19 15:30 | 190
2015-09-19 15:45 | 193
2015-09-19 16:00 | 190
2015-09-19 16:15 | 225
2015-09-19 16:30 | 186
2015-09-19 16:45 | 201
2015-09-19 17:00 | 201
2015-09-19 17:15 | 201
2015-09-19 17:30 | 204
2015-09-19 17:45 | 203
2015-09-19 18:00 | 190
2015-09-19 18:15 | 197
2015-09-19 18:30 | 204
2015-09-19 18:45 | 190
2015-09-19 19:00 | 194
2015-09-19 19:15 | 168
2015-09-19 19:30 | 176
2015-09-19 19:45 | 191
2015-09-19 20:00 | 163
2015-09-19 20:15 | 175
2015-09-19 20:30 | 163
2015-09-19 20:45 | 163
2015-09-19 21:00 | 175
2015-09-19 21:15 | 160
2015-09-19 21:30 | 158
2015-09-19 21:45 | 158
2015-09-19 22:00 | 155
2015-09-19 22:15 | 171
2015-09-19 22:30 | 152
2015-09-19 22:45 | 160
2015-09-19 23:00 | 152
2015-09-19 23:15 | 150
2015-09-19 23:30 | 154
2015-09-19 23:45 | 156
2015-09-20 | 147
2015-09-20 00:15 | 155
2015-09-20 00:30 | 154
2015-09-20 00:45 | 149
2015-09-20 01:00 | 159
2015-09-20 01:15 | 154
2015-09-20 01:30 | 153
2015-09-20 01:45 | 142
2015-09-20 02:00 | 150
2015-09-20 02:15 | 141
2015-09-20 02:30 | 155
2015-09-20 02:45 | 139
2015-09-20 03:00 | 150
2015-09-20 03:15 | 137
2015-09-20 03:30 | 147
2015-09-20 03:45 | 140
2015-09-20 04:00 | 144
2015-09-20 04:15 | 143
2015-09-20 04:30 | 145
2015-09-20 04:45 | 140
2015-09-20 05:00 | 135
2015-09-20 05:15 | 146
2015-09-20 05:30 | 136
2015-09-20 05:45 | 148
2015-09-20 06:00 | 130
2015-09-20 06:15 | 152
2015-09-20 06:30 | 139
2015-09-20 06:45 | 144
2015-09-20 07:00 | 143
2015-09-20 07:15 | 138
2015-09-20 07:30 | 145
2015-09-20 07:45 | 139
2015-09-20 08:00 | 146
2015-09-20 08:15 | 138
2015-09-20 08:30 | 142
2015-09-20 08:45 | 146
2015-09-20 09:00 | 147
2015-09-20 09:15 | 151
2015-09-20 09:30 | 153
2015-09-20 09:45 | 149
2015-09-20 10:00 | 161
2015-09-20 10:15 | 153
2015-09-20 10:30 | 155
2015-09-20 10:45 | 166
2015-09-20 11:00 | 158
2015-09-20 11:15 | 168
2015-09-20 11:30 | 169
2015-09-20 11:45 | 169
2015-09-20 12:00 | 179
2015-09-20 12:15 | 170
2015-09-20 12:30 | 185
2015-09-20 12:45 | 193
2015-09-20 13:00 | 181
2015-09-20 13:15 | 209
2015-09-20 13:30 | 193
2015-09-20 13:45 | 205
2015-09-20 14:00 | 192
2015-09-20 14:15 | 205
2015-09-20 14:30 | 205
2015-09-20 14:45 | 210
2015-09-20 15:00 | 219
2015-09-20 15:15 | 214
2015-09-20 15:30 | 222
2015-09-20 15:45 | 212
2015-09-20 16:00 | 231
2015-09-20 16:15 | 216
2015-09-20 16:30 | 224
2015-09-20 16:45 | 216
2015-09-20 17:00 | 213
2015-09-20 17:15 | 227
2015-09-20 17:30 | 209
2015-09-20 17:45 | 221
2015-09-20 18:00 | 212
2015-09-20 18:15 | 214
2015-09-20 18:30 | 206
2015-09-20 18:45 | 217
2015-09-20 19:00 | 199
2015-09-20 19:15 | 194
2015-09-20 19:30 | 191
2015-09-20 19:45 | 183
2015-09-20 20:00 | 192
2015-09-20 20:15 | 181
2015-09-20 20:30 | 172
2015-09-20 20:45 | 182
2015-09-20 21:00 | 179
2015-09-20 21:15 | 166
2015-09-20 21:30 | 171
2015-09-20 21:45 | 175
2015-09-20 22:00 | 164
2015-09-20 22:15 | 165
2015-09-20 22:30 | 171
2015-09-20 22:45 | 159
2015-09-20 23:00 | 170
2015-09-20 23:15 | 166
2015-09-20 23:30 | 152
2015-09-20 23:45 | 166
2015-09-21 | 161
2015-09-21 00:15 | 157
2015-09-21 00:30 | 163
2015-09-21 00:45 | 156
2015-09-21 01:00 | 159
2015-09-21 01:15 | 153
2015-09-21 01:30 | 157
2015-09-21 01:45 | 160
2015-09-21 02:00 | 153
2015-09-21 02:15 | 161
2015-09-21 02:30 | 150
2015-09-21 02:45 | 159
2015-09-21 03:00 | 155
2015-09-21 03:15 | 150
2015-09-21 03:30 | 158
2015-09-21 03:45 | 150
2015-09-21 04:00 | 154
2015-09-21 04:15 | 155
2015-09-21 04:30 | 147
2015-09-21 04:45 | 158
2015-09-21 05:00 | 146
2015-09-21 05:15 | 151
2015-09-21 05:30 | 157
2015-09-21 05:45 | 143
2015-09-21 06:00 | 154
2015-09-21 06:15 | 155
2015-09-21 06:30 | 143
2015-09-21 06:45 | 155
2015-09-21 07:00 | 152
2015-09-21 07:15 | 149
2015-09-21 07:30 | 150
2015-09-21 07:45 | 143
2015-09-21 08:00 | 164
2015-09-21 08:15 | 167
2015-09-21 08:30 | 168
2015-09-21 08:45 | 180
2015-09-21 09:00 | 163
2015-09-21 09:15 | 187
2015-09-21 09:30 | 185
2015-09-21 09:45 | 196
2015-09-21 10:00 | 202
2015-09-21 10:15 | 193
2015-09-21 10:30 | 205
2015-09-21 10:45 | 206
2015-09-21 11:00 | 206
2015-09-21 11:15 | 227
2015-09-21 11:30 | 208
2015-09-21 11:45 | 225
2015-09-21 12:00 | 217
2015-09-21 12:15 | 227
2015-09-21 12:30 | 230
2015-09-21 12:45 | 245
2015-09-21 13:00 | 233
2015-09-21 13:15 | 244
2015-09-21 13:30 | 246
2015-09-21 13:45 | 253
2015-09-21 14:00 | 258
2015-09-21 14:15 | 254
2015-09-21 14:30 | 257
2015-09-21 14:45 | 260
2015-09-21 15:00 | 258
2015-09-21 15:15 | 274
2015-09-21 15:30 | 260
2015-09-21 15:45 | 268
2015-09-21 16:00 | 263
2015-09-21 16:15 | 263
2015-09-21 16:30 | 264
2015-09-21 16:45 | 267
2015-09-21 17:00 | 256
2015-09-21 17:15 | 250
2015-09-21 17:30 | 258
2015-09-21 17:45 | 248
2015-09-21 18:00 | 242
2015-09-21 18:15 | 244
2015-09-21 18:30 | 237
2015-09-21 18:45 | 237
2015-09-21 19:00 | 232
2015-09-21 19:15 | 222
2015-09-21 19:30 | 213
2015-09-21 19:45 | 214
2015-09-21 20:00 | 223
2015-09-21 20:15 | 207
2015-09-21 20:30 | 199
2015-09-21 20:45 | 200
2015-09-21 21:00 | 193
2015-09-21 21:15 | 200
2015-09-21 21:30 | 188
2015-09-21 21:45 | 185
2015-09-21 22:00 | 183
2015-09-21 22:15 | 185
2015-09-21 22:30 | 204
2015-09-21 22:45 | 188
2015-09-21 23:00 | 192
2015-09-21 23:15 | 186
2015-09-21 23:30 | 189
2015-09-21 23:45 | 201
2015-09-22 | 183
2015-09-22 00:15 | 185
2015-09-22 00:30 | 181
2015-09-22 00:45 | 180
2015-09-22 01:00 | 191
2015-09-22 01:15 | 175
2015-09-22 01:30 | 171
2015-09-22 01:45 | 175
2015-09-22 02:00 | 187
2015-09-22 02:15 | 175
2015-09-22 02:30 | 173
2015-09-22 02:45 | 167
2015-09-22 03:00 | 169
2015-09-22 03:15 | 182
2015-09-22 03:30 | 165
2015-09-22 03:45 | 165
2015-09-22 04:00 | 156
2015-09-22 04:15 | 170
2015-09-22 04:30 | 162
2015-09-22 04:45 | 158
2015-09-22 05:00 | 153
2015-09-22 05:15 | 162
2015-09-22 05:30 | 173
2015-09-22 05:45 | 157
2015-09-22 06:00 | 158
2015-09-22 06:15 | 157
2015-09-22 06:30 | 159
2015-09-22 06:45 | 174
2015-09-22 07:00 | 156
2015-09-22 07:15 | 157
2015-09-22 07:30 | 153
2015-09-22 07:45 | 167
2015-09-22 08:00 | 173
2015-09-22 08:15 | 163
2015-09-22 08:30 | 169
2015-09-22 08:45 | 171
2015-09-22 09:00 | 192
2015-09-22 09:15 | 181
2015-09-22 09:30 | 184
2015-09-22 09:45 | 179
2015-09-22 10:00 | 176
2015-09-22 10:15 | 198
2015-09-22 10:30 | 193
2015-09-22 10:45 | 182
2015-09-22 11:00 | 191
2015-09-22 11:15 | 191
2015-09-22 11:30 | 215
2015-09-22 11:45 | 207
2015-09-22 12:00 | 206
2015-09-22 12:15 | 206
2015-09-22 12:30 | 205
2015-09-22 12:45 | 225
2015-09-22 13:00 | 217
2015-09-22 13:15 | 215
2015-09-22 13:30 | 212
2015-09-22 13:45 | 226
2015-09-22 14:00 | 226
2015-09-22 14:15 | 213
2015-09-22 14:30 | 228
2015-09-22 14:45 | 224
2015-09-22 15:00 | 230
2015-09-22 15:15 | 203
2015-09-22 15:30 | 218
2015-09-22 15:45 | 215
2015-09-22 16:00 | 226
2015-09-22 16:15 | 218
2015-09-22 16:30 | 209
2015-09-22 16:45 | 207
2015-09-22 17:00 | 213
2015-09-22 17:15 | 221
2015-09-22 17:30 | 206
2015-09-22 17:45 | 207
2015-09-22 18:00 | 199
2015-09-22 18:15 | 204
2015-09-22 18:30 | 208
2015-09-22 18:45 | 197
2015-09-22 19:00 | 185
2015-09-22 19:15 | 128
2015-09-22 19:30 | 125
2015-09-22 19:45 | 142
2015-09-22 20:00 | 129
2015-09-22 20:15 | 127
2015-09-22 20:30 | 129
2015-09-22 20:45 | 128
2015-09-22 21:00 | 139
2015-09-22 21:15 | 120
2015-09-22 21:30 | 111
2015-09-22 21:45 | 112
2015-09-22 22:00 | 124
2015-09-22 22:15 | 117
2015-09-22 22:30 | 119
2015-09-22 22:45 | 116
2015-09-22 23:00 | 114
2015-09-22 23:15 | 128
2015-09-22 23:30 | 114
2015-09-22 23:45 | 112
2015-09-23 | 108
2015-09-23 00:15 | 108
2015-09-23 00:30 | 110
2015-09-23 00:45 | 106
2015-09-23 01:00 | 117
2015-09-23 01:15 | 113
2015-09-23 01:30 | 108
2015-09-23 01:45 | 109
2015-09-23 02:00 | 115
2015-09-23 02:15 | 110
2015-09-23 02:30 | 110
2015-09-23 02:45 | 106
2015-09-23 03:00 | 108
2015-09-23 03:15 | 117
2015-09-23 03:30 | 107
2015-09-23 03:45 | 110
2015-09-23 04:00 | 104
2015-09-23 04:15 | 117
2015-09-23 04:30 | 111
2015-09-23 04:45 | 108
2015-09-23 05:00 | 108
2015-09-23 05:15 | 108
2015-09-23 05:30 | 116
2015-09-23 05:45 | 107
2015-09-23 06:00 | 107
2015-09-23 06:15 | 111
2015-09-23 06:30 | 115
2015-09-23 06:45 | 113
2015-09-23 07:00 | 113
2015-09-23 07:15 | 145
2015-09-23 07:30 | 149
2015-09-23 07:45 | 150
2015-09-23 08:00 | 150
2015-09-23 08:15 | 152
2015-09-23 08:30 | 163
2015-09-23 08:45 | 164
2015-09-23 09:00 | 165
2015-09-23 09:15 | 173
2015-09-23 09:30 | 176
2015-09-23 09:45 | 194
2015-09-23 10:00 | 184
2015-09-23 10:15 | 190
2015-09-23 10:30 | 202
2015-09-23 10:45 | 210
2015-09-23 11:00 | 208
2015-09-23 11:15 | 214
2015-09-23 11:30 | 213
2015-09-23 11:45 | 205
2015-09-23 12:00 | 217
2015-09-23 12:15 | 215
2015-09-23 12:30 | 209
2015-09-23 12:45 | 211
2015-09-23 13:00 | 197
2015-09-23 13:15 | 215
2015-09-23 13:30 | 215
2015-09-23 13:45 | 208
2015-09-23 14:00 | 219
2015-09-23 14:15 | 221
2015-09-23 14:30 | 218
2015-09-23 14:45 | 224
2015-09-23 15:00 | 220
2015-09-23 15:15 | 231
2015-09-23 15:30 | 229
2015-09-23 15:45 | 231
2015-09-23 16:00 | 221
2015-09-23 16:15 | 230
2015-09-23 16:30 | 213
2015-09-23 16:45 | 235
2015-09-23 17:00 | 223
2015-09-23 17:15 | 219
2015-09-23 17:30 | 219
2015-09-23 17:45 | 224
2015-09-23 18:00 | 218
2015-09-23 18:15 | 217
2015-09-23 18:30 | 208
2015-09-23 18:45 | 197
2015-09-23 19:00 | 214
2015-09-23 19:15 | 122
2015-09-23 19:30 | 125
2015-09-23 19:45 | 122
2015-09-23 20:00 | 122
2015-09-23 20:15 | 129
2015-09-23 20:30 | 123
2015-09-23 20:45 | 122
2015-09-23 21:00 | 121
2015-09-23 21:15 | 122
2015-09-23 21:30 | 117
2015-09-23 21:45 | 118
2015-09-23 22:00 | 116
2015-09-23 22:15 | 116
2015-09-23 22:30 | 120
2015-09-23 22:45 | 123
2015-09-23 23:00 | 124
2015-09-23 23:15 | 123
2015-09-23 23:30 | 117
2015-09-23 23:45 | 121
2015-09-24 | 121
2015-09-24 00:15 | 110
2015-09-24 00:30 | 121
2015-09-24 00:45 | 113
2015-09-24 01:00 | 112
2015-09-24 01:15 | 106
2015-09-24 01:30 | 114
2015-09-24 01:45 | 108
2015-09-24 02:00 | 116
2015-09-24 02:15 | 106
2015-09-24 02:30 | 112
2015-09-24 02:45 | 106
2015-09-24 03:00 | 112
2015-09-24 03:15 | 110
2015-09-24 03:30 | 107
2015-09-24 03:45 | 109
2015-09-24 04:00 | 112
2015-09-24 04:15 | 109
2015-09-24 04:30 | 107
2015-09-24 04:45 | 107
2015-09-24 05:00 | 110
2015-09-24 05:15 | 109
2015-09-24 05:30 | 108
2015-09-24 05:45 | 106
2015-09-24 06:00 | 107
2015-09-24 06:15 | 113
2015-09-24 06:30 | 112
2015-09-24 06:45 | 117
2015-09-24 07:00 | 112
2015-09-24 07:15 | 200
2015-09-24 07:30 | 179
2015-09-24 07:45 | 170
2015-09-24 08:00 | 168
2015-09-24 08:15 | 178
2015-09-24 08:30 | 182
2015-09-24 08:45 | 189
2015-09-24 09:00 | 189
2015-09-24 09:15 | 191
2015-09-24 09:30 | 200
2015-09-24 09:45 | 208
2015-09-24 10:00 | 203
2015-09-24 10:15 | 214
2015-09-24 10:30 | 217
2015-09-24 10:45 | 213
2015-09-24 11:00 | 211
2015-09-24 11:15 | 209
2015-09-24 11:30 | 220
2015-09-24 11:45 | 227
2015-09-24 12:00 | 217
2015-09-24 12:15 | 226
2015-09-24 12:30 | 228
2015-09-24 12:45 | 226
2015-09-24 13:00 | 245
2015-09-24 13:15 | 242
2015-09-24 13:30 | 230
2015-09-24 13:45 | 239
2015-09-24 14:00 | 250
2015-09-24 14:15 | 250
2015-09-24 14:30 | 246
2015-09-24 14:45 | 252
2015-09-24 15:00 | 245
2015-09-24 15:15 | 259
2015-09-24 15:30 | 250
2015-09-24 15:45 | 261
2015-09-24 16:00 | 242
2015-09-24 16:15 | 263
2015-09-24 16:30 | 238
2015-09-24 16:45 | 253
2015-09-24 17:00 | 240
2015-09-24 17:15 | 254
2015-09-24 17:30 | 242
2015-09-24 17:45 | 254
2015-09-24 18:00 | 245
2015-09-24 18:15 | 240
2015-09-24 18:30 | 241
2015-09-24 18:45 | 232
2015-09-24 19:00 | 218
2015-09-24 19:15 | 143
2015-09-24 19:30 | 126
2015-09-24 19:45 | 131
2015-09-24 20:00 | 127
2015-09-24 20:15 | 128
2015-09-24 20:30 | 139
2015-09-24 20:45 | 128
2015-09-24 21:00 | 129
2015-09-24 21:15 | 116
2015-09-24 21:30 | 119
2015-09-24 21:45 | 115
2015-09-24 22:00 | 114
2015-09-24 22:15 | 114
2015-09-24 22:30 | 119
2015-09-24 22:45 | 117
2015-09-24 23:00 | 128
2015-09-24 23:15 | 119
2015-09-24 23:30 | 116
2015-09-24 23:45 | 115
2015-09-25 | 112
2015-09-25 00:15 | 116
2015-09-25 00:30 | 111
2015-09-25 00:45 | 116
2015-09-25 01:00 | 111
2015-09-25 01:15 | 115
2015-09-25 01:30 | 106
2015-09-25 01:45 | 112
2015-09-25 02:00 | 110
2015-09-25 02:15 | 110
2015-09-25 02:30 | 105
2015-09-25 02:45 | 112
2015-09-25 03:00 | 111
2015-09-25 03:15 | 109
2015-09-25 03:30 | 109
2015-09-25 03:45 | 106
2015-09-25 04:00 | 113
2015-09-25 04:15 | 111
2015-09-25 04:30 | 109
2015-09-25 04:45 | 108
2015-09-25 05:00 | 109
2015-09-25 05:15 | 110
2015-09-25 05:30 | 108
2015-09-25 05:45 | 103
2015-09-25 06:00 | 109
2015-09-25 06:15 | 111
2015-09-25 06:30 | 115
2015-09-25 06:45 | 113
2015-09-25 07:00 | 114
2015-09-25 07:15 | 216
2015-09-25 07:30 | 204
2015-09-25 07:45 | 174
2015-09-25 08:00 | 185
2015-09-25 08:15 | 191
2015-09-25 08:30 | 185
2015-09-25 08:45 | 181
2015-09-25 09:00 | 189
2015-09-25 09:15 | 210
2015-09-25 09:30 | 205
2015-09-25 09:45 | 210
2015-09-25 10:00 | 202
2015-09-25 10:15 | 205
2015-09-25 10:30 | 207
2015-09-25 10:45 | 213
2015-09-25 11:00 | 209
2015-09-25 11:15 | 204
2015-09-25 11:30 | 221
2015-09-25 11:45 | 215
2015-09-25 12:00 | 227
2015-09-25 12:15 | 223
2015-09-25 12:30 | 217
2015-09-25 12:45 | 237
2015-09-25 13:00 | 235
2015-09-25 13:15 | 234
2015-09-25 13:30 | 229
2015-09-25 13:45 | 242
2015-09-25 14:00 | 243
2015-09-25 14:15 | 255
2015-09-25 14:30 | 251
2015-09-25 14:45 | 243
2015-09-25 15:00 | 238
2015-09-25 15:15 | 243
2015-09-25 15:30 | 242
2015-09-25 15:45 | 252
2015-09-25 16:00 | 236
2015-09-25 16:15 | 231
2015-09-25 16:30 | 208
2015-09-25 16:45 | 208
2015-09-25 17:00 | 232
2015-09-25 17:15 | 222
2015-09-25 17:30 | 219
2015-09-25 17:45 | 217
2015-09-25 18:00 | 229
2015-09-25 18:15 | 221
2015-09-25 18:30 | 204
2015-09-25 18:45 | 207
2015-09-25 19:00 | 197
2015-09-25 19:15 | 132
2015-09-25 19:30 | 120
2015-09-25 19:45 | 120
2015-09-25 20:00 | 116
2015-09-25 20:15 | 126
2015-09-25 20:30 | 123
2015-09-25 20:45 | 123
2015-09-25 21:00 | 122
2015-09-25 21:15 | 111
2015-09-25 21:30 | 111
2015-09-25 21:45 | 113
2015-09-25 22:00 | 107
2015-09-25 22:15 | 108
2015-09-25 22:30 | 112
2015-09-25 22:45 | 114
2015-09-25 23:00 | 110
2015-09-25 23:15 | 110
2015-09-25 23:30 | 106
2015-09-25 23:45 | 109
2015-09-26 | 109
2015-09-26 00:15 | 106
2015-09-26 00:30 | 113
2015-09-26 00:45 | 115
2015-09-26 01:00 | 105
2015-09-26 01:15 | 108
2015-09-26 01:30 | 114
2015-09-26 01:45 | 112
2015-09-26 02:00 | 109
2015-09-26 02:15 | 107
2015-09-26 02:30 | 107
2015-09-26 02:45 | 115
2015-09-26 03:00 | 105
2015-09-26 03:15 | 110
2015-09-26 03:30 | 105
2015-09-26 03:45 | 112
2015-09-26 04:00 | 107
2015-09-26 04:15 | 112
2015-09-26 04:30 | 110
2015-09-26 04:45 | 107
2015-09-26 05:00 | 105
2015-09-26 05:15 | 116
2015-09-26 05:30 | 107
2015-09-26 05:45 | 107
2015-09-26 06:00 | 105
2015-09-26 06:15 | 105
2015-09-26 06:30 | 109
2015-09-26 06:45 | 111
2015-09-26 07:00 | 110
2015-09-26 07:15 | 110
2015-09-26 07:30 | 109
2015-09-26 07:45 | 108
2015-09-26 08:00 | 102
2015-09-26 08:15 | 104
2015-09-26 08:30 | 108
2015-09-26 08:45 | 105
2015-09-26 09:00 | 108
2015-09-26 09:15 | 107
2015-09-26 09:30 | 105
2015-09-26 09:45 | 110
2015-09-26 10:00 | 109
2015-09-26 10:15 | 104
2015-09-26 10:30 | 107
2015-09-26 10:45 | 112
2015-09-26 11:00 | 107
2015-09-26 11:15 | 104
2015-09-26 11:30 | 111
2015-09-26 11:45 | 104
2015-09-26 12:00 | 107
2015-09-26 12:15 | 112
2015-09-26 12:30 | 107
2015-09-26 12:45 | 109
2015-09-26 13:00 | 107
2015-09-26 13:15 | 118
2015-09-26 13:30 | 110
2015-09-26 13:45 | 110
2015-09-26 14:00 | 110
2015-09-26 14:15 | 113
2015-09-26 14:30 | 107
2015-09-26 14:45 | 111
2015-09-26 15:00 | 107
2015-09-26 15:15 | 113
2015-09-26 15:30 | 110
2015-09-26 15:45 | 106
2015-09-26 16:00 | 105
2015-09-26 16:15 | 105
2015-09-26 16:30 | 107
2015-09-26 16:45 | 109
2015-09-26 17:00 | 109
2015-09-26 17:15 | 110
2015-09-26 17:30 | 106
2015-09-26 17:45 | 116
2015-09-26 18:00 | 109
2015-09-26 18:15 | 107
2015-09-26 18:30 | 106
2015-09-26 18:45 | 109
2015-09-26 19:00 | 113
2015-09-26 19:15 | 109
2015-09-26 19:30 | 115
2015-09-26 19:45 | 107
2015-09-26 20:00 | 109
2015-09-26 20:15 | 114
2015-09-26 20:30 | 110
2015-09-26 20:45 | 109
2015-09-26 21:00 | 108
2015-09-26 21:15 | 108
2015-09-26 21:30 | 111
2015-09-26 21:45 | 110
2015-09-26 22:00 | 108
2015-09-26 22:15 | 107
2015-09-26 22:30 | 113
2015-09-26 22:45 | 108
2015-09-26 23:00 | 110
2015-09-26 23:15 | 106
2015-09-26 23:30 | 108
2015-09-26 23:45 | 107
2015-09-27 | 110
2015-09-27 00:15 | 112
2015-09-27 00:30 | 111
2015-09-27 00:45 | 110
2015-09-27 01:00 | 108
2015-09-27 01:15 | 112
2015-09-27 01:30 | 109
2015-09-27 01:45 | 108
2015-09-27 02:00 | 105
2015-09-27 02:15 | 112
2015-09-27 02:30 | 110
2015-09-27 02:45 | 110
2015-09-27 03:00 | 108
2015-09-27 03:15 | 105
2015-09-27 03:30 | 105
2015-09-27 03:45 | 107
2015-09-27 04:00 | 104
2015-09-27 04:15 | 110
2015-09-27 04:30 | 119
2015-09-27 04:45 | 106
2015-09-27 05:00 | 111
2015-09-27 05:15 | 111
2015-09-27 05:30 | 105
2015-09-27 05:45 | 105
2015-09-27 06:00 | 107
2015-09-27 06:15 | 108
2015-09-27 06:30 | 107
2015-09-27 06:45 | 109
2015-09-27 07:00 | 116
2015-09-27 07:15 | 117
2015-09-27 07:30 | 109
2015-09-27 07:45 | 119
2015-09-27 08:00 | 113
2015-09-27 08:15 | 117
2015-09-27 08:30 | 114
2015-09-27 08:45 | 108
2015-09-27 09:00 | 118
2015-09-27 09:15 | 109
2015-09-27 09:30 | 111
2015-09-27 09:45 | 108
2015-09-27 10:00 | 111
2015-09-27 10:15 | 111
2015-09-27 10:30 | 116
2015-09-27 10:45 | 113
2015-09-27 11:00 | 110
2015-09-27 11:15 | 114
2015-09-27 11:30 | 107
2015-09-27 11:45 | 115
2015-09-27 12:00 | 117
2015-09-27 12:15 | 117
2015-09-27 12:30 | 112
2015-09-27 12:45 | 115
2015-09-27 13:00 | 113
2015-09-27 13:15 | 112
2015-09-27 13:30 | 111
2015-09-27 13:45 | 110
2015-09-27 14:00 | 117
2015-09-27 14:15 | 116
2015-09-27 14:30 | 116
2015-09-27 14:45 | 114
2015-09-27 15:00 | 119
2015-09-27 15:15 | 119
2015-09-27 15:30 | 116
2015-09-27 15:45 | 115
2015-09-27 16:00 | 109
2015-09-27 16:15 | 114
2015-09-27 16:30 | 113
2015-09-27 16:45 | 111
2015-09-27 17:00 | 111
2015-09-27 17:15 | 113
2015-09-27 17:30 | 120
2015-09-27 17:45 | 115
2015-09-27 18:00 | 115
2015-09-27 18:15 | 117
2015-09-27 18:30 | 112
2015-09-27 18:45 | 121
2015-09-27 19:00 | 112
2015-09-27 19:15 | 116
2015-09-27 19:30 | 110
2015-09-27 19:45 | 113
2015-09-27 20:00 | 113
2015-09-27 20:15 | 113
2015-09-27 20:30 | 115
2015-09-27 20:45 | 114
2015-09-27 21:00 | 123
2015-09-27 21:15 | 107
2015-09-27 21:30 | 108
2015-09-27 21:45 | 103
2015-09-27 22:00 | 106
2015-09-27 22:15 | 104
2015-09-27 22:30 | 103
2015-09-27 22:45 | 103
2015-09-27 23:00 | 97
2015-09-27 23:15 | 101
2015-09-27 23:30 | 105
2015-09-27 23:45 | 99
2015-09-28 | 100
2015-09-28 00:15 | 101
2015-09-28 00:30 | 101
2015-09-28 00:45 | 101
2015-09-28 01:00 | 104
2015-09-28 01:15 | 102
2015-09-28 01:30 | 104
2015-09-28 01:45 | 98
2015-09-28 02:00 | 100
2015-09-28 02:15 | 107
2015-09-28 02:30 | 97
2015-09-28 02:45 | 100
2015-09-28 03:00 | 99
2015-09-28 03:15 | 105
2015-09-28 03:30 | 102
2015-09-28 03:45 | 98
2015-09-28 04:00 | 101
2015-09-28 04:15 | 102
2015-09-28 04:30 | 97
2015-09-28 04:45 | 102
2015-09-28 05:00 | 99
2015-09-28 05:15 | 101
2015-09-28 05:30 | 105
2015-09-28 05:45 | 101
2015-09-28 06:00 | 104
2015-09-28 06:15 | 99
2015-09-28 06:30 | 100
2015-09-28 06:45 | 106
2015-09-28 07:00 | 102
2015-09-28 07:15 | 234
2015-09-28 07:30 | 262
2015-09-28 07:45 | 241
2015-09-28 08:00 | 232
2015-09-28 08:15 | 222
2015-09-28 08:30 | 205
2015-09-28 08:45 | 219
2015-09-28 09:00 | 215
2015-09-28 09:15 | 215
2015-09-28 09:30 | 217
2015-09-28 09:45 | 221
2015-09-28 10:00 | 222
2015-09-28 10:15 | 221
2015-09-28 10:30 | 217
2015-09-28 10:45 | 204
2015-09-28 11:00 | 218
2015-09-28 11:15 | 224
2015-09-28 11:30 | 233
2015-09-28 11:45 | 220
2015-09-28 12:00 | 229
2015-09-28 12:15 | 224
2015-09-28 12:30 | 246
2015-09-28 12:45 | 235
2015-09-28 13:00 | 230
2015-09-28 13:15 | 236
2015-09-28 13:30 | 245
2015-09-28 13:45 | 248
2015-09-28 14:00 | 260
2015-09-28 14:15 | 245
2015-09-28 14:30 | 258
2015-09-28 14:45 | 241
2015-09-28 15:00 | 242
2015-09-28 15:15 | 232
2015-09-28 15:30 | 246
2015-09-28 15:45 | 243
2015-09-28 16:00 | 236
2015-09-28 16:15 | 231
2015-09-28 16:30 | 227
2015-09-28 16:45 | 241
2015-09-28 17:00 | 242
2015-09-28 17:15 | 234
2015-09-28 17:30 | 233
2015-09-28 17:45 | 233
2015-09-28 18:00 | 228
2015-09-28 18:15 | 230
2015-09-28 18:30 | 234
2015-09-28 18:45 | 214
2015-09-28 19:00 | 200
2015-09-28 19:15 | 122
2015-09-28 19:30 | 131
2015-09-28 19:45 | 133
2015-09-28 20:00 | 128
2015-09-28 20:15 | 126
2015-09-28 20:30 | 124
2015-09-28 20:45 | 127
2015-09-28 21:00 | 126
2015-09-28 21:15 | 115
2015-09-28 21:30 | 109
2015-09-28 21:45 | 117
2015-09-28 22:00 | 121
2015-09-28 22:15 | 111
2015-09-28 22:30 | 118
2015-09-28 22:45 | 119
2015-09-28 23:00 | 116
2015-09-28 23:15 | 128
2015-09-28 23:30 | 120
2015-09-28 23:45 | 119
2015-09-29 | 117
2015-09-29 00:15 | 120
2015-09-29 00:30 | 118
2015-09-29 00:45 | 106
2015-09-29 01:00 | 109
2015-09-29 01:15 | 109
2015-09-29 01:30 | 112
2015-09-29 01:45 | 111
2015-09-29 02:00 | 108
2015-09-29 02:15 | 111
2015-09-29 02:30 | 110
2015-09-29 02:45 | 113
2015-09-29 03:00 | 109
2015-09-29 03:15 | 113
2015-09-29 03:30 | 104
2015-09-29 03:45 | 112
2015-09-29 04:00 | 112
2015-09-29 04:15 | 108
2015-09-29 04:30 | 106
2015-09-29 04:45 | 114
2015-09-29 05:00 | 107
2015-09-29 05:15 | 111
2015-09-29 05:30 | 109
2015-09-29 05:45 | 104
2015-09-29 06:00 | 116
2015-09-29 06:15 | 109
2015-09-29 06:30 | 108
2015-09-29 06:45 | 105
2015-09-29 07:00 | 108
2015-09-29 07:15 | 243
2015-09-29 07:30 | 208
2015-09-29 07:45 | 172
2015-09-29 08:00 | 171
2015-09-29 08:15 | 166
2015-09-29 08:30 | 187
2015-09-29 08:45 | 188
2015-09-29 09:00 | 174
2015-09-29 09:15 | 175
2015-09-29 09:30 | 190
2015-09-29 09:45 | 201
2015-09-29 10:00 | 202
2015-09-29 10:15 | 201
2015-09-29 10:30 | 201
2015-09-29 10:45 | 202
2015-09-29 11:00 | 205
2015-09-29 11:15 | 218
2015-09-29 11:30 | 227
2015-09-29 11:45 | 221
2015-09-29 12:00 | 210
2015-09-29 12:15 | 218
2015-09-29 12:30 | 211
2015-09-29 12:45 | 223
2015-09-29 13:00 | 212
2015-09-29 13:15 | 208
2015-09-29 13:30 | 217
2015-09-29 13:45 | 219
2015-09-29 14:00 | 228
2015-09-29 14:15 | 211
2015-09-29 14:30 | 218
2015-09-29 14:45 | 210
2015-09-29 15:00 | 208
2015-09-29 15:15 | 220
2015-09-29 15:30 | 220
2015-09-29 15:45 | 212
2015-09-29 16:00 | 213
2015-09-29 16:15 | 223
2015-09-29 16:30 | 216
2015-09-29 16:45 | 221
2015-09-29 17:00 | 212
2015-09-29 17:15 | 212
2015-09-29 17:30 | 200
2015-09-29 17:45 | 204
2015-09-29 18:00 | 208
2015-09-29 18:15 | 203
2015-09-29 18:30 | 199
2015-09-29 18:45 | 196
2015-09-29 19:00 | 186
2015-09-29 19:15 | 131
2015-09-29 19:30 | 135
2015-09-29 19:45 | 121
2015-09-29 20:00 | 121
2015-09-29 20:15 | 122
2015-09-29 20:30 | 129
2015-09-29 20:45 | 122
2015-09-29 21:00 | 122
2015-09-29 21:15 | 120
2015-09-29 21:30 | 116
2015-09-29 21:45 | 123
2015-09-29 22:00 | 118
2015-09-29 22:15 | 118
2015-09-29 22:30 | 114
2015-09-29 22:45 | 125
2015-09-29 23:00 | 119
2015-09-29 23:15 | 123
2015-09-29 23:30 | 131
2015-09-29 23:45 | 119
2015-09-30 | 129
2015-09-30 00:15 | 124
2015-09-30 00:30 | 118
2015-09-30 00:45 | 118
2015-09-30 01:00 | 118
2015-09-30 01:15 | 120
2015-09-30 01:30 | 111
2015-09-30 01:45 | 109
2015-09-30 02:00 | 107
2015-09-30 02:15 | 110
2015-09-30 02:30 | 114
2015-09-30 02:45 | 111
2015-09-30 03:00 | 108
2015-09-30 03:15 | 103
2015-09-30 03:30 | 111
2015-09-30 03:45 | 105
2015-09-30 04:00 | 114
2015-09-30 04:15 | 110
2015-09-30 04:30 | 109
2015-09-30 04:45 | 107
2015-09-30 05:00 | 110
2015-09-30 05:15 | 117
2015-09-30 05:30 | 109
2015-09-30 05:45 | 105
2015-09-30 06:00 | 112
2015-09-30 06:15 | 118
2015-09-30 06:30 | 113
2015-09-30 06:45 | 118
2015-09-30 07:00 | 111
2015-09-30 07:15 | 210
2015-09-30 07:30 | 197
2015-09-30 07:45 | 170
2015-09-30 08:00 | 173
2015-09-30 08:15 | 179
2015-09-30 08:30 | 184
2015-09-30 08:45 | 174
2015-09-30 09:00 | 183
2015-09-30 09:15 | 184
2015-09-30 09:30 | 189
2015-09-30 09:45 | 194
2015-09-30 10:00 | 201
2015-09-30 10:15 | 191
2015-09-30 10:30 | 192
2015-09-30 10:45 | 194
2015-09-30 11:00 | 209
2015-09-30 11:15 | 198
2015-09-30 11:30 | 202
2015-09-30 11:45 | 211
2015-09-30 12:00 | 207
2015-09-30 12:15 | 192
2015-09-30 12:30 | 192
2015-09-30 12:45 | 193
2015-09-30 13:00 | 189
2015-09-30 13:15 | 186
2015-09-30 13:30 | 193
2015-09-30 13:45 | 204
2015-09-30 14:00 | 201
2015-09-30 14:15 | 193
2015-09-30 14:30 | 192
2015-09-30 14:45 | 197
2015-09-30 15:00 | 212
2015-09-30 15:15 | 191
2015-09-30 15:30 | 191
2015-09-30 15:45 | 194
2015-09-30 16:00 | 193
2015-09-30 16:15 | 211
2015-09-30 16:30 | 194
2015-09-30 16:45 | 191
2015-09-30 17:00 | 197
2015-09-30 17:15 | 198
2015-09-30 17:30 | 209
2015-09-30 17:45 | 187
2015-09-30 18:00 | 191
2015-09-30 18:15 | 196
2015-09-30 18:30 | 189
2015-09-30 18:45 | 203
2015-09-30 19:00 | 197
2015-09-30 19:15 | 125
2015-09-30 19:30 | 128
2015-09-30 19:45 | 126
2015-09-30 20:00 | 142
2015-09-30 20:15 | 130
2015-09-30 20:30 | 131
2015-09-30 20:45 | 128
2015-09-30 21:00 | 124
2015-09-30 21:15 | 134
2015-09-30 21:30 | 110
2015-09-30 21:45 | 115
2015-09-30 22:00 | 106
2015-09-30 22:15 | 118
2015-09-30 22:30 | 117
2015-09-30 22:45 | 112
2015-09-30 23:00 | 112
2015-09-30 23:15 | 107
2015-09-30 23:30 | 115
2015-09-30 23:45 | 112
2015-10-01 | 109
2015-10-01 00:15 | 107
2015-10-01 00:30 | 117
2015-10-01 00:45 | 114
2015-10-01 01:00 | 107
2015-10-01 01:15 | 114
2015-10-01 01:30 | 109
2015-10-01 01:45 | 110
2015-10-01 02:00 | 105
2015-10-01 02:15 | 111
2015-10-01 02:30 | 117
2015-10-01 02:45 | 106
2015-10-01 03:00 | 108
2015-10-01 03:15 | 108
2015-10-01 03:30 | 109
2015-10-01 03:45 | 116
2015-10-01 04:00 | 109
2015-10-01 04:15 | 108
2015-10-01 04:30 | 107
2015-10-01 04:45 | 109
2015-10-01 05:00 | 113
2015-10-01 05:15 | 110
2015-10-01 05:30 | 110
2015-10-01 05:45 | 110
2015-10-01 06:00 | 118
2015-10-01 06:15 | 113
2015-10-01 06:30 | 115
2015-10-01 06:45 | 112
2015-10-01 07:00 | 111
2015-10-01 07:15 | 204
2015-10-01 07:30 | 183
2015-10-01 07:45 | 181
2015-10-01 08:00 | 178
2015-10-01 08:15 | 178
2015-10-01 08:30 | 181
2015-10-01 08:45 | 186
2015-10-01 09:00 | 197
2015-10-01 09:15 | 187
2015-10-01 09:30 | 186
2015-10-01 09:45 | 186
2015-10-01 10:00 | 186
2015-10-01 10:15 | 204
2015-10-01 10:30 | 188
2015-10-01 10:45 | 194
2015-10-01 11:00 | 199
2015-10-01 11:15 | 197
2015-10-01 11:30 | 192
2015-10-01 11:45 | 205
2015-10-01 12:00 | 208
2015-10-01 12:15 | 192
2015-10-01 12:30 | 195
2015-10-01 12:45 | 200
2015-10-01 13:00 | 209
2015-10-01 13:15 | 207
2015-10-01 13:30 | 198
2015-10-01 13:45 | 207
2015-10-01 14:00 | 209
2015-10-01 14:15 | 213
2015-10-01 14:30 | 210
2015-10-01 14:45 | 210
2015-10-01 15:00 | 206
2015-10-01 15:15 | 212
2015-10-01 15:30 | 201
2015-10-01 15:45 | 218
2015-10-01 16:00 | 197
2015-10-01 16:15 | 203
2015-10-01 16:30 | 196
2015-10-01 16:45 | 203
2015-10-01 17:00 | 211
2015-10-01 17:15 | 217
2015-10-01 17:30 | 203
2015-10-01 17:45 | 218
2015-10-01 18:00 | 199
2015-10-01 18:15 | 210
2015-10-01 18:30 | 202
2015-10-01 18:45 | 213
2015-10-01 19:00 | 201
2015-10-01 19:15 | 123
2015-10-01 19:30 | 126
2015-10-01 19:45 | 121
2015-10-01 20:00 | 126
2015-10-01 20:15 | 133
2015-10-01 20:30 | 122
2015-10-01 20:45 | 124
2015-10-01 21:00 | 120
2015-10-01 21:15 | 127
2015-10-01 21:30 | 121
2015-10-01 21:45 | 117
2015-10-01 22:00 | 118
2015-10-01 22:15 | 120
2015-10-01 22:30 | 127
2015-10-01 22:45 | 128
2015-10-01 23:00 | 125
2015-10-01 23:15 | 123
2015-10-01 23:30 | 121
2015-10-01 23:45 | 130
2015-10-02 | 122
2015-10-02 00:15 | 120
2015-10-02 00:30 | 120
2015-10-02 00:45 | 114
2015-10-02 01:00 | 122
2015-10-02 01:15 | 110
2015-10-02 01:30 | 113
2015-10-02 01:45 | 108
2015-10-02 02:00 | 113
2015-10-02 02:15 | 116
2015-10-02 02:30 | 110
2015-10-02 02:45 | 111
2015-10-02 03:00 | 107
2015-10-02 03:15 | 110
2015-10-02 03:30 | 115
2015-10-02 03:45 | 109
2015-10-02 04:00 | 106
2015-10-02 04:15 | 113
2015-10-02 04:30 | 113
2015-10-02 04:45 | 110
2015-10-02 05:00 | 110
2015-10-02 05:15 | 105
2015-10-02 05:30 | 116
2015-10-02 05:45 | 113
2015-10-02 06:00 | 116
2015-10-02 06:15 | 117
2015-10-02 06:30 | 111
2015-10-02 06:45 | 123
2015-10-02 07:00 | 115
2015-10-02 07:15 | 170
2015-10-02 07:30 | 166
2015-10-02 07:45 | 162
2015-10-02 08:00 | 179
2015-10-02 08:15 | 167
2015-10-02 08:30 | 180
2015-10-02 08:45 | 186
2015-10-02 09:00 | 200
2015-10-02 09:15 | 199
2015-10-02 09:30 | 199
2015-10-02 09:45 | 193
2015-10-02 10:00 | 204
2015-10-02 10:15 | 212
2015-10-02 10:30 | 203
2015-10-02 10:45 | 198
2015-10-02 11:00 | 201
2015-10-02 11:15 | 213
2015-10-02 11:30 | 215
2015-10-02 11:45 | 209
2015-10-02 12:00 | 205
2015-10-02 12:15 | 203
2015-10-02 12:30 | 218
2015-10-02 12:45 | 211
2015-10-02 13:00 | 200
2015-10-02 13:15 | 203
2015-10-02 13:30 | 204
2015-10-02 13:45 | 212
2015-10-02 14:00 | 210
2015-10-02 14:15 | 218
2015-10-02 14:30 | 229
2015-10-02 14:45 | 224
2015-10-02 15:00 | 220
2015-10-02 15:15 | 219
2015-10-02 15:30 | 217
2015-10-02 15:45 | 238
2015-10-02 16:00 | 215
2015-10-02 16:15 | 230
2015-10-02 16:30 | 219
2015-10-02 16:45 | 217
2015-10-02 17:00 | 222
2015-10-02 17:15 | 231
2015-10-02 17:30 | 210
2015-10-02 17:45 | 216
2015-10-02 18:00 | 212
2015-10-02 18:15 | 221
2015-10-02 18:30 | 201
2015-10-02 18:45 | 207
2015-10-02 19:00 | 191
2015-10-02 19:15 | 129
2015-10-02 19:30 | 129
2015-10-02 19:45 | 123
2015-10-02 20:00 | 118
2015-10-02 20:15 | 129
2015-10-02 20:30 | 123
2015-10-02 20:45 | 119
2015-10-02 21:00 | 119
2015-10-02 21:15 | 114
2015-10-02 21:30 | 113
2015-10-02 21:45 | 110
2015-10-02 22:00 | 107
2015-10-02 22:15 | 112
2015-10-02 22:30 | 120
2015-10-02 22:45 | 108
2015-10-02 23:00 | 110
2015-10-02 23:15 | 107
2015-10-02 23:30 | 106
2015-10-02 23:45 | 115
2015-10-03 | 107
2015-10-03 00:15 | 100
2015-10-03 00:30 | 97
2015-10-03 00:45 | 102
2015-10-03 01:00 | 94
2015-10-03 01:15 | 97
2015-10-03 01:30 | 94
2015-10-03 01:45 | 94
2015-10-03 02:00 | 103
2015-10-03 02:15 | 95
2015-10-03 02:30 | 100
2015-10-03 02:45 | 95
2015-10-03 03:00 | 92
2015-10-03 03:15 | 102
2015-10-03 03:30 | 94
2015-10-03 03:45 | 95
2015-10-03 04:00 | 96
2015-10-03 04:15 | 99
2015-10-03 04:30 | 97
2015-10-03 04:45 | 96
2015-10-03 05:00 | 90
2015-10-03 05:15 | 97
2015-10-03 05:30 | 92
2015-10-03 05:45 | 100
2015-10-03 06:00 | 99
2015-10-03 06:15 | 96
2015-10-03 06:30 | 99
2015-10-03 06:45 | 93
2015-10-03 07:00 | 96
2015-10-03 07:15 | 98
2015-10-03 07:30 | 90
2015-10-03 07:45 | 90
2015-10-03 08:00 | 98
2015-10-03 08:15 | 88
2015-10-03 08:30 | 94
2015-10-03 08:45 | 89
2015-10-03 09:00 | 89
2015-10-03 09:15 | 95
2015-10-03 09:30 | 85
2015-10-03 09:45 | 97
2015-10-03 10:00 | 100
2015-10-03 10:15 | 88
2015-10-03 10:30 | 91
2015-10-03 10:45 | 93
2015-10-03 11:00 | 90
2015-10-03 11:15 | 97
2015-10-03 11:30 | 94
2015-10-03 11:45 | 91
2015-10-03 12:00 | 88
2015-10-03 12:15 | 97
2015-10-03 12:30 | 93
2015-10-03 12:45 | 92
2015-10-03 13:00 | 88
2015-10-03 13:15 | 100
2015-10-03 13:30 | 92
2015-10-03 13:45 | 94
2015-10-03 14:00 | 95
2015-10-03 14:15 | 93
2015-10-03 14:30 | 98
2015-10-03 14:45 | 94
2015-10-03 15:00 | 95
2015-10-03 15:15 | 89
2015-10-03 15:30 | 94
2015-10-03 15:45 | 95
2015-10-03 16:00 | 97
2015-10-03 16:15 | 95
2015-10-03 16:30 | 97
2015-10-03 16:45 | 96
2015-10-03 17:00 | 92
2015-10-03 17:15 | 103
2015-10-03 17:30 | 97
2015-10-03 17:45 | 101
2015-10-03 18:00 | 98
2015-10-03 18:15 | 102
2015-10-03 18:30 | 98
2015-10-03 18:45 | 101
2015-10-03 19:00 | 97
2015-10-03 19:15 | 98
2015-10-03 19:30 | 105
2015-10-03 19:45 | 96
2015-10-03 20:00 | 98
2015-10-03 20:15 | 94
2015-10-03 20:30 | 99
2015-10-03 20:45 | 96
2015-10-03 21:00 | 96
2015-10-03 21:15 | 104
2015-10-03 21:30 | 99
2015-10-03 21:45 | 102
2015-10-03 22:00 | 104
2015-10-03 22:15 | 101
2015-10-03 22:30 | 98
2015-10-03 22:45 | 104
2015-10-03 23:00 | 96
2015-10-03 23:15 | 102
2015-10-03 23:30 | 97
2015-10-03 23:45 | 97
2015-10-04 | 96
2015-10-04 00:15 | 96
2015-10-04 00:30 | 100
2015-10-04 00:45 | 97
2015-10-04 01:00 | 96
2015-10-04 01:15 | 101
2015-10-04 01:30 | 96
2015-10-04 01:45 | 94
2015-10-04 02:00 | 96
2015-10-04 02:15 | 93
2015-10-04 02:30 | 98
2015-10-04 02:45 | 98
2015-10-04 03:00 | 98
2015-10-04 03:15 | 100
2015-10-04 03:30 | 95
2015-10-04 03:45 | 96
2015-10-04 04:00 | 94
2015-10-04 04:15 | 96
2015-10-04 04:30 | 97
2015-10-04 04:45 | 99
2015-10-04 05:00 | 99
2015-10-04 05:15 | 95
2015-10-04 05:30 | 97
2015-10-04 05:45 | 99
2015-10-04 06:00 | 103
2015-10-04 06:15 | 97
2015-10-04 06:30 | 98
2015-10-04 06:45 | 100
2015-10-04 07:00 | 102
2015-10-04 07:15 | 98
2015-10-04 07:30 | 96
2015-10-04 07:45 | 94
2015-10-04 08:00 | 101
2015-10-04 08:15 | 101
2015-10-04 08:30 | 99
2015-10-04 08:45 | 112
2015-10-04 09:00 | 103
2015-10-04 09:15 | 102
2015-10-04 09:30 | 103
2015-10-04 09:45 | 102
2015-10-04 10:00 | 105
2015-10-04 10:15 | 103
2015-10-04 10:30 | 100
2015-10-04 10:45 | 105
2015-10-04 11:00 | 100
2015-10-04 11:15 | 104
2015-10-04 11:30 | 102
2015-10-04 11:45 | 103
2015-10-04 12:00 | 99
2015-10-04 12:15 | 107
2015-10-04 12:30 | 106
2015-10-04 12:45 | 106
2015-10-04 13:00 | 101
2015-10-04 13:15 | 104
2015-10-04 13:30 | 104
2015-10-04 13:45 | 100
2015-10-04 14:00 | 109
2015-10-04 14:15 | 106
2015-10-04 14:30 | 105
2015-10-04 14:45 | 107
2015-10-04 15:00 | 109
2015-10-04 15:15 | 108
2015-10-04 15:30 | 107
2015-10-04 15:45 | 101
2015-10-04 16:00 | 107
2015-10-04 16:15 | 102
2015-10-04 16:30 | 104
2015-10-04 16:45 | 102
2015-10-04 17:00 | 104
2015-10-04 17:15 | 104
2015-10-04 17:30 | 111
2015-10-04 17:45 | 109
2015-10-04 18:00 | 107
2015-10-04 18:15 | 109
2015-10-04 18:30 | 106
2015-10-04 18:45 | 112
2015-10-04 19:00 | 107
2015-10-04 19:15 | 106
2015-10-04 19:30 | 104
2015-10-04 19:45 | 112
2015-10-04 20:00 | 107
2015-10-04 20:15 | 108
2015-10-04 20:30 | 108
2015-10-04 20:45 | 110
2015-10-04 21:00 | 105
2015-10-04 21:15 | 107
2015-10-04 21:30 | 105
2015-10-04 21:45 | 99
2015-10-04 22:00 | 100
2015-10-04 22:15 | 98
2015-10-04 22:30 | 106
2015-10-04 22:45 | 101
2015-10-04 23:00 | 101
2015-10-04 23:15 | 101
2015-10-04 23:30 | 99
2015-10-04 23:45 | 105
2015-10-05 | 101
2015-10-05 00:15 | 98
2015-10-05 00:30 | 104
2015-10-05 00:45 | 100
2015-10-05 01:00 | 98
2015-10-05 01:15 | 108
2015-10-05 01:30 | 99
2015-10-05 01:45 | 103
2015-10-05 02:00 | 98
2015-10-05 02:15 | 100
2015-10-05 02:30 | 101
2015-10-05 02:45 | 97
2015-10-05 03:00 | 101
2015-10-05 03:15 | 99
2015-10-05 03:30 | 100
2015-10-05 03:45 | 106
2015-10-05 04:00 | 101
2015-10-05 04:15 | 98
2015-10-05 04:30 | 102
2015-10-05 04:45 | 101
2015-10-05 05:00 | 102
2015-10-05 05:15 | 102
2015-10-05 05:30 | 106
2015-10-05 05:45 | 106
2015-10-05 06:00 | 100
2015-10-05 06:15 | 111
2015-10-05 06:30 | 105
2015-10-05 06:45 | 104
2015-10-05 07:00 | 106
2015-10-05 07:15 | 184
2015-10-05 07:30 | 168
2015-10-05 07:45 | 159
2015-10-05 08:00 | 158
2015-10-05 08:15 | 166
2015-10-05 08:30 | 170
2015-10-05 08:45 | 179
2015-10-05 09:00 | 191
2015-10-05 09:15 | 200
2015-10-05 09:30 | 207
2015-10-05 09:45 | 216
2015-10-05 10:00 | 202
2015-10-05 10:15 | 208
2015-10-05 10:30 | 213
2015-10-05 10:45 | 224
2015-10-05 11:00 | 231
2015-10-05 11:15 | 216
2015-10-05 11:30 | 222
2015-10-05 11:45 | 214
2015-10-05 12:00 | 235
2015-10-05 12:15 | 223
2015-10-05 12:30 | 219
2015-10-05 12:45 | 215
2015-10-05 13:00 | 234
2015-10-05 13:15 | 231
2015-10-05 13:30 | 231
2015-10-05 13:45 | 234
2015-10-05 14:00 | 231
2015-10-05 14:15 | 251
2015-10-05 14:30 | 242
2015-10-05 14:45 | 244
2015-10-05 15:00 | 235
2015-10-05 15:15 | 241
2015-10-05 15:30 | 239
2015-10-05 15:45 | 226
2015-10-05 16:00 | 232
2015-10-05 16:15 | 237
2015-10-05 16:30 | 232
2015-10-05 16:45 | 241
2015-10-05 17:00 | 233
2015-10-05 17:15 | 231
2015-10-05 17:30 | 229
2015-10-05 17:45 | 222
2015-10-05 18:00 | 227
2015-10-05 18:15 | 227
2015-10-05 18:30 | 221
2015-10-05 18:45 | 218
2015-10-05 19:00 | 210
2015-10-05 19:15 | 126
2015-10-05 19:30 | 117
2015-10-05 19:45 | 118
2015-10-05 20:00 | 112
2015-10-05 20:15 | 119
2015-10-05 20:30 | 113
2015-10-05 20:45 | 110
2015-10-05 21:00 | 106
2015-10-05 21:15 | 114
2015-10-05 21:30 | 103
2015-10-05 21:45 | 108
2015-10-05 22:00 | 99
2015-10-05 22:15 | 110
2015-10-05 22:30 | 107
2015-10-05 22:45 | 105
2015-10-05 23:00 | 104
2015-10-05 23:15 | 102
2015-10-05 23:30 | 105
2015-10-05 23:45 | 107
2015-10-06 | 104
2015-10-06 00:15 | 99
2015-10-06 00:30 | 104
2015-10-06 00:45 | 110
2015-10-06 01:00 | 102
2015-10-06 01:15 | 104
2015-10-06 01:30 | 98
2015-10-06 01:45 | 101
2015-10-06 02:00 | 104
2015-10-06 02:15 | 98
2015-10-06 02:30 | 107
2015-10-06 02:45 | 101
2015-10-06 03:00 | 100
2015-10-06 03:15 | 100
2015-10-06 03:30 | 101
2015-10-06 03:45 | 100
2015-10-06 04:00 | 113
2015-10-06 04:15 | 103
2015-10-06 04:30 | 104
2015-10-06 04:45 | 101
2015-10-06 05:00 | 106
2015-10-06 05:15 | 107
2015-10-06 05:30 | 104
2015-10-06 05:45 | 98
2015-10-06 06:00 | 104
2015-10-06 06:15 | 104
2015-10-06 06:30 | 104
2015-10-06 06:45 | 107
2015-10-06 07:00 | 104
2015-10-06 07:15 | 177
2015-10-06 07:30 | 155
2015-10-06 07:45 | 148
2015-10-06 08:00 | 157
2015-10-06 08:15 | 160
2015-10-06 08:30 | 165
2015-10-06 08:45 | 164
2015-10-06 09:00 | 183
2015-10-06 09:15 | 189
2015-10-06 09:30 | 183
2015-10-06 09:45 | 200
2015-10-06 10:00 | 196
2015-10-06 10:15 | 193
2015-10-06 10:30 | 209
2015-10-06 10:45 | 221
2015-10-06 11:00 | 214
2015-10-06 11:15 | 213
2015-10-06 11:30 | 211
2015-10-06 11:45 | 219
2015-10-06 12:00 | 234
2015-10-06 12:15 | 227
2015-10-06 12:30 | 222
2015-10-06 12:45 | 212
2015-10-06 13:00 | 221
2015-10-06 13:15 | 224
2015-10-06 13:30 | 224
2015-10-06 13:45 | 229
2015-10-06 14:00 | 237
2015-10-06 14:15 | 245
2015-10-06 14:30 | 244
2015-10-06 14:45 | 253
2015-10-06 15:00 | 238
2015-10-06 15:15 | 237
2015-10-06 15:30 | 255
2015-10-06 15:45 | 237
2015-10-06 16:00 | 232
2015-10-06 16:15 | 234
2015-10-06 16:30 | 226
2015-10-06 16:45 | 230
2015-10-06 17:00 | 233
2015-10-06 17:15 | 225
2015-10-06 17:30 | 224
2015-10-06 17:45 | 227
2015-10-06 18:00 | 230
2015-10-06 18:15 | 223
2015-10-06 18:30 | 224
2015-10-06 18:45 | 219
2015-10-06 19:00 | 204
2015-10-06 19:15 | 146
2015-10-06 19:30 | 133
2015-10-06 19:45 | 137
2015-10-06 20:00 | 130
2015-10-06 20:15 | 130
2015-10-06 20:30 | 128
2015-10-06 20:45 | 130
2015-10-06 21:00 | 130
2015-10-06 21:15 | 118
2015-10-06 21:30 | 122
2015-10-06 21:45 | 110
2015-10-06 22:00 | 111
2015-10-06 22:15 | 111
2015-10-06 22:30 | 114
2015-10-06 22:45 | 117
2015-10-06 23:00 | 113
2015-10-06 23:15 | 111
2015-10-06 23:30 | 110
2015-10-06 23:45 | 115
2015-10-07 | 112
2015-10-07 00:15 | 111
2015-10-07 00:30 | 110
2015-10-07 00:45 | 108
2015-10-07 01:00 | 117
2015-10-07 01:15 | 111
2015-10-07 01:30 | 112
2015-10-07 01:45 | 110
2015-10-07 02:00 | 111
2015-10-07 02:15 | 118
2015-10-07 02:30 | 110
2015-10-07 02:45 | 108
2015-10-07 03:00 | 109
2015-10-07 03:15 | 110
2015-10-07 03:30 | 117
2015-10-07 03:45 | 110
2015-10-07 04:00 | 110
2015-10-07 04:15 | 107
2015-10-07 04:30 | 116
2015-10-07 04:45 | 111
2015-10-07 05:00 | 113
2015-10-07 05:15 | 106
2015-10-07 05:30 | 109
2015-10-07 05:45 | 112
2015-10-07 06:00 | 116
2015-10-07 06:15 | 119
2015-10-07 06:30 | 118
2015-10-07 06:45 | 115
2015-10-07 07:00 | 114
2015-10-07 07:15 | 236
2015-10-07 07:30 | 200
2015-10-07 07:45 | 193
2015-10-07 08:00 | 178
2015-10-07 08:15 | 184
2015-10-07 08:30 | 201
2015-10-07 08:45 | 184
2015-10-07 09:00 | 190
2015-10-07 09:15 | 198
2015-10-07 09:30 | 207
2015-10-07 09:45 | 194
2015-10-07 10:00 | 199
2015-10-07 10:15 | 211
2015-10-07 10:30 | 219
2015-10-07 10:45 | 236
2015-10-07 11:00 | 222
2015-10-07 11:15 | 212
2015-10-07 11:30 | 215
2015-10-07 11:45 | 222
2015-10-07 12:00 | 226
2015-10-07 12:15 | 219
2015-10-07 12:30 | 225
2015-10-07 12:45 | 230
2015-10-07 13:00 | 223
2015-10-07 13:15 | 239
2015-10-07 13:30 | 243
2015-10-07 13:45 | 236
2015-10-07 14:00 | 238
2015-10-07 14:15 | 230
2015-10-07 14:30 | 229
2015-10-07 14:45 | 254
2015-10-07 15:00 | 243
2015-10-07 15:15 | 246
2015-10-07 15:30 | 233
2015-10-07 15:45 | 245
2015-10-07 16:00 | 239
2015-10-07 16:15 | 243
2015-10-07 16:30 | 231
2015-10-07 16:45 | 231
2015-10-07 17:00 | 230
2015-10-07 17:15 | 225
2015-10-07 17:30 | 236
2015-10-07 17:45 | 228
2015-10-07 18:00 | 214
2015-10-07 18:15 | 227
2015-10-07 18:30 | 217
2015-10-07 18:45 | 227
2015-10-07 19:00 | 213
2015-10-07 19:15 | 142
2015-10-07 19:30 | 126
2015-10-07 19:45 | 127
2015-10-07 20:00 | 124
2015-10-07 20:15 | 123
2015-10-07 20:30 | 134
2015-10-07 20:45 | 126
2015-10-07 21:00 | 120
2015-10-07 21:15 | 110
2015-10-07 21:30 | 117
2015-10-07 21:45 | 110
2015-10-07 22:00 | 110
2015-10-07 22:15 | 109
2015-10-07 22:30 | 107
2015-10-07 22:45 | 118
2015-10-07 23:00 | 110
2015-10-07 23:15 | 107
2015-10-07 23:30 | 108
2015-10-07 23:45 | 110
2015-10-08 | 115
2015-10-08 00:15 | 107
2015-10-08 00:30 | 108
2015-10-08 00:45 | 106
2015-10-08 01:00 | 110
2015-10-08 01:15 | 114
2015-10-08 01:30 | 108
2015-10-08 01:45 | 107
2015-10-08 02:00 | 105
2015-10-08 02:15 | 114
2015-10-08 02:30 | 109
2015-10-08 02:45 | 109
2015-10-08 03:00 | 105
2015-10-08 03:15 | 106
2015-10-08 03:30 | 118
2015-10-08 03:45 | 104
2015-10-08 04:00 | 106
2015-10-08 04:15 | 104
2015-10-08 04:30 | 111
2015-10-08 04:45 | 111
2015-10-08 05:00 | 109
2015-10-08 05:15 | 107
2015-10-08 05:30 | 108
2015-10-08 05:45 | 112
2015-10-08 06:00 | 110
2015-10-08 06:15 | 112
2015-10-08 06:30 | 108
2015-10-08 06:45 | 112
2015-10-08 07:00 | 111
2015-10-08 07:15 | 213
2015-10-08 07:30 | 217
2015-10-08 07:45 | 162
2015-10-08 08:00 | 169
2015-10-08 08:15 | 175
2015-10-08 08:30 | 191
2015-10-08 08:45 | 198
2015-10-08 09:00 | 183
2015-10-08 09:15 | 195
2015-10-08 09:30 | 212
2015-10-08 09:45 | 198
2015-10-08 10:00 | 201
2015-10-08 10:15 | 202
2015-10-08 10:30 | 219
2015-10-08 10:45 | 216
2015-10-08 11:00 | 214
2015-10-08 11:15 | 207
2015-10-08 11:30 | 215
2015-10-08 11:45 | 229
2015-10-08 12:00 | 224
2015-10-08 12:15 | 222
2015-10-08 12:30 | 215
2015-10-08 12:45 | 222
2015-10-08 13:00 | 244
2015-10-08 13:15 | 216
2015-10-08 13:30 | 235
2015-10-08 13:45 | 223
2015-10-08 14:00 | 243
2015-10-08 14:15 | 240
2015-10-08 14:30 | 238
2015-10-08 14:45 | 238
2015-10-08 15:00 | 251
2015-10-08 15:15 | 243
2015-10-08 15:30 | 228
2015-10-08 15:45 | 234
2015-10-08 16:00 | 237
2015-10-08 16:15 | 243
2015-10-08 16:30 | 229
2015-10-08 16:45 | 224
2015-10-08 17:00 | 234
2015-10-08 17:15 | 219
2015-10-08 17:30 | 236
2015-10-08 17:45 | 226
2015-10-08 18:00 | 209
2015-10-08 18:15 | 216
2015-10-08 18:30 | 205
2015-10-08 18:45 | 220
2015-10-08 19:00 | 202
2015-10-08 19:15 | 125
2015-10-08 19:30 | 122
2015-10-08 19:45 | 126
2015-10-08 20:00 | 118
2015-10-08 20:15 | 115
2015-10-08 20:30 | 113
2015-10-08 20:45 | 115
2015-10-08 21:00 | 107
2015-10-08 21:15 | 108
2015-10-08 21:30 | 104
2015-10-08 21:45 | 104
2015-10-08 22:00 | 112
2015-10-08 22:15 | 103
2015-10-08 22:30 | 103
2015-10-08 22:45 | 103
2015-10-08 23:00 | 104
2015-10-08 23:15 | 101
2015-10-08 23:30 | 112
2015-10-08 23:45 | 103
2015-10-09 | 106
2015-10-09 00:15 | 101
2015-10-09 00:30 | 102
2015-10-09 00:45 | 107
2015-10-09 01:00 | 104
2015-10-09 01:15 | 103
2015-10-09 01:30 | 106
2015-10-09 01:45 | 113
2015-10-09 02:00 | 102
2015-10-09 02:15 | 106
2015-10-09 02:30 | 99
2015-10-09 02:45 | 103
2015-10-09 03:00 | 111
2015-10-09 03:15 | 102
2015-10-09 03:30 | 107
2015-10-09 03:45 | 104
2015-10-09 04:00 | 105
2015-10-09 04:15 | 107
2015-10-09 04:30 | 103
2015-10-09 04:45 | 100
2015-10-09 05:00 | 104
2015-10-09 05:15 | 100
2015-10-09 05:30 | 106
2015-10-09 05:45 | 103
2015-10-09 06:00 | 108
2015-10-09 06:15 | 107
2015-10-09 06:30 | 106
2015-10-09 06:45 | 115
2015-10-09 07:00 | 112
2015-10-09 07:15 | 187
2015-10-09 07:30 | 174
2015-10-09 07:45 | 164
2015-10-09 08:00 | 168
2015-10-09 08:15 | 156
2015-10-09 08:30 | 164
2015-10-09 08:45 | 177
2015-10-09 09:00 | 198
2015-10-09 09:15 | 180
2015-10-09 09:30 | 193
2015-10-09 09:45 | 189
2015-10-09 10:00 | 189
2015-10-09 10:15 | 202
2015-10-09 10:30 | 212
2015-10-09 10:45 | 222
2015-10-09 11:00 | 212
2015-10-09 11:15 | 215
2015-10-09 11:30 | 216
2015-10-09 11:45 | 223
2015-10-09 12:00 | 230
2015-10-09 12:15 | 217
2015-10-09 12:30 | 224
2015-10-09 12:45 | 220
2015-10-09 13:00 | 222
2015-10-09 13:15 | 235
2015-10-09 13:30 | 214
2015-10-09 13:45 | 221
2015-10-09 14:00 | 225
2015-10-09 14:15 | 236
2015-10-09 14:30 | 224
2015-10-09 14:45 | 227
2015-10-09 15:00 | 223
2015-10-09 15:15 | 222
2015-10-09 15:30 | 245
2015-10-09 15:45 | 223
2015-10-09 16:00 | 236
2015-10-09 16:15 | 218
2015-10-09 16:30 | 225
2015-10-09 16:45 | 235
2015-10-09 17:00 | 219
2015-10-09 17:15 | 232
2015-10-09 17:30 | 225
2015-10-09 17:45 | 218
2015-10-09 18:00 | 214
2015-10-09 18:15 | 210
2015-10-09 18:30 | 205
2015-10-09 18:45 | 212
2015-10-09 19:00 | 197
2015-10-09 19:15 | 122
2015-10-09 19:30 | 125
2015-10-09 19:45 | 133
2015-10-09 20:00 | 128
2015-10-09 20:15 | 121
2015-10-09 20:30 | 120
2015-10-09 20:45 | 124
2015-10-09 21:00 | 127
2015-10-09 21:15 | 115
2015-10-09 21:30 | 108
2015-10-09 21:45 | 116
2015-10-09 22:00 | 119
2015-10-09 22:15 | 108
2015-10-09 22:30 | 111
2015-10-09 22:45 | 106
2015-10-09 23:00 | 111
2015-10-09 23:15 | 115
2015-10-09 23:30 | 110
2015-10-09 23:45 | 109
2015-10-10 | 110
2015-10-10 00:15 | 109
2015-10-10 00:30 | 114
2015-10-10 00:45 | 110
2015-10-10 01:00 | 108
2015-10-10 01:15 | 112
2015-10-10 01:30 | 108
2015-10-10 01:45 | 111
2015-10-10 02:00 | 117
2015-10-10 02:15 | 108
2015-10-10 02:30 | 101
2015-10-10 02:45 | 100
2015-10-10 03:00 | 98
2015-10-10 03:15 | 99
2015-10-10 03:30 | 100
2015-10-10 03:45 | 99
2015-10-10 04:00 | 101
2015-10-10 04:15 | 97
2015-10-10 04:30 | 98
2015-10-10 04:45 | 105
2015-10-10 05:00 | 103
2015-10-10 05:15 | 102
2015-10-10 05:30 | 96
2015-10-10 05:45 | 103
2015-10-10 06:00 | 103
2015-10-10 06:15 | 95
2015-10-10 06:30 | 99
2015-10-10 06:45 | 101
2015-10-10 07:00 | 101
2015-10-10 07:15 | 103
2015-10-10 07:30 | 97
2015-10-10 07:45 | 93
2015-10-10 08:00 | 97
2015-10-10 08:15 | 94
2015-10-10 08:30 | 95
2015-10-10 08:45 | 98
2015-10-10 09:00 | 100
2015-10-10 09:15 | 99
2015-10-10 09:30 | 95
2015-10-10 09:45 | 94
2015-10-10 10:00 | 94
2015-10-10 10:15 | 94
2015-10-10 10:30 | 99
2015-10-10 10:45 | 94
2015-10-10 11:00 | 97
2015-10-10 11:15 | 98
2015-10-10 11:30 | 96
2015-10-10 11:45 | 92
2015-10-10 12:00 | 95
2015-10-10 12:15 | 96
2015-10-10 12:30 | 98
2015-10-10 12:45 | 100
2015-10-10 13:00 | 97
2015-10-10 13:15 | 100
2015-10-10 13:30 | 108
2015-10-10 13:45 | 97
2015-10-10 14:00 | 101
2015-10-10 14:15 | 96
2015-10-10 14:30 | 100
2015-10-10 14:45 | 95
2015-10-10 15:00 | 110
2015-10-10 15:15 | 99
2015-10-10 15:30 | 101
2015-10-10 15:45 | 101
2015-10-10 16:00 | 100
2015-10-10 16:15 | 104
2015-10-10 16:30 | 101
2015-10-10 16:45 | 100
2015-10-10 17:00 | 99
2015-10-10 17:15 | 109
2015-10-10 17:30 | 107
2015-10-10 17:45 | 105
2015-10-10 18:00 | 104
2015-10-10 18:15 | 104
2015-10-10 18:30 | 107
2015-10-10 18:45 | 105
2015-10-10 19:00 | 105
2015-10-10 19:15 | 102
2015-10-10 19:30 | 109
2015-10-10 19:45 | 106
2015-10-10 20:00 | 104
2015-10-10 20:15 | 105
2015-10-10 20:30 | 104
2015-10-10 20:45 | 109
2015-10-10 21:00 | 106
2015-10-10 21:15 | 103
2015-10-10 21:30 | 103
2015-10-10 21:45 | 105
2015-10-10 22:00 | 106
2015-10-10 22:15 | 103
2015-10-10 22:30 | 102
2015-10-10 22:45 | 100
2015-10-10 23:00 | 105
2015-10-10 23:15 | 98
2015-10-10 23:30 | 100
2015-10-10 23:45 | 101
2015-10-11 | 98
2015-10-11 00:15 | 100
2015-10-11 00:30 | 98
2015-10-11 00:45 | 95
2015-10-11 01:00 | 95
2015-10-11 01:15 | 94
2015-10-11 01:30 | 95
2015-10-11 01:45 | 96
2015-10-11 02:00 | 95
2015-10-11 02:15 | 104
2015-10-11 02:30 | 96
2015-10-11 02:45 | 93
2015-10-11 03:00 | 94
2015-10-11 03:15 | 94
2015-10-11 03:30 | 93
2015-10-11 03:45 | 103
2015-10-11 04:00 | 97
2015-10-11 04:15 | 97
2015-10-11 04:30 | 94
2015-10-11 04:45 | 96
2015-10-11 05:00 | 105
2015-10-11 05:15 | 96
2015-10-11 05:30 | 96
2015-10-11 05:45 | 96
2015-10-11 06:00 | 100
2015-10-11 06:15 | 99
2015-10-11 06:30 | 98
2015-10-11 06:45 | 104
2015-10-11 07:00 | 104
2015-10-11 07:15 | 105
2015-10-11 07:30 | 101
2015-10-11 07:45 | 98
2015-10-11 08:00 | 105
2015-10-11 08:15 | 102
2015-10-11 08:30 | 101
2015-10-11 08:45 | 103
2015-10-11 09:00 | 96
2015-10-11 09:15 | 104
2015-10-11 09:30 | 95
2015-10-11 09:45 | 93
2015-10-11 10:00 | 92
2015-10-11 10:15 | 97
2015-10-11 10:30 | 91
2015-10-11 10:45 | 100
2015-10-11 11:00 | 96
2015-10-11 11:15 | 93
2015-10-11 11:30 | 96
2015-10-11 11:45 | 94
2015-10-11 12:00 | 98
2015-10-11 12:15 | 96
2015-10-11 12:30 | 93
2015-10-11 12:45 | 96
2015-10-11 13:00 | 98
2015-10-11 13:15 | 99
2015-10-11 13:30 | 97
2015-10-11 13:45 | 94
2015-10-11 14:00 | 98
2015-10-11 14:15 | 104
2015-10-11 14:30 | 98
2015-10-11 14:45 | 98
2015-10-11 15:00 | 101
2015-10-11 15:15 | 104
2015-10-11 15:30 | 100
2015-10-11 15:45 | 97
2015-10-11 16:00 | 99
2015-10-11 16:15 | 98
2015-10-11 16:30 | 103
2015-10-11 16:45 | 99
2015-10-11 17:00 | 105
2015-10-11 17:15 | 97
2015-10-11 17:30 | 104
2015-10-11 17:45 | 106
2015-10-11 18:00 | 104
2015-10-11 18:15 | 101
2015-10-11 18:30 | 98
2015-10-11 18:45 | 104
2015-10-11 19:00 | 102
2015-10-11 19:15 | 103
2015-10-11 19:30 | 100
2015-10-11 19:45 | 97
2015-10-11 20:00 | 106
2015-10-11 20:15 | 100
2015-10-11 20:30 | 100
2015-10-11 20:45 | 102
2015-10-11 21:00 | 99
2015-10-11 21:15 | 103
2015-10-11 21:30 | 96
2015-10-11 21:45 | 96
2015-10-11 22:00 | 95
2015-10-11 22:15 | 98
2015-10-11 22:30 | 96
2015-10-11 22:45 | 102
2015-10-11 23:00 | 100
2015-10-11 23:15 | 97
2015-10-11 23:30 | 102
2015-10-11 23:45 | 93
2015-10-12 | 103
2015-10-12 00:15 | 100
2015-10-12 00:30 | 96
2015-10-12 00:45 | 98
2015-10-12 01:00 | 102
2015-10-12 01:15 | 100
2015-10-12 01:30 | 99
2015-10-12 01:45 | 101
2015-10-12 02:00 | 96
2015-10-12 02:15 | 103
2015-10-12 02:30 | 96
2015-10-12 02:45 | 101
2015-10-12 03:00 | 93
2015-10-12 03:15 | 102
2015-10-12 03:30 | 98
2015-10-12 03:45 | 97
2015-10-12 04:00 | 98
2015-10-12 04:15 | 96
2015-10-12 04:30 | 100
2015-10-12 04:45 | 100
2015-10-12 05:00 | 96
2015-10-12 05:15 | 96
2015-10-12 05:30 | 99
2015-10-12 05:45 | 95
2015-10-12 06:00 | 101
2015-10-12 06:15 | 103
2015-10-12 06:30 | 100
2015-10-12 06:45 | 98
2015-10-12 07:00 | 98
2015-10-12 07:15 | 204
2015-10-12 07:30 | 188
2015-10-12 07:45 | 163
2015-10-12 08:00 | 163
2015-10-12 08:15 | 163
2015-10-12 08:30 | 184
2015-10-12 08:45 | 195
2015-10-12 09:00 | 204
2015-10-12 09:15 | 205
2015-10-12 09:30 | 208
2015-10-12 09:45 | 220
2015-10-12 10:00 | 227
2015-10-12 10:15 | 222
2015-10-12 10:30 | 215
2015-10-12 10:45 | 217
2015-10-12 11:00 | 208
2015-10-12 11:15 | 221
2015-10-12 11:30 | 212
2015-10-12 11:45 | 216
2015-10-12 12:00 | 233
2015-10-12 12:15 | 238
2015-10-12 12:30 | 241
2015-10-12 12:45 | 224
2015-10-12 13:00 | 238
2015-10-12 13:15 | 253
2015-10-12 13:30 | 254
2015-10-12 13:45 | 245
2015-10-12 14:00 | 251
2015-10-12 14:15 | 245
2015-10-12 14:30 | 251
2015-10-12 14:45 | 243
2015-10-12 15:00 | 265
2015-10-12 15:15 | 254
2015-10-12 15:30 | 268
2015-10-12 15:45 | 254
2015-10-12 16:00 | 269
2015-10-12 16:15 | 256
2015-10-12 16:30 | 257
2015-10-12 16:45 | 253
2015-10-12 17:00 | 253
2015-10-12 17:15 | 255
2015-10-12 17:30 | 247
2015-10-12 17:45 | 262
2015-10-12 18:00 | 241
2015-10-12 18:15 | 244
2015-10-12 18:30 | 229
2015-10-12 18:45 | 222
2015-10-12 19:00 | 220
2015-10-12 19:15 | 138
2015-10-12 19:30 | 124
2015-10-12 19:45 | 124
2015-10-12 20:00 | 116
2015-10-12 20:15 | 110
2015-10-12 20:30 | 114
2015-10-12 20:45 | 111
2015-10-12 21:00 | 121
2015-10-12 21:15 | 107
2015-10-12 21:30 | 105
2015-10-12 21:45 | 101
2015-10-12 22:00 | 108
2015-10-12 22:15 | 108
2015-10-12 22:30 | 106
2015-10-12 22:45 | 102
2015-10-12 23:00 | 98
2015-10-12 23:15 | 105
2015-10-12 23:30 | 105
2015-10-12 23:45 | 102
2015-10-13 | 104
2015-10-13 00:15 | 98
2015-10-13 00:30 | 110
2015-10-13 00:45 | 102
2015-10-13 01:00 | 105
2015-10-13 01:15 | 102
2015-10-13 01:30 | 103
2015-10-13 01:45 | 103
2015-10-13 02:00 | 101
2015-10-13 02:15 | 96
2015-10-13 02:30 | 100
2015-10-13 02:45 | 105
2015-10-13 03:00 | 99
2015-10-13 03:15 | 99
2015-10-13 03:30 | 98
2015-10-13 03:45 | 103
2015-10-13 04:00 | 101
2015-10-13 04:15 | 99
2015-10-13 04:30 | 97
2015-10-13 04:45 | 100
2015-10-13 05:00 | 98
2015-10-13 05:15 | 102
2015-10-13 05:30 | 103
2015-10-13 05:45 | 101
2015-10-13 06:00 | 98
2015-10-13 06:15 | 100
2015-10-13 06:30 | 104
2015-10-13 06:45 | 106
2015-10-13 07:00 | 105
2015-10-13 07:15 | 220
2015-10-13 07:30 | 211
2015-10-13 07:45 | 172
2015-10-13 08:00 | 174
2015-10-13 08:15 | 172
2015-10-13 08:30 | 197
2015-10-13 08:45 | 215
2015-10-13 09:00 | 193
2015-10-13 09:15 | 192
2015-10-13 09:30 | 213
2015-10-13 09:45 | 217
2015-10-13 10:00 | 213
2015-10-13 10:15 | 219
2015-10-13 10:30 | 220
2015-10-13 10:45 | 224
2015-10-13 11:00 | 230
2015-10-13 11:15 | 247
2015-10-13 11:30 | 229
2015-10-13 11:45 | 243
2015-10-13 12:00 | 239
2015-10-13 12:15 | 259
2015-10-13 12:30 | 252
2015-10-13 12:45 | 256
2015-10-13 13:00 | 252
2015-10-13 13:15 | 264
2015-10-13 13:30 | 246
2015-10-13 13:45 | 256
2015-10-13 14:00 | 254
2015-10-13 14:15 | 265
2015-10-13 14:30 | 254
2015-10-13 14:45 | 250
2015-10-13 15:00 | 260
2015-10-13 15:15 | 257
2015-10-13 15:30 | 253
2015-10-13 15:45 | 240
2015-10-13 16:00 | 247
2015-10-13 16:15 | 247
2015-10-13 16:30 | 251
2015-10-13 16:45 | 239
2015-10-13 17:00 | 246
2015-10-13 17:15 | 243
2015-10-13 17:30 | 246
2015-10-13 17:45 | 244
2015-10-13 18:00 | 229
2015-10-13 18:15 | 229
2015-10-13 18:30 | 226
2015-10-13 18:45 | 216
2015-10-13 19:00 | 217
2015-10-13 19:15 | 130
2015-10-13 19:30 | 126
2015-10-13 19:45 | 118
2015-10-13 20:00 | 123
2015-10-13 20:15 | 122
2015-10-13 20:30 | 113
2015-10-13 20:45 | 114
2015-10-13 21:00 | 107
2015-10-13 21:15 | 112
2015-10-13 21:30 | 104
2015-10-13 21:45 | 106
2015-10-13 22:00 | 100
2015-10-13 22:15 | 103
2015-10-13 22:30 | 111
2015-10-13 22:45 | 100
2015-10-13 23:00 | 104
2015-10-13 23:15 | 102
2015-10-13 23:30 | 104
2015-10-13 23:45 | 103
2015-10-14 | 105
2015-10-14 00:15 | 99
2015-10-14 00:30 | 105
2015-10-14 00:45 | 107
2015-10-14 01:00 | 102
2015-10-14 01:15 | 104
2015-10-14 01:30 | 100
2015-10-14 01:45 | 101
2015-10-14 02:00 | 103
2015-10-14 02:15 | 109
2015-10-14 02:30 | 101
2015-10-14 02:45 | 107
2015-10-14 03:00 | 100
2015-10-14 03:15 | 107
2015-10-14 03:30 | 104
2015-10-14 03:45 | 101
2015-10-14 04:00 | 99
2015-10-14 04:15 | 109
2015-10-14 04:30 | 104
2015-10-14 04:45 | 103
2015-10-14 05:00 | 102
2015-10-14 05:15 | 105
2015-10-14 05:30 | 105
2015-10-14 05:45 | 104
2015-10-14 06:00 | 101
2015-10-14 06:15 | 104
2015-10-14 06:30 | 101
2015-10-14 06:45 | 107
2015-10-14 07:00 | 114
2015-10-14 07:15 | 234
2015-10-14 07:30 | 207
2015-10-14 07:45 | 190
2015-10-14 08:00 | 175
2015-10-14 08:15 | 194
2015-10-14 08:30 | 185
2015-10-14 08:45 | 186
2015-10-14 09:00 | 209
2015-10-14 09:15 | 215
2015-10-14 09:30 | 213
2015-10-14 09:45 | 215
2015-10-14 10:00 | 212
2015-10-14 10:15 | 220
2015-10-14 10:30 | 216
2015-10-14 10:45 | 237
2015-10-14 11:00 | 222
2015-10-14 11:15 | 222
2015-10-14 11:30 | 236
2015-10-14 11:45 | 234
2015-10-14 12:00 | 244
2015-10-14 12:15 | 230
2015-10-14 12:30 | 235
2015-10-14 12:45 | 236
2015-10-14 13:00 | 231
2015-10-14 13:15 | 228
2015-10-14 13:30 | 235
2015-10-14 13:45 | 238
2015-10-14 14:00 | 237
2015-10-14 14:15 | 233
2015-10-14 14:30 | 233
2015-10-14 14:45 | 234
2015-10-14 15:00 | 255
2015-10-14 15:15 | 239
2015-10-14 15:30 | 239
2015-10-14 15:45 | 234
2015-10-14 16:00 | 238
2015-10-14 16:15 | 250
2015-10-14 16:30 | 242
2015-10-14 16:45 | 236
2015-10-14 17:00 | 233
2015-10-14 17:15 | 225
2015-10-14 17:30 | 225
2015-10-14 17:45 | 227
2015-10-14 18:00 | 227
2015-10-14 18:15 | 218
2015-10-14 18:30 | 216
2015-10-14 18:45 | 214
2015-10-14 19:00 | 209
2015-10-14 19:15 | 125
2015-10-14 19:30 | 126
2015-10-14 19:45 | 122
2015-10-14 20:00 | 129
2015-10-14 20:15 | 126
2015-10-14 20:30 | 123
2015-10-14 20:45 | 118
2015-10-14 21:00 | 110
2015-10-14 21:15 | 110
2015-10-14 21:30 | 106
2015-10-14 21:45 | 103
2015-10-14 22:00 | 101
2015-10-14 22:15 | 103
2015-10-14 22:30 | 107
2015-10-14 22:45 | 102
2015-10-14 23:00 | 105
2015-10-14 23:15 | 98
2015-10-14 23:30 | 107
2015-10-14 23:45 | 103
2015-10-15 | 102
2015-10-15 00:15 | 98
2015-10-15 00:30 | 100
2015-10-15 00:45 | 101
2015-10-15 01:00 | 110
2015-10-15 01:15 | 99
2015-10-15 01:30 | 101
2015-10-15 01:45 | 97
2015-10-15 02:00 | 104
2015-10-15 02:15 | 102
2015-10-15 02:30 | 99
2015-10-15 02:45 | 96
2015-10-15 03:00 | 105
2015-10-15 03:15 | 103
2015-10-15 03:30 | 99
2015-10-15 03:45 | 104
2015-10-15 04:00 | 94
2015-10-15 04:15 | 100
2015-10-15 04:30 | 105
2015-10-15 04:45 | 100
2015-10-15 05:00 | 99
2015-10-15 05:15 | 100
2015-10-15 05:30 | 100
2015-10-15 05:45 | 103
2015-10-15 06:00 | 108
2015-10-15 06:15 | 99
2015-10-15 06:30 | 107
2015-10-15 06:45 | 97
2015-10-15 07:00 | 102
2015-10-15 07:15 | 243
2015-10-15 07:30 | 229
2015-10-15 07:45 | 215
2015-10-15 08:00 | 218
2015-10-15 08:15 | 216
2015-10-15 08:30 | 212
2015-10-15 08:45 | 202
2015-10-15 09:00 | 193
2015-10-15 09:15 | 192
2015-10-15 09:30 | 213
2015-10-15 09:45 | 213
2015-10-15 10:00 | 199
2015-10-15 10:15 | 203
2015-10-15 10:30 | 222
2015-10-15 10:45 | 216
2015-10-15 11:00 | 207
2015-10-15 11:15 | 211
2015-10-15 11:30 | 232
2015-10-15 11:45 | 220
2015-10-15 12:00 | 209
2015-10-15 12:15 | 210
2015-10-15 12:30 | 211
2015-10-15 12:45 | 216
2015-10-15 13:00 | 230
2015-10-15 13:15 | 203
2015-10-15 13:30 | 210
2015-10-15 13:45 | 203
2015-10-15 14:00 | 211
2015-10-15 14:15 | 218
2015-10-15 14:30 | 223
2015-10-15 14:45 | 213
2015-10-15 15:00 | 221
2015-10-15 15:15 | 212
2015-10-15 15:30 | 209
2015-10-15 15:45 | 211
2015-10-15 16:00 | 200
2015-10-15 16:15 | 208
2015-10-15 16:30 | 208
2015-10-15 16:45 | 203
2015-10-15 17:00 | 203
2015-10-15 17:15 | 199
2015-10-15 17:30 | 219
2015-10-15 17:45 | 230
2015-10-15 18:00 | 211
2015-10-15 18:15 | 222
2015-10-15 18:30 | 211
2015-10-15 18:45 | 212
2015-10-15 19:00 | 202
2015-10-15 19:15 | 131
2015-10-15 19:30 | 134
2015-10-15 19:45 | 128
2015-10-15 20:00 | 129
2015-10-15 20:15 | 124
2015-10-15 20:30 | 126
2015-10-15 20:45 | 131
2015-10-15 21:00 | 124
2015-10-15 21:15 | 115
2015-10-15 21:30 | 107
2015-10-15 21:45 | 112
2015-10-15 22:00 | 120
2015-10-15 22:15 | 115
2015-10-15 22:30 | 115
2015-10-15 22:45 | 115
2015-10-15 23:00 | 111
2015-10-15 23:15 | 126
2015-10-15 23:30 | 112
2015-10-15 23:45 | 113
2015-10-16 | 107
2015-10-16 00:15 | 113
2015-10-16 00:30 | 111
2015-10-16 00:45 | 104
2015-10-16 01:00 | 97
2015-10-16 01:15 | 94
2015-10-16 01:30 | 99
2015-10-16 01:45 | 97
2015-10-16 02:00 | 98
2015-10-16 02:15 | 90
2015-10-16 02:30 | 103
2015-10-16 02:45 | 100
2015-10-16 03:00 | 96
2015-10-16 03:15 | 96
2015-10-16 03:30 | 92
2015-10-16 03:45 | 97
2015-10-16 04:00 | 101
2015-10-16 04:15 | 93
2015-10-16 04:30 | 94
2015-10-16 04:45 | 97
2015-10-16 05:00 | 101
2015-10-16 05:15 | 95
2015-10-16 05:30 | 97
2015-10-16 05:45 | 90
2015-10-16 06:00 | 103
2015-10-16 06:15 | 98
2015-10-16 06:30 | 98
2015-10-16 06:45 | 101
2015-10-16 07:00 | 98
2015-10-16 07:15 | 209
2015-10-16 07:30 | 201
2015-10-16 07:45 | 193
2015-10-16 08:00 | 181
2015-10-16 08:15 | 173
2015-10-16 08:30 | 172
2015-10-16 08:45 | 179
2015-10-16 09:00 | 186
2015-10-16 09:15 | 175
2015-10-16 09:30 | 188
2015-10-16 09:45 | 184
2015-10-16 10:00 | 186
2015-10-16 10:15 | 197
2015-10-16 10:30 | 210
2015-10-16 10:45 | 195
2015-10-16 11:00 | 202
2015-10-16 11:15 | 206
2015-10-16 11:30 | 195
2015-10-16 11:45 | 205
2015-10-16 12:00 | 201
2015-10-16 12:15 | 198
2015-10-16 12:30 | 191
2015-10-16 12:45 | 207
2015-10-16 13:00 | 190
2015-10-16 13:15 | 190
2015-10-16 13:30 | 194
2015-10-16 13:45 | 211
2015-10-16 14:00 | 200
2015-10-16 14:15 | 200
2015-10-16 14:30 | 204
2015-10-16 14:45 | 206
2015-10-16 15:00 | 210
2015-10-16 15:15 | 226
2015-10-16 15:30 | 209
2015-10-16 15:45 | 210
2015-10-16 16:00 | 209
2015-10-16 16:15 | 211
2015-10-16 16:30 | 224
2015-10-16 16:45 | 203
2015-10-16 17:00 | 211
2015-10-16 17:15 | 209
2015-10-16 17:30 | 216
2015-10-16 17:45 | 219
2015-10-16 18:00 | 198
2015-10-16 18:15 | 213
2015-10-16 18:30 | 206
2015-10-16 18:45 | 221
2015-10-16 19:00 | 215
2015-10-16 19:15 | 118
2015-10-16 19:30 | 122
2015-10-16 19:45 | 119
2015-10-16 20:00 | 115
2015-10-16 20:15 | 135
2015-10-16 20:30 | 117
2015-10-16 20:45 | 116
2015-10-16 21:00 | 121
2015-10-16 21:15 | 112
2015-10-16 21:30 | 102
2015-10-16 21:45 | 102
2015-10-16 22:00 | 102
2015-10-16 22:15 | 105
2015-10-16 22:30 | 111
2015-10-16 22:45 | 99
2015-10-16 23:00 | 102
2015-10-16 23:15 | 97
2015-10-16 23:30 | 104
2015-10-16 23:45 | 108
2015-10-17 | 98
2015-10-17 00:15 | 109
2015-10-17 00:30 | 99
2015-10-17 00:45 | 101
2015-10-17 01:00 | 99
2015-10-17 01:15 | 107
2015-10-17 01:30 | 101
2015-10-17 01:45 | 100
2015-10-17 02:00 | 100
2015-10-17 02:15 | 102
2015-10-17 02:30 | 109
2015-10-17 02:45 | 99
2015-10-17 03:00 | 101
2015-10-17 03:15 | 97
2015-10-17 03:30 | 109
2015-10-17 03:45 | 100
2015-10-17 04:00 | 99
2015-10-17 04:15 | 100
2015-10-17 04:30 | 101
2015-10-17 04:45 | 106
2015-10-17 05:00 | 100
2015-10-17 05:15 | 99
2015-10-17 05:30 | 97
2015-10-17 05:45 | 101
2015-10-17 06:00 | 107
2015-10-17 06:15 | 103
2015-10-17 06:30 | 110
2015-10-17 06:45 | 99
2015-10-17 07:00 | 105
2015-10-17 07:15 | 110
2015-10-17 07:30 | 101
2015-10-17 07:45 | 96
2015-10-17 08:00 | 98
2015-10-17 08:15 | 103
2015-10-17 08:30 | 99
2015-10-17 08:45 | 115
2015-10-17 09:00 | 105
2015-10-17 09:15 | 101
2015-10-17 09:30 | 103
2015-10-17 09:45 | 102
2015-10-17 10:00 | 100
2015-10-17 10:15 | 103
2015-10-17 10:30 | 112
2015-10-17 10:45 | 106
2015-10-17 11:00 | 106
2015-10-17 11:15 | 101
2015-10-17 11:30 | 111
2015-10-17 11:45 | 112
2015-10-17 12:00 | 104
2015-10-17 12:15 | 105
2015-10-17 12:30 | 101
2015-10-17 12:45 | 101
2015-10-17 13:00 | 110
2015-10-17 13:15 | 99
2015-10-17 13:30 | 103
2015-10-17 13:45 | 101
2015-10-17 14:00 | 110
2015-10-17 14:15 | 105
2015-10-17 14:30 | 102
2015-10-17 14:45 | 100
2015-10-17 15:00 | 103
2015-10-17 15:15 | 110
2015-10-17 15:30 | 100
2015-10-17 15:45 | 104
2015-10-17 16:00 | 99
2015-10-17 16:15 | 112
2015-10-17 16:30 | 102
2015-10-17 16:45 | 103
2015-10-17 17:00 | 103
2015-10-17 17:15 | 111
2015-10-17 17:30 | 116
2015-10-17 17:45 | 107
2015-10-17 18:00 | 107
2015-10-17 18:15 | 107
2015-10-17 18:30 | 114
2015-10-17 18:45 | 108
2015-10-17 19:00 | 110
2015-10-17 19:15 | 104
2015-10-17 19:30 | 113
2015-10-17 19:45 | 109
2015-10-17 20:00 | 109
2015-10-17 20:15 | 106
2015-10-17 20:30 | 108
2015-10-17 20:45 | 113
2015-10-17 21:00 | 107
2015-10-17 21:15 | 106
2015-10-17 21:30 | 99
2015-10-17 21:45 | 104
2015-10-17 22:00 | 104
2015-10-17 22:15 | 102
2015-10-17 22:30 | 96
2015-10-17 22:45 | 101
2015-10-17 23:00 | 96
2015-10-17 23:15 | 105
2015-10-17 23:30 | 104
2015-10-17 23:45 | 101
2015-10-18 | 101
2015-10-18 00:15 | 99
2015-10-18 00:30 | 104
2015-10-18 00:45 | 96
2015-10-18 01:00 | 92
2015-10-18 01:15 | 91
2015-10-18 01:30 | 101
2015-10-18 01:45 | 91
2015-10-18 02:00 | 96
2015-10-18 02:15 | 89
2015-10-18 02:30 | 101
2015-10-18 02:45 | 96
2015-10-18 03:00 | 93
2015-10-18 03:15 | 90
2015-10-18 03:30 | 95
2015-10-18 03:45 | 96
2015-10-18 04:00 | 96
2015-10-18 04:15 | 92
2015-10-18 04:30 | 89
2015-10-18 04:45 | 94
2015-10-18 05:00 | 97
2015-10-18 05:15 | 95
2015-10-18 05:30 | 91
2015-10-18 05:45 | 101
2015-10-18 06:00 | 98
2015-10-18 06:15 | 107
2015-10-18 06:30 | 110
2015-10-18 06:45 | 108
2015-10-18 07:00 | 111
2015-10-18 07:15 | 104
2015-10-18 07:30 | 101
2015-10-18 07:45 | 102
2015-10-18 08:00 | 97
2015-10-18 08:15 | 108
2015-10-18 08:30 | 98
2015-10-18 08:45 | 99
2015-10-18 09:00 | 99
2015-10-18 09:15 | 104
2015-10-18 09:30 | 97
2015-10-18 09:45 | 101
2015-10-18 10:00 | 94
2015-10-18 10:15 | 105
2015-10-18 10:30 | 99
2015-10-18 10:45 | 99
2015-10-18 11:00 | 97
2015-10-18 11:15 | 96
2015-10-18 11:30 | 95
2015-10-18 11:45 | 106
2015-10-18 12:00 | 101
2015-10-18 12:15 | 96
2015-10-18 12:30 | 96
2015-10-18 12:45 | 101
2015-10-18 13:00 | 100
2015-10-18 13:15 | 99
2015-10-18 13:30 | 96
2015-10-18 13:45 | 102
2015-10-18 14:00 | 101
2015-10-18 14:15 | 98
2015-10-18 14:30 | 100
2015-10-18 14:45 | 101
2015-10-18 15:00 | 108
2015-10-18 15:15 | 100
2015-10-18 15:30 | 100
2015-10-18 15:45 | 94
2015-10-18 16:00 | 101
2015-10-18 16:15 | 95
2015-10-18 16:30 | 101
2015-10-18 16:45 | 101
2015-10-18 17:00 | 103
2015-10-18 17:15 | 101
2015-10-18 17:30 | 102
2015-10-18 17:45 | 111
2015-10-18 18:00 | 110
2015-10-18 18:15 | 113
2015-10-18 18:30 | 107
2015-10-18 18:45 | 117
2015-10-18 19:00 | 111
2015-10-18 19:15 | 111
2015-10-18 19:30 | 108
2015-10-18 19:45 | 103
2015-10-18 20:00 | 105
2015-10-18 20:15 | 107
2015-10-18 20:30 | 104
2015-10-18 20:45 | 104
2015-10-18 21:00 | 111
2015-10-18 21:15 | 104
2015-10-18 21:30 | 98
2015-10-18 21:45 | 95
2015-10-18 22:00 | 92
2015-10-18 22:15 | 99
2015-10-18 22:30 | 98
2015-10-18 22:45 | 95
2015-10-18 23:00 | 95
2015-10-18 23:15 | 95
2015-10-18 23:30 | 95
2015-10-18 23:45 | 97
2015-10-19 | 101
2015-10-19 00:15 | 98
2015-10-19 00:30 | 96
2015-10-19 00:45 | 91
2015-10-19 01:00 | 97
2015-10-19 01:15 | 102
2015-10-19 01:30 | 94
2015-10-19 01:45 | 95
2015-10-19 02:00 | 97
2015-10-19 02:15 | 105
2015-10-19 02:30 | 99
2015-10-19 02:45 | 94
2015-10-19 03:00 | 98
2015-10-19 03:15 | 98
2015-10-19 03:30 | 97
2015-10-19 03:45 | 97
2015-10-19 04:00 | 105
2015-10-19 04:15 | 96
2015-10-19 04:30 | 98
2015-10-19 04:45 | 91
2015-10-19 05:00 | 98
2015-10-19 05:15 | 97
2015-10-19 05:30 | 97
2015-10-19 05:45 | 95
2015-10-19 06:00 | 98
2015-10-19 06:15 | 100
2015-10-19 06:30 | 98
2015-10-19 06:45 | 95
2015-10-19 07:00 | 100
2015-10-19 07:15 | 214
2015-10-19 07:30 | 196
2015-10-19 07:45 | 189
2015-10-19 08:00 | 187
2015-10-19 08:15 | 181
2015-10-19 08:30 | 177
2015-10-19 08:45 | 177
2015-10-19 09:00 | 173
2015-10-19 09:15 | 176
2015-10-19 09:30 | 183
2015-10-19 09:45 | 178
2015-10-19 10:00 | 179
2015-10-19 10:15 | 177
2015-10-19 10:30 | 178
2015-10-19 10:45 | 184
2015-10-19 11:00 | 171
2015-10-19 11:15 | 180
2015-10-19 11:30 | 178
2015-10-19 11:45 | 188
2015-10-19 12:00 | 176
2015-10-19 12:15 | 181
2015-10-19 12:30 | 176
2015-10-19 12:45 | 179
2015-10-19 13:00 | 193
2015-10-19 13:15 | 193
2015-10-19 13:30 | 190
2015-10-19 13:45 | 186
2015-10-19 14:00 | 194
2015-10-19 14:15 | 202
2015-10-19 14:30 | 193
2015-10-19 14:45 | 200
2015-10-19 15:00 | 203
2015-10-19 15:15 | 208
2015-10-19 15:30 | 199
2015-10-19 15:45 | 223
2015-10-19 16:00 | 210
2015-10-19 16:15 | 209
2015-10-19 16:30 | 208
2015-10-19 16:45 | 204
2015-10-19 17:00 | 190
2015-10-19 17:15 | 203
2015-10-19 17:30 | 189
2015-10-19 17:45 | 191
2015-10-19 18:00 | 183
2015-10-19 18:15 | 190
2015-10-19 18:30 | 196
2015-10-19 18:45 | 182
2015-10-19 19:00 | 178
2015-10-19 19:15 | 118
2015-10-19 19:30 | 127
2015-10-19 19:45 | 132
2015-10-19 20:00 | 125
2015-10-19 20:15 | 119
2015-10-19 20:30 | 120
2015-10-19 20:45 | 132
2015-10-19 21:00 | 122
2015-10-19 21:15 | 116
2015-10-19 21:30 | 108
2015-10-19 21:45 | 111
2015-10-19 22:00 | 122
2015-10-19 22:15 | 108
2015-10-19 22:30 | 109
2015-10-19 22:45 | 109
2015-10-19 23:00 | 121
2015-10-19 23:15 | 113
2015-10-19 23:30 | 110
2015-10-19 23:45 | 107
2015-10-20 | 105
2015-10-20 00:15 | 108
2015-10-20 00:30 | 105
2015-10-20 00:45 | 107
2015-10-20 01:00 | 103
2015-10-20 01:15 | 102
2015-10-20 01:30 | 111
2015-10-20 01:45 | 104
2015-10-20 02:00 | 110
2015-10-20 02:15 | 107
2015-10-20 02:30 | 108
2015-10-20 02:45 | 107
2015-10-20 03:00 | 104
2015-10-20 03:15 | 102
2015-10-20 03:30 | 99
2015-10-20 03:45 | 105
2015-10-20 04:00 | 108
2015-10-20 04:15 | 102
2015-10-20 04:30 | 104
2015-10-20 04:45 | 103
2015-10-20 05:00 | 107
2015-10-20 05:15 | 105
2015-10-20 05:30 | 101
2015-10-20 05:45 | 105
2015-10-20 06:00 | 103
2015-10-20 06:15 | 112
2015-10-20 06:30 | 103
2015-10-20 06:45 | 104
2015-10-20 07:00 | 107
2015-10-20 07:15 | 151
2015-10-20 07:30 | 140
2015-10-20 07:45 | 144
2015-10-20 08:00 | 150
2015-10-20 08:15 | 164
2015-10-20 08:30 | 147
2015-10-20 08:45 | 152
2015-10-20 09:00 | 159
2015-10-20 09:15 | 172
2015-10-20 09:30 | 175
2015-10-20 09:45 | 175
2015-10-20 10:00 | 188
2015-10-20 10:15 | 173
2015-10-20 10:30 | 166
2015-10-20 10:45 | 181
2015-10-20 11:00 | 194
2015-10-20 11:15 | 175
2015-10-20 11:30 | 185
2015-10-20 11:45 | 181
2015-10-20 12:00 | 192
2015-10-20 12:15 | 189
2015-10-20 12:30 | 184
2015-10-20 12:45 | 181
2015-10-20 13:00 | 189
2015-10-20 13:15 | 208
2015-10-20 13:30 | 184
2015-10-20 13:45 | 190
2015-10-20 14:00 | 186
2015-10-20 14:15 | 188
2015-10-20 14:30 | 208
2015-10-20 14:45 | 186
2015-10-20 15:00 | 194
2015-10-20 15:15 | 202
2015-10-20 15:30 | 213
2015-10-20 15:45 | 206
2015-10-20 16:00 | 202
2015-10-20 16:15 | 199
2015-10-20 16:30 | 192
2015-10-20 16:45 | 209
2015-10-20 17:00 | 193
2015-10-20 17:15 | 198
2015-10-20 17:30 | 196
2015-10-20 17:45 | 200
2015-10-20 18:00 | 193
2015-10-20 18:15 | 188
2015-10-20 18:30 | 191
2015-10-20 18:45 | 184
2015-10-20 19:00 | 193
2015-10-20 19:15 | 118
2015-10-20 19:30 | 118
2015-10-20 19:45 | 119
2015-10-20 20:00 | 125
2015-10-20 20:15 | 126
2015-10-20 20:30 | 122
2015-10-20 20:45 | 113
2015-10-20 21:00 | 116
2015-10-20 21:15 | 113
2015-10-20 21:30 | 103
2015-10-20 21:45 | 107
2015-10-20 22:00 | 119
2015-10-20 22:15 | 112
2015-10-20 22:30 | 111
2015-10-20 22:45 | 109
2015-10-20 23:00 | 114
2015-10-20 23:15 | 114
2015-10-20 23:30 | 111
2015-10-20 23:45 | 109
2015-10-21 | 113
2015-10-21 00:15 | 114
2015-10-21 00:30 | 105
2015-10-21 00:45 | 101
2015-10-21 01:00 | 100
2015-10-21 01:15 | 104
2015-10-21 01:30 | 102
2015-10-21 01:45 | 109
2015-10-21 02:00 | 103
2015-10-21 02:15 | 103
2015-10-21 02:30 | 103
2015-10-21 02:45 | 104
2015-10-21 03:00 | 108
2015-10-21 03:15 | 102
2015-10-21 03:30 | 101
2015-10-21 03:45 | 108
2015-10-21 04:00 | 104
2015-10-21 04:15 | 103
2015-10-21 04:30 | 101
2015-10-21 04:45 | 105
2015-10-21 05:00 | 102
2015-10-21 05:15 | 111
2015-10-21 05:30 | 105
2015-10-21 05:45 | 102
2015-10-21 06:00 | 99
2015-10-21 06:15 | 105
2015-10-21 06:30 | 102
2015-10-21 06:45 | 113
2015-10-21 07:00 | 109
2015-10-21 07:15 | 150
2015-10-21 07:30 | 129
2015-10-21 07:45 | 141
2015-10-21 08:00 | 151
2015-10-21 08:15 | 148
2015-10-21 08:30 | 144
2015-10-21 08:45 | 170
2015-10-21 09:00 | 151
2015-10-21 09:15 | 166
2015-10-21 09:30 | 159
2015-10-21 09:45 | 177
2015-10-21 10:00 | 174
2015-10-21 10:15 | 175
2015-10-21 10:30 | 192
2015-10-21 10:45 | 178
2015-10-21 11:00 | 183
2015-10-21 11:15 | 176
2015-10-21 11:30 | 179
2015-10-21 11:45 | 187
2015-10-21 12:00 | 175
2015-10-21 12:15 | 188
2015-10-21 12:30 | 180
2015-10-21 12:45 | 173
2015-10-21 13:00 | 190
2015-10-21 13:15 | 178
2015-10-21 13:30 | 175
2015-10-21 13:45 | 187
2015-10-21 14:00 | 186
2015-10-21 14:15 | 189
2015-10-21 14:30 | 207
2015-10-21 14:45 | 194
2015-10-21 15:00 | 208
2015-10-21 15:15 | 203
2015-10-21 15:30 | 202
2015-10-21 15:45 | 216
2015-10-21 16:00 | 202
2015-10-21 16:15 | 201
2015-10-21 16:30 | 210
2015-10-21 16:45 | 217
2015-10-21 17:00 | 196
2015-10-21 17:15 | 206
2015-10-21 17:30 | 197
2015-10-21 17:45 | 189
2015-10-21 18:00 | 203
2015-10-21 18:15 | 184
2015-10-21 18:30 | 191
2015-10-21 18:45 | 187
2015-10-21 19:00 | 195
2015-10-21 19:15 | 121
2015-10-21 19:30 | 121
2015-10-21 19:45 | 120
2015-10-21 20:00 | 118
2015-10-21 20:15 | 130
2015-10-21 20:30 | 116
2015-10-21 20:45 | 119
2015-10-21 21:00 | 112
2015-10-21 21:15 | 119
2015-10-21 21:30 | 106
2015-10-21 21:45 | 106
2015-10-21 22:00 | 101
2015-10-21 22:15 | 106
2015-10-21 22:30 | 110
2015-10-21 22:45 | 102
2015-10-21 23:00 | 105
2015-10-21 23:15 | 100
2015-10-21 23:30 | 104
2015-10-21 23:45 | 105
2015-10-22 | 101
2015-10-22 00:15 | 102
2015-10-22 00:30 | 99
2015-10-22 00:45 | 104
2015-10-22 01:00 | 108
2015-10-22 01:15 | 105
2015-10-22 01:30 | 99
2015-10-22 01:45 | 100
2015-10-22 02:00 | 99
2015-10-22 02:15 | 109
2015-10-22 02:30 | 103
2015-10-22 02:45 | 102
2015-10-22 03:00 | 100
2015-10-22 03:15 | 102
2015-10-22 03:30 | 103
2015-10-22 03:45 | 98
2015-10-22 04:00 | 106
2015-10-22 04:15 | 105
2015-10-22 04:30 | 101
2015-10-22 04:45 | 101
2015-10-22 05:00 | 111
2015-10-22 05:15 | 104
2015-10-22 05:30 | 104
2015-10-22 05:45 | 98
2015-10-22 06:00 | 109
2015-10-22 06:15 | 106
2015-10-22 06:30 | 103
2015-10-22 06:45 | 105
2015-10-22 07:00 | 106
2015-10-22 07:15 | 153
2015-10-22 07:30 | 156
2015-10-22 07:45 | 148
2015-10-22 08:00 | 158
2015-10-22 08:15 | 151
2015-10-22 08:30 | 164
2015-10-22 08:45 | 158
2015-10-22 09:00 | 154
2015-10-22 09:15 | 163
2015-10-22 09:30 | 171
2015-10-22 09:45 | 171
2015-10-22 10:00 | 166
2015-10-22 10:15 | 176
2015-10-22 10:30 | 174
2015-10-22 10:45 | 179
2015-10-22 11:00 | 193
2015-10-22 11:15 | 187
2015-10-22 11:30 | 175
2015-10-22 11:45 | 179
2015-10-22 12:00 | 186
2015-10-22 12:15 | 191
2015-10-22 12:30 | 186
2015-10-22 12:45 | 179
2015-10-22 13:00 | 192
2015-10-22 13:15 | 192
2015-10-22 13:30 | 190
2015-10-22 13:45 | 194
2015-10-22 14:00 | 188
2015-10-22 14:15 | 205
2015-10-22 14:30 | 195
2015-10-22 14:45 | 203
2015-10-22 15:00 | 198
2015-10-22 15:15 | 204
2015-10-22 15:30 | 211
2015-10-22 15:45 | 197
2015-10-22 16:00 | 199
2015-10-22 16:15 | 198
2015-10-22 16:30 | 208
2015-10-22 16:45 | 201
2015-10-22 17:00 | 199
2015-10-22 17:15 | 204
2015-10-22 17:30 | 192
2015-10-22 17:45 | 185
2015-10-22 18:00 | 203
2015-10-22 18:15 | 196
2015-10-22 18:30 | 187
2015-10-22 18:45 | 178
2015-10-22 19:00 | 185
2015-10-22 19:15 | 132
2015-10-22 19:30 | 120
2015-10-22 19:45 | 117
2015-10-22 20:00 | 115
2015-10-22 20:15 | 122
2015-10-22 20:30 | 118
2015-10-22 20:45 | 117
2015-10-22 21:00 | 114
2015-10-22 21:15 | 117
2015-10-22 21:30 | 110
2015-10-22 21:45 | 105
2015-10-22 22:00 | 105
2015-10-22 22:15 | 105
2015-10-22 22:30 | 112
2015-10-22 22:45 | 106
2015-10-22 23:00 | 103
2015-10-22 23:15 | 100
2015-10-22 23:30 | 105
2015-10-22 23:45 | 108
2015-10-23 | 103
2015-10-23 00:15 | 102
2015-10-23 00:30 | 100
2015-10-23 00:45 | 109
2015-10-23 01:00 | 104
2015-10-23 01:15 | 108
2015-10-23 01:30 | 102
2015-10-23 01:45 | 98
2015-10-23 02:00 | 109
2015-10-23 02:15 | 99
2015-10-23 02:30 | 102
2015-10-23 02:45 | 98
2015-10-23 03:00 | 103
2015-10-23 03:15 | 103
2015-10-23 03:30 | 99
2015-10-23 03:45 | 96
2015-10-23 04:00 | 97
2015-10-23 04:15 | 100
2015-10-23 04:30 | 100
2015-10-23 04:45 | 105
2015-10-23 05:00 | 100
2015-10-23 05:15 | 102
2015-10-23 05:30 | 99
2015-10-23 05:45 | 105
2015-10-23 06:00 | 102
2015-10-23 06:15 | 105
2015-10-23 06:30 | 103
2015-10-23 06:45 | 113
2015-10-23 07:00 | 107
2015-10-23 07:15 | 149
2015-10-23 07:30 | 139
2015-10-23 07:45 | 147
2015-10-23 08:00 | 150
2015-10-23 08:15 | 146
2015-10-23 08:30 | 150
2015-10-23 08:45 | 151
2015-10-23 09:00 | 165
2015-10-23 09:15 | 161
2015-10-23 09:30 | 170
2015-10-23 09:45 | 169
2015-10-23 10:00 | 170
2015-10-23 10:15 | 184
2015-10-23 10:30 | 166
2015-10-23 10:45 | 176
2015-10-23 11:00 | 180
2015-10-23 11:15 | 187
2015-10-23 11:30 | 186
2015-10-23 11:45 | 185
2015-10-23 12:00 | 173
2015-10-23 12:15 | 178
2015-10-23 12:30 | 181
2015-10-23 12:45 | 176
2015-10-23 13:00 | 188
2015-10-23 13:15 | 179
2015-10-23 13:30 | 175
2015-10-23 13:45 | 183
2015-10-23 14:00 | 191
2015-10-23 14:15 | 190
2015-10-23 14:30 | 182
2015-10-23 14:45 | 183
2015-10-23 15:00 | 202
2015-10-23 15:15 | 192
2015-10-23 15:30 | 185
2015-10-23 15:45 | 176
2015-10-23 16:00 | 186
2015-10-23 16:15 | 191
2015-10-23 16:30 | 173
2015-10-23 16:45 | 186
2015-10-23 17:00 | 175
2015-10-23 17:15 | 184
2015-10-23 17:30 | 195
2015-10-23 17:45 | 173
2015-10-23 18:00 | 178
2015-10-23 18:15 | 179
2015-10-23 18:30 | 186
2015-10-23 18:45 | 169
2015-10-23 19:00 | 178
2015-10-23 19:15 | 114
2015-10-23 19:30 | 113
2015-10-23 19:45 | 127
2015-10-23 20:00 | 112
2015-10-23 20:15 | 114
2015-10-23 20:30 | 112
2015-10-23 20:45 | 118
2015-10-23 21:00 | 120
2015-10-23 21:15 | 105
2015-10-23 21:30 | 102
2015-10-23 21:45 | 101
2015-10-23 22:00 | 105
2015-10-23 22:15 | 103
2015-10-23 22:30 | 108
2015-10-23 22:45 | 96
2015-10-23 23:00 | 104
2015-10-23 23:15 | 103
2015-10-23 23:30 | 101
2015-10-23 23:45 | 102
2015-10-24 | 99
2015-10-24 00:15 | 97
2015-10-24 00:30 | 106
2015-10-24 00:45 | 95
2015-10-24 01:00 | 93
2015-10-24 01:15 | 89
2015-10-24 01:30 | 88
2015-10-24 01:45 | 94
2015-10-24 02:00 | 92
2015-10-24 02:15 | 93
2015-10-24 02:30 | 87
2015-10-24 02:45 | 95
2015-10-24 03:00 | 94
2015-10-24 03:15 | 90
2015-10-24 03:30 | 89
2015-10-24 03:45 | 89
2015-10-24 04:00 | 92
2015-10-24 04:15 | 92
2015-10-24 04:30 | 89
2015-10-24 04:45 | 91
2015-10-24 05:00 | 92
2015-10-24 05:15 | 88
2015-10-24 05:30 | 103
2015-10-24 05:45 | 89
2015-10-24 06:00 | 95
2015-10-24 06:15 | 89
2015-10-24 06:30 | 87
2015-10-24 06:45 | 96
2015-10-24 07:00 | 91
2015-10-24 07:15 | 92
2015-10-24 07:30 | 91
2015-10-24 07:45 | 82
2015-10-24 08:00 | 89
2015-10-24 08:15 | 88
2015-10-24 08:30 | 84
2015-10-24 08:45 | 87
2015-10-24 09:00 | 86
2015-10-24 09:15 | 94
2015-10-24 09:30 | 90
2015-10-24 09:45 | 91
2015-10-24 10:00 | 91
2015-10-24 10:15 | 86
2015-10-24 10:30 | 85
2015-10-24 10:45 | 89
2015-10-24 11:00 | 84
2015-10-24 11:15 | 95
2015-10-24 11:30 | 89
2015-10-24 11:45 | 87
2015-10-24 12:00 | 85
2015-10-24 12:15 | 87
2015-10-24 12:30 | 92
2015-10-24 12:45 | 86
2015-10-24 13:00 | 93
2015-10-24 13:15 | 84
2015-10-24 13:30 | 99
2015-10-24 13:45 | 90
2015-10-24 14:00 | 88
2015-10-24 14:15 | 84
2015-10-24 14:30 | 89
2015-10-24 14:45 | 86
2015-10-24 15:00 | 94
2015-10-24 15:15 | 90
2015-10-24 15:30 | 89
2015-10-24 15:45 | 91
2015-10-24 16:00 | 87
2015-10-24 16:15 | 95
2015-10-24 16:30 | 88
2015-10-24 16:45 | 88
2015-10-24 17:00 | 95
2015-10-24 17:15 | 102
2015-10-24 17:30 | 94
2015-10-24 17:45 | 94
2015-10-24 18:00 | 90
2015-10-24 18:15 | 90
2015-10-24 18:30 | 97
2015-10-24 18:45 | 91
2015-10-24 19:00 | 92
2015-10-24 19:15 | 93
2015-10-24 19:30 | 92
2015-10-24 19:45 | 93
2015-10-24 20:00 | 99
2015-10-24 20:15 | 92
2015-10-24 20:30 | 93
2015-10-24 20:45 | 90
2015-10-24 21:00 | 92
2015-10-24 21:15 | 94
2015-10-24 21:30 | 87
2015-10-24 21:45 | 97
2015-10-24 22:00 | 98
2015-10-24 22:15 | 94
2015-10-24 22:30 | 88
2015-10-24 22:45 | 98
2015-10-24 23:00 | 91
2015-10-24 23:15 | 93
2015-10-24 23:30 | 87
2015-10-24 23:45 | 94
2015-10-25 | 94
2015-10-25 00:15 | 92
2015-10-25 00:30 | 95
2015-10-25 00:45 | 89
2015-10-25 01:00 | 93
2015-10-25 01:15 | 89
2015-10-25 01:30 | 91
2015-10-25 01:45 | 91
2015-10-25 02:00 | 89
2015-10-25 02:15 | 95
2015-10-25 02:30 | 89
2015-10-25 02:45 | 98
2015-10-25 03:00 | 92
2015-10-25 03:15 | 91
2015-10-25 03:30 | 93
2015-10-25 03:45 | 96
2015-10-25 04:00 | 91
2015-10-25 04:15 | 90
2015-10-25 04:30 | 91
2015-10-25 04:45 | 102
2015-10-25 05:00 | 89
2015-10-25 05:15 | 93
2015-10-25 05:30 | 90
2015-10-25 05:45 | 95
2015-10-25 06:00 | 100
2015-10-25 06:15 | 97
2015-10-25 06:30 | 91
2015-10-25 06:45 | 93
2015-10-25 07:00 | 91
2015-10-25 07:15 | 100
2015-10-25 07:30 | 95
2015-10-25 07:45 | 97
2015-10-25 08:00 | 97
2015-10-25 08:15 | 99
2015-10-25 08:30 | 105
2015-10-25 08:45 | 97
2015-10-25 09:00 | 106
2015-10-25 09:15 | 109
2015-10-25 09:30 | 98
2015-10-25 09:45 | 102
2015-10-25 10:00 | 100
2015-10-25 10:15 | 106
2015-10-25 10:30 | 101
2015-10-25 10:45 | 100
2015-10-25 11:00 | 97
2015-10-25 11:15 | 105
2015-10-25 11:30 | 102
2015-10-25 11:45 | 100
2015-10-25 12:00 | 98
2015-10-25 12:15 | 101
2015-10-25 12:30 | 99
2015-10-25 12:45 | 107
2015-10-25 13:00 | 100
2015-10-25 13:15 | 101
2015-10-25 13:30 | 107
2015-10-25 13:45 | 107
2015-10-25 14:00 | 106
2015-10-25 14:15 | 105
2015-10-25 14:30 | 101
2015-10-25 14:45 | 107
2015-10-25 15:00 | 109
2015-10-25 15:15 | 103
2015-10-25 15:30 | 109
2015-10-25 15:45 | 104
2015-10-25 16:00 | 112
2015-10-25 16:15 | 107
2015-10-25 16:30 | 110
2015-10-25 16:45 | 107
2015-10-25 17:00 | 116
2015-10-25 17:15 | 116
2015-10-25 17:30 | 119
2015-10-25 17:45 | 118
2015-10-25 18:00 | 118
2015-10-25 18:15 | 116
2015-10-25 18:30 | 111
2015-10-25 18:45 | 114
2015-10-25 19:00 | 108
2015-10-25 19:15 | 112
2015-10-25 19:30 | 110
2015-10-25 19:45 | 116
2015-10-25 20:00 | 108
2015-10-25 20:15 | 102
2015-10-25 20:30 | 98
2015-10-25 20:45 | 97
2015-10-25 21:00 | 105
2015-10-25 21:15 | 98
2015-10-25 21:30 | 101
2015-10-25 21:45 | 95
2015-10-25 22:00 | 99
2015-10-25 22:15 | 106
2015-10-25 22:30 | 102
2015-10-25 22:45 | 101
2015-10-25 23:00 | 98
2015-10-25 23:15 | 99
2015-10-25 23:30 | 99
2015-10-25 23:45 | 104
2015-10-26 | 104
2015-10-26 00:15 | 100
2015-10-26 00:30 | 98
2015-10-26 00:45 | 103
2015-10-26 01:00 | 97
2015-10-26 01:15 | 95
2015-10-26 01:30 | 106
2015-10-26 01:45 | 99
2015-10-26 02:00 | 98
2015-10-26 02:15 | 94
2015-10-26 02:30 | 101
2015-10-26 02:45 | 101
2015-10-26 03:00 | 96
2015-10-26 03:15 | 97
2015-10-26 03:30 | 104
2015-10-26 03:45 | 98
2015-10-26 04:00 | 99
2015-10-26 04:15 | 94
2015-10-26 04:30 | 103
2015-10-26 04:45 | 99
2015-10-26 05:00 | 100
2015-10-26 05:15 | 99
2015-10-26 05:30 | 98
2015-10-26 05:45 | 100
2015-10-26 06:00 | 103
2015-10-26 06:15 | 152
2015-10-26 06:30 | 134
2015-10-26 06:45 | 128
2015-10-26 07:00 | 128
2015-10-26 07:15 | 124
2015-10-26 07:30 | 127
2015-10-26 07:45 | 140
2015-10-26 08:00 | 158
2015-10-26 08:15 | 148
2015-10-26 08:30 | 147
2015-10-26 08:45 | 152
2015-10-26 09:00 | 157
2015-10-26 09:15 | 166
2015-10-26 09:30 | 162
2015-10-26 09:45 | 171
2015-10-26 10:00 | 170
2015-10-26 10:15 | 176
2015-10-26 10:30 | 172
2015-10-26 10:45 | 174
2015-10-26 11:00 | 176
2015-10-26 11:15 | 189
2015-10-26 11:30 | 192
2015-10-26 11:45 | 184
2015-10-26 12:00 | 175
2015-10-26 12:15 | 182
2015-10-26 12:30 | 184
2015-10-26 12:45 | 195
2015-10-26 13:00 | 188
2015-10-26 13:15 | 187
2015-10-26 13:30 | 191
2015-10-26 13:45 | 209
2015-10-26 14:00 | 205
2015-10-26 14:15 | 202
2015-10-26 14:30 | 213
2015-10-26 14:45 | 194
2015-10-26 15:00 | 197
2015-10-26 15:15 | 192
2015-10-26 15:30 | 184
2015-10-26 15:45 | 191
2015-10-26 16:00 | 193
2015-10-26 16:15 | 191
2015-10-26 16:30 | 191
2015-10-26 16:45 | 170
2015-10-26 17:00 | 183
2015-10-26 17:15 | 192
2015-10-26 17:30 | 176
2015-10-26 17:45 | 181
2015-10-26 18:00 | 178
2015-10-26 18:15 | 129
2015-10-26 18:30 | 117
2015-10-26 18:45 | 114
2015-10-26 19:00 | 118
2015-10-26 19:15 | 110
2015-10-26 19:30 | 122
2015-10-26 19:45 | 116
2015-10-26 20:00 | 118
2015-10-26 20:15 | 112
2015-10-26 20:30 | 108
2015-10-26 20:45 | 106
2015-10-26 21:00 | 105
2015-10-26 21:15 | 111
2015-10-26 21:30 | 101
2015-10-26 21:45 | 103
2015-10-26 22:00 | 96
2015-10-26 22:15 | 101
2015-10-26 22:30 | 103
2015-10-26 22:45 | 96
2015-10-26 23:00 | 94
2015-10-26 23:15 | 95
2015-10-26 23:30 | 96
2015-10-26 23:45 | 93
2015-10-27 | 106
2015-10-27 00:15 | 97
2015-10-27 00:30 | 99
2015-10-27 00:45 | 95
2015-10-27 01:00 | 95
2015-10-27 01:15 | 105
2015-10-27 01:30 | 96
2015-10-27 01:45 | 97
2015-10-27 02:00 | 98
2015-10-27 02:15 | 102
2015-10-27 02:30 | 98
2015-10-27 02:45 | 97
2015-10-27 03:00 | 95
2015-10-27 03:15 | 100
2015-10-27 03:30 | 101
2015-10-27 03:45 | 98
2015-10-27 04:00 | 98
2015-10-27 04:15 | 98
2015-10-27 04:30 | 102
2015-10-27 04:45 | 99
2015-10-27 05:00 | 100
2015-10-27 05:15 | 99
2015-10-27 05:30 | 102
2015-10-27 05:45 | 102
2015-10-27 06:00 | 109
2015-10-27 06:15 | 161
2015-10-27 06:30 | 149
2015-10-27 06:45 | 142
2015-10-27 07:00 | 142
2015-10-27 07:15 | 142
2015-10-27 07:30 | 146
2015-10-27 07:45 | 146
2015-10-27 08:00 | 144
2015-10-27 08:15 | 142
2015-10-27 08:30 | 159
2015-10-27 08:45 | 167
2015-10-27 09:00 | 161
2015-10-27 09:15 | 165
2015-10-27 09:30 | 155
2015-10-27 09:45 | 176
2015-10-27 10:00 | 176
2015-10-27 10:15 | 167
2015-10-27 10:30 | 179
2015-10-27 10:45 | 179
2015-10-27 11:00 | 173
2015-10-27 11:15 | 194
2015-10-27 11:30 | 180
2015-10-27 11:45 | 182
2015-10-27 12:00 | 169
2015-10-27 12:15 | 188
2015-10-27 12:30 | 196
2015-10-27 12:45 | 174
2015-10-27 13:00 | 188
2015-10-27 13:15 | 183
2015-10-27 13:30 | 172
2015-10-27 13:45 | 182
2015-10-27 14:00 | 181
2015-10-27 14:15 | 191
2015-10-27 14:30 | 175
2015-10-27 14:45 | 178
2015-10-27 15:00 | 181
2015-10-27 15:15 | 172
2015-10-27 15:30 | 179
2015-10-27 15:45 | 197
2015-10-27 16:00 | 177
2015-10-27 16:15 | 177
2015-10-27 16:30 | 183
2015-10-27 16:45 | 181
2015-10-27 17:00 | 189
2015-10-27 17:15 | 188
2015-10-27 17:30 | 181
2015-10-27 17:45 | 182
2015-10-27 18:00 | 181
2015-10-27 18:15 | 135
2015-10-27 18:30 | 128
2015-10-27 18:45 | 120
2015-10-27 19:00 | 119
2015-10-27 19:15 | 134
2015-10-27 19:30 | 125
2015-10-27 19:45 | 123
2015-10-27 20:00 | 119
2015-10-27 20:15 | 110
2015-10-27 20:30 | 106
2015-10-27 20:45 | 117
2015-10-27 21:00 | 106
2015-10-27 21:15 | 107
2015-10-27 21:30 | 108
2015-10-27 21:45 | 111
2015-10-27 22:00 | 118
2015-10-27 22:15 | 113
2015-10-27 22:30 | 116
2015-10-27 22:45 | 104
2015-10-27 23:00 | 108
2015-10-27 23:15 | 107
2015-10-27 23:30 | 112
2015-10-27 23:45 | 106
2015-10-28 | 103
2015-10-28 00:15 | 101
2015-10-28 00:30 | 100
2015-10-28 00:45 | 111
2015-10-28 01:00 | 101
2015-10-28 01:15 | 99
2015-10-28 01:30 | 99
2015-10-28 01:45 | 107
2015-10-28 02:00 | 100
2015-10-28 02:15 | 102
2015-10-28 02:30 | 99
2015-10-28 02:45 | 96
2015-10-28 03:00 | 111
2015-10-28 03:15 | 102
2015-10-28 03:30 | 102
2015-10-28 03:45 | 99
2015-10-28 04:00 | 104
2015-10-28 04:15 | 105
2015-10-28 04:30 | 101
2015-10-28 04:45 | 101
2015-10-28 05:00 | 100
2015-10-28 05:15 | 106
2015-10-28 05:30 | 109
2015-10-28 05:45 | 103
2015-10-28 06:00 | 110
2015-10-28 06:15 | 155
2015-10-28 06:30 | 150
2015-10-28 06:45 | 162
2015-10-28 07:00 | 143
2015-10-28 07:15 | 159
2015-10-28 07:30 | 151
2015-10-28 07:45 | 163
2015-10-28 08:00 | 175
2015-10-28 08:15 | 166
2015-10-28 08:30 | 174
2015-10-28 08:45 | 179
2015-10-28 09:00 | 182
2015-10-28 09:15 | 196
2015-10-28 09:30 | 190
2015-10-28 09:45 | 178
2015-10-28 10:00 | 186
2015-10-28 10:15 | 188
2015-10-28 10:30 | 188
2015-10-28 10:45 | 194
2015-10-28 11:00 | 186
2015-10-28 11:15 | 179
2015-10-28 11:30 | 187
2015-10-28 11:45 | 188
2015-10-28 12:00 | 185
2015-10-28 12:15 | 188
2015-10-28 12:30 | 182
2015-10-28 12:45 | 181
2015-10-28 13:00 | 190
2015-10-28 13:15 | 198
2015-10-28 13:30 | 195
2015-10-28 13:45 | 195
2015-10-28 14:00 | 196
2015-10-28 14:15 | 191
2015-10-28 14:30 | 196
2015-10-28 14:45 | 195
2015-10-28 15:00 | 197
2015-10-28 15:15 | 196
2015-10-28 15:30 | 190
2015-10-28 15:45 | 199
2015-10-28 16:00 | 195
2015-10-28 16:15 | 203
2015-10-28 16:30 | 202
2015-10-28 16:45 | 186
2015-10-28 17:00 | 185
2015-10-28 17:15 | 194
2015-10-28 17:30 | 185
2015-10-28 17:45 | 179
2015-10-28 18:00 | 182
2015-10-28 18:15 | 131
2015-10-28 18:30 | 123
2015-10-28 18:45 | 122
2015-10-28 19:00 | 124
2015-10-28 19:15 | 123
2015-10-28 19:30 | 131
2015-10-28 19:45 | 128
2015-10-28 20:00 | 124
2015-10-28 20:15 | 119
2015-10-28 20:30 | 110
2015-10-28 20:45 | 115
2015-10-28 21:00 | 111
2015-10-28 21:15 | 115
2015-10-28 21:30 | 107
2015-10-28 21:45 | 121
2015-10-28 22:00 | 122
2015-10-28 22:15 | 129
2015-10-28 22:30 | 131
2015-10-28 22:45 | 119
2015-10-28 23:00 | 122
2015-10-28 23:15 | 118
2015-10-28 23:30 | 120
2015-10-28 23:45 | 118
2015-10-29 | 105
2015-10-29 00:15 | 106
2015-10-29 00:30 | 107
2015-10-29 00:45 | 110
2015-10-29 01:00 | 100
2015-10-29 01:15 | 103
2015-10-29 01:30 | 98
2015-10-29 01:45 | 104
2015-10-29 02:00 | 110
2015-10-29 02:15 | 100
2015-10-29 02:30 | 102
2015-10-29 02:45 | 97
2015-10-29 03:00 | 107
2015-10-29 03:15 | 108
2015-10-29 03:30 | 101
2015-10-29 03:45 | 101
2015-10-29 04:00 | 113
2015-10-29 04:15 | 103
2015-10-29 04:30 | 103
2015-10-29 04:45 | 100
2015-10-29 05:00 | 109
2015-10-29 05:15 | 109
2015-10-29 05:30 | 108
2015-10-29 05:45 | 105
2015-10-29 06:00 | 111
2015-10-29 06:15 | 136
2015-10-29 06:30 | 133
2015-10-29 06:45 | 141
2015-10-29 07:00 | 143
2015-10-29 07:15 | 159
2015-10-29 07:30 | 149
2015-10-29 07:45 | 159
2015-10-29 08:00 | 169
2015-10-29 08:15 | 172
2015-10-29 08:30 | 172
2015-10-29 08:45 | 180
2015-10-29 09:00 | 168
2015-10-29 09:15 | 174
2015-10-29 09:30 | 175
2015-10-29 09:45 | 183
2015-10-29 10:00 | 187
2015-10-29 10:15 | 186
2015-10-29 10:30 | 180
2015-10-29 10:45 | 189
2015-10-29 11:00 | 191
2015-10-29 11:15 | 176
2015-10-29 11:30 | 175
2015-10-29 11:45 | 183
2015-10-29 12:00 | 185
2015-10-29 12:15 | 186
2015-10-29 12:30 | 189
2015-10-29 12:45 | 185
2015-10-29 13:00 | 185
2015-10-29 13:15 | 206
2015-10-29 13:30 | 186
2015-10-29 13:45 | 187
2015-10-29 14:00 | 187
2015-10-29 14:15 | 188
2015-10-29 14:30 | 215
2015-10-29 14:45 | 186
2015-10-29 15:00 | 189
2015-10-29 15:15 | 199
2015-10-29 15:30 | 181
2015-10-29 15:45 | 202
2015-10-29 16:00 | 195
2015-10-29 16:15 | 180
2015-10-29 16:30 | 183
2015-10-29 16:45 | 185
2015-10-29 17:00 | 189
2015-10-29 17:15 | 190
2015-10-29 17:30 | 187
2015-10-29 17:45 | 175
2015-10-29 18:00 | 180
2015-10-29 18:15 | 140
2015-10-29 18:30 | 121
2015-10-29 18:45 | 123
2015-10-29 19:00 | 121
2015-10-29 19:15 | 127
2015-10-29 19:30 | 131
2015-10-29 19:45 | 125
2015-10-29 20:00 | 121
2015-10-29 20:15 | 106
2015-10-29 20:30 | 109
2015-10-29 20:45 | 114
2015-10-29 21:00 | 110
2015-10-29 21:15 | 110
2015-10-29 21:30 | 107
2015-10-29 21:45 | 120
2015-10-29 22:00 | 119
2015-10-29 22:15 | 112
2015-10-29 22:30 | 119
2015-10-29 22:45 | 113
2015-10-29 23:00 | 119
2015-10-29 23:15 | 125
2015-10-29 23:30 | 116
2015-10-29 23:45 | 111
2015-10-30 | 114
2015-10-30 00:15 | 112
2015-10-30 00:30 | 111
2015-10-30 00:45 | 111
2015-10-30 01:00 | 104
2015-10-30 01:15 | 103
2015-10-30 01:30 | 106
2015-10-30 01:45 | 102
2015-10-30 02:00 | 103
2015-10-30 02:15 | 105
2015-10-30 02:30 | 108
2015-10-30 02:45 | 104
2015-10-30 03:00 | 100
2015-10-30 03:15 | 110
2015-10-30 03:30 | 104
2015-10-30 03:45 | 105
2015-10-30 04:00 | 104
2015-10-30 04:15 | 108
2015-10-30 04:30 | 107
2015-10-30 04:45 | 102
2015-10-30 05:00 | 103
2015-10-30 05:15 | 106
2015-10-30 05:30 | 108
2015-10-30 05:45 | 119
2015-10-30 06:00 | 112
2015-10-30 06:15 | 131
2015-10-30 06:30 | 131
2015-10-30 06:45 | 135
2015-10-30 07:00 | 136
2015-10-30 07:15 | 135
2015-10-30 07:30 | 149
2015-10-30 07:45 | 149
2015-10-30 08:00 | 161
2015-10-30 08:15 | 159
2015-10-30 08:30 | 169
2015-10-30 08:45 | 159
2015-10-30 09:00 | 162
2015-10-30 09:15 | 162
2015-10-30 09:30 | 159
2015-10-30 09:45 | 145
2015-10-30 10:00 | 144
2015-10-30 10:15 | 143
2015-10-30 10:30 | 159
2015-10-30 10:45 | 172
2015-10-30 11:00 | 167
2015-10-30 11:15 | 166
2015-10-30 11:30 | 164
2015-10-30 11:45 | 158
2015-10-30 12:00 | 158
2015-10-30 12:15 | 159
2015-10-30 12:30 | 160
2015-10-30 12:45 | 163
2015-10-30 13:00 | 162
2015-10-30 13:15 | 163
2015-10-30 13:30 | 163
2015-10-30 13:45 | 167
2015-10-30 14:00 | 174
2015-10-30 14:15 | 167
2015-10-30 14:30 | 175
2015-10-30 14:45 | 179
2015-10-30 15:00 | 174
2015-10-30 15:15 | 167
2015-10-30 15:30 | 170
2015-10-30 15:45 | 158
2015-10-30 16:00 | 163
2015-10-30 16:15 | 163
2015-10-30 16:30 | 160
2015-10-30 16:45 | 161
2015-10-30 17:00 | 164
2015-10-30 17:15 | 164
2015-10-30 17:30 | 161
2015-10-30 17:45 | 171
2015-10-30 18:00 | 164
2015-10-30 18:15 | 125
2015-10-30 18:30 | 124
2015-10-30 18:45 | 115
2015-10-30 19:00 | 121
2015-10-30 19:15 | 124
2015-10-30 19:30 | 118
2015-10-30 19:45 | 120
2015-10-30 20:00 | 121
2015-10-30 20:15 | 114
2015-10-30 20:30 | 114
2015-10-30 20:45 | 117
2015-10-30 21:00 | 114
2015-10-30 21:15 | 121
2015-10-30 21:30 | 112
2015-10-30 21:45 | 118
2015-10-30 22:00 | 114
2015-10-30 22:15 | 112
2015-10-30 22:30 | 119
2015-10-30 22:45 | 116
2015-10-30 23:00 | 115
2015-10-30 23:15 | 110
2015-10-30 23:30 | 115
2015-10-30 23:45 | 111
2015-10-31 | 120
2015-10-31 00:15 | 117
2015-10-31 00:30 | 107
2015-10-31 00:45 | 106
2015-10-31 01:00 | 107
2015-10-31 01:15 | 104
2015-10-31 01:30 | 111
2015-10-31 01:45 | 107
2015-10-31 02:00 | 109
2015-10-31 02:15 | 103
2015-10-31 02:30 | 108
2015-10-31 02:45 | 111
2015-10-31 03:00 | 101
2015-10-31 03:15 | 104
2015-10-31 03:30 | 107
2015-10-31 03:45 | 106
2015-10-31 04:00 | 107
2015-10-31 04:15 | 105
2015-10-31 04:30 | 105
2015-10-31 04:45 | 112
2015-10-31 05:00 | 102
2015-10-31 05:15 | 104
2015-10-31 05:30 | 103
2015-10-31 05:45 | 105
2015-10-31 06:00 | 104
2015-10-31 06:15 | 110
2015-10-31 06:30 | 104
2015-10-31 06:45 | 99
2015-10-31 07:00 | 98
2015-10-31 07:15 | 100
2015-10-31 07:30 | 98
2015-10-31 07:45 | 101
2015-10-31 08:00 | 102
2015-10-31 08:15 | 97
2015-10-31 08:30 | 96
2015-10-31 08:45 | 100
2015-10-31 09:00 | 99
2015-10-31 09:15 | 101
2015-10-31 09:30 | 101
2015-10-31 09:45 | 101
2015-10-31 10:00 | 108
2015-10-31 10:15 | 98
2015-10-31 10:30 | 98
2015-10-31 10:45 | 99
2015-10-31 11:00 | 98
2015-10-31 11:15 | 96
2015-10-31 11:30 | 105
2015-10-31 11:45 | 102
2015-10-31 12:00 | 100
2015-10-31 12:15 | 97
2015-10-31 12:30 | 105
2015-10-31 12:45 | 103
2015-10-31 13:00 | 100
2015-10-31 13:15 | 99
2015-10-31 13:30 | 101
2015-10-31 13:45 | 100
2015-10-31 14:00 | 105
2015-10-31 14:15 | 100
2015-10-31 14:30 | 102
2015-10-31 14:45 | 99
2015-10-31 15:00 | 104
2015-10-31 15:15 | 100
2015-10-31 15:30 | 104
2015-10-31 15:45 | 103
2015-10-31 16:00 | 106
2015-10-31 16:15 | 103
2015-10-31 16:30 | 110
2015-10-31 16:45 | 109
2015-10-31 17:00 | 106
2015-10-31 17:15 | 105
2015-10-31 17:30 | 106
2015-10-31 17:45 | 110
2015-10-31 18:00 | 104
2015-10-31 18:15 | 105
2015-10-31 18:30 | 103
2015-10-31 18:45 | 103
2015-10-31 19:00 | 105
2015-10-31 19:15 | 109
2015-10-31 19:30 | 109
2015-10-31 19:45 | 104
2015-10-31 20:00 | 102
2015-10-31 20:15 | 113
2015-10-31 20:30 | 104
2015-10-31 20:45 | 106
2015-10-31 21:00 | 103
2015-10-31 21:15 | 110
2015-10-31 21:30 | 105
2015-10-31 21:45 | 109
2015-10-31 22:00 | 100
2015-10-31 22:15 | 106
2015-10-31 22:30 | 101
2015-10-31 22:45 | 105
2015-10-31 23:00 | 107
2015-10-31 23:15 | 104
2015-10-31 23:30 | 94
2015-10-31 23:45 | 92

## User Inputs and DR Shed Results
User Inputs
ADR Site Description | Data | Note
Name | {id:smallofficecz03-26}
Building Type | Office
HVAC Type | Central Plant | RTU Duty Cycling is not available for HVAC Type "Central Plant".
Zipcode | 94720
NewCustomers | Yes
Peak Demand (kW) | 322 | From meter data
County | Alameda
PG&E Climate Zone | 4
CEC Climate Zone | 3 | CZ03
Building Size | MediumOffice
DR Shed Results of HVAC Temperature Setpoint Reset
HVAC Temp Reset DR Shed Capacity Calculation
Percent of Bldg Floor Area that Temp Reset will Apply (0-100) | 100
Precool Period Temp Offset (°F) | 0
DR Event Period Temp Offset (°F) | 4
Average DR Potential (kW) | 25.7944
Min DR Potential (kW) | 22.4825
Max DR Potential (kW) | 28.7122
HVAC Temp Reset DR Shed Estimates (kW) for Peak Temps in Building's Climate Zone
Temperature Range | Peak OAT (F) | Estimated kW Shed
1 | 61.6926 | 22.4825
2 | 67.6092 | 23.3098
3 | 72.1396 | 24.5008
4 | 76.9243 | 25.7384
5 | 82.1462 | 28.7122
6 | 87.5605 | 28.0092
7 | 90.7944 | 27.8077

## CSSB
Date | Date | weekday | Hour | Demand | OAT | TempRange | Holiday and ADR Days |  | Summary of Load and OAT in Summer
2015-05-01 01:00 | 2015-05-01 | 5 | 1 | 208 | 63.7333 | 1 | 2015-01-01 | New Years' Day | Temp Ranges | Average of OAT | Average of Demand
2015-05-01 01:15 | 2015-05-01 | 5 | 1 | 208 | 62.7333 | 1 | 2015-01-19 | Martin Luther King | 1 | 61.6926 | 224.6336
2015-05-01 01:30 | 2015-05-01 | 5 | 1 | 196 | 61.7333 | 1 | 2015-02-16 | Washington's Birthday | 2 | 67.6092 | 227.4739
2015-05-01 01:45 | 2015-05-01 | 5 | 1 | 205 | 60.7333 | 1 | 2015-05-25 | Memorial Day | 3 | 72.1396 | 234.9057
2015-05-01 02:00 | 2015-05-01 | 5 | 2 | 196 | 59.9333 | 1 | 2015-07-03 | Independence Day | 4 | 76.9243 | 242.2877
2015-05-01 02:15 | 2015-05-01 | 5 | 2 | 205 | 59.6833 | 1 | 2015-09-07 | Labor Day | 5 | 82.1462 | 265.0244
2015-05-01 02:30 | 2015-05-01 | 5 | 2 | 187 | 59.4333 | 1 | 2015-10-12 | Columbus Day | 6 | 87.5605 | 253.4255
2015-05-01 02:45 | 2015-05-01 | 5 | 2 | 185 | 59.1833 | 1 | 2015-11-11 | Veterans Day | 7 | 90.7944 | 248.6667
2015-05-01 03:00 | 2015-05-01 | 5 | 3 | 169 | 58.9333 | 1 | 2015-11-26 | Thanksgiving Day
2015-05-01 03:15 | 2015-05-01 | 5 | 3 | 180 | 58.6833 | 1 | 2015-12-25 | Christmas Day
2015-05-01 03:30 | 2015-05-01 | 5 | 3 | 171 | 58.4333 | 1 | 2015-06-12 | 2015 ADR Days | range_id | avg_temp | avg_demand
2015-05-01 03:45 | 2015-05-01 | 5 | 3 | 180 | 58.1833 | 1 | 2015-06-25 | 2015 ADR Days | 1 | 61.6787 | 225.0538
2015-05-01 04:00 | 2015-05-01 | 5 | 4 | 163 | 58 | 1 | 2015-06-26 | 2015 ADR Days | 2 | 67.5862 | 228.0693
2015-05-01 04:15 | 2015-05-01 | 5 | 4 | 174 | 58 | 1 | 2015-07-01 | 2015 ADR Days | 3 | 72.1434 | 234.6141
2015-05-01 04:30 | 2015-05-01 | 5 | 4 | 172 | 58 | 1 | 2015-07-28 | 2015 ADR Days | 4 | 76.9271 | 241.8531
2015-05-01 04:45 | 2015-05-01 | 5 | 4 | 167 | 58 | 1 | 2015-07-29 | 2015 ADR Days | 5 | 82.1516 | 265.6203
2015-05-01 05:00 | 2015-05-01 | 5 | 5 | 166 | 58.0667 | 1 | 2015-07-30 | 2015 ADR Days | 6 | 87.593 | 251.0217
2015-05-01 05:15 | 2015-05-01 | 5 | 5 | 163 | 58.3167 | 1 | 2015-08-17 | 2015 ADR Days | 7 | 90.7944 | 253.6667
2015-05-01 05:30 | 2015-05-01 | 5 | 5 | 161 | 58.5667 | 1 | 2015-08-18 | 2015 ADR Days
2015-05-01 05:45 | 2015-05-01 | 5 | 5 | 169 | 58.8167 | 1 | 2015-08-27 | 2015 ADR Days
2015-05-01 06:00 | 2015-05-01 | 5 | 6 | 158 | 59.2667 | 1
2015-05-01 06:15 | 2015-05-01 | 5 | 6 | 167 | 60.2667 | 1
2015-05-01 06:30 | 2015-05-01 | 5 | 6 | 173 | 61.2667 | 1
2015-05-01 06:45 | 2015-05-01 | 5 | 6 | 164 | 62.2667 | 1
2015-05-01 07:00 | 2015-05-01 | 5 | 7 | 176 | 63.4 | 1
2015-05-01 07:15 | 2015-05-01 | 5 | 7 | 168 | 64.9 | 1
2015-05-01 07:30 | 2015-05-01 | 5 | 7 | 179 | 66.4 | 2
2015-05-01 07:45 | 2015-05-01 | 5 | 7 | 178 | 67.9 | 2
2015-05-01 08:00 | 2015-05-01 | 5 | 8 | 183 | 68.8 | 2
2015-05-01 08:15 | 2015-05-01 | 5 | 8 | 223 | 68.05 | 2
2015-05-01 08:30 | 2015-05-01 | 5 | 8 | 210 | 67.3 | 2
2015-05-01 08:45 | 2015-05-01 | 5 | 8 | 251 | 66.55 | 2
2015-05-01 09:00 | 2015-05-01 | 5 | 9 | 249 | 66.0667 | 2
2015-05-01 09:15 | 2015-05-01 | 5 | 9 | 243 | 66.3167 | 2
2015-05-01 09:30 | 2015-05-01 | 5 | 9 | 262 | 66.5667 | 2
2015-05-01 09:45 | 2015-05-01 | 5 | 9 | 259 | 66.8167 | 2
2015-05-01 10:00 | 2015-05-01 | 5 | 10 | 263 | 67.0667 | 2
2015-05-01 10:15 | 2015-05-01 | 5 | 10 | 278 | 67.3167 | 2
2015-05-01 10:30 | 2015-05-01 | 5 | 10 | 257 | 67.5667 | 2
2015-05-01 10:45 | 2015-05-01 | 5 | 10 | 266 | 67.8167 | 2
2015-05-01 11:00 | 2015-05-01 | 5 | 11 | 260 | 68.2667 | 2
2015-05-01 11:15 | 2015-05-01 | 5 | 11 | 279 | 69.2667 | 2
2015-05-01 11:30 | 2015-05-01 | 5 | 11 | 282 | 70.2667 | 3
2015-05-01 11:45 | 2015-05-01 | 5 | 11 | 293 | 71.2667 | 3
2015-05-01 12:00 | 2015-05-01 | 5 | 12 | 290 | 71.9333 | 3
2015-05-01 12:15 | 2015-05-01 | 5 | 12 | 289 | 71.6833 | 3
2015-05-01 12:30 | 2015-05-01 | 5 | 12 | 297 | 71.4333 | 3
2015-05-01 12:45 | 2015-05-01 | 5 | 12 | 288 | 71.1833 | 3
2015-05-01 13:00 | 2015-05-01 | 5 | 13 | 297 | 70.907 | 3
2015-05-01 13:15 | 2015-05-01 | 5 | 13 | 288 | 70.5581 | 3
2015-05-01 13:30 | 2015-05-01 | 5 | 13 | 305 | 70.2093 | 3
2015-05-01 13:45 | 2015-05-01 | 5 | 13 | 299 | 68.9412 | 2
2015-05-01 14:00 | 2015-05-01 | 5 | 14 | 309 | 66.9333 | 2
2015-05-01 14:15 | 2015-05-01 | 5 | 14 | 318 | 66.6833 | 2
2015-05-01 14:30 | 2015-05-01 | 5 | 14 | 320 | 66.4333 | 2
2015-05-01 14:45 | 2015-05-01 | 5 | 14 | 314 | 66.1833 | 2
2015-05-01 15:00 | 2015-05-01 | 5 | 15 | 312 | 65.9333 | 2
2015-05-01 15:15 | 2015-05-01 | 5 | 15 | 315 | 65.6833 | 2
2015-05-01 15:30 | 2015-05-01 | 5 | 15 | 319 | 65.4333 | 2
2015-05-01 15:45 | 2015-05-01 | 5 | 15 | 317 | 65.1833 | 2
2015-05-01 16:00 | 2015-05-01 | 5 | 16 | 319 | 64.8 | 1
2015-05-01 16:15 | 2015-05-01 | 5 | 16 | 304 | 64.05 | 1
2015-05-01 16:30 | 2015-05-01 | 5 | 16 | 295 | 63.3 | 1
2015-05-01 16:45 | 2015-05-01 | 5 | 16 | 301 | 62.55 | 1
2015-05-01 17:00 | 2015-05-01 | 5 | 17 | 307 | 61.8 | 1
2015-05-01 17:15 | 2015-05-01 | 5 | 17 | 296 | 61.05 | 1
2015-05-01 17:30 | 2015-05-01 | 5 | 17 | 282 | 60.3 | 1
2015-05-01 17:45 | 2015-05-01 | 5 | 17 | 284 | 59.55 | 1
2015-05-01 18:00 | 2015-05-01 | 5 | 18 | 282 | 58.8667 | 1
2015-05-01 18:15 | 2015-05-01 | 5 | 18 | 283 | 58.3667 | 1
2015-05-01 18:30 | 2015-05-01 | 5 | 18 | 278 | 57.8667 | 1
2015-05-01 18:45 | 2015-05-01 | 5 | 18 | 262 | 57.3667 | 1
2015-05-01 19:00 | 2015-05-01 | 5 | 19 | 272 | 57 | 1
2015-05-01 19:15 | 2015-05-01 | 5 | 19 | 256 | 57 | 1
2015-05-01 19:30 | 2015-05-01 | 5 | 19 | 258 | 57 | 1
2015-05-01 19:45 | 2015-05-01 | 5 | 19 | 241 | 57 | 1
2015-05-01 20:00 | 2015-05-01 | 5 | 20 | 250 | 56.9333 | 1
2015-05-01 20:15 | 2015-05-01 | 5 | 20 | 227 | 56.6833 | 1
2015-05-01 20:30 | 2015-05-01 | 5 | 20 | 206 | 56.4333 | 1
2015-05-01 20:45 | 2015-05-01 | 5 | 20 | 209 | 56.1833 | 1
2015-05-01 21:00 | 2015-05-01 | 5 | 21 | 202 | 56 | 1
2015-05-01 21:15 | 2015-05-01 | 5 | 21 | 183 | 56 | 1
2015-05-01 21:30 | 2015-05-01 | 5 | 21 | 182 | 56 | 1
2015-05-01 21:45 | 2015-05-01 | 5 | 21 | 181 | 56 | 1
2015-05-01 22:00 | 2015-05-01 | 5 | 22 | 189 | 55.9333 | 1
2015-05-01 22:15 | 2015-05-01 | 5 | 22 | 191 | 55.6833 | 1
2015-05-01 22:30 | 2015-05-01 | 5 | 22 | 167 | 55.4333 | 1
2015-05-01 22:45 | 2015-05-01 | 5 | 22 | 179 | 55.1833 | 1
2015-05-01 23:00 | 2015-05-01 | 5 | 23 | 178 | 54.9333 | 1
2015-05-01 23:15 | 2015-05-01 | 5 | 23 | 172 | 54.6833 | 1
2015-05-01 23:30 | 2015-05-01 | 5 | 23 | 183 | 54.4333 | 1
2015-05-01 23:45 | 2015-05-01 | 5 | 23 | 184 | 54.1833 | 1
2015-05-02 | 2015-05-02 | 6 | 0 | 178 | 54 | 1
2015-05-02 00:15 | 2015-05-02 | 6 | 0 | 187 | 54 | 1
2015-05-02 00:30 | 2015-05-02 | 6 | 0 | 167 | 54 | 1
2015-05-02 00:45 | 2015-05-02 | 6 | 0 | 167 | 54 | 1
2015-05-02 01:00 | 2015-05-02 | 6 | 1 | 171 | 53.9333 | 1
2015-05-02 01:15 | 2015-05-02 | 6 | 1 | 169 | 53.6833 | 1
2015-05-02 01:30 | 2015-05-02 | 6 | 1 | 164 | 53.4333 | 1
2015-05-02 01:45 | 2015-05-02 | 6 | 1 | 169 | 53.1833 | 1
2015-05-02 02:00 | 2015-05-02 | 6 | 2 | 162 | 53.2105 | 1
2015-05-02 02:15 | 2015-05-02 | 6 | 2 | 163 | 54 | 1
2015-05-02 02:30 | 2015-05-02 | 6 | 2 | 162 | 54 | 1
2015-05-02 02:45 | 2015-05-02 | 6 | 2 | 159 | 54 | 1
2015-05-02 03:00 | 2015-05-02 | 6 | 3 | 156 | 54 | 1
2015-05-02 03:15 | 2015-05-02 | 6 | 3 | 160 | 53.82 | 1
2015-05-02 03:30 | 2015-05-02 | 6 | 3 | 157 | 53.52 | 1
2015-05-02 03:45 | 2015-05-02 | 6 | 3 | 161 | 53.22 | 1
2015-05-02 04:00 | 2015-05-02 | 6 | 4 | 158 | 53.0667 | 1
2015-05-02 04:15 | 2015-05-02 | 6 | 4 | 160 | 53.3167 | 1
2015-05-02 04:30 | 2015-05-02 | 6 | 4 | 168 | 53.5667 | 1
2015-05-02 04:45 | 2015-05-02 | 6 | 4 | 161 | 53.8167 | 1
2015-05-02 05:00 | 2015-05-02 | 6 | 5 | 156 | 53.9333 | 1
2015-05-02 05:15 | 2015-05-02 | 6 | 5 | 156 | 53.6833 | 1
2015-05-02 05:30 | 2015-05-02 | 6 | 5 | 151 | 53.4333 | 1
2015-05-02 05:45 | 2015-05-02 | 6 | 5 | 155 | 53.1833 | 1
2015-05-02 06:00 | 2015-05-02 | 6 | 6 | 155 | 53.0667 | 1
2015-05-02 06:15 | 2015-05-02 | 6 | 6 | 161 | 53.3167 | 1
2015-05-02 06:30 | 2015-05-02 | 6 | 6 | 169 | 53.5667 | 1
2015-05-02 06:45 | 2015-05-02 | 6 | 6 | 158 | 53.8167 | 1
2015-05-02 07:00 | 2015-05-02 | 6 | 7 | 167 | 54.2 | 1
2015-05-02 07:15 | 2015-05-02 | 6 | 7 | 160 | 54.95 | 1
2015-05-02 07:30 | 2015-05-02 | 6 | 7 | 162 | 55.7 | 1
2015-05-02 07:45 | 2015-05-02 | 6 | 7 | 160 | 56.45 | 1
2015-05-02 08:00 | 2015-05-02 | 6 | 8 | 155 | 57.2 | 1
2015-05-02 08:15 | 2015-05-02 | 6 | 8 | 161 | 57.95 | 1
2015-05-02 08:30 | 2015-05-02 | 6 | 8 | 168 | 58.7 | 1
2015-05-02 08:45 | 2015-05-02 | 6 | 8 | 159 | 59.45 | 1
2015-05-02 09:00 | 2015-05-02 | 6 | 9 | 167 | 60.1333 | 1
2015-05-02 09:15 | 2015-05-02 | 6 | 9 | 157 | 60.6333 | 1
2015-05-02 09:30 | 2015-05-02 | 6 | 9 | 189 | 61.1333 | 1
2015-05-02 09:45 | 2015-05-02 | 6 | 9 | 166 | 61.6333 | 1
2015-05-02 10:00 | 2015-05-02 | 6 | 10 | 178 | 62 | 1
2015-05-02 10:15 | 2015-05-02 | 6 | 10 | 180 | 62 | 1
2015-05-02 10:30 | 2015-05-02 | 6 | 10 | 180 | 62 | 1
2015-05-02 10:45 | 2015-05-02 | 6 | 10 | 192 | 62 | 1
2015-05-02 11:00 | 2015-05-02 | 6 | 11 | 214 | 62.1333 | 1
2015-05-02 11:15 | 2015-05-02 | 6 | 11 | 213 | 62.6333 | 1
2015-05-02 11:30 | 2015-05-02 | 6 | 11 | 207 | 63.1333 | 1
2015-05-02 11:45 | 2015-05-02 | 6 | 11 | 217 | 63.6333 | 1
2015-05-02 12:00 | 2015-05-02 | 6 | 12 | 221 | 64.1333 | 1
2015-05-02 12:15 | 2015-05-02 | 6 | 12 | 210 | 64.6333 | 1
2015-05-02 12:30 | 2015-05-02 | 6 | 12 | 222 | 65.1333 | 2
2015-05-02 12:45 | 2015-05-02 | 6 | 12 | 214 | 65.6333 | 2
2015-05-02 13:00 | 2015-05-02 | 6 | 13 | 212 | 66 | 2
2015-05-02 13:15 | 2015-05-02 | 6 | 13 | 221 | 66 | 2
2015-05-02 13:30 | 2015-05-02 | 6 | 13 | 219 | 66 | 2
2015-05-02 13:45 | 2015-05-02 | 6 | 13 | 220 | 66 | 2
2015-05-02 14:00 | 2015-05-02 | 6 | 14 | 238 | 65.9333 | 2
2015-05-02 14:15 | 2015-05-02 | 6 | 14 | 225 | 65.6833 | 2
2015-05-02 14:30 | 2015-05-02 | 6 | 14 | 225 | 65.4333 | 2
2015-05-02 14:45 | 2015-05-02 | 6 | 14 | 222 | 65.1833 | 2
2015-05-02 15:00 | 2015-05-02 | 6 | 15 | 239 | 64.8667 | 1
2015-05-02 15:15 | 2015-05-02 | 6 | 15 | 237 | 64.3667 | 1
2015-05-02 15:30 | 2015-05-02 | 6 | 15 | 234 | 63.8667 | 1
2015-05-02 15:45 | 2015-05-02 | 6 | 15 | 235 | 63.3667 | 1
2015-05-02 16:00 | 2015-05-02 | 6 | 16 | 227 | 62.8667 | 1
2015-05-02 16:15 | 2015-05-02 | 6 | 16 | 245 | 62.3667 | 1
2015-05-02 16:30 | 2015-05-02 | 6 | 16 | 229 | 61.8667 | 1
2015-05-02 16:45 | 2015-05-02 | 6 | 16 | 242 | 61.3667 | 1
2015-05-02 17:00 | 2015-05-02 | 6 | 17 | 226 | 60.8667 | 1
2015-05-02 17:15 | 2015-05-02 | 6 | 17 | 228 | 60.3667 | 1
2015-05-02 17:30 | 2015-05-02 | 6 | 17 | 230 | 59.8667 | 1
2015-05-02 17:45 | 2015-05-02 | 6 | 17 | 226 | 59.3667 | 1
2015-05-02 18:00 | 2015-05-02 | 6 | 18 | 234 | 58.8667 | 1
2015-05-02 18:15 | 2015-05-02 | 6 | 18 | 217 | 58.3667 | 1
2015-05-02 18:30 | 2015-05-02 | 6 | 18 | 219 | 57.8667 | 1
2015-05-02 18:45 | 2015-05-02 | 6 | 18 | 215 | 57.3667 | 1
2015-05-02 19:00 | 2015-05-02 | 6 | 19 | 212 | 56.8667 | 1
2015-05-02 19:15 | 2015-05-02 | 6 | 19 | 190 | 56.3667 | 1
2015-05-02 19:30 | 2015-05-02 | 6 | 19 | 189 | 55.8667 | 1
2015-05-02 19:45 | 2015-05-02 | 6 | 19 | 194 | 55.3667 | 1
2015-05-02 20:00 | 2015-05-02 | 6 | 20 | 184 | 55 | 1
2015-05-02 20:15 | 2015-05-02 | 6 | 20 | 180 | 55 | 1
2015-05-02 20:30 | 2015-05-02 | 6 | 20 | 187 | 55 | 1
2015-05-02 20:45 | 2015-05-02 | 6 | 20 | 171 | 55 | 1
2015-05-02 21:00 | 2015-05-02 | 6 | 21 | 172 | 54.9333 | 1
2015-05-02 21:15 | 2015-05-02 | 6 | 21 | 170 | 54.6833 | 1
2015-05-02 21:30 | 2015-05-02 | 6 | 21 | 171 | 54.4333 | 1
2015-05-02 21:45 | 2015-05-02 | 6 | 21 | 169 | 54.1833 | 1
2015-05-02 22:00 | 2015-05-02 | 6 | 22 | 161 | 54 | 1
2015-05-02 22:15 | 2015-05-02 | 6 | 22 | 153 | 54 | 1
2015-05-02 22:30 | 2015-05-02 | 6 | 22 | 162 | 54 | 1
2015-05-02 22:45 | 2015-05-02 | 6 | 22 | 159 | 54 | 1
2015-05-02 23:00 | 2015-05-02 | 6 | 23 | 162 | 53.9333 | 1
2015-05-02 23:15 | 2015-05-02 | 6 | 23 | 158 | 53.6833 | 1
2015-05-02 23:30 | 2015-05-02 | 6 | 23 | 169 | 53.4333 | 1
2015-05-02 23:45 | 2015-05-02 | 6 | 23 | 160 | 53.1833 | 1
2015-05-03 | 2015-05-03 | 7 | 0 | 156 | 53 | 1
2015-05-03 00:15 | 2015-05-03 | 7 | 0 | 154 | 53 | 1
2015-05-03 00:30 | 2015-05-03 | 7 | 0 | 162 | 53 | 1
2015-05-03 00:45 | 2015-05-03 | 7 | 0 | 155 | 53 | 1
2015-05-03 01:00 | 2015-05-03 | 7 | 1 | 153 | 53.0667 | 1
2015-05-03 01:15 | 2015-05-03 | 7 | 1 | 150 | 53.3167 | 1
2015-05-03 01:30 | 2015-05-03 | 7 | 1 | 159 | 53.5667 | 1
2015-05-03 01:45 | 2015-05-03 | 7 | 1 | 157 | 53.8167 | 1
2015-05-03 02:00 | 2015-05-03 | 7 | 2 | 147 | 53.9333 | 1
2015-05-03 02:15 | 2015-05-03 | 7 | 2 | 150 | 53.6833 | 1
2015-05-03 02:30 | 2015-05-03 | 7 | 2 | 149 | 53.4333 | 1
2015-05-03 02:45 | 2015-05-03 | 7 | 2 | 152 | 53.1833 | 1
2015-05-03 03:00 | 2015-05-03 | 7 | 3 | 162 | 52.9333 | 1
2015-05-03 03:15 | 2015-05-03 | 7 | 3 | 157 | 52.6833 | 1
2015-05-03 03:30 | 2015-05-03 | 7 | 3 | 161 | 52.4333 | 1
2015-05-03 03:45 | 2015-05-03 | 7 | 3 | 152 | 52.1833 | 1
2015-05-03 04:00 | 2015-05-03 | 7 | 4 | 163 | 52 | 1
2015-05-03 04:15 | 2015-05-03 | 7 | 4 | 147 | 52 | 1
2015-05-03 04:30 | 2015-05-03 | 7 | 4 | 162 | 52 | 1
2015-05-03 04:45 | 2015-05-03 | 7 | 4 | 152 | 52 | 1
2015-05-03 05:00 | 2015-05-03 | 7 | 5 | 151 | 52 | 1
2015-05-03 05:15 | 2015-05-03 | 7 | 5 | 146 | 52 | 1
2015-05-03 05:30 | 2015-05-03 | 7 | 5 | 163 | 52.2778 | 1
2015-05-03 05:45 | 2015-05-03 | 7 | 5 | 147 | 52.6944 | 1
2015-05-03 06:00 | 2015-05-03 | 7 | 6 | 152 | 53.1333 | 1
2015-05-03 06:15 | 2015-05-03 | 7 | 6 | 151 | 53.6333 | 1
2015-05-03 06:30 | 2015-05-03 | 7 | 6 | 154 | 54 | 1
2015-05-03 06:45 | 2015-05-03 | 7 | 6 | 163 | 54 | 1
2015-05-03 07:00 | 2015-05-03 | 7 | 7 | 161 | 54.2 | 1
2015-05-03 07:15 | 2015-05-03 | 7 | 7 | 156 | 54.95 | 1
2015-05-03 07:30 | 2015-05-03 | 7 | 7 | 164 | 55.7 | 1
2015-05-03 07:45 | 2015-05-03 | 7 | 7 | 161 | 56.45 | 1
2015-05-03 08:00 | 2015-05-03 | 7 | 8 | 165 | 57.1333 | 1
2015-05-03 08:15 | 2015-05-03 | 7 | 8 | 169 | 57.6333 | 1
2015-05-03 08:30 | 2015-05-03 | 7 | 8 | 170 | 58.1333 | 1
2015-05-03 08:45 | 2015-05-03 | 7 | 8 | 179 | 58.6333 | 1
2015-05-03 09:00 | 2015-05-03 | 7 | 9 | 172 | 59.1333 | 1
2015-05-03 09:15 | 2015-05-03 | 7 | 9 | 170 | 59.6333 | 1
2015-05-03 09:30 | 2015-05-03 | 7 | 9 | 169 | 60.1333 | 1
2015-05-03 09:45 | 2015-05-03 | 7 | 9 | 174 | 60.6333 | 1
2015-05-03 10:00 | 2015-05-03 | 7 | 10 | 173 | 61.0667 | 1
2015-05-03 10:15 | 2015-05-03 | 7 | 10 | 174 | 61.3167 | 1
2015-05-03 10:30 | 2015-05-03 | 7 | 10 | 174 | 61.5667 | 1
2015-05-03 10:45 | 2015-05-03 | 7 | 10 | 186 | 61.8167 | 1
2015-05-03 11:00 | 2015-05-03 | 7 | 11 | 174 | 62.1333 | 1
2015-05-03 11:15 | 2015-05-03 | 7 | 11 | 187 | 62.6333 | 1
2015-05-03 11:30 | 2015-05-03 | 7 | 11 | 227 | 63.1333 | 1
2015-05-03 11:45 | 2015-05-03 | 7 | 11 | 202 | 63.6333 | 1
2015-05-03 12:00 | 2015-05-03 | 7 | 12 | 214 | 64.0667 | 1
2015-05-03 12:15 | 2015-05-03 | 7 | 12 | 218 | 64.3167 | 1
2015-05-03 12:30 | 2015-05-03 | 7 | 12 | 216 | 64.5667 | 1
2015-05-03 12:45 | 2015-05-03 | 7 | 12 | 224 | 64.8167 | 1
2015-05-03 13:00 | 2015-05-03 | 7 | 13 | 233 | 64.9333 | 1
2015-05-03 13:15 | 2015-05-03 | 7 | 13 | 214 | 64.6833 | 1
2015-05-03 13:30 | 2015-05-03 | 7 | 13 | 228 | 64.4333 | 1
2015-05-03 13:45 | 2015-05-03 | 7 | 13 | 221 | 64.1833 | 1
2015-05-03 14:00 | 2015-05-03 | 7 | 14 | 218 | 64 | 1
2015-05-03 14:15 | 2015-05-03 | 7 | 14 | 229 | 64 | 1
2015-05-03 14:30 | 2015-05-03 | 7 | 14 | 222 | 64 | 1
2015-05-03 14:45 | 2015-05-03 | 7 | 14 | 231 | 64 | 1
2015-05-03 15:00 | 2015-05-03 | 7 | 15 | 228 | 63.9333 | 1
2015-05-03 15:15 | 2015-05-03 | 7 | 15 | 228 | 63.6833 | 1
2015-05-03 15:30 | 2015-05-03 | 7 | 15 | 242 | 63.4333 | 1
2015-05-03 15:45 | 2015-05-03 | 7 | 15 | 226 | 63.1833 | 1
2015-05-03 16:00 | 2015-05-03 | 7 | 16 | 237 | 62.8667 | 1
2015-05-03 16:15 | 2015-05-03 | 7 | 16 | 219 | 62.3667 | 1
2015-05-03 16:30 | 2015-05-03 | 7 | 16 | 226 | 61.8667 | 1
2015-05-03 16:45 | 2015-05-03 | 7 | 16 | 227 | 61.3667 | 1
2015-05-03 17:00 | 2015-05-03 | 7 | 17 | 236 | 60.8 | 1
2015-05-03 17:15 | 2015-05-03 | 7 | 17 | 223 | 60.05 | 1
2015-05-03 17:30 | 2015-05-03 | 7 | 17 | 220 | 59.3 | 1
2015-05-03 17:45 | 2015-05-03 | 7 | 17 | 216 | 58.55 | 1
2015-05-03 18:00 | 2015-05-03 | 7 | 18 | 225 | 57.8667 | 1
2015-05-03 18:15 | 2015-05-03 | 7 | 18 | 212 | 57.3667 | 1
2015-05-03 18:30 | 2015-05-03 | 7 | 18 | 203 | 56.8667 | 1
2015-05-03 18:45 | 2015-05-03 | 7 | 18 | 194 | 56.3667 | 1
2015-05-03 19:00 | 2015-05-03 | 7 | 19 | 194 | 55.9333 | 1
2015-05-03 19:15 | 2015-05-03 | 7 | 19 | 186 | 55.6833 | 1
2015-05-03 19:30 | 2015-05-03 | 7 | 19 | 191 | 55.4333 | 1
2015-05-03 19:45 | 2015-05-03 | 7 | 19 | 178 | 55.1833 | 1
2015-05-03 20:00 | 2015-05-03 | 7 | 20 | 200 | 54.9333 | 1
2015-05-03 20:15 | 2015-05-03 | 7 | 20 | 182 | 54.6833 | 1
2015-05-03 20:30 | 2015-05-03 | 7 | 20 | 181 | 54.4333 | 1
2015-05-03 20:45 | 2015-05-03 | 7 | 20 | 176 | 54.1833 | 1
2015-05-03 21:00 | 2015-05-03 | 7 | 21 | 183 | 54 | 1
2015-05-03 21:15 | 2015-05-03 | 7 | 21 | 163 | 54 | 1
2015-05-03 21:30 | 2015-05-03 | 7 | 21 | 158 | 54 | 1
2015-05-03 21:45 | 2015-05-03 | 7 | 21 | 167 | 54 | 1
2015-05-03 22:00 | 2015-05-03 | 7 | 22 | 162 | 53.9333 | 1
2015-05-03 22:15 | 2015-05-03 | 7 | 22 | 156 | 53.6833 | 1
2015-05-03 22:30 | 2015-05-03 | 7 | 22 | 156 | 53.4333 | 1
2015-05-03 22:45 | 2015-05-03 | 7 | 22 | 159 | 53.1833 | 1
2015-05-03 23:00 | 2015-05-03 | 7 | 23 | 164 | 53 | 1
2015-05-03 23:15 | 2015-05-03 | 7 | 23 | 156 | 53 | 1
2015-05-03 23:30 | 2015-05-03 | 7 | 23 | 158 | 53 | 1
2015-05-03 23:45 | 2015-05-03 | 7 | 23 | 149 | 53 | 1
2015-05-04 | 2015-05-04 | 1 | 0 | 157 | 53 | 1
2015-05-04 00:15 | 2015-05-04 | 1 | 0 | 157 | 53 | 1
2015-05-04 00:30 | 2015-05-04 | 1 | 0 | 155 | 53 | 1
2015-05-04 00:45 | 2015-05-04 | 1 | 0 | 163 | 53 | 1
2015-05-04 01:00 | 2015-05-04 | 1 | 1 | 153 | 52.9333 | 1
2015-05-04 01:15 | 2015-05-04 | 1 | 1 | 153 | 52.6833 | 1
2015-05-04 01:30 | 2015-05-04 | 1 | 1 | 153 | 52.4333 | 1
2015-05-04 01:45 | 2015-05-04 | 1 | 1 | 158 | 52.1833 | 1
2015-05-04 02:00 | 2015-05-04 | 1 | 2 | 161 | 52 | 1
2015-05-04 02:15 | 2015-05-04 | 1 | 2 | 151 | 52 | 1
2015-05-04 02:30 | 2015-05-04 | 1 | 2 | 152 | 52 | 1
2015-05-04 02:45 | 2015-05-04 | 1 | 2 | 152 | 52 | 1
2015-05-04 03:00 | 2015-05-04 | 1 | 3 | 164 | 52 | 1
2015-05-04 03:15 | 2015-05-04 | 1 | 3 | 146 | 52 | 1
2015-05-04 03:30 | 2015-05-04 | 1 | 3 | 150 | 52 | 1
2015-05-04 03:45 | 2015-05-04 | 1 | 3 | 146 | 52 | 1
2015-05-04 04:00 | 2015-05-04 | 1 | 4 | 160 | 52 | 1
2015-05-04 04:15 | 2015-05-04 | 1 | 4 | 147 | 52 | 1
2015-05-04 04:30 | 2015-05-04 | 1 | 4 | 149 | 52 | 1
2015-05-04 04:45 | 2015-05-04 | 1 | 4 | 149 | 52 | 1
2015-05-04 05:00 | 2015-05-04 | 1 | 5 | 146 | 52 | 1
2015-05-04 05:15 | 2015-05-04 | 1 | 5 | 160 | 52 | 1
2015-05-04 05:30 | 2015-05-04 | 1 | 5 | 144 | 52 | 1
2015-05-04 05:45 | 2015-05-04 | 1 | 5 | 145 | 52 | 1
2015-05-04 06:00 | 2015-05-04 | 1 | 6 | 152 | 52 | 1
2015-05-04 06:15 | 2015-05-04 | 1 | 6 | 155 | 52 | 1
2015-05-04 06:30 | 2015-05-04 | 1 | 6 | 149 | 52 | 1
2015-05-04 06:45 | 2015-05-04 | 1 | 6 | 152 | 52 | 1
2015-05-04 07:00 | 2015-05-04 | 1 | 7 | 80 | 52.0667 | 1
2015-05-04 07:15 | 2015-05-04 | 1 | 7 | 47 | 52.3167 | 1
2015-05-04 07:30 | 2015-05-04 | 1 | 7 | 47 | 52.5667 | 1
2015-05-04 07:45 | 2015-05-04 | 1 | 7 | 57 | 52.8167 | 1
2015-05-04 08:00 | 2015-05-04 | 1 | 8 | 63 | 53.069 | 1
2015-05-04 08:15 | 2015-05-04 | 1 | 8 | 64 | 53.3276 | 1
2015-05-04 08:30 | 2015-05-04 | 1 | 8 | 63 | 53.5862 | 1
2015-05-04 08:45 | 2015-05-04 | 1 | 8 | 62 | 53.8448 | 1
2015-05-04 09:00 | 2015-05-04 | 1 | 9 | 71 | 53 | 1
2015-05-04 09:15 | 2015-05-04 | 1 | 9 | 130 | 53 | 1
2015-05-04 09:30 | 2015-05-04 | 1 | 9 | 165 | 53 | 1
2015-05-04 09:45 | 2015-05-04 | 1 | 9 | 169 | 53 | 1
2015-05-04 10:00 | 2015-05-04 | 1 | 10 | 173 | 53.2424 | 1
2015-05-04 10:15 | 2015-05-04 | 1 | 10 | 178 | 54.1515 | 1
2015-05-04 10:30 | 2015-05-04 | 1 | 10 | 178 | 55.037 | 1
2015-05-04 10:45 | 2015-05-04 | 1 | 10 | 178 | 55.5926 | 1
2015-05-04 11:00 | 2015-05-04 | 1 | 11 | 175 | 56.1333 | 1
2015-05-04 11:15 | 2015-05-04 | 1 | 11 | 187 | 56.6333 | 1
2015-05-04 11:30 | 2015-05-04 | 1 | 11 | 204 | 57.1333 | 1
2015-05-04 11:45 | 2015-05-04 | 1 | 11 | 208 | 57.6333 | 1
2015-05-04 12:00 | 2015-05-04 | 1 | 12 | 212 | 58.0667 | 1
2015-05-04 12:15 | 2015-05-04 | 1 | 12 | 192 | 58.3167 | 1
2015-05-04 12:30 | 2015-05-04 | 1 | 12 | 213 | 58.5667 | 1
2015-05-04 12:45 | 2015-05-04 | 1 | 12 | 203 | 58.8167 | 1
2015-05-04 13:00 | 2015-05-04 | 1 | 13 | 206 | 59.2963 | 1
2015-05-04 13:15 | 2015-05-04 | 1 | 13 | 213 | 60.4074 | 1
2015-05-04 13:30 | 2015-05-04 | 1 | 13 | 200 | 60.5758 | 1
2015-05-04 13:45 | 2015-05-04 | 1 | 13 | 212 | 59.6667 | 1
2015-05-04 14:00 | 2015-05-04 | 1 | 14 | 211 | 59 | 1
2015-05-04 14:15 | 2015-05-04 | 1 | 14 | 209 | 59 | 1
2015-05-04 14:30 | 2015-05-04 | 1 | 14 | 227 | 58.3 | 1
2015-05-04 14:45 | 2015-05-04 | 1 | 14 | 209 | 57.55 | 1
2015-05-04 15:00 | 2015-05-04 | 1 | 15 | 219 | 56.9333 | 1
2015-05-04 15:15 | 2015-05-04 | 1 | 15 | 227 | 56.6833 | 1
2015-05-04 15:30 | 2015-05-04 | 1 | 15 | 215 | 56.4333 | 1
2015-05-04 15:45 | 2015-05-04 | 1 | 15 | 230 | 56.1833 | 1
2015-05-04 16:00 | 2015-05-04 | 1 | 16 | 210 | 56 | 1
2015-05-04 16:15 | 2015-05-04 | 1 | 16 | 224 | 56 | 1
2015-05-04 16:30 | 2015-05-04 | 1 | 16 | 227 | 56 | 1
2015-05-04 16:45 | 2015-05-04 | 1 | 16 | 214 | 56 | 1
2015-05-04 17:00 | 2015-05-04 | 1 | 17 | 227 | 55.9333 | 1
2015-05-04 17:15 | 2015-05-04 | 1 | 17 | 211 | 55.6833 | 1
2015-05-04 17:30 | 2015-05-04 | 1 | 17 | 216 | 55.4333 | 1
2015-05-04 17:45 | 2015-05-04 | 1 | 17 | 215 | 55.1833 | 1
2015-05-04 18:00 | 2015-05-04 | 1 | 18 | 209 | 54.9333 | 1
2015-05-04 18:15 | 2015-05-04 | 1 | 18 | 203 | 54.6833 | 1
2015-05-04 18:30 | 2015-05-04 | 1 | 18 | 195 | 54.4333 | 1
2015-05-04 18:45 | 2015-05-04 | 1 | 18 | 204 | 54.1833 | 1
2015-05-04 19:00 | 2015-05-04 | 1 | 19 | 195 | 54 | 1
2015-05-04 19:15 | 2015-05-04 | 1 | 19 | 189 | 54 | 1
2015-05-04 19:30 | 2015-05-04 | 1 | 19 | 184 | 54 | 1
2015-05-04 19:45 | 2015-05-04 | 1 | 19 | 185 | 54 | 1
2015-05-04 20:00 | 2015-05-04 | 1 | 20 | 171 | 54 | 1
2015-05-04 20:15 | 2015-05-04 | 1 | 20 | 171 | 54 | 1
2015-05-04 20:30 | 2015-05-04 | 1 | 20 | 171 | 54 | 1
2015-05-04 20:45 | 2015-05-04 | 1 | 20 | 170 | 54 | 1
2015-05-04 21:00 | 2015-05-04 | 1 | 21 | 172 | 53.9333 | 1
2015-05-04 21:15 | 2015-05-04 | 1 | 21 | 163 | 53.6833 | 1
2015-05-04 21:30 | 2015-05-04 | 1 | 21 | 148 | 53.4333 | 1
2015-05-04 21:45 | 2015-05-04 | 1 | 21 | 148 | 53.1833 | 1
2015-05-04 22:00 | 2015-05-04 | 1 | 22 | 146 | 53.1429 | 1
2015-05-04 22:15 | 2015-05-04 | 1 | 22 | 152 | 53.6786 | 1
2015-05-04 22:30 | 2015-05-04 | 1 | 22 | 151 | 53.8125 | 1
2015-05-04 22:45 | 2015-05-04 | 1 | 22 | 151 | 53.3438 | 1
2015-05-04 23:00 | 2015-05-04 | 1 | 23 | 150 | 53 | 1
2015-05-04 23:15 | 2015-05-04 | 1 | 23 | 150 | 53 | 1
2015-05-04 23:30 | 2015-05-04 | 1 | 23 | 154 | 53 | 1
2015-05-04 23:45 | 2015-05-04 | 1 | 23 | 151 | 53 | 1
2015-05-05 | 2015-05-05 | 2 | 0 | 158 | 53 | 1
2015-05-05 00:15 | 2015-05-05 | 2 | 0 | 153 | 53 | 1
2015-05-05 00:30 | 2015-05-05 | 2 | 0 | 149 | 53 | 1
2015-05-05 00:45 | 2015-05-05 | 2 | 0 | 145 | 53 | 1
2015-05-05 01:00 | 2015-05-05 | 2 | 1 | 142 | 52.9333 | 1
2015-05-05 01:15 | 2015-05-05 | 2 | 1 | 142 | 52.6833 | 1
2015-05-05 01:30 | 2015-05-05 | 2 | 1 | 133 | 52.4333 | 1
2015-05-05 01:45 | 2015-05-05 | 2 | 1 | 138 | 52.1833 | 1
2015-05-05 02:00 | 2015-05-05 | 2 | 2 | 133 | 52 | 1
2015-05-05 02:15 | 2015-05-05 | 2 | 2 | 138 | 52 | 1
2015-05-05 02:30 | 2015-05-05 | 2 | 2 | 133 | 52 | 1
2015-05-05 02:45 | 2015-05-05 | 2 | 2 | 135 | 52 | 1
2015-05-05 03:00 | 2015-05-05 | 2 | 3 | 135 | 52 | 1
2015-05-05 03:15 | 2015-05-05 | 2 | 3 | 134 | 52 | 1
2015-05-05 03:30 | 2015-05-05 | 2 | 3 | 135 | 52 | 1
2015-05-05 03:45 | 2015-05-05 | 2 | 3 | 133 | 52 | 1
2015-05-05 04:00 | 2015-05-05 | 2 | 4 | 136 | 52.0667 | 1
2015-05-05 04:15 | 2015-05-05 | 2 | 4 | 131 | 52.3167 | 1
2015-05-05 04:30 | 2015-05-05 | 2 | 4 | 136 | 52.5667 | 1
2015-05-05 04:45 | 2015-05-05 | 2 | 4 | 130 | 52.8167 | 1
2015-05-05 05:00 | 2015-05-05 | 2 | 5 | 134 | 53 | 1
2015-05-05 05:15 | 2015-05-05 | 2 | 5 | 130 | 53 | 1
2015-05-05 05:30 | 2015-05-05 | 2 | 5 | 133 | 53 | 1
2015-05-05 05:45 | 2015-05-05 | 2 | 5 | 131 | 53 | 1
2015-05-05 06:00 | 2015-05-05 | 2 | 6 | 134 | 53 | 1
2015-05-05 06:15 | 2015-05-05 | 2 | 6 | 136 | 53 | 1
2015-05-05 06:30 | 2015-05-05 | 2 | 6 | 136 | 53 | 1
2015-05-05 06:45 | 2015-05-05 | 2 | 6 | 133 | 53 | 1
2015-05-05 07:00 | 2015-05-05 | 2 | 7 | 135 | 53.1333 | 1
2015-05-05 07:15 | 2015-05-05 | 2 | 7 | 134 | 53.6333 | 1
2015-05-05 07:30 | 2015-05-05 | 2 | 7 | 140 | 54.1333 | 1
2015-05-05 07:45 | 2015-05-05 | 2 | 7 | 149 | 54.6333 | 1
2015-05-05 08:00 | 2015-05-05 | 2 | 8 | 157 | 55.1333 | 1
2015-05-05 08:15 | 2015-05-05 | 2 | 8 | 156 | 55.6333 | 1
2015-05-05 08:30 | 2015-05-05 | 2 | 8 | 158 | 56.1333 | 1
2015-05-05 08:45 | 2015-05-05 | 2 | 8 | 161 | 56.6333 | 1
2015-05-05 09:00 | 2015-05-05 | 2 | 9 | 167 | 57 | 1
2015-05-05 09:15 | 2015-05-05 | 2 | 9 | 178 | 57 | 1
2015-05-05 09:30 | 2015-05-05 | 2 | 9 | 175 | 57 | 1
2015-05-05 09:45 | 2015-05-05 | 2 | 9 | 174 | 57 | 1
2015-05-05 10:00 | 2015-05-05 | 2 | 10 | 177 | 57.2 | 1
2015-05-05 10:15 | 2015-05-05 | 2 | 10 | 187 | 57.95 | 1
2015-05-05 10:30 | 2015-05-05 | 2 | 10 | 198 | 58.7 | 1
2015-05-05 10:45 | 2015-05-05 | 2 | 10 | 199 | 59.45 | 1
2015-05-05 11:00 | 2015-05-05 | 2 | 11 | 191 | 60 | 1
2015-05-05 11:15 | 2015-05-05 | 2 | 11 | 202 | 60 | 1
2015-05-05 11:30 | 2015-05-05 | 2 | 11 | 205 | 60 | 1
2015-05-05 11:45 | 2015-05-05 | 2 | 11 | 209 | 60 | 1
2015-05-05 12:00 | 2015-05-05 | 2 | 12 | 216 | 60.0667 | 1
2015-05-05 12:15 | 2015-05-05 | 2 | 12 | 206 | 60.3167 | 1
2015-05-05 12:30 | 2015-05-05 | 2 | 12 | 218 | 60.5667 | 1
2015-05-05 12:45 | 2015-05-05 | 2 | 12 | 216 | 60.8167 | 1
2015-05-05 13:00 | 2015-05-05 | 2 | 13 | 214 | 61 | 1
2015-05-05 13:15 | 2015-05-05 | 2 | 13 | 219 | 61 | 1
2015-05-05 13:30 | 2015-05-05 | 2 | 13 | 226 | 61 | 1
2015-05-05 13:45 | 2015-05-05 | 2 | 13 | 216 | 61 | 1
2015-05-05 14:00 | 2015-05-05 | 2 | 14 | 232 | 60.9333 | 1
2015-05-05 14:15 | 2015-05-05 | 2 | 14 | 228 | 60.6833 | 1
2015-05-05 14:30 | 2015-05-05 | 2 | 14 | 216 | 60.4333 | 1
2015-05-05 14:45 | 2015-05-05 | 2 | 14 | 230 | 60.1833 | 1
2015-05-05 15:00 | 2015-05-05 | 2 | 15 | 222 | 59.9333 | 1
2015-05-05 15:15 | 2015-05-05 | 2 | 15 | 229 | 59.6833 | 1
2015-05-05 15:30 | 2015-05-05 | 2 | 15 | 241 | 59.4333 | 1
2015-05-05 15:45 | 2015-05-05 | 2 | 15 | 228 | 59.1833 | 1
2015-05-05 16:00 | 2015-05-05 | 2 | 16 | 220 | 58.8667 | 1
2015-05-05 16:15 | 2015-05-05 | 2 | 16 | 244 | 58.3667 | 1
2015-05-05 16:30 | 2015-05-05 | 2 | 16 | 228 | 57.8667 | 1
2015-05-05 16:45 | 2015-05-05 | 2 | 16 | 232 | 57.3667 | 1
2015-05-05 17:00 | 2015-05-05 | 2 | 17 | 233 | 56.9333 | 1
2015-05-05 17:15 | 2015-05-05 | 2 | 17 | 234 | 56.6833 | 1
2015-05-05 17:30 | 2015-05-05 | 2 | 17 | 222 | 56.4333 | 1
2015-05-05 17:45 | 2015-05-05 | 2 | 17 | 209 | 56.1833 | 1
2015-05-05 18:00 | 2015-05-05 | 2 | 18 | 219 | 55.9333 | 1
2015-05-05 18:15 | 2015-05-05 | 2 | 18 | 213 | 55.6833 | 1
2015-05-05 18:30 | 2015-05-05 | 2 | 18 | 205 | 55.4333 | 1
2015-05-05 18:45 | 2015-05-05 | 2 | 18 | 196 | 55.1833 | 1
2015-05-05 19:00 | 2015-05-05 | 2 | 19 | 201 | 54.9333 | 1
2015-05-05 19:15 | 2015-05-05 | 2 | 19 | 193 | 54.6833 | 1
2015-05-05 19:30 | 2015-05-05 | 2 | 19 | 197 | 54.4333 | 1
2015-05-05 19:45 | 2015-05-05 | 2 | 19 | 190 | 54.1833 | 1
2015-05-05 20:00 | 2015-05-05 | 2 | 20 | 185 | 54 | 1
2015-05-05 20:15 | 2015-05-05 | 2 | 20 | 185 | 54 | 1
2015-05-05 20:30 | 2015-05-05 | 2 | 20 | 182 | 54 | 1
2015-05-05 20:45 | 2015-05-05 | 2 | 20 | 173 | 54 | 1
2015-05-05 21:00 | 2015-05-05 | 2 | 21 | 176 | 53.9333 | 1
2015-05-05 21:15 | 2015-05-05 | 2 | 21 | 159 | 53.6833 | 1
2015-05-05 21:30 | 2015-05-05 | 2 | 21 | 162 | 53.4333 | 1
2015-05-05 21:45 | 2015-05-05 | 2 | 21 | 154 | 53.1833 | 1
2015-05-05 22:00 | 2015-05-05 | 2 | 22 | 158 | 53 | 1
2015-05-05 22:15 | 2015-05-05 | 2 | 22 | 153 | 53 | 1
2015-05-05 22:30 | 2015-05-05 | 2 | 22 | 158 | 53 | 1
2015-05-05 22:45 | 2015-05-05 | 2 | 22 | 158 | 53 | 1
2015-05-05 23:00 | 2015-05-05 | 2 | 23 | 163 | 52.9333 | 1
2015-05-05 23:15 | 2015-05-05 | 2 | 23 | 155 | 52.6833 | 1
2015-05-05 23:30 | 2015-05-05 | 2 | 23 | 155 | 52.4333 | 1
2015-05-05 23:45 | 2015-05-05 | 2 | 23 | 155 | 52.1833 | 1
2015-05-06 | 2015-05-06 | 3 | 0 | 154 | 52 | 1
2015-05-06 00:15 | 2015-05-06 | 3 | 0 | 153 | 52 | 1
2015-05-06 00:30 | 2015-05-06 | 3 | 0 | 152 | 52 | 1
2015-05-06 00:45 | 2015-05-06 | 3 | 0 | 147 | 52 | 1
2015-05-06 01:00 | 2015-05-06 | 3 | 1 | 152 | 52 | 1
2015-05-06 01:15 | 2015-05-06 | 3 | 1 | 145 | 52 | 1
2015-05-06 01:30 | 2015-05-06 | 3 | 1 | 149 | 52 | 1
2015-05-06 01:45 | 2015-05-06 | 3 | 1 | 144 | 52 | 1
2015-05-06 02:00 | 2015-05-06 | 3 | 2 | 146 | 51.9333 | 1
2015-05-06 02:15 | 2015-05-06 | 3 | 2 | 145 | 51.6833 | 1
2015-05-06 02:30 | 2015-05-06 | 3 | 2 | 145 | 51.4333 | 1
2015-05-06 02:45 | 2015-05-06 | 3 | 2 | 146 | 51.1833 | 1
2015-05-06 03:00 | 2015-05-06 | 3 | 3 | 140 | 51.2222 | 1
2015-05-06 03:15 | 2015-05-06 | 3 | 3 | 143 | 51.9762 | 1
2015-05-06 03:30 | 2015-05-06 | 3 | 3 | 142 | 51.619 | 1
2015-05-06 03:45 | 2015-05-06 | 3 | 3 | 145 | 51.2619 | 1
2015-05-06 04:00 | 2015-05-06 | 3 | 4 | 143 | 51.1818 | 1
2015-05-06 04:15 | 2015-05-06 | 3 | 4 | 141 | 51.8636 | 1
2015-05-06 04:30 | 2015-05-06 | 3 | 4 | 144 | 51.6842 | 1
2015-05-06 04:45 | 2015-05-06 | 3 | 4 | 143 | 51.2895 | 1
2015-05-06 05:00 | 2015-05-06 | 3 | 5 | 134 | 51.1026 | 1
2015-05-06 05:15 | 2015-05-06 | 3 | 5 | 141 | 51.4872 | 1
2015-05-06 05:30 | 2015-05-06 | 3 | 5 | 135 | 51.8718 | 1
2015-05-06 05:45 | 2015-05-06 | 3 | 5 | 139 | 51.5238 | 1
2015-05-06 06:00 | 2015-05-06 | 3 | 6 | 141 | 51.1333 | 1
2015-05-06 06:15 | 2015-05-06 | 3 | 6 | 141 | 51.6333 | 1
2015-05-06 06:30 | 2015-05-06 | 3 | 6 | 143 | 52.1333 | 1
2015-05-06 06:45 | 2015-05-06 | 3 | 6 | 146 | 52.6333 | 1
2015-05-06 07:00 | 2015-05-06 | 3 | 7 | 144 | 53.1333 | 1
2015-05-06 07:15 | 2015-05-06 | 3 | 7 | 145 | 53.6333 | 1
2015-05-06 07:30 | 2015-05-06 | 3 | 7 | 150 | 54.1333 | 1
2015-05-06 07:45 | 2015-05-06 | 3 | 7 | 151 | 54.6333 | 1
2015-05-06 08:00 | 2015-05-06 | 3 | 8 | 165 | 55.2 | 1
2015-05-06 08:15 | 2015-05-06 | 3 | 8 | 166 | 55.95 | 1
2015-05-06 08:30 | 2015-05-06 | 3 | 8 | 170 | 56.7 | 1
2015-05-06 08:45 | 2015-05-06 | 3 | 8 | 179 | 57.45 | 1
2015-05-06 09:00 | 2015-05-06 | 3 | 9 | 179 | 58 | 1
2015-05-06 09:15 | 2015-05-06 | 3 | 9 | 188 | 58 | 1
2015-05-06 09:30 | 2015-05-06 | 3 | 9 | 184 | 58 | 1
2015-05-06 09:45 | 2015-05-06 | 3 | 9 | 192 | 58 | 1
2015-05-06 10:00 | 2015-05-06 | 3 | 10 | 189 | 58.2 | 1
2015-05-06 10:15 | 2015-05-06 | 3 | 10 | 199 | 58.95 | 1
2015-05-06 10:30 | 2015-05-06 | 3 | 10 | 199 | 59.7 | 1
2015-05-06 10:45 | 2015-05-06 | 3 | 10 | 203 | 60.45 | 1
2015-05-06 11:00 | 2015-05-06 | 3 | 11 | 203 | 61.2927 | 1
2015-05-06 11:15 | 2015-05-06 | 3 | 11 | 205 | 62.3902 | 1
2015-05-06 11:30 | 2015-05-06 | 3 | 11 | 210 | 63.4878 | 1
2015-05-06 11:45 | 2015-05-06 | 3 | 11 | 210 | 64 | 1
2015-05-06 12:00 | 2015-05-06 | 3 | 12 | 203 | 63.9333 | 1
2015-05-06 12:15 | 2015-05-06 | 3 | 12 | 212 | 63.6833 | 1
2015-05-06 12:30 | 2015-05-06 | 3 | 12 | 211 | 63.4333 | 1
2015-05-06 12:45 | 2015-05-06 | 3 | 12 | 203 | 63.1833 | 1
2015-05-06 13:00 | 2015-05-06 | 3 | 13 | 210 | 63 | 1
2015-05-06 13:15 | 2015-05-06 | 3 | 13 | 217 | 63 | 1
2015-05-06 13:30 | 2015-05-06 | 3 | 13 | 211 | 63 | 1
2015-05-06 13:45 | 2015-05-06 | 3 | 13 | 227 | 63 | 1
2015-05-06 14:00 | 2015-05-06 | 3 | 14 | 232 | 63 | 1
2015-05-06 14:15 | 2015-05-06 | 3 | 14 | 217 | 63 | 1
2015-05-06 14:30 | 2015-05-06 | 3 | 14 | 236 | 63 | 1
2015-05-06 14:45 | 2015-05-06 | 3 | 14 | 233 | 63 | 1
2015-05-06 15:00 | 2015-05-06 | 3 | 15 | 230 | 62.8667 | 1
2015-05-06 15:15 | 2015-05-06 | 3 | 15 | 249 | 62.3667 | 1
2015-05-06 15:30 | 2015-05-06 | 3 | 15 | 238 | 61.8667 | 1
2015-05-06 15:45 | 2015-05-06 | 3 | 15 | 248 | 61.3667 | 1
2015-05-06 16:00 | 2015-05-06 | 3 | 16 | 244 | 60.9333 | 1
2015-05-06 16:15 | 2015-05-06 | 3 | 16 | 248 | 60.6833 | 1
2015-05-06 16:30 | 2015-05-06 | 3 | 16 | 252 | 60.4333 | 1
2015-05-06 16:45 | 2015-05-06 | 3 | 16 | 249 | 60.1833 | 1
2015-05-06 17:00 | 2015-05-06 | 3 | 17 | 253 | 59.8 | 1
2015-05-06 17:15 | 2015-05-06 | 3 | 17 | 240 | 59.05 | 1
2015-05-06 17:30 | 2015-05-06 | 3 | 17 | 243 | 58.3 | 1
2015-05-06 17:45 | 2015-05-06 | 3 | 17 | 245 | 57.55 | 1
2015-05-06 18:00 | 2015-05-06 | 3 | 18 | 232 | 56.8667 | 1
2015-05-06 18:15 | 2015-05-06 | 3 | 18 | 244 | 56.3667 | 1
2015-05-06 18:30 | 2015-05-06 | 3 | 18 | 229 | 55.8667 | 1
2015-05-06 18:45 | 2015-05-06 | 3 | 18 | 227 | 55.3667 | 1
2015-05-06 19:00 | 2015-05-06 | 3 | 19 | 226 | 54.8667 | 1
2015-05-06 19:15 | 2015-05-06 | 3 | 19 | 217 | 54.3667 | 1
2015-05-06 19:30 | 2015-05-06 | 3 | 19 | 219 | 53.8667 | 1
2015-05-06 19:45 | 2015-05-06 | 3 | 19 | 212 | 53.3667 | 1
2015-05-06 20:00 | 2015-05-06 | 3 | 20 | 211 | 53 | 1
2015-05-06 20:15 | 2015-05-06 | 3 | 20 | 200 | 53 | 1
2015-05-06 20:30 | 2015-05-06 | 3 | 20 | 201 | 53 | 1
2015-05-06 20:45 | 2015-05-06 | 3 | 20 | 192 | 53 | 1
2015-05-06 21:00 | 2015-05-06 | 3 | 21 | 194 | 53 | 1
2015-05-06 21:15 | 2015-05-06 | 3 | 21 | 172 | 53 | 1
2015-05-06 21:30 | 2015-05-06 | 3 | 21 | 164 | 53 | 1
2015-05-06 21:45 | 2015-05-06 | 3 | 21 | 167 | 53 | 1
2015-05-06 22:00 | 2015-05-06 | 3 | 22 | 169 | 52.9333 | 1
2015-05-06 22:15 | 2015-05-06 | 3 | 22 | 168 | 52.6833 | 1
2015-05-06 22:30 | 2015-05-06 | 3 | 22 | 161 | 52.4333 | 1
2015-05-06 22:45 | 2015-05-06 | 3 | 22 | 159 | 52.1833 | 1
2015-05-06 23:00 | 2015-05-06 | 3 | 23 | 163 | 52 | 1
2015-05-06 23:15 | 2015-05-06 | 3 | 23 | 158 | 52 | 1
2015-05-06 23:30 | 2015-05-06 | 3 | 23 | 154 | 52 | 1
2015-05-06 23:45 | 2015-05-06 | 3 | 23 | 152 | 52 | 1
2015-05-07 | 2015-05-07 | 4 | 0 | 148 | 52 | 1
2015-05-07 00:15 | 2015-05-07 | 4 | 0 | 150 | 52 | 1
2015-05-07 00:30 | 2015-05-07 | 4 | 0 | 143 | 52 | 1
2015-05-07 00:45 | 2015-05-07 | 4 | 0 | 146 | 52 | 1
2015-05-07 01:00 | 2015-05-07 | 4 | 1 | 148 | 51.9333 | 1
2015-05-07 01:15 | 2015-05-07 | 4 | 1 | 143 | 51.6833 | 1
2015-05-07 01:30 | 2015-05-07 | 4 | 1 | 147 | 51.4333 | 1
2015-05-07 01:45 | 2015-05-07 | 4 | 1 | 142 | 51.1833 | 1
2015-05-07 02:00 | 2015-05-07 | 4 | 2 | 141 | 51 | 1
2015-05-07 02:15 | 2015-05-07 | 4 | 2 | 142 | 51 | 1
2015-05-07 02:30 | 2015-05-07 | 4 | 2 | 140 | 51 | 1
2015-05-07 02:45 | 2015-05-07 | 4 | 2 | 138 | 51 | 1
2015-05-07 03:00 | 2015-05-07 | 4 | 3 | 135 | 50.9333 | 1
2015-05-07 03:15 | 2015-05-07 | 4 | 3 | 137 | 50.6833 | 1
2015-05-07 03:30 | 2015-05-07 | 4 | 3 | 137 | 50.4333 | 1
2015-05-07 03:45 | 2015-05-07 | 4 | 3 | 135 | 50.1833 | 1
2015-05-07 04:00 | 2015-05-07 | 4 | 4 | 141 | 50 | 1
2015-05-07 04:15 | 2015-05-07 | 4 | 4 | 137 | 50 | 1
2015-05-07 04:30 | 2015-05-07 | 4 | 4 | 139 | 50 | 1
2015-05-07 04:45 | 2015-05-07 | 4 | 4 | 142 | 50 | 1
2015-05-07 05:00 | 2015-05-07 | 4 | 5 | 137 | 50.0667 | 1
2015-05-07 05:15 | 2015-05-07 | 4 | 5 | 141 | 50.3167 | 1
2015-05-07 05:30 | 2015-05-07 | 4 | 5 | 138 | 50.5667 | 1
2015-05-07 05:45 | 2015-05-07 | 4 | 5 | 141 | 50.8167 | 1
2015-05-07 06:00 | 2015-05-07 | 4 | 6 | 133 | 51.1333 | 1
2015-05-07 06:15 | 2015-05-07 | 4 | 6 | 137 | 51.6333 | 1
2015-05-07 06:30 | 2015-05-07 | 4 | 6 | 138 | 52.1333 | 1
2015-05-07 06:45 | 2015-05-07 | 4 | 6 | 138 | 52.6333 | 1
2015-05-07 07:00 | 2015-05-07 | 4 | 7 | 137 | 53.1333 | 1
2015-05-07 07:15 | 2015-05-07 | 4 | 7 | 137 | 53.6333 | 1
2015-05-07 07:30 | 2015-05-07 | 4 | 7 | 138 | 54.1333 | 1
2015-05-07 07:45 | 2015-05-07 | 4 | 7 | 148 | 54.6333 | 1
2015-05-07 08:00 | 2015-05-07 | 4 | 8 | 152 | 55.1333 | 1
2015-05-07 08:15 | 2015-05-07 | 4 | 8 | 159 | 55.6333 | 1
2015-05-07 08:30 | 2015-05-07 | 4 | 8 | 160 | 56.1333 | 1
2015-05-07 08:45 | 2015-05-07 | 4 | 8 | 172 | 56.6333 | 1
2015-05-07 09:00 | 2015-05-07 | 4 | 9 | 172 | 57.2 | 1
2015-05-07 09:15 | 2015-05-07 | 4 | 9 | 175 | 57.95 | 1
2015-05-07 09:30 | 2015-05-07 | 4 | 9 | 176 | 58.7 | 1
2015-05-07 09:45 | 2015-05-07 | 4 | 9 | 181 | 59.45 | 1
2015-05-07 10:00 | 2015-05-07 | 4 | 10 | 170 | 60.0667 | 1
2015-05-07 10:15 | 2015-05-07 | 4 | 10 | 173 | 60.3167 | 1
2015-05-07 10:30 | 2015-05-07 | 4 | 10 | 176 | 60.5667 | 1
2015-05-07 10:45 | 2015-05-07 | 4 | 10 | 179 | 60.8167 | 1
2015-05-07 11:00 | 2015-05-07 | 4 | 11 | 190 | 61 | 1
2015-05-07 11:15 | 2015-05-07 | 4 | 11 | 185 | 60.8039 | 1
2015-05-07 11:30 | 2015-05-07 | 4 | 11 | 200 | 60.5098 | 1
2015-05-07 11:45 | 2015-05-07 | 4 | 11 | 186 | 60.2157 | 1
2015-05-07 12:00 | 2015-05-07 | 4 | 12 | 196 | 60.0667 | 1
2015-05-07 12:15 | 2015-05-07 | 4 | 12 | 185 | 60.3167 | 1
2015-05-07 12:30 | 2015-05-07 | 4 | 12 | 187 | 60.5667 | 1
2015-05-07 12:45 | 2015-05-07 | 4 | 12 | 178 | 60.8167 | 1
2015-05-07 13:00 | 2015-05-07 | 4 | 13 | 189 | 61.2 | 1
2015-05-07 13:15 | 2015-05-07 | 4 | 13 | 183 | 61.95 | 1
2015-05-07 13:30 | 2015-05-07 | 4 | 13 | 185 | 62.7 | 1
2015-05-07 13:45 | 2015-05-07 | 4 | 13 | 181 | 63.45 | 1
2015-05-07 14:00 | 2015-05-07 | 4 | 14 | 182 | 64.1333 | 1
2015-05-07 14:15 | 2015-05-07 | 4 | 14 | 185 | 64.6333 | 1
2015-05-07 14:30 | 2015-05-07 | 4 | 14 | 179 | 65.1333 | 2
2015-05-07 14:45 | 2015-05-07 | 4 | 14 | 186 | 65.6333 | 2
2015-05-07 15:00 | 2015-05-07 | 4 | 15 | 188 | 65.7333 | 2
2015-05-07 15:15 | 2015-05-07 | 4 | 15 | 196 | 64.7333 | 1
2015-05-07 15:30 | 2015-05-07 | 4 | 15 | 195 | 63.7333 | 1
2015-05-07 15:45 | 2015-05-07 | 4 | 15 | 205 | 62.7333 | 1
2015-05-07 16:00 | 2015-05-07 | 4 | 16 | 204 | 62 | 1
2015-05-07 16:15 | 2015-05-07 | 4 | 16 | 191 | 62 | 1
2015-05-07 16:30 | 2015-05-07 | 4 | 16 | 193 | 62 | 1
2015-05-07 16:45 | 2015-05-07 | 4 | 16 | 178 | 62 | 1
2015-05-07 17:00 | 2015-05-07 | 4 | 17 | 180 | 62.0667 | 1
2015-05-07 17:15 | 2015-05-07 | 4 | 17 | 176 | 62.3167 | 1
2015-05-07 17:30 | 2015-05-07 | 4 | 17 | 183 | 62.5667 | 1
2015-05-07 17:45 | 2015-05-07 | 4 | 17 | 174 | 62.8167 | 1
2015-05-07 18:00 | 2015-05-07 | 4 | 18 | 185 | 62.8 | 1
2015-05-07 18:15 | 2015-05-07 | 4 | 18 | 175 | 62.05 | 1
2015-05-07 18:30 | 2015-05-07 | 4 | 18 | 186 | 61.3 | 1
2015-05-07 18:45 | 2015-05-07 | 4 | 18 | 166 | 60.55 | 1
2015-05-07 19:00 | 2015-05-07 | 4 | 19 | 180 | 59.7333 | 1
2015-05-07 19:15 | 2015-05-07 | 4 | 19 | 168 | 58.7333 | 1
2015-05-07 19:30 | 2015-05-07 | 4 | 19 | 179 | 57.7333 | 1
2015-05-07 19:45 | 2015-05-07 | 4 | 19 | 164 | 56.7333 | 1
2015-05-07 20:00 | 2015-05-07 | 4 | 20 | 166 | 55.8667 | 1
2015-05-07 20:15 | 2015-05-07 | 4 | 20 | 165 | 55.3667 | 1
2015-05-07 20:30 | 2015-05-07 | 4 | 20 | 172 | 54.8667 | 1
2015-05-07 20:45 | 2015-05-07 | 4 | 20 | 168 | 54.3667 | 1
2015-05-07 21:00 | 2015-05-07 | 4 | 21 | 165 | 54 | 1
2015-05-07 21:15 | 2015-05-07 | 4 | 21 | 153 | 54 | 1
2015-05-07 21:30 | 2015-05-07 | 4 | 21 | 151 | 54 | 1
2015-05-07 21:45 | 2015-05-07 | 4 | 21 | 158 | 54 | 1
2015-05-07 22:00 | 2015-05-07 | 4 | 22 | 157 | 53.9333 | 1
2015-05-07 22:15 | 2015-05-07 | 4 | 22 | 146 | 53.6833 | 1
2015-05-07 22:30 | 2015-05-07 | 4 | 22 | 146 | 53.4333 | 1
2015-05-07 22:45 | 2015-05-07 | 4 | 22 | 145 | 53.1833 | 1
2015-05-07 23:00 | 2015-05-07 | 4 | 23 | 165 | 52.9333 | 1
2015-05-07 23:15 | 2015-05-07 | 4 | 23 | 149 | 52.6833 | 1
2015-05-07 23:30 | 2015-05-07 | 4 | 23 | 152 | 52.4333 | 1
2015-05-07 23:45 | 2015-05-07 | 4 | 23 | 143 | 52.1833 | 1
2015-05-08 | 2015-05-08 | 5 | 0 | 160 | 52 | 1
2015-05-08 00:15 | 2015-05-08 | 5 | 0 | 145 | 52 | 1
2015-05-08 00:30 | 2015-05-08 | 5 | 0 | 147 | 52 | 1
2015-05-08 00:45 | 2015-05-08 | 5 | 0 | 140 | 52 | 1
2015-05-08 01:00 | 2015-05-08 | 5 | 1 | 144 | 52.0667 | 1
2015-05-08 01:15 | 2015-05-08 | 5 | 1 | 142 | 52.3167 | 1
2015-05-08 01:30 | 2015-05-08 | 5 | 1 | 156 | 52.5667 | 1
2015-05-08 01:45 | 2015-05-08 | 5 | 1 | 141 | 52.8167 | 1
2015-05-08 02:00 | 2015-05-08 | 5 | 2 | 141 | 53 | 1
2015-05-08 02:15 | 2015-05-08 | 5 | 2 | 144 | 53 | 1
2015-05-08 02:30 | 2015-05-08 | 5 | 2 | 141 | 53 | 1
2015-05-08 02:45 | 2015-05-08 | 5 | 2 | 138 | 53 | 1
2015-05-08 03:00 | 2015-05-08 | 5 | 3 | 139 | 52.9333 | 1
2015-05-08 03:15 | 2015-05-08 | 5 | 3 | 133 | 52.6833 | 1
2015-05-08 03:30 | 2015-05-08 | 5 | 3 | 137 | 52.4333 | 1
2015-05-08 03:45 | 2015-05-08 | 5 | 3 | 138 | 52.1833 | 1
2015-05-08 04:00 | 2015-05-08 | 5 | 4 | 138 | 51.8667 | 1
2015-05-08 04:15 | 2015-05-08 | 5 | 4 | 136 | 51.3667 | 1
2015-05-08 04:30 | 2015-05-08 | 5 | 4 | 132 | 50.8667 | 1
2015-05-08 04:45 | 2015-05-08 | 5 | 4 | 133 | 50.3667 | 1
2015-05-08 05:00 | 2015-05-08 | 5 | 5 | 134 | 50.0667 | 1
2015-05-08 05:15 | 2015-05-08 | 5 | 5 | 137 | 50.3167 | 1
2015-05-08 05:30 | 2015-05-08 | 5 | 5 | 138 | 50.5667 | 1
2015-05-08 05:45 | 2015-05-08 | 5 | 5 | 136 | 50.8167 | 1
2015-05-08 06:00 | 2015-05-08 | 5 | 6 | 133 | 51.2 | 1
2015-05-08 06:15 | 2015-05-08 | 5 | 6 | 136 | 51.95 | 1
2015-05-08 06:30 | 2015-05-08 | 5 | 6 | 142 | 52.7 | 1
2015-05-08 06:45 | 2015-05-08 | 5 | 6 | 143 | 53.45 | 1
2015-05-08 07:00 | 2015-05-08 | 5 | 7 | 142 | 54.2667 | 1
2015-05-08 07:15 | 2015-05-08 | 5 | 7 | 141 | 55.2667 | 1
2015-05-08 07:30 | 2015-05-08 | 5 | 7 | 140 | 56.2667 | 1
2015-05-08 07:45 | 2015-05-08 | 5 | 7 | 145 | 57.2667 | 1
2015-05-08 08:00 | 2015-05-08 | 5 | 8 | 152 | 58.0667 | 1
2015-05-08 08:15 | 2015-05-08 | 5 | 8 | 159 | 58.3167 | 1
2015-05-08 08:30 | 2015-05-08 | 5 | 8 | 161 | 58.5667 | 1
2015-05-08 08:45 | 2015-05-08 | 5 | 8 | 166 | 58.8167 | 1
2015-05-08 09:00 | 2015-05-08 | 5 | 9 | 169 | 59.1333 | 1
2015-05-08 09:15 | 2015-05-08 | 5 | 9 | 175 | 59.6333 | 1
2015-05-08 09:30 | 2015-05-08 | 5 | 9 | 179 | 60.1333 | 1
2015-05-08 09:45 | 2015-05-08 | 5 | 9 | 180 | 60.6333 | 1
2015-05-08 10:00 | 2015-05-08 | 5 | 10 | 174 | 61.0667 | 1
2015-05-08 10:15 | 2015-05-08 | 5 | 10 | 191 | 61.3167 | 1
2015-05-08 10:30 | 2015-05-08 | 5 | 10 | 197 | 61.5667 | 1
2015-05-08 10:45 | 2015-05-08 | 5 | 10 | 211 | 61.8167 | 1
2015-05-08 11:00 | 2015-05-08 | 5 | 11 | 199 | 62.0667 | 1
2015-05-08 11:15 | 2015-05-08 | 5 | 11 | 207 | 62.3167 | 1
2015-05-08 11:30 | 2015-05-08 | 5 | 11 | 204 | 62.5667 | 1
2015-05-08 11:45 | 2015-05-08 | 5 | 11 | 194 | 62.8167 | 1
2015-05-08 12:00 | 2015-05-08 | 5 | 12 | 188 | 63.2667 | 1
2015-05-08 12:15 | 2015-05-08 | 5 | 12 | 198 | 64.2667 | 1
2015-05-08 12:30 | 2015-05-08 | 5 | 12 | 193 | 65.2667 | 2
2015-05-08 12:45 | 2015-05-08 | 5 | 12 | 198 | 66.2667 | 2
2015-05-08 13:00 | 2015-05-08 | 5 | 13 | 199 | 67.0667 | 2
2015-05-08 13:15 | 2015-05-08 | 5 | 13 | 199 | 67.3167 | 2
2015-05-08 13:30 | 2015-05-08 | 5 | 13 | 214 | 67.5667 | 2
2015-05-08 13:45 | 2015-05-08 | 5 | 13 | 209 | 67.8167 | 2
2015-05-08 14:00 | 2015-05-08 | 5 | 14 | 212 | 67.8 | 2
2015-05-08 14:15 | 2015-05-08 | 5 | 14 | 226 | 67.05 | 2
2015-05-08 14:30 | 2015-05-08 | 5 | 14 | 222 | 66.3 | 2
2015-05-08 14:45 | 2015-05-08 | 5 | 14 | 219 | 65.55 | 2
2015-05-08 15:00 | 2015-05-08 | 5 | 15 | 230 | 64.9333 | 1
2015-05-08 15:15 | 2015-05-08 | 5 | 15 | 220 | 64.6833 | 1
2015-05-08 15:30 | 2015-05-08 | 5 | 15 | 222 | 64.4333 | 1
2015-05-08 15:45 | 2015-05-08 | 5 | 15 | 261 | 64.1833 | 1
2015-05-08 16:00 | 2015-05-08 | 5 | 16 | 291 | 63.8 | 1
2015-05-08 16:15 | 2015-05-08 | 5 | 16 | 232 | 63.05 | 1
2015-05-08 16:30 | 2015-05-08 | 5 | 16 | 217 | 62.3 | 1
2015-05-08 16:45 | 2015-05-08 | 5 | 16 | 218 | 61.55 | 1
2015-05-08 17:00 | 2015-05-08 | 5 | 17 | 222 | 60.8667 | 1
2015-05-08 17:15 | 2015-05-08 | 5 | 17 | 205 | 60.3667 | 1
2015-05-08 17:30 | 2015-05-08 | 5 | 17 | 213 | 59.8667 | 1
2015-05-08 17:45 | 2015-05-08 | 5 | 17 | 208 | 59.3667 | 1
2015-05-08 18:00 | 2015-05-08 | 5 | 18 | 212 | 58.7333 | 1
2015-05-08 18:15 | 2015-05-08 | 5 | 18 | 218 | 57.7333 | 1
2015-05-08 18:30 | 2015-05-08 | 5 | 18 | 198 | 56.7333 | 1
2015-05-08 18:45 | 2015-05-08 | 5 | 18 | 208 | 55.7333 | 1
2015-05-08 19:00 | 2015-05-08 | 5 | 19 | 193 | 55 | 1
2015-05-08 19:15 | 2015-05-08 | 5 | 19 | 207 | 55 | 1
2015-05-08 19:30 | 2015-05-08 | 5 | 19 | 193 | 55 | 1
2015-05-08 19:45 | 2015-05-08 | 5 | 19 | 187 | 55 | 1
2015-05-08 20:00 | 2015-05-08 | 5 | 20 | 196 | 54.9333 | 1
2015-05-08 20:15 | 2015-05-08 | 5 | 20 | 191 | 54.6833 | 1
2015-05-08 20:30 | 2015-05-08 | 5 | 20 | 189 | 54.4333 | 1
2015-05-08 20:45 | 2015-05-08 | 5 | 20 | 179 | 54.1833 | 1
2015-05-08 21:00 | 2015-05-08 | 5 | 21 | 183 | 54 | 1
2015-05-08 21:15 | 2015-05-08 | 5 | 21 | 164 | 54 | 1
2015-05-08 21:30 | 2015-05-08 | 5 | 21 | 154 | 54 | 1
2015-05-08 21:45 | 2015-05-08 | 5 | 21 | 149 | 54 | 1
2015-05-08 22:00 | 2015-05-08 | 5 | 22 | 154 | 53.9333 | 1
2015-05-08 22:15 | 2015-05-08 | 5 | 22 | 156 | 53.6833 | 1
2015-05-08 22:30 | 2015-05-08 | 5 | 22 | 150 | 53.4333 | 1
2015-05-08 22:45 | 2015-05-08 | 5 | 22 | 149 | 53.1833 | 1
2015-05-08 23:00 | 2015-05-08 | 5 | 23 | 149 | 53.4444 | 1
2015-05-08 23:15 | 2015-05-08 | 5 | 23 | 160 | 54 | 1
2015-05-08 23:30 | 2015-05-08 | 5 | 23 | 150 | 54 | 1
2015-05-08 23:45 | 2015-05-08 | 5 | 23 | 147 | 54 | 1
2015-05-09 | 2015-05-09 | 6 | 0 | 146 | 52.0667 | 1
2015-05-09 00:15 | 2015-05-09 | 6 | 0 | 152 | 52.3167 | 1
2015-05-09 00:30 | 2015-05-09 | 6 | 0 | 155 | 52.5667 | 1
2015-05-09 00:45 | 2015-05-09 | 6 | 0 | 146 | 52.8167 | 1
2015-05-09 01:00 | 2015-05-09 | 6 | 1 | 145 | 53 | 1
2015-05-09 01:15 | 2015-05-09 | 6 | 1 | 146 | 53 | 1
2015-05-09 01:30 | 2015-05-09 | 6 | 1 | 161 | 53 | 1
2015-05-09 01:45 | 2015-05-09 | 6 | 1 | 146 | 53 | 1
2015-05-09 02:00 | 2015-05-09 | 6 | 2 | 147 | 53 | 1
2015-05-09 02:15 | 2015-05-09 | 6 | 2 | 142 | 53 | 1
2015-05-09 02:30 | 2015-05-09 | 6 | 2 | 148 | 53 | 1
2015-05-09 02:45 | 2015-05-09 | 6 | 2 | 157 | 53 | 1
2015-05-09 03:00 | 2015-05-09 | 6 | 3 | 144 | 53 | 1
2015-05-09 03:15 | 2015-05-09 | 6 | 3 | 141 | 53 | 1
2015-05-09 03:30 | 2015-05-09 | 6 | 3 | 148 | 53 | 1
2015-05-09 03:45 | 2015-05-09 | 6 | 3 | 150 | 53 | 1
2015-05-09 04:00 | 2015-05-09 | 6 | 4 | 143 | 53 | 1
2015-05-09 04:15 | 2015-05-09 | 6 | 4 | 142 | 53 | 1
2015-05-09 04:30 | 2015-05-09 | 6 | 4 | 141 | 53 | 1
2015-05-09 04:45 | 2015-05-09 | 6 | 4 | 148 | 53 | 1
2015-05-09 05:00 | 2015-05-09 | 6 | 5 | 155 | 53 | 1
2015-05-09 05:15 | 2015-05-09 | 6 | 5 | 143 | 53 | 1
2015-05-09 05:30 | 2015-05-09 | 6 | 5 | 143 | 53 | 1
2015-05-09 05:45 | 2015-05-09 | 6 | 5 | 145 | 53 | 1
2015-05-09 06:00 | 2015-05-09 | 6 | 6 | 158 | 53.0667 | 1
2015-05-09 06:15 | 2015-05-09 | 6 | 6 | 146 | 53.3167 | 1
2015-05-09 06:30 | 2015-05-09 | 6 | 6 | 145 | 53.5667 | 1
2015-05-09 06:45 | 2015-05-09 | 6 | 6 | 148 | 53.8167 | 1
2015-05-09 07:00 | 2015-05-09 | 6 | 7 | 150 | 54 | 1
2015-05-09 07:15 | 2015-05-09 | 6 | 7 | 152 | 54 | 1
2015-05-09 07:30 | 2015-05-09 | 6 | 7 | 143 | 54 | 1
2015-05-09 07:45 | 2015-05-09 | 6 | 7 | 143 | 54 | 1
2015-05-09 08:00 | 2015-05-09 | 6 | 8 | 140 | 54.0909 | 1
2015-05-09 08:15 | 2015-05-09 | 6 | 8 | 143 | 54.4318 | 1
2015-05-09 08:30 | 2015-05-09 | 6 | 8 | 154 | 54.7727 | 1
2015-05-09 08:45 | 2015-05-09 | 6 | 8 | 144 | 55 | 1
2015-05-09 09:00 | 2015-05-09 | 6 | 9 | 146 | 55.0667 | 1
2015-05-09 09:15 | 2015-05-09 | 6 | 9 | 149 | 55.3167 | 1
2015-05-09 09:30 | 2015-05-09 | 6 | 9 | 162 | 55.5667 | 1
2015-05-09 09:45 | 2015-05-09 | 6 | 9 | 149 | 55.8167 | 1
2015-05-09 10:00 | 2015-05-09 | 6 | 10 | 147 | 56.0667 | 1
2015-05-09 10:15 | 2015-05-09 | 6 | 10 | 144 | 56.3167 | 1
2015-05-09 10:30 | 2015-05-09 | 6 | 10 | 141 | 56.5667 | 1
2015-05-09 10:45 | 2015-05-09 | 6 | 10 | 140 | 56.8167 | 1
2015-05-09 11:00 | 2015-05-09 | 6 | 11 | 165 | 57.2 | 1
2015-05-09 11:15 | 2015-05-09 | 6 | 11 | 147 | 57.95 | 1
2015-05-09 11:30 | 2015-05-09 | 6 | 11 | 155 | 58.7 | 1
2015-05-09 11:45 | 2015-05-09 | 6 | 11 | 152 | 59.45 | 1
2015-05-09 12:00 | 2015-05-09 | 6 | 12 | 157 | 60.0952 | 1
2015-05-09 12:15 | 2015-05-09 | 6 | 12 | 167 | 60.4524 | 1
2015-05-09 12:30 | 2015-05-09 | 6 | 12 | 157 | 60.8095 | 1
2015-05-09 12:45 | 2015-05-09 | 6 | 12 | 162 | 61.3889 | 1
2015-05-09 13:00 | 2015-05-09 | 6 | 13 | 159 | 62.1333 | 1
2015-05-09 13:15 | 2015-05-09 | 6 | 13 | 155 | 62.6333 | 1
2015-05-09 13:30 | 2015-05-09 | 6 | 13 | 168 | 63.1333 | 1
2015-05-09 13:45 | 2015-05-09 | 6 | 13 | 161 | 63.6333 | 1
2015-05-09 14:00 | 2015-05-09 | 6 | 14 | 164 | 63.9333 | 1
2015-05-09 14:15 | 2015-05-09 | 6 | 14 | 161 | 63.6833 | 1
2015-05-09 14:30 | 2015-05-09 | 6 | 14 | 157 | 63.4333 | 1
2015-05-09 14:45 | 2015-05-09 | 6 | 14 | 169 | 63.1833 | 1
2015-05-09 15:00 | 2015-05-09 | 6 | 15 | 168 | 62.8 | 1
2015-05-09 15:15 | 2015-05-09 | 6 | 15 | 177 | 62.05 | 1
2015-05-09 15:30 | 2015-05-09 | 6 | 15 | 179 | 61.3 | 1
2015-05-09 15:45 | 2015-05-09 | 6 | 15 | 169 | 60.55 | 1
2015-05-09 16:00 | 2015-05-09 | 6 | 16 | 174 | 59.7333 | 1
2015-05-09 16:15 | 2015-05-09 | 6 | 16 | 181 | 58.7333 | 1
2015-05-09 16:30 | 2015-05-09 | 6 | 16 | 170 | 57.7333 | 1
2015-05-09 16:45 | 2015-05-09 | 6 | 16 | 180 | 56.7333 | 1
2015-05-09 17:00 | 2015-05-09 | 6 | 17 | 178 | 55.7143 | 1
2015-05-09 17:15 | 2015-05-09 | 6 | 17 | 170 | 55 | 1
2015-05-09 17:30 | 2015-05-09 | 6 | 17 | 181 | 55 | 1
2015-05-09 17:45 | 2015-05-09 | 6 | 17 | 169 | 55 | 1
2015-05-09 18:00 | 2015-05-09 | 6 | 18 | 180 | 55 | 1
2015-05-09 18:15 | 2015-05-09 | 6 | 18 | 186 | 55 | 1
2015-05-09 18:30 | 2015-05-09 | 6 | 18 | 167 | 55 | 1
2015-05-09 18:45 | 2015-05-09 | 6 | 18 | 185 | 55 | 1
2015-05-09 19:00 | 2015-05-09 | 6 | 19 | 170 | 54.9333 | 1
2015-05-09 19:15 | 2015-05-09 | 6 | 19 | 170 | 54.6833 | 1
2015-05-09 19:30 | 2015-05-09 | 6 | 19 | 170 | 54.4333 | 1
2015-05-09 19:45 | 2015-05-09 | 6 | 19 | 169 | 54.1833 | 1
2015-05-09 20:00 | 2015-05-09 | 6 | 20 | 163 | 54 | 1
2015-05-09 20:15 | 2015-05-09 | 6 | 20 | 164 | 54 | 1
2015-05-09 20:30 | 2015-05-09 | 6 | 20 | 161 | 54 | 1
2015-05-09 20:45 | 2015-05-09 | 6 | 20 | 159 | 54 | 1
2015-05-09 21:00 | 2015-05-09 | 6 | 21 | 163 | 54 | 1
2015-05-09 21:15 | 2015-05-09 | 6 | 21 | 169 | 54 | 1
2015-05-09 21:30 | 2015-05-09 | 6 | 21 | 154 | 54 | 1
2015-05-09 21:45 | 2015-05-09 | 6 | 21 | 160 | 54 | 1
2015-05-09 22:00 | 2015-05-09 | 6 | 22 | 155 | 54 | 1
2015-05-09 22:15 | 2015-05-09 | 6 | 22 | 167 | 54 | 1
2015-05-09 22:30 | 2015-05-09 | 6 | 22 | 151 | 53.8667 | 1
2015-05-09 22:45 | 2015-05-09 | 6 | 22 | 155 | 53.3667 | 1
2015-05-09 23:00 | 2015-05-09 | 6 | 23 | 154 | 53 | 1
2015-05-09 23:15 | 2015-05-09 | 6 | 23 | 163 | 53 | 1
2015-05-09 23:30 | 2015-05-09 | 6 | 23 | 158 | 53 | 1
2015-05-09 23:45 | 2015-05-09 | 6 | 23 | 153 | 53 | 1
2015-05-10 | 2015-05-10 | 7 | 0 | 153 | 52.9333 | 1
2015-05-10 00:15 | 2015-05-10 | 7 | 0 | 170 | 52.6833 | 1
2015-05-10 00:30 | 2015-05-10 | 7 | 0 | 155 | 52.4333 | 1
2015-05-10 00:45 | 2015-05-10 | 7 | 0 | 151 | 52.1833 | 1
2015-05-10 01:00 | 2015-05-10 | 7 | 1 | 147 | 52 | 1
2015-05-10 01:15 | 2015-05-10 | 7 | 1 | 164 | 52 | 1
2015-05-10 01:30 | 2015-05-10 | 7 | 1 | 149 | 52 | 1
2015-05-10 01:45 | 2015-05-10 | 7 | 1 | 150 | 52 | 1
2015-05-10 02:00 | 2015-05-10 | 7 | 2 | 146 | 52 | 1
2015-05-10 02:15 | 2015-05-10 | 7 | 2 | 155 | 52 | 1
2015-05-10 02:30 | 2015-05-10 | 7 | 2 | 150 | 52 | 1
2015-05-10 02:45 | 2015-05-10 | 7 | 2 | 142 | 52 | 1
2015-05-10 03:00 | 2015-05-10 | 7 | 3 | 150 | 52 | 1
2015-05-10 03:15 | 2015-05-10 | 7 | 3 | 145 | 52 | 1
2015-05-10 03:30 | 2015-05-10 | 7 | 3 | 142 | 52 | 1
2015-05-10 03:45 | 2015-05-10 | 7 | 3 | 143 | 52 | 1
2015-05-10 04:00 | 2015-05-10 | 7 | 4 | 157 | 52 | 1
2015-05-10 04:15 | 2015-05-10 | 7 | 4 | 142 | 52 | 1
2015-05-10 04:30 | 2015-05-10 | 7 | 4 | 140 | 52 | 1
2015-05-10 04:45 | 2015-05-10 | 7 | 4 | 141 | 52 | 1
2015-05-10 05:00 | 2015-05-10 | 7 | 5 | 156 | 52 | 1
2015-05-10 05:15 | 2015-05-10 | 7 | 5 | 144 | 52 | 1
2015-05-10 05:30 | 2015-05-10 | 7 | 5 | 151 | 52 | 1
2015-05-10 05:45 | 2015-05-10 | 7 | 5 | 155 | 52 | 1
2015-05-10 06:00 | 2015-05-10 | 7 | 6 | 162 | 52 | 1
2015-05-10 06:15 | 2015-05-10 | 7 | 6 | 147 | 52 | 1
2015-05-10 06:30 | 2015-05-10 | 7 | 6 | 149 | 52 | 1
2015-05-10 06:45 | 2015-05-10 | 7 | 6 | 146 | 52 | 1
2015-05-10 07:00 | 2015-05-10 | 7 | 7 | 154 | 52.0667 | 1
2015-05-10 07:15 | 2015-05-10 | 7 | 7 | 161 | 52.3167 | 1
2015-05-10 07:30 | 2015-05-10 | 7 | 7 | 155 | 52.5667 | 1
2015-05-10 07:45 | 2015-05-10 | 7 | 7 | 156 | 52.8167 | 1
2015-05-10 08:00 | 2015-05-10 | 7 | 8 | 156 | 53.0667 | 1
2015-05-10 08:15 | 2015-05-10 | 7 | 8 | 172 | 53.3167 | 1
2015-05-10 08:30 | 2015-05-10 | 7 | 8 | 155 | 53.5667 | 1
2015-05-10 08:45 | 2015-05-10 | 7 | 8 | 159 | 53.8167 | 1
2015-05-10 09:00 | 2015-05-10 | 7 | 9 | 154 | 54.1333 | 1
2015-05-10 09:15 | 2015-05-10 | 7 | 9 | 161 | 54.6333 | 1
2015-05-10 09:30 | 2015-05-10 | 7 | 9 | 162 | 55.1333 | 1
2015-05-10 09:45 | 2015-05-10 | 7 | 9 | 175 | 55.6333 | 1
2015-05-10 10:00 | 2015-05-10 | 7 | 10 | 162 | 56.1333 | 1
2015-05-10 10:15 | 2015-05-10 | 7 | 10 | 177 | 56.6333 | 1
2015-05-10 10:30 | 2015-05-10 | 7 | 10 | 174 | 57.2667 | 1
2015-05-10 10:45 | 2015-05-10 | 7 | 10 | 178 | 58.2667 | 1
2015-05-10 11:00 | 2015-05-10 | 7 | 11 | 185 | 59 | 1
2015-05-10 11:15 | 2015-05-10 | 7 | 11 | 182 | 59 | 1
2015-05-10 11:30 | 2015-05-10 | 7 | 11 | 184 | 59.0714 | 1
2015-05-10 11:45 | 2015-05-10 | 7 | 11 | 176 | 59.6071 | 1
2015-05-10 12:00 | 2015-05-10 | 7 | 12 | 178 | 60.0667 | 1
2015-05-10 12:15 | 2015-05-10 | 7 | 12 | 196 | 60.3167 | 1
2015-05-10 12:30 | 2015-05-10 | 7 | 12 | 169 | 60.5667 | 1
2015-05-10 12:45 | 2015-05-10 | 7 | 12 | 184 | 60.8167 | 1
2015-05-10 13:00 | 2015-05-10 | 7 | 13 | 181 | 60.9333 | 1
2015-05-10 13:15 | 2015-05-10 | 7 | 13 | 176 | 60.6833 | 1
2015-05-10 13:30 | 2015-05-10 | 7 | 13 | 184 | 60.4333 | 1
2015-05-10 13:45 | 2015-05-10 | 7 | 13 | 180 | 60.1833 | 1
2015-05-10 14:00 | 2015-05-10 | 7 | 14 | 177 | 60 | 1
2015-05-10 14:15 | 2015-05-10 | 7 | 14 | 187 | 60 | 1
2015-05-10 14:30 | 2015-05-10 | 7 | 14 | 174 | 60 | 1
2015-05-10 14:45 | 2015-05-10 | 7 | 14 | 178 | 60 | 1
2015-05-10 15:00 | 2015-05-10 | 7 | 15 | 185 | 59.9333 | 1
2015-05-10 15:15 | 2015-05-10 | 7 | 15 | 199 | 59.6833 | 1
2015-05-10 15:30 | 2015-05-10 | 7 | 15 | 186 | 59.4333 | 1
2015-05-10 15:45 | 2015-05-10 | 7 | 15 | 192 | 59.1833 | 1
2015-05-10 16:00 | 2015-05-10 | 7 | 16 | 191 | 58.9333 | 1
2015-05-10 16:15 | 2015-05-10 | 7 | 16 | 190 | 58.6833 | 1
2015-05-10 16:30 | 2015-05-10 | 7 | 16 | 197 | 58.4333 | 1
2015-05-10 16:45 | 2015-05-10 | 7 | 16 | 187 | 58.1833 | 1
2015-05-10 17:00 | 2015-05-10 | 7 | 17 | 186 | 57.8667 | 1
2015-05-10 17:15 | 2015-05-10 | 7 | 17 | 194 | 57.3667 | 1
2015-05-10 17:30 | 2015-05-10 | 7 | 17 | 188 | 56.8667 | 1
2015-05-10 17:45 | 2015-05-10 | 7 | 17 | 179 | 56.3667 | 1
2015-05-10 18:00 | 2015-05-10 | 7 | 18 | 197 | 55.9333 | 1
2015-05-10 18:15 | 2015-05-10 | 7 | 18 | 178 | 55.6833 | 1
2015-05-10 18:30 | 2015-05-10 | 7 | 18 | 195 | 55.4333 | 1
2015-05-10 18:45 | 2015-05-10 | 7 | 18 | 180 | 55.1833 | 1
2015-05-10 19:00 | 2015-05-10 | 7 | 19 | 172 | 55 | 1
2015-05-10 19:15 | 2015-05-10 | 7 | 19 | 183 | 55 | 1
2015-05-10 19:30 | 2015-05-10 | 7 | 19 | 174 | 55 | 1
2015-05-10 19:45 | 2015-05-10 | 7 | 19 | 169 | 55 | 1
2015-05-10 20:00 | 2015-05-10 | 7 | 20 | 177 | 55 | 1
2015-05-10 20:15 | 2015-05-10 | 7 | 20 | 166 | 55 | 1
2015-05-10 20:30 | 2015-05-10 | 7 | 20 | 176 | 55 | 1
2015-05-10 20:45 | 2015-05-10 | 7 | 20 | 168 | 55 | 1
2015-05-10 21:00 | 2015-05-10 | 7 | 21 | 167 | 54.9333 | 1
2015-05-10 21:15 | 2015-05-10 | 7 | 21 | 155 | 54.6833 | 1
2015-05-10 21:30 | 2015-05-10 | 7 | 21 | 154 | 54.4333 | 1
2015-05-10 21:45 | 2015-05-10 | 7 | 21 | 153 | 54.1833 | 1
2015-05-10 22:00 | 2015-05-10 | 7 | 22 | 147 | 54 | 1
2015-05-10 22:15 | 2015-05-10 | 7 | 22 | 147 | 54 | 1
2015-05-10 22:30 | 2015-05-10 | 7 | 22 | 146 | 54 | 1
2015-05-10 22:45 | 2015-05-10 | 7 | 22 | 151 | 54 | 1
2015-05-10 23:00 | 2015-05-10 | 7 | 23 | 154 | 53.9333 | 1
2015-05-10 23:15 | 2015-05-10 | 7 | 23 | 147 | 53.6833 | 1
2015-05-10 23:30 | 2015-05-10 | 7 | 23 | 161 | 53.4333 | 1
2015-05-10 23:45 | 2015-05-10 | 7 | 23 | 155 | 53.1833 | 1
2015-05-11 | 2015-05-11 | 1 | 0 | 157 | 53 | 1
2015-05-11 00:15 | 2015-05-11 | 1 | 0 | 151 | 53 | 1
2015-05-11 00:30 | 2015-05-11 | 1 | 0 | 141 | 53 | 1
2015-05-11 00:45 | 2015-05-11 | 1 | 0 | 140 | 53 | 1
2015-05-11 01:00 | 2015-05-11 | 1 | 1 | 143 | 53 | 1
2015-05-11 01:15 | 2015-05-11 | 1 | 1 | 152 | 53 | 1
2015-05-11 01:30 | 2015-05-11 | 1 | 1 | 145 | 53 | 1
2015-05-11 01:45 | 2015-05-11 | 1 | 1 | 152 | 53 | 1
2015-05-11 02:00 | 2015-05-11 | 1 | 2 | 145 | 53 | 1
2015-05-11 02:15 | 2015-05-11 | 1 | 2 | 154 | 53 | 1
2015-05-11 02:30 | 2015-05-11 | 1 | 2 | 140 | 53 | 1
2015-05-11 02:45 | 2015-05-11 | 1 | 2 | 147 | 53 | 1
2015-05-11 03:00 | 2015-05-11 | 1 | 3 | 146 | 53.0851 | 1
2015-05-11 03:15 | 2015-05-11 | 1 | 3 | 140 | 53.4043 | 1
2015-05-11 03:30 | 2015-05-11 | 1 | 3 | 155 | 53.7234 | 1
2015-05-11 03:45 | 2015-05-11 | 1 | 3 | 140 | 53.6364 | 1
2015-05-11 04:00 | 2015-05-11 | 1 | 4 | 153 | 52 | 1
2015-05-11 04:15 | 2015-05-11 | 1 | 4 | 142 | 52 | 1
2015-05-11 04:30 | 2015-05-11 | 1 | 4 | 158 | 52 | 1
2015-05-11 04:45 | 2015-05-11 | 1 | 4 | 139 | 52 | 1
2015-05-11 05:00 | 2015-05-11 | 1 | 5 | 154 | 52 | 1
2015-05-11 05:15 | 2015-05-11 | 1 | 5 | 149 | 52 | 1
2015-05-11 05:30 | 2015-05-11 | 1 | 5 | 148 | 52 | 1
2015-05-11 05:45 | 2015-05-11 | 1 | 5 | 145 | 52 | 1
2015-05-11 06:00 | 2015-05-11 | 1 | 6 | 150 | 52.2857 | 1
2015-05-11 06:15 | 2015-05-11 | 1 | 6 | 141 | 53.3571 | 1
2015-05-11 06:30 | 2015-05-11 | 1 | 6 | 142 | 53.8125 | 1
2015-05-11 06:45 | 2015-05-11 | 1 | 6 | 157 | 53.3438 | 1
2015-05-11 07:00 | 2015-05-11 | 1 | 7 | 141 | 53.1333 | 1
2015-05-11 07:15 | 2015-05-11 | 1 | 7 | 142 | 53.6333 | 1
2015-05-11 07:30 | 2015-05-11 | 1 | 7 | 147 | 54.1333 | 1
2015-05-11 07:45 | 2015-05-11 | 1 | 7 | 150 | 54.6333 | 1
2015-05-11 08:00 | 2015-05-11 | 1 | 8 | 159 | 55.0667 | 1
2015-05-11 08:15 | 2015-05-11 | 1 | 8 | 157 | 55.3167 | 1
2015-05-11 08:30 | 2015-05-11 | 1 | 8 | 166 | 55.5667 | 1
2015-05-11 08:45 | 2015-05-11 | 1 | 8 | 166 | 55.8167 | 1
2015-05-11 09:00 | 2015-05-11 | 1 | 9 | 177 | 56.0755 | 1
2015-05-11 09:15 | 2015-05-11 | 1 | 9 | 178 | 56.3585 | 1
2015-05-11 09:30 | 2015-05-11 | 1 | 9 | 180 | 56.6415 | 1
2015-05-11 09:45 | 2015-05-11 | 1 | 9 | 175 | 56.9245 | 1
2015-05-11 10:00 | 2015-05-11 | 1 | 10 | 192 | 58.0667 | 1
2015-05-11 10:15 | 2015-05-11 | 1 | 10 | 206 | 58.3167 | 1
2015-05-11 10:30 | 2015-05-11 | 1 | 10 | 205 | 58.5667 | 1
2015-05-11 10:45 | 2015-05-11 | 1 | 10 | 207 | 58.8167 | 1
2015-05-11 11:00 | 2015-05-11 | 1 | 11 | 203 | 59.0667 | 1
2015-05-11 11:15 | 2015-05-11 | 1 | 11 | 207 | 59.3167 | 1
2015-05-11 11:30 | 2015-05-11 | 1 | 11 | 222 | 59.5667 | 1
2015-05-11 11:45 | 2015-05-11 | 1 | 11 | 219 | 59.8167 | 1
2015-05-11 12:00 | 2015-05-11 | 1 | 12 | 225 | 60.6667 | 1
2015-05-11 12:15 | 2015-05-11 | 1 | 12 | 217 | 60.7593 | 1
2015-05-11 12:30 | 2015-05-11 | 1 | 12 | 214 | 60.4815 | 1
2015-05-11 12:45 | 2015-05-11 | 1 | 12 | 205 | 60.2037 | 1
2015-05-11 13:00 | 2015-05-11 | 1 | 13 | 208 | 60 | 1
2015-05-11 13:15 | 2015-05-11 | 1 | 13 | 194 | 60 | 1
2015-05-11 13:30 | 2015-05-11 | 1 | 13 | 208 | 60 | 1
2015-05-11 13:45 | 2015-05-11 | 1 | 13 | 206 | 60 | 1
2015-05-11 14:00 | 2015-05-11 | 1 | 14 | 201 | 59.9333 | 1
2015-05-11 14:15 | 2015-05-11 | 1 | 14 | 209 | 59.6833 | 1
2015-05-11 14:30 | 2015-05-11 | 1 | 14 | 196 | 59.4333 | 1
2015-05-11 14:45 | 2015-05-11 | 1 | 14 | 214 | 59.1833 | 1
2015-05-11 15:00 | 2015-05-11 | 1 | 15 | 211 | 59 | 1
2015-05-11 15:15 | 2015-05-11 | 1 | 15 | 201 | 59 | 1
2015-05-11 15:30 | 2015-05-11 | 1 | 15 | 212 | 59 | 1
2015-05-11 15:45 | 2015-05-11 | 1 | 15 | 204 | 59 | 1
2015-05-11 16:00 | 2015-05-11 | 1 | 16 | 202 | 58.8667 | 1
2015-05-11 16:15 | 2015-05-11 | 1 | 16 | 196 | 58.3667 | 1
2015-05-11 16:30 | 2015-05-11 | 1 | 16 | 192 | 57.8667 | 1
2015-05-11 16:45 | 2015-05-11 | 1 | 16 | 197 | 57.3667 | 1
2015-05-11 17:00 | 2015-05-11 | 1 | 17 | 190 | 56.9333 | 1
2015-05-11 17:15 | 2015-05-11 | 1 | 17 | 200 | 56.6833 | 1
2015-05-11 17:30 | 2015-05-11 | 1 | 17 | 186 | 56.4333 | 1
2015-05-11 17:45 | 2015-05-11 | 1 | 17 | 187 | 56.1833 | 1
2015-05-11 18:00 | 2015-05-11 | 1 | 18 | 184 | 55.8667 | 1
2015-05-11 18:15 | 2015-05-11 | 1 | 18 | 186 | 55.3667 | 1
2015-05-11 18:30 | 2015-05-11 | 1 | 18 | 181 | 54.8667 | 1
2015-05-11 18:45 | 2015-05-11 | 1 | 18 | 178 | 54.3667 | 1
2015-05-11 19:00 | 2015-05-11 | 1 | 19 | 177 | 53.9333 | 1
2015-05-11 19:15 | 2015-05-11 | 1 | 19 | 172 | 53.6833 | 1
2015-05-11 19:30 | 2015-05-11 | 1 | 19 | 176 | 53.4333 | 1
2015-05-11 19:45 | 2015-05-11 | 1 | 19 | 175 | 53.1833 | 1
2015-05-11 20:00 | 2015-05-11 | 1 | 20 | 169 | 53 | 1
2015-05-11 20:15 | 2015-05-11 | 1 | 20 | 169 | 53 | 1
2015-05-11 20:30 | 2015-05-11 | 1 | 20 | 167 | 53 | 1
2015-05-11 20:45 | 2015-05-11 | 1 | 20 | 172 | 53 | 1
2015-05-11 21:00 | 2015-05-11 | 1 | 21 | 164 | 52.9333 | 1
2015-05-11 21:15 | 2015-05-11 | 1 | 21 | 158 | 52.6833 | 1
2015-05-11 21:30 | 2015-05-11 | 1 | 21 | 151 | 52.4333 | 1
2015-05-11 21:45 | 2015-05-11 | 1 | 21 | 154 | 52.1833 | 1
2015-05-11 22:00 | 2015-05-11 | 1 | 22 | 153 | 52 | 1
2015-05-11 22:15 | 2015-05-11 | 1 | 22 | 155 | 52 | 1
2015-05-11 22:30 | 2015-05-11 | 1 | 22 | 151 | 52 | 1
2015-05-11 22:45 | 2015-05-11 | 1 | 22 | 149 | 52 | 1
2015-05-11 23:00 | 2015-05-11 | 1 | 23 | 150 | 52 | 1
2015-05-11 23:15 | 2015-05-11 | 1 | 23 | 152 | 52 | 1
2015-05-11 23:30 | 2015-05-11 | 1 | 23 | 145 | 52 | 1
2015-05-11 23:45 | 2015-05-11 | 1 | 23 | 147 | 52 | 1
2015-05-12 | 2015-05-12 | 2 | 0 | 145 | 51.9333 | 1
2015-05-12 00:15 | 2015-05-12 | 2 | 0 | 148 | 51.6833 | 1
2015-05-12 00:30 | 2015-05-12 | 2 | 0 | 140 | 51.4333 | 1
2015-05-12 00:45 | 2015-05-12 | 2 | 0 | 148 | 51.1833 | 1
2015-05-12 01:00 | 2015-05-12 | 2 | 1 | 139 | 51 | 1
2015-05-12 01:15 | 2015-05-12 | 2 | 1 | 145 | 51 | 1
2015-05-12 01:30 | 2015-05-12 | 2 | 1 | 139 | 51 | 1
2015-05-12 01:45 | 2015-05-12 | 2 | 1 | 145 | 51 | 1
2015-05-12 02:00 | 2015-05-12 | 2 | 2 | 137 | 51 | 1
2015-05-12 02:15 | 2015-05-12 | 2 | 2 | 142 | 51 | 1
2015-05-12 02:30 | 2015-05-12 | 2 | 2 | 138 | 51 | 1
2015-05-12 02:45 | 2015-05-12 | 2 | 2 | 139 | 51 | 1
2015-05-12 03:00 | 2015-05-12 | 2 | 3 | 141 | 51 | 1
2015-05-12 03:15 | 2015-05-12 | 2 | 3 | 139 | 51 | 1
2015-05-12 03:30 | 2015-05-12 | 2 | 3 | 137 | 51 | 1
2015-05-12 03:45 | 2015-05-12 | 2 | 3 | 141 | 51 | 1
2015-05-12 04:00 | 2015-05-12 | 2 | 4 | 138 | 51 | 1
2015-05-12 04:15 | 2015-05-12 | 2 | 4 | 138 | 51 | 1
2015-05-12 04:30 | 2015-05-12 | 2 | 4 | 139 | 51 | 1
2015-05-12 04:45 | 2015-05-12 | 2 | 4 | 140 | 51 | 1
2015-05-12 05:00 | 2015-05-12 | 2 | 5 | 143 | 51.0667 | 1
2015-05-12 05:15 | 2015-05-12 | 2 | 5 | 138 | 51.3167 | 1
2015-05-12 05:30 | 2015-05-12 | 2 | 5 | 137 | 51.5667 | 1
2015-05-12 05:45 | 2015-05-12 | 2 | 5 | 140 | 51.8167 | 1
2015-05-12 06:00 | 2015-05-12 | 2 | 6 | 138 | 52.0667 | 1
2015-05-12 06:15 | 2015-05-12 | 2 | 6 | 138 | 52.3167 | 1
2015-05-12 06:30 | 2015-05-12 | 2 | 6 | 140 | 52.5667 | 1
2015-05-12 06:45 | 2015-05-12 | 2 | 6 | 138 | 52.8167 | 1
2015-05-12 07:00 | 2015-05-12 | 2 | 7 | 141 | 53.1333 | 1
2015-05-12 07:15 | 2015-05-12 | 2 | 7 | 141 | 53.6333 | 1
2015-05-12 07:30 | 2015-05-12 | 2 | 7 | 140 | 54.1333 | 1
2015-05-12 07:45 | 2015-05-12 | 2 | 7 | 155 | 54.6333 | 1
2015-05-12 08:00 | 2015-05-12 | 2 | 8 | 153 | 55.1333 | 1
2015-05-12 08:15 | 2015-05-12 | 2 | 8 | 158 | 55.6333 | 1
2015-05-12 08:30 | 2015-05-12 | 2 | 8 | 157 | 56.1333 | 1
2015-05-12 08:45 | 2015-05-12 | 2 | 8 | 158 | 56.6333 | 1
2015-05-12 09:00 | 2015-05-12 | 2 | 9 | 162 | 57 | 1
2015-05-12 09:15 | 2015-05-12 | 2 | 9 | 167 | 57 | 1
2015-05-12 09:30 | 2015-05-12 | 2 | 9 | 172 | 57 | 1
2015-05-12 09:45 | 2015-05-12 | 2 | 9 | 177 | 57 | 1
2015-05-12 10:00 | 2015-05-12 | 2 | 10 | 177 | 57.1333 | 1
2015-05-12 10:15 | 2015-05-12 | 2 | 10 | 192 | 57.6333 | 1
2015-05-12 10:30 | 2015-05-12 | 2 | 10 | 183 | 58.1333 | 1
2015-05-12 10:45 | 2015-05-12 | 2 | 10 | 181 | 58.6333 | 1
2015-05-12 11:00 | 2015-05-12 | 2 | 11 | 189 | 59.1333 | 1
2015-05-12 11:15 | 2015-05-12 | 2 | 11 | 193 | 59.6333 | 1
2015-05-12 11:30 | 2015-05-12 | 2 | 11 | 184 | 60.1333 | 1
2015-05-12 11:45 | 2015-05-12 | 2 | 11 | 187 | 60.6333 | 1
2015-05-12 12:00 | 2015-05-12 | 2 | 12 | 188 | 61 | 1
2015-05-12 12:15 | 2015-05-12 | 2 | 12 | 183 | 61 | 1
2015-05-12 12:30 | 2015-05-12 | 2 | 12 | 184 | 61 | 1
2015-05-12 12:45 | 2015-05-12 | 2 | 12 | 189 | 61 | 1
2015-05-12 13:00 | 2015-05-12 | 2 | 13 | 195 | 61.0667 | 1
2015-05-12 13:15 | 2015-05-12 | 2 | 13 | 186 | 61.3167 | 1
2015-05-12 13:30 | 2015-05-12 | 2 | 13 | 196 | 61.5667 | 1
2015-05-12 13:45 | 2015-05-12 | 2 | 13 | 191 | 61.8167 | 1
2015-05-12 14:00 | 2015-05-12 | 2 | 14 | 188 | 61.9333 | 1
2015-05-12 14:15 | 2015-05-12 | 2 | 14 | 190 | 61.6833 | 1
2015-05-12 14:30 | 2015-05-12 | 2 | 14 | 232 | 61.4333 | 1
2015-05-12 14:45 | 2015-05-12 | 2 | 14 | 225 | 61.1833 | 1
2015-05-12 15:00 | 2015-05-12 | 2 | 15 | 239 | 60.8 | 1
2015-05-12 15:15 | 2015-05-12 | 2 | 15 | 231 | 60.05 | 1
2015-05-12 15:30 | 2015-05-12 | 2 | 15 | 238 | 59.3 | 1
2015-05-12 15:45 | 2015-05-12 | 2 | 15 | 228 | 58.55 | 1
2015-05-12 16:00 | 2015-05-12 | 2 | 16 | 244 | 57.8667 | 1
2015-05-12 16:15 | 2015-05-12 | 2 | 16 | 238 | 57.3667 | 1
2015-05-12 16:30 | 2015-05-12 | 2 | 16 | 230 | 56.8667 | 1
2015-05-12 16:45 | 2015-05-12 | 2 | 16 | 232 | 56.3667 | 1
2015-05-12 17:00 | 2015-05-12 | 2 | 17 | 240 | 55.9333 | 1
2015-05-12 17:15 | 2015-05-12 | 2 | 17 | 220 | 55.6833 | 1
2015-05-12 17:30 | 2015-05-12 | 2 | 17 | 209 | 55.4333 | 1
2015-05-12 17:45 | 2015-05-12 | 2 | 17 | 219 | 55.1833 | 1
2015-05-12 18:00 | 2015-05-12 | 2 | 18 | 193 | 54.9333 | 1
2015-05-12 18:15 | 2015-05-12 | 2 | 18 | 199 | 54.6833 | 1
2015-05-12 18:30 | 2015-05-12 | 2 | 18 | 188 | 54.4333 | 1
2015-05-12 18:45 | 2015-05-12 | 2 | 18 | 183 | 54.1833 | 1
2015-05-12 19:00 | 2015-05-12 | 2 | 19 | 181 | 53.9333 | 1
2015-05-12 19:15 | 2015-05-12 | 2 | 19 | 176 | 53.6833 | 1
2015-05-12 19:30 | 2015-05-12 | 2 | 19 | 173 | 53.4333 | 1
2015-05-12 19:45 | 2015-05-12 | 2 | 19 | 173 | 53.1833 | 1
2015-05-12 20:00 | 2015-05-12 | 2 | 20 | 168 | 53 | 1
2015-05-12 20:15 | 2015-05-12 | 2 | 20 | 169 | 53 | 1
2015-05-12 20:30 | 2015-05-12 | 2 | 20 | 169 | 53 | 1
2015-05-12 20:45 | 2015-05-12 | 2 | 20 | 165 | 53 | 1
2015-05-12 21:00 | 2015-05-12 | 2 | 21 | 165 | 53 | 1
2015-05-12 21:15 | 2015-05-12 | 2 | 21 | 153 | 53 | 1
2015-05-12 21:30 | 2015-05-12 | 2 | 21 | 148 | 53 | 1
2015-05-12 21:45 | 2015-05-12 | 2 | 21 | 151 | 53 | 1
2015-05-12 22:00 | 2015-05-12 | 2 | 22 | 150 | 53 | 1
2015-05-12 22:15 | 2015-05-12 | 2 | 22 | 158 | 53 | 1
2015-05-12 22:30 | 2015-05-12 | 2 | 22 | 154 | 53 | 1
2015-05-12 22:45 | 2015-05-12 | 2 | 22 | 154 | 53 | 1
2015-05-12 23:00 | 2015-05-12 | 2 | 23 | 156 | 53 | 1
2015-05-12 23:15 | 2015-05-12 | 2 | 23 | 150 | 53 | 1
2015-05-12 23:30 | 2015-05-12 | 2 | 23 | 151 | 53 | 1
2015-05-12 23:45 | 2015-05-12 | 2 | 23 | 147 | 53 | 1
2015-05-13 | 2015-05-13 | 3 | 0 | 146 | 53 | 1
2015-05-13 00:15 | 2015-05-13 | 3 | 0 | 149 | 53 | 1
2015-05-13 00:30 | 2015-05-13 | 3 | 0 | 144 | 53 | 1
2015-05-13 00:45 | 2015-05-13 | 3 | 0 | 150 | 53 | 1
2015-05-13 01:00 | 2015-05-13 | 3 | 1 | 145 | 52.9333 | 1
2015-05-13 01:15 | 2015-05-13 | 3 | 1 | 147 | 52.6833 | 1
2015-05-13 01:30 | 2015-05-13 | 3 | 1 | 144 | 52.4333 | 1
2015-05-13 01:45 | 2015-05-13 | 3 | 1 | 144 | 52.1833 | 1
2015-05-13 02:00 | 2015-05-13 | 3 | 2 | 147 | 52 | 1
2015-05-13 02:15 | 2015-05-13 | 3 | 2 | 141 | 52 | 1
2015-05-13 02:30 | 2015-05-13 | 3 | 2 | 141 | 52 | 1
2015-05-13 02:45 | 2015-05-13 | 3 | 2 | 142 | 52 | 1
2015-05-13 03:00 | 2015-05-13 | 3 | 3 | 143 | 52 | 1
2015-05-13 03:15 | 2015-05-13 | 3 | 3 | 143 | 52 | 1
2015-05-13 03:30 | 2015-05-13 | 3 | 3 | 142 | 52 | 1
2015-05-13 03:45 | 2015-05-13 | 3 | 3 | 141 | 52 | 1
2015-05-13 04:00 | 2015-05-13 | 3 | 4 | 144 | 52 | 1
2015-05-13 04:15 | 2015-05-13 | 3 | 4 | 141 | 52 | 1
2015-05-13 04:30 | 2015-05-13 | 3 | 4 | 147 | 52 | 1
2015-05-13 04:45 | 2015-05-13 | 3 | 4 | 138 | 52 | 1
2015-05-13 05:00 | 2015-05-13 | 3 | 5 | 143 | 52.0667 | 1
2015-05-13 05:15 | 2015-05-13 | 3 | 5 | 142 | 52.3167 | 1
2015-05-13 05:30 | 2015-05-13 | 3 | 5 | 142 | 52.5667 | 1
2015-05-13 05:45 | 2015-05-13 | 3 | 5 | 142 | 52.8167 | 1
2015-05-13 06:00 | 2015-05-13 | 3 | 6 | 145 | 53.1333 | 1
2015-05-13 06:15 | 2015-05-13 | 3 | 6 | 141 | 53.6333 | 1
2015-05-13 06:30 | 2015-05-13 | 3 | 6 | 147 | 54.1333 | 1
2015-05-13 06:45 | 2015-05-13 | 3 | 6 | 143 | 54.6333 | 1
2015-05-13 07:00 | 2015-05-13 | 3 | 7 | 147 | 55.0667 | 1
2015-05-13 07:15 | 2015-05-13 | 3 | 7 | 146 | 55.3167 | 1
2015-05-13 07:30 | 2015-05-13 | 3 | 7 | 145 | 55.5667 | 1
2015-05-13 07:45 | 2015-05-13 | 3 | 7 | 155 | 55.8167 | 1
2015-05-13 08:00 | 2015-05-13 | 3 | 8 | 152 | 56.1481 | 1
2015-05-13 08:15 | 2015-05-13 | 3 | 8 | 159 | 56.7037 | 1
2015-05-13 08:30 | 2015-05-13 | 3 | 8 | 158 | 57.4242 | 1
2015-05-13 08:45 | 2015-05-13 | 3 | 8 | 166 | 58.3333 | 1
2015-05-13 09:00 | 2015-05-13 | 3 | 9 | 178 | 58.8621 | 1
2015-05-13 09:15 | 2015-05-13 | 3 | 9 | 182 | 58.3448 | 1
2015-05-13 09:30 | 2015-05-13 | 3 | 9 | 192 | 57.8276 | 1
2015-05-13 09:45 | 2015-05-13 | 3 | 9 | 187 | 57.3103 | 1
2015-05-13 10:00 | 2015-05-13 | 3 | 10 | 200 | 59.0667 | 1
2015-05-13 10:15 | 2015-05-13 | 3 | 10 | 210 | 59.3167 | 1
2015-05-13 10:30 | 2015-05-13 | 3 | 10 | 215 | 59.5667 | 1
2015-05-13 10:45 | 2015-05-13 | 3 | 10 | 206 | 59.8167 | 1
2015-05-13 11:00 | 2015-05-13 | 3 | 11 | 214 | 60.2 | 1
2015-05-13 11:15 | 2015-05-13 | 3 | 11 | 211 | 60.95 | 1
2015-05-13 11:30 | 2015-05-13 | 3 | 11 | 206 | 61.7 | 1
2015-05-13 11:45 | 2015-05-13 | 3 | 11 | 220 | 62.45 | 1
2015-05-13 12:00 | 2015-05-13 | 3 | 12 | 214 | 63 | 1
2015-05-13 12:15 | 2015-05-13 | 3 | 12 | 211 | 63 | 1
2015-05-13 12:30 | 2015-05-13 | 3 | 12 | 221 | 63 | 1
2015-05-13 12:45 | 2015-05-13 | 3 | 12 | 210 | 63 | 1
2015-05-13 13:00 | 2015-05-13 | 3 | 13 | 217 | 63.0667 | 1
2015-05-13 13:15 | 2015-05-13 | 3 | 13 | 223 | 63.3167 | 1
2015-05-13 13:30 | 2015-05-13 | 3 | 13 | 217 | 63.5667 | 1
2015-05-13 13:45 | 2015-05-13 | 3 | 13 | 219 | 63.8167 | 1
2015-05-13 14:00 | 2015-05-13 | 3 | 14 | 228 | 64 | 1
2015-05-13 14:15 | 2015-05-13 | 3 | 14 | 218 | 64 | 1
2015-05-13 14:30 | 2015-05-13 | 3 | 14 | 219 | 64 | 1
2015-05-13 14:45 | 2015-05-13 | 3 | 14 | 227 | 64 | 1
2015-05-13 15:00 | 2015-05-13 | 3 | 15 | 227 | 63.8667 | 1
2015-05-13 15:15 | 2015-05-13 | 3 | 15 | 214 | 63.3667 | 1
2015-05-13 15:30 | 2015-05-13 | 3 | 15 | 227 | 62.8667 | 1
2015-05-13 15:45 | 2015-05-13 | 3 | 15 | 225 | 62.3667 | 1
2015-05-13 16:00 | 2015-05-13 | 3 | 16 | 213 | 61.9333 | 1
2015-05-13 16:15 | 2015-05-13 | 3 | 16 | 228 | 61.6833 | 1
2015-05-13 16:30 | 2015-05-13 | 3 | 16 | 224 | 61.4333 | 1
2015-05-13 16:45 | 2015-05-13 | 3 | 16 | 223 | 61.1833 | 1
2015-05-13 17:00 | 2015-05-13 | 3 | 17 | 223 | 60.8667 | 1
2015-05-13 17:15 | 2015-05-13 | 3 | 17 | 229 | 60.3667 | 1
2015-05-13 17:30 | 2015-05-13 | 3 | 17 | 221 | 59.8667 | 1
2015-05-13 17:45 | 2015-05-13 | 3 | 17 | 221 | 59.3667 | 1
2015-05-13 18:00 | 2015-05-13 | 3 | 18 | 226 | 58.8667 | 1
2015-05-13 18:15 | 2015-05-13 | 3 | 18 | 224 | 58.3667 | 1
2015-05-13 18:30 | 2015-05-13 | 3 | 18 | 210 | 57.8667 | 1
2015-05-13 18:45 | 2015-05-13 | 3 | 18 | 218 | 57.3667 | 1
2015-05-13 19:00 | 2015-05-13 | 3 | 19 | 209 | 57 | 1
2015-05-13 19:15 | 2015-05-13 | 3 | 19 | 200 | 57 | 1
2015-05-13 19:30 | 2015-05-13 | 3 | 19 | 213 | 57 | 1
2015-05-13 19:45 | 2015-05-13 | 3 | 19 | 192 | 57 | 1
2015-05-13 20:00 | 2015-05-13 | 3 | 20 | 200 | 56.9333 | 1
2015-05-13 20:15 | 2015-05-13 | 3 | 20 | 193 | 56.6833 | 1
2015-05-13 20:30 | 2015-05-13 | 3 | 20 | 182 | 56.4333 | 1
2015-05-13 20:45 | 2015-05-13 | 3 | 20 | 182 | 56.1833 | 1
2015-05-13 21:00 | 2015-05-13 | 3 | 21 | 183 | 56.069 | 1
2015-05-13 21:15 | 2015-05-13 | 3 | 21 | 174 | 56.3276 | 1
2015-05-13 21:30 | 2015-05-13 | 3 | 21 | 157 | 56.5862 | 1
2015-05-13 21:45 | 2015-05-13 | 3 | 21 | 162 | 56.8448 | 1
2015-05-13 22:00 | 2015-05-13 | 3 | 22 | 154 | 57 | 1
2015-05-13 22:15 | 2015-05-13 | 3 | 22 | 163 | 57 | 1
2015-05-13 22:30 | 2015-05-13 | 3 | 22 | 160 | 57 | 1
2015-05-13 22:45 | 2015-05-13 | 3 | 22 | 165 | 57 | 1
2015-05-13 23:00 | 2015-05-13 | 3 | 23 | 161 | 57 | 1
2015-05-13 23:15 | 2015-05-13 | 3 | 23 | 160 | 57 | 1
2015-05-13 23:30 | 2015-05-13 | 3 | 23 | 158 | 57 | 1
2015-05-13 23:45 | 2015-05-13 | 3 | 23 | 157 | 57 | 1
2015-05-14 | 2015-05-14 | 4 | 0 | 154 | 57 | 1
2015-05-14 00:15 | 2015-05-14 | 4 | 0 | 149 | 57 | 1
2015-05-14 00:30 | 2015-05-14 | 4 | 0 | 153 | 57 | 1
2015-05-14 00:45 | 2015-05-14 | 4 | 0 | 147 | 57 | 1
2015-05-14 01:00 | 2015-05-14 | 4 | 1 | 151 | 56.9333 | 1
2015-05-14 01:15 | 2015-05-14 | 4 | 1 | 145 | 56.6833 | 1
2015-05-14 01:30 | 2015-05-14 | 4 | 1 | 150 | 56.4333 | 1
2015-05-14 01:45 | 2015-05-14 | 4 | 1 | 142 | 56.1833 | 1
2015-05-14 02:00 | 2015-05-14 | 4 | 2 | 149 | 56.0667 | 1
2015-05-14 02:15 | 2015-05-14 | 4 | 2 | 143 | 56.3167 | 1
2015-05-14 02:30 | 2015-05-14 | 4 | 2 | 145 | 56.5667 | 1
2015-05-14 02:45 | 2015-05-14 | 4 | 2 | 146 | 56.8167 | 1
2015-05-14 03:00 | 2015-05-14 | 4 | 3 | 143 | 57 | 1
2015-05-14 03:15 | 2015-05-14 | 4 | 3 | 146 | 57 | 1
2015-05-14 03:30 | 2015-05-14 | 4 | 3 | 142 | 57 | 1
2015-05-14 03:45 | 2015-05-14 | 4 | 3 | 146 | 57 | 1
2015-05-14 04:00 | 2015-05-14 | 4 | 4 | 142 | 56.9333 | 1
2015-05-14 04:15 | 2015-05-14 | 4 | 4 | 147 | 56.6833 | 1
2015-05-14 04:30 | 2015-05-14 | 4 | 4 | 144 | 56.4333 | 1
2015-05-14 04:45 | 2015-05-14 | 4 | 4 | 140 | 56.1833 | 1
2015-05-14 05:00 | 2015-05-14 | 4 | 5 | 142 | 55.7895 | 1
2015-05-14 05:15 | 2015-05-14 | 4 | 5 | 138 | 55 | 1
2015-05-14 05:30 | 2015-05-14 | 4 | 5 | 145 | 55.7317 | 1
2015-05-14 05:45 | 2015-05-14 | 4 | 5 | 143 | 56.4634 | 1
2015-05-14 06:00 | 2015-05-14 | 4 | 6 | 148 | 57 | 1
2015-05-14 06:15 | 2015-05-14 | 4 | 6 | 142 | 57 | 1
2015-05-14 06:30 | 2015-05-14 | 4 | 6 | 147 | 57 | 1
2015-05-14 06:45 | 2015-05-14 | 4 | 6 | 143 | 57 | 1
2015-05-14 07:00 | 2015-05-14 | 4 | 7 | 149 | 57.1333 | 1
2015-05-14 07:15 | 2015-05-14 | 4 | 7 | 146 | 57.6333 | 1
2015-05-14 07:30 | 2015-05-14 | 4 | 7 | 148 | 58.1333 | 1
2015-05-14 07:45 | 2015-05-14 | 4 | 7 | 152 | 58.6333 | 1
2015-05-14 08:00 | 2015-05-14 | 4 | 8 | 161 | 59.1333 | 1
2015-05-14 08:15 | 2015-05-14 | 4 | 8 | 162 | 59.6333 | 1
2015-05-14 08:30 | 2015-05-14 | 4 | 8 | 164 | 60.1333 | 1
2015-05-14 08:45 | 2015-05-14 | 4 | 8 | 164 | 60.6333 | 1
2015-05-14 09:00 | 2015-05-14 | 4 | 9 | 170 | 60.9333 | 1
2015-05-14 09:15 | 2015-05-14 | 4 | 9 | 174 | 60.6833 | 1
2015-05-14 09:30 | 2015-05-14 | 4 | 9 | 191 | 60.4333 | 1
2015-05-14 09:45 | 2015-05-14 | 4 | 9 | 193 | 60.1833 | 1
2015-05-14 10:00 | 2015-05-14 | 4 | 10 | 203 | 60.2553 | 1
2015-05-14 10:15 | 2015-05-14 | 4 | 10 | 215 | 61.2128 | 1
2015-05-14 10:30 | 2015-05-14 | 4 | 10 | 208 | 62.1702 | 1
2015-05-14 10:45 | 2015-05-14 | 4 | 10 | 212 | 63 | 1
2015-05-14 11:00 | 2015-05-14 | 4 | 11 | 216 | 63 | 1
2015-05-14 11:15 | 2015-05-14 | 4 | 11 | 215 | 62.82 | 1
2015-05-14 11:30 | 2015-05-14 | 4 | 11 | 223 | 62.52 | 1
2015-05-14 11:45 | 2015-05-14 | 4 | 11 | 209 | 62.22 | 1
2015-05-14 12:00 | 2015-05-14 | 4 | 12 | 215 | 62 | 1
2015-05-14 12:15 | 2015-05-14 | 4 | 12 | 211 | 62 | 1
2015-05-14 12:30 | 2015-05-14 | 4 | 12 | 209 | 62 | 1
2015-05-14 12:45 | 2015-05-14 | 4 | 12 | 198 | 62 | 1
2015-05-14 13:00 | 2015-05-14 | 4 | 13 | 188 | 62.1333 | 1
2015-05-14 13:15 | 2015-05-14 | 4 | 13 | 185 | 62.6333 | 1
2015-05-14 13:30 | 2015-05-14 | 4 | 13 | 182 | 63.1333 | 1
2015-05-14 13:45 | 2015-05-14 | 4 | 13 | 189 | 63.6333 | 1
2015-05-14 14:00 | 2015-05-14 | 4 | 14 | 193 | 64.0667 | 1
2015-05-14 14:15 | 2015-05-14 | 4 | 14 | 187 | 64.3167 | 1
2015-05-14 14:30 | 2015-05-14 | 4 | 14 | 204 | 64.5667 | 1
2015-05-14 14:45 | 2015-05-14 | 4 | 14 | 223 | 64.8167 | 1
2015-05-14 15:00 | 2015-05-14 | 4 | 15 | 196 | 64.9333 | 1
2015-05-14 15:15 | 2015-05-14 | 4 | 15 | 192 | 64.6833 | 1
2015-05-14 15:30 | 2015-05-14 | 4 | 15 | 186 | 64.4333 | 1
2015-05-14 15:45 | 2015-05-14 | 4 | 15 | 192 | 64.1833 | 1
2015-05-14 16:00 | 2015-05-14 | 4 | 16 | 196 | 63.8667 | 1
2015-05-14 16:15 | 2015-05-14 | 4 | 16 | 191 | 63.3667 | 1
2015-05-14 16:30 | 2015-05-14 | 4 | 16 | 177 | 62.8667 | 1
2015-05-14 16:45 | 2015-05-14 | 4 | 16 | 189 | 62.3667 | 1
2015-05-14 17:00 | 2015-05-14 | 4 | 17 | 189 | 61.8667 | 1
2015-05-14 17:15 | 2015-05-14 | 4 | 17 | 191 | 61.3667 | 1
2015-05-14 17:30 | 2015-05-14 | 4 | 17 | 184 | 60.8667 | 1
2015-05-14 17:45 | 2015-05-14 | 4 | 17 | 187 | 60.3667 | 1
2015-05-14 18:00 | 2015-05-14 | 4 | 18 | 196 | 59.9333 | 1
2015-05-14 18:15 | 2015-05-14 | 4 | 18 | 182 | 59.6833 | 1
2015-05-14 18:30 | 2015-05-14 | 4 | 18 | 180 | 59.4333 | 1
2015-05-14 18:45 | 2015-05-14 | 4 | 18 | 177 | 59.1833 | 1
2015-05-14 19:00 | 2015-05-14 | 4 | 19 | 178 | 58.8667 | 1
2015-05-14 19:15 | 2015-05-14 | 4 | 19 | 191 | 58.3667 | 1
2015-05-14 19:30 | 2015-05-14 | 4 | 19 | 176 | 57.8667 | 1
2015-05-14 19:45 | 2015-05-14 | 4 | 19 | 185 | 57.3667 | 1
2015-05-14 20:00 | 2015-05-14 | 4 | 20 | 173 | 56.9333 | 1
2015-05-14 20:15 | 2015-05-14 | 4 | 20 | 176 | 56.6833 | 1
2015-05-14 20:30 | 2015-05-14 | 4 | 20 | 172 | 56.4333 | 1
2015-05-14 20:45 | 2015-05-14 | 4 | 20 | 186 | 56.1833 | 1
2015-05-14 21:00 | 2015-05-14 | 4 | 21 | 175 | 56 | 1
2015-05-14 21:15 | 2015-05-14 | 4 | 21 | 158 | 56 | 1
2015-05-14 21:30 | 2015-05-14 | 4 | 21 | 154 | 56 | 1
2015-05-14 21:45 | 2015-05-14 | 4 | 21 | 158 | 56 | 1
2015-05-14 22:00 | 2015-05-14 | 4 | 22 | 167 | 56 | 1
2015-05-14 22:15 | 2015-05-14 | 4 | 22 | 166 | 56 | 1
2015-05-14 22:30 | 2015-05-14 | 4 | 22 | 155 | 56 | 1
2015-05-14 22:45 | 2015-05-14 | 4 | 22 | 159 | 56 | 1
2015-05-14 23:00 | 2015-05-14 | 4 | 23 | 157 | 55.9333 | 1
2015-05-14 23:15 | 2015-05-14 | 4 | 23 | 170 | 55.6833 | 1
2015-05-14 23:30 | 2015-05-14 | 4 | 23 | 153 | 55.4333 | 1
2015-05-14 23:45 | 2015-05-14 | 4 | 23 | 151 | 55.1833 | 1
2015-05-15 | 2015-05-15 | 5 | 0 | 146 | 54.9333 | 1
2015-05-15 00:15 | 2015-05-15 | 5 | 0 | 162 | 54.6833 | 1
2015-05-15 00:30 | 2015-05-15 | 5 | 0 | 146 | 54.4333 | 1
2015-05-15 00:45 | 2015-05-15 | 5 | 0 | 149 | 54.1833 | 1
2015-05-15 01:00 | 2015-05-15 | 5 | 1 | 144 | 54 | 1
2015-05-15 01:15 | 2015-05-15 | 5 | 1 | 148 | 54 | 1
2015-05-15 01:30 | 2015-05-15 | 5 | 1 | 152 | 54 | 1
2015-05-15 01:45 | 2015-05-15 | 5 | 1 | 159 | 54 | 1
2015-05-15 02:00 | 2015-05-15 | 5 | 2 | 147 | 54 | 1
2015-05-15 02:15 | 2015-05-15 | 5 | 2 | 147 | 54 | 1
2015-05-15 02:30 | 2015-05-15 | 5 | 2 | 144 | 54 | 1
2015-05-15 02:45 | 2015-05-15 | 5 | 2 | 149 | 54 | 1
2015-05-15 03:00 | 2015-05-15 | 5 | 3 | 144 | 53.9333 | 1
2015-05-15 03:15 | 2015-05-15 | 5 | 3 | 157 | 53.6833 | 1
2015-05-15 03:30 | 2015-05-15 | 5 | 3 | 144 | 53.4333 | 1
2015-05-15 03:45 | 2015-05-15 | 5 | 3 | 145 | 53.1833 | 1
2015-05-15 04:00 | 2015-05-15 | 5 | 4 | 138 | 53 | 1
2015-05-15 04:15 | 2015-05-15 | 5 | 4 | 141 | 53 | 1
2015-05-15 04:30 | 2015-05-15 | 5 | 4 | 143 | 53 | 1
2015-05-15 04:45 | 2015-05-15 | 5 | 4 | 142 | 53 | 1
2015-05-15 05:00 | 2015-05-15 | 5 | 5 | 139 | 53 | 1
2015-05-15 05:15 | 2015-05-15 | 5 | 5 | 137 | 53 | 1
2015-05-15 05:30 | 2015-05-15 | 5 | 5 | 147 | 53 | 1
2015-05-15 05:45 | 2015-05-15 | 5 | 5 | 139 | 53 | 1
2015-05-15 06:00 | 2015-05-15 | 5 | 6 | 136 | 53.1333 | 1
2015-05-15 06:15 | 2015-05-15 | 5 | 6 | 141 | 53.6333 | 1
2015-05-15 06:30 | 2015-05-15 | 5 | 6 | 143 | 54.1333 | 1
2015-05-15 06:45 | 2015-05-15 | 5 | 6 | 145 | 54.6333 | 1
2015-05-15 07:00 | 2015-05-15 | 5 | 7 | 149 | 55.0667 | 1
2015-05-15 07:15 | 2015-05-15 | 5 | 7 | 147 | 55.3167 | 1
2015-05-15 07:30 | 2015-05-15 | 5 | 7 | 146 | 55.5667 | 1
2015-05-15 07:45 | 2015-05-15 | 5 | 7 | 154 | 55.8167 | 1
2015-05-15 08:00 | 2015-05-15 | 5 | 8 | 156 | 56.0667 | 1
2015-05-15 08:15 | 2015-05-15 | 5 | 8 | 155 | 56.3167 | 1
2015-05-15 08:30 | 2015-05-15 | 5 | 8 | 159 | 56.5667 | 1
2015-05-15 08:45 | 2015-05-15 | 5 | 8 | 157 | 56.8167 | 1
2015-05-15 09:00 | 2015-05-15 | 5 | 9 | 158 | 57.0667 | 1
2015-05-15 09:15 | 2015-05-15 | 5 | 9 | 165 | 57.3167 | 1
2015-05-15 09:30 | 2015-05-15 | 5 | 9 | 170 | 57.5667 | 1
2015-05-15 09:45 | 2015-05-15 | 5 | 9 | 185 | 57.8167 | 1
2015-05-15 10:00 | 2015-05-15 | 5 | 10 | 196 | 58 | 1
2015-05-15 10:15 | 2015-05-15 | 5 | 10 | 198 | 58 | 1
2015-05-15 10:30 | 2015-05-15 | 5 | 10 | 190 | 58 | 1
2015-05-15 10:45 | 2015-05-15 | 5 | 10 | 203 | 58 | 1
2015-05-15 11:00 | 2015-05-15 | 5 | 11 | 194 | 58.2 | 1
2015-05-15 11:15 | 2015-05-15 | 5 | 11 | 202 | 58.95 | 1
2015-05-15 11:30 | 2015-05-15 | 5 | 11 | 187 | 59.7 | 1
2015-05-15 11:45 | 2015-05-15 | 5 | 11 | 191 | 60.45 | 1
2015-05-15 12:00 | 2015-05-15 | 5 | 12 | 212 | 61 | 1
2015-05-15 12:15 | 2015-05-15 | 5 | 12 | 193 | 61 | 1
2015-05-15 12:30 | 2015-05-15 | 5 | 12 | 202 | 61 | 1
2015-05-15 12:45 | 2015-05-15 | 5 | 12 | 185 | 61 | 1
2015-05-15 13:00 | 2015-05-15 | 5 | 13 | 203 | 60.9333 | 1
2015-05-15 13:15 | 2015-05-15 | 5 | 13 | 212 | 60.6833 | 1
2015-05-15 13:30 | 2015-05-15 | 5 | 13 | 198 | 60.4333 | 1
2015-05-15 13:45 | 2015-05-15 | 5 | 13 | 211 | 60.1833 | 1
2015-05-15 14:00 | 2015-05-15 | 5 | 14 | 200 | 60 | 1
2015-05-15 14:15 | 2015-05-15 | 5 | 14 | 207 | 60 | 1
2015-05-15 14:30 | 2015-05-15 | 5 | 14 | 217 | 60 | 1
2015-05-15 14:45 | 2015-05-15 | 5 | 14 | 205 | 60 | 1
2015-05-15 15:00 | 2015-05-15 | 5 | 15 | 215 | 59.9333 | 1
2015-05-15 15:15 | 2015-05-15 | 5 | 15 | 206 | 59.6833 | 1
2015-05-15 15:30 | 2015-05-15 | 5 | 15 | 201 | 59.4333 | 1
2015-05-15 15:45 | 2015-05-15 | 5 | 15 | 211 | 59.1833 | 1
2015-05-15 16:00 | 2015-05-15 | 5 | 16 | 217 | 58.9333 | 1
2015-05-15 16:15 | 2015-05-15 | 5 | 16 | 207 | 58.6833 | 1
2015-05-15 16:30 | 2015-05-15 | 5 | 16 | 210 | 58.4333 | 1
2015-05-15 16:45 | 2015-05-15 | 5 | 16 | 205 | 58.1833 | 1
2015-05-15 17:00 | 2015-05-15 | 5 | 17 | 202 | 58 | 1
2015-05-15 17:15 | 2015-05-15 | 5 | 17 | 205 | 58 | 1
2015-05-15 17:30 | 2015-05-15 | 5 | 17 | 207 | 58 | 1
2015-05-15 17:45 | 2015-05-15 | 5 | 17 | 202 | 58 | 1
2015-05-15 18:00 | 2015-05-15 | 5 | 18 | 195 | 57.9333 | 1
2015-05-15 18:15 | 2015-05-15 | 5 | 18 | 194 | 57.6833 | 1
2015-05-15 18:30 | 2015-05-15 | 5 | 18 | 197 | 57.4333 | 1
2015-05-15 18:45 | 2015-05-15 | 5 | 18 | 192 | 57.1833 | 1
2015-05-15 19:00 | 2015-05-15 | 5 | 19 | 183 | 56.9333 | 1
2015-05-15 19:15 | 2015-05-15 | 5 | 19 | 182 | 56.6833 | 1
2015-05-15 19:30 | 2015-05-15 | 5 | 19 | 174 | 56.4333 | 1
2015-05-15 19:45 | 2015-05-15 | 5 | 19 | 165 | 56.1833 | 1
2015-05-15 20:00 | 2015-05-15 | 5 | 20 | 168 | 56 | 1
2015-05-15 20:15 | 2015-05-15 | 5 | 20 | 156 | 56 | 1
2015-05-15 20:30 | 2015-05-15 | 5 | 20 | 162 | 56 | 1
2015-05-15 20:45 | 2015-05-15 | 5 | 20 | 156 | 56 | 1
2015-05-15 21:00 | 2015-05-15 | 5 | 21 | 164 | 55.9286 | 1
2015-05-15 21:15 | 2015-05-15 | 5 | 21 | 142 | 55.6607 | 1
2015-05-15 21:30 | 2015-05-15 | 5 | 21 | 138 | 55.3929 | 1
2015-05-15 21:45 | 2015-05-15 | 5 | 21 | 136 | 55.125 | 1
2015-05-15 22:00 | 2015-05-15 | 5 | 22 | 139 | 55.9333 | 1
2015-05-15 22:15 | 2015-05-15 | 5 | 22 | 146 | 55.6833 | 1
2015-05-15 22:30 | 2015-05-15 | 5 | 22 | 141 | 55.4333 | 1
2015-05-15 22:45 | 2015-05-15 | 5 | 22 | 140 | 55.1833 | 1
2015-05-15 23:00 | 2015-05-15 | 5 | 23 | 140 | 55 | 1
2015-05-15 23:15 | 2015-05-15 | 5 | 23 | 140 | 55 | 1
2015-05-15 23:30 | 2015-05-15 | 5 | 23 | 139 | 55 | 1
2015-05-15 23:45 | 2015-05-15 | 5 | 23 | 143 | 55 | 1
2015-05-16 | 2015-05-16 | 6 | 0 | 138 | 54.9333 | 1
2015-05-16 00:15 | 2015-05-16 | 6 | 0 | 136 | 54.6833 | 1
2015-05-16 00:30 | 2015-05-16 | 6 | 0 | 135 | 54.4333 | 1
2015-05-16 00:45 | 2015-05-16 | 6 | 0 | 134 | 54.1833 | 1
2015-05-16 01:00 | 2015-05-16 | 6 | 1 | 134 | 54 | 1
2015-05-16 01:15 | 2015-05-16 | 6 | 1 | 137 | 54 | 1
2015-05-16 01:30 | 2015-05-16 | 6 | 1 | 136 | 54 | 1
2015-05-16 01:45 | 2015-05-16 | 6 | 1 | 132 | 54 | 1
2015-05-16 02:00 | 2015-05-16 | 6 | 2 | 132 | 54 | 1
2015-05-16 02:15 | 2015-05-16 | 6 | 2 | 130 | 54 | 1
2015-05-16 02:30 | 2015-05-16 | 6 | 2 | 136 | 54 | 1
2015-05-16 02:45 | 2015-05-16 | 6 | 2 | 134 | 54 | 1
2015-05-16 03:00 | 2015-05-16 | 6 | 3 | 144 | 54 | 1
2015-05-16 03:15 | 2015-05-16 | 6 | 3 | 133 | 54 | 1
2015-05-16 03:30 | 2015-05-16 | 6 | 3 | 133 | 54 | 1
2015-05-16 03:45 | 2015-05-16 | 6 | 3 | 131 | 54 | 1
2015-05-16 04:00 | 2015-05-16 | 6 | 4 | 134 | 54 | 1
2015-05-16 04:15 | 2015-05-16 | 6 | 4 | 132 | 54 | 1
2015-05-16 04:30 | 2015-05-16 | 6 | 4 | 133 | 54 | 1
2015-05-16 04:45 | 2015-05-16 | 6 | 4 | 130 | 54 | 1
2015-05-16 05:00 | 2015-05-16 | 6 | 5 | 138 | 54.0667 | 1
2015-05-16 05:15 | 2015-05-16 | 6 | 5 | 133 | 54.3167 | 1
2015-05-16 05:30 | 2015-05-16 | 6 | 5 | 138 | 54.5667 | 1
2015-05-16 05:45 | 2015-05-16 | 6 | 5 | 135 | 54.8167 | 1
2015-05-16 06:00 | 2015-05-16 | 6 | 6 | 136 | 55 | 1
2015-05-16 06:15 | 2015-05-16 | 6 | 6 | 133 | 55 | 1
2015-05-16 06:30 | 2015-05-16 | 6 | 6 | 135 | 55 | 1
2015-05-16 06:45 | 2015-05-16 | 6 | 6 | 132 | 55 | 1
2015-05-16 07:00 | 2015-05-16 | 6 | 7 | 135 | 55 | 1
2015-05-16 07:15 | 2015-05-16 | 6 | 7 | 136 | 55 | 1
2015-05-16 07:30 | 2015-05-16 | 6 | 7 | 131 | 55 | 1
2015-05-16 07:45 | 2015-05-16 | 6 | 7 | 132 | 55 | 1
2015-05-16 08:00 | 2015-05-16 | 6 | 8 | 132 | 55.0667 | 1
2015-05-16 08:15 | 2015-05-16 | 6 | 8 | 131 | 55.3167 | 1
2015-05-16 08:30 | 2015-05-16 | 6 | 8 | 135 | 55.5667 | 1
2015-05-16 08:45 | 2015-05-16 | 6 | 8 | 132 | 55.8167 | 1
2015-05-16 09:00 | 2015-05-16 | 6 | 9 | 134 | 56 | 1
2015-05-16 09:15 | 2015-05-16 | 6 | 9 | 139 | 56 | 1
2015-05-16 09:30 | 2015-05-16 | 6 | 9 | 138 | 56 | 1
2015-05-16 09:45 | 2015-05-16 | 6 | 9 | 140 | 56 | 1
2015-05-16 10:00 | 2015-05-16 | 6 | 10 | 150 | 56.1333 | 1
2015-05-16 10:15 | 2015-05-16 | 6 | 10 | 149 | 56.6333 | 1
2015-05-16 10:30 | 2015-05-16 | 6 | 10 | 151 | 57.1333 | 1
2015-05-16 10:45 | 2015-05-16 | 6 | 10 | 144 | 57.6333 | 1
2015-05-16 11:00 | 2015-05-16 | 6 | 11 | 161 | 58 | 1
2015-05-16 11:15 | 2015-05-16 | 6 | 11 | 157 | 58 | 1
2015-05-16 11:30 | 2015-05-16 | 6 | 11 | 173 | 58 | 1
2015-05-16 11:45 | 2015-05-16 | 6 | 11 | 152 | 58 | 1
2015-05-16 12:00 | 2015-05-16 | 6 | 12 | 166 | 58 | 1
2015-05-16 12:15 | 2015-05-16 | 6 | 12 | 161 | 58 | 1
2015-05-16 12:30 | 2015-05-16 | 6 | 12 | 161 | 58 | 1
2015-05-16 12:45 | 2015-05-16 | 6 | 12 | 168 | 58 | 1
2015-05-16 13:00 | 2015-05-16 | 6 | 13 | 171 | 58.0667 | 1
2015-05-16 13:15 | 2015-05-16 | 6 | 13 | 182 | 58.3167 | 1
2015-05-16 13:30 | 2015-05-16 | 6 | 13 | 170 | 58.5667 | 1
2015-05-16 13:45 | 2015-05-16 | 6 | 13 | 178 | 58.8167 | 1
2015-05-16 14:00 | 2015-05-16 | 6 | 14 | 175 | 59.0667 | 1
2015-05-16 14:15 | 2015-05-16 | 6 | 14 | 181 | 59.3167 | 1
2015-05-16 14:30 | 2015-05-16 | 6 | 14 | 179 | 59.5667 | 1
2015-05-16 14:45 | 2015-05-16 | 6 | 14 | 172 | 59.8167 | 1
2015-05-16 15:00 | 2015-05-16 | 6 | 15 | 173 | 59.913 | 1
2015-05-16 15:15 | 2015-05-16 | 6 | 15 | 195 | 59.587 | 1
2015-05-16 15:30 | 2015-05-16 | 6 | 15 | 173 | 59.2609 | 1
2015-05-16 15:45 | 2015-05-16 | 6 | 15 | 185 | 59 | 1
2015-05-16 16:00 | 2015-05-16 | 6 | 16 | 180 | 59 | 1
2015-05-16 16:15 | 2015-05-16 | 6 | 16 | 185 | 59 | 1
2015-05-16 16:30 | 2015-05-16 | 6 | 16 | 201 | 59 | 1
2015-05-16 16:45 | 2015-05-16 | 6 | 16 | 186 | 59 | 1
2015-05-16 17:00 | 2015-05-16 | 6 | 17 | 185 | 58.9333 | 1
2015-05-16 17:15 | 2015-05-16 | 6 | 17 | 187 | 58.6833 | 1
2015-05-16 17:30 | 2015-05-16 | 6 | 17 | 188 | 58.4333 | 1
2015-05-16 17:45 | 2015-05-16 | 6 | 17 | 192 | 58.1833 | 1
2015-05-16 18:00 | 2015-05-16 | 6 | 18 | 175 | 57.9333 | 1
2015-05-16 18:15 | 2015-05-16 | 6 | 18 | 177 | 57.6833 | 1
2015-05-16 18:30 | 2015-05-16 | 6 | 18 | 171 | 57.4333 | 1
2015-05-16 18:45 | 2015-05-16 | 6 | 18 | 179 | 57.1833 | 1
2015-05-16 19:00 | 2015-05-16 | 6 | 19 | 171 | 56.9333 | 1
2015-05-16 19:15 | 2015-05-16 | 6 | 19 | 165 | 56.6833 | 1
2015-05-16 19:30 | 2015-05-16 | 6 | 19 | 166 | 56.4333 | 1
2015-05-16 19:45 | 2015-05-16 | 6 | 19 | 159 | 56.1833 | 1
2015-05-16 20:00 | 2015-05-16 | 6 | 20 | 171 | 55.9048 | 1
2015-05-16 20:15 | 2015-05-16 | 6 | 20 | 147 | 55.5476 | 1
2015-05-16 20:30 | 2015-05-16 | 6 | 20 | 143 | 55.1905 | 1
2015-05-16 20:45 | 2015-05-16 | 6 | 20 | 140 | 55 | 1
2015-05-16 21:00 | 2015-05-16 | 6 | 21 | 143 | 55 | 1
2015-05-16 21:15 | 2015-05-16 | 6 | 21 | 141 | 55 | 1
2015-05-16 21:30 | 2015-05-16 | 6 | 21 | 154 | 55 | 1
2015-05-16 21:45 | 2015-05-16 | 6 | 21 | 138 | 55 | 1
2015-05-16 22:00 | 2015-05-16 | 6 | 22 | 138 | 55 | 1
2015-05-16 22:15 | 2015-05-16 | 6 | 22 | 136 | 55 | 1
2015-05-16 22:30 | 2015-05-16 | 6 | 22 | 137 | 55 | 1
2015-05-16 22:45 | 2015-05-16 | 6 | 22 | 144 | 55 | 1
2015-05-16 23:00 | 2015-05-16 | 6 | 23 | 152 | 55 | 1
2015-05-16 23:15 | 2015-05-16 | 6 | 23 | 139 | 55 | 1
2015-05-16 23:30 | 2015-05-16 | 6 | 23 | 137 | 55 | 1
2015-05-16 23:45 | 2015-05-16 | 6 | 23 | 142 | 55 | 1
2015-05-17 | 2015-05-17 | 7 | 0 | 144 | 55 | 1
2015-05-17 00:15 | 2015-05-17 | 7 | 0 | 139 | 55 | 1
2015-05-17 00:30 | 2015-05-17 | 7 | 0 | 135 | 55 | 1
2015-05-17 00:45 | 2015-05-17 | 7 | 0 | 135 | 55 | 1
2015-05-17 01:00 | 2015-05-17 | 7 | 1 | 141 | 55 | 1
2015-05-17 01:15 | 2015-05-17 | 7 | 1 | 135 | 55 | 1
2015-05-17 01:30 | 2015-05-17 | 7 | 1 | 136 | 55 | 1
2015-05-17 01:45 | 2015-05-17 | 7 | 1 | 132 | 55 | 1
2015-05-17 02:00 | 2015-05-17 | 7 | 2 | 134 | 55 | 1
2015-05-17 02:15 | 2015-05-17 | 7 | 2 | 132 | 55 | 1
2015-05-17 02:30 | 2015-05-17 | 7 | 2 | 140 | 55 | 1
2015-05-17 02:45 | 2015-05-17 | 7 | 2 | 136 | 55 | 1
2015-05-17 03:00 | 2015-05-17 | 7 | 3 | 131 | 55 | 1
2015-05-17 03:15 | 2015-05-17 | 7 | 3 | 133 | 55 | 1
2015-05-17 03:30 | 2015-05-17 | 7 | 3 | 139 | 55 | 1
2015-05-17 03:45 | 2015-05-17 | 7 | 3 | 133 | 55 | 1
2015-05-17 04:00 | 2015-05-17 | 7 | 4 | 147 | 55 | 1
2015-05-17 04:15 | 2015-05-17 | 7 | 4 | 136 | 55 | 1
2015-05-17 04:30 | 2015-05-17 | 7 | 4 | 143 | 55 | 1
2015-05-17 04:45 | 2015-05-17 | 7 | 4 | 135 | 55 | 1
2015-05-17 05:00 | 2015-05-17 | 7 | 5 | 148 | 55 | 1
2015-05-17 05:15 | 2015-05-17 | 7 | 5 | 135 | 55 | 1
2015-05-17 05:30 | 2015-05-17 | 7 | 5 | 135 | 55 | 1
2015-05-17 05:45 | 2015-05-17 | 7 | 5 | 134 | 55 | 1
2015-05-17 06:00 | 2015-05-17 | 7 | 6 | 137 | 55.0667 | 1
2015-05-17 06:15 | 2015-05-17 | 7 | 6 | 134 | 55.3167 | 1
2015-05-17 06:30 | 2015-05-17 | 7 | 6 | 152 | 55.5667 | 1
2015-05-17 06:45 | 2015-05-17 | 7 | 6 | 139 | 55.8167 | 1
2015-05-17 07:00 | 2015-05-17 | 7 | 7 | 146 | 56 | 1
2015-05-17 07:15 | 2015-05-17 | 7 | 7 | 145 | 56 | 1
2015-05-17 07:30 | 2015-05-17 | 7 | 7 | 148 | 56 | 1
2015-05-17 07:45 | 2015-05-17 | 7 | 7 | 147 | 56 | 1
2015-05-17 08:00 | 2015-05-17 | 7 | 8 | 159 | 56 | 1
2015-05-17 08:15 | 2015-05-17 | 7 | 8 | 147 | 56 | 1
2015-05-17 08:30 | 2015-05-17 | 7 | 8 | 146 | 56 | 1
2015-05-17 08:45 | 2015-05-17 | 7 | 8 | 144 | 56 | 1
2015-05-17 09:00 | 2015-05-17 | 7 | 9 | 149 | 56.1333 | 1
2015-05-17 09:15 | 2015-05-17 | 7 | 9 | 151 | 56.6333 | 1
2015-05-17 09:30 | 2015-05-17 | 7 | 9 | 156 | 57.1333 | 1
2015-05-17 09:45 | 2015-05-17 | 7 | 9 | 147 | 57.6333 | 1
2015-05-17 10:00 | 2015-05-17 | 7 | 10 | 154 | 58 | 1
2015-05-17 10:15 | 2015-05-17 | 7 | 10 | 152 | 58 | 1
2015-05-17 10:30 | 2015-05-17 | 7 | 10 | 160 | 58 | 1
2015-05-17 10:45 | 2015-05-17 | 7 | 10 | 171 | 58 | 1
2015-05-17 11:00 | 2015-05-17 | 7 | 11 | 181 | 58.2 | 1
2015-05-17 11:15 | 2015-05-17 | 7 | 11 | 160 | 58.95 | 1
2015-05-17 11:30 | 2015-05-17 | 7 | 11 | 175 | 59.7 | 1
2015-05-17 11:45 | 2015-05-17 | 7 | 11 | 183 | 60.45 | 1
2015-05-17 12:00 | 2015-05-17 | 7 | 12 | 182 | 60.9333 | 1
2015-05-17 12:15 | 2015-05-17 | 7 | 12 | 177 | 60.6833 | 1
2015-05-17 12:30 | 2015-05-17 | 7 | 12 | 172 | 60.4333 | 1
2015-05-17 12:45 | 2015-05-17 | 7 | 12 | 189 | 60.1833 | 1
2015-05-17 13:00 | 2015-05-17 | 7 | 13 | 174 | 60 | 1
2015-05-17 13:15 | 2015-05-17 | 7 | 13 | 196 | 60 | 1
2015-05-17 13:30 | 2015-05-17 | 7 | 13 | 184 | 60 | 1
2015-05-17 13:45 | 2015-05-17 | 7 | 13 | 179 | 60 | 1
2015-05-17 14:00 | 2015-05-17 | 7 | 14 | 187 | 60 | 1
2015-05-17 14:15 | 2015-05-17 | 7 | 14 | 172 | 60 | 1
2015-05-17 14:30 | 2015-05-17 | 7 | 14 | 186 | 60 | 1
2015-05-17 14:45 | 2015-05-17 | 7 | 14 | 193 | 60 | 1
2015-05-17 15:00 | 2015-05-17 | 7 | 15 | 191 | 60 | 1
2015-05-17 15:15 | 2015-05-17 | 7 | 15 | 192 | 60 | 1
2015-05-17 15:30 | 2015-05-17 | 7 | 15 | 176 | 60 | 1
2015-05-17 15:45 | 2015-05-17 | 7 | 15 | 196 | 60 | 1
2015-05-17 16:00 | 2015-05-17 | 7 | 16 | 194 | 59.9333 | 1
2015-05-17 16:15 | 2015-05-17 | 7 | 16 | 183 | 59.6833 | 1
2015-05-17 16:30 | 2015-05-17 | 7 | 16 | 188 | 59.4333 | 1
2015-05-17 16:45 | 2015-05-17 | 7 | 16 | 184 | 59.1833 | 1
2015-05-17 17:00 | 2015-05-17 | 7 | 17 | 194 | 58.9333 | 1
2015-05-17 17:15 | 2015-05-17 | 7 | 17 | 185 | 58.6833 | 1
2015-05-17 17:30 | 2015-05-17 | 7 | 17 | 193 | 58.4333 | 1
2015-05-17 17:45 | 2015-05-17 | 7 | 17 | 176 | 58.1833 | 1
2015-05-17 18:00 | 2015-05-17 | 7 | 18 | 176 | 57.9333 | 1
2015-05-17 18:15 | 2015-05-17 | 7 | 18 | 180 | 57.6833 | 1
2015-05-17 18:30 | 2015-05-17 | 7 | 18 | 189 | 57.4333 | 1
2015-05-17 18:45 | 2015-05-17 | 7 | 18 | 181 | 57.1833 | 1
2015-05-17 19:00 | 2015-05-17 | 7 | 19 | 179 | 56.9333 | 1
2015-05-17 19:15 | 2015-05-17 | 7 | 19 | 175 | 56.6833 | 1
2015-05-17 19:30 | 2015-05-17 | 7 | 19 | 165 | 56.4333 | 1
2015-05-17 19:45 | 2015-05-17 | 7 | 19 | 169 | 56.1833 | 1
2015-05-17 20:00 | 2015-05-17 | 7 | 20 | 156 | 56.0667 | 1
2015-05-17 20:15 | 2015-05-17 | 7 | 20 | 166 | 56.3167 | 1
2015-05-17 20:30 | 2015-05-17 | 7 | 20 | 160 | 56.5667 | 1
2015-05-17 20:45 | 2015-05-17 | 7 | 20 | 158 | 56.8167 | 1
2015-05-17 21:00 | 2015-05-17 | 7 | 21 | 168 | 56.9333 | 1
2015-05-17 21:15 | 2015-05-17 | 7 | 21 | 145 | 56.6833 | 1
2015-05-17 21:30 | 2015-05-17 | 7 | 21 | 141 | 56.4333 | 1
2015-05-17 21:45 | 2015-05-17 | 7 | 21 | 136 | 56.1833 | 1
2015-05-17 22:00 | 2015-05-17 | 7 | 22 | 138 | 56 | 1
2015-05-17 22:15 | 2015-05-17 | 7 | 22 | 136 | 56 | 1
2015-05-17 22:30 | 2015-05-17 | 7 | 22 | 138 | 56 | 1
2015-05-17 22:45 | 2015-05-17 | 7 | 22 | 140 | 56 | 1
2015-05-17 23:00 | 2015-05-17 | 7 | 23 | 138 | 56 | 1
2015-05-17 23:15 | 2015-05-17 | 7 | 23 | 135 | 56 | 1
2015-05-17 23:30 | 2015-05-17 | 7 | 23 | 138 | 56 | 1
2015-05-17 23:45 | 2015-05-17 | 7 | 23 | 142 | 56 | 1
2015-05-18 | 2015-05-18 | 1 | 0 | 139 | 55.9333 | 1
2015-05-18 00:15 | 2015-05-18 | 1 | 0 | 136 | 55.6833 | 1
2015-05-18 00:30 | 2015-05-18 | 1 | 0 | 134 | 55.4333 | 1
2015-05-18 00:45 | 2015-05-18 | 1 | 0 | 132 | 55.1833 | 1
2015-05-18 01:00 | 2015-05-18 | 1 | 1 | 133 | 55 | 1
2015-05-18 01:15 | 2015-05-18 | 1 | 1 | 137 | 55 | 1
2015-05-18 01:30 | 2015-05-18 | 1 | 1 | 134 | 55 | 1
2015-05-18 01:45 | 2015-05-18 | 1 | 1 | 135 | 55 | 1
2015-05-18 02:00 | 2015-05-18 | 1 | 2 | 135 | 55 | 1
2015-05-18 02:15 | 2015-05-18 | 1 | 2 | 137 | 55 | 1
2015-05-18 02:30 | 2015-05-18 | 1 | 2 | 135 | 55 | 1
2015-05-18 02:45 | 2015-05-18 | 1 | 2 | 142 | 55 | 1
2015-05-18 03:00 | 2015-05-18 | 1 | 3 | 137 | 55 | 1
2015-05-18 03:15 | 2015-05-18 | 1 | 3 | 136 | 55 | 1
2015-05-18 03:30 | 2015-05-18 | 1 | 3 | 134 | 55 | 1
2015-05-18 03:45 | 2015-05-18 | 1 | 3 | 132 | 55 | 1
2015-05-18 04:00 | 2015-05-18 | 1 | 4 | 135 | 55 | 1
2015-05-18 04:15 | 2015-05-18 | 1 | 4 | 139 | 55 | 1
2015-05-18 04:30 | 2015-05-18 | 1 | 4 | 136 | 55 | 1
2015-05-18 04:45 | 2015-05-18 | 1 | 4 | 134 | 55 | 1
2015-05-18 05:00 | 2015-05-18 | 1 | 5 | 131 | 55 | 1
2015-05-18 05:15 | 2015-05-18 | 1 | 5 | 135 | 55 | 1
2015-05-18 05:30 | 2015-05-18 | 1 | 5 | 135 | 55 | 1
2015-05-18 05:45 | 2015-05-18 | 1 | 5 | 134 | 55 | 1
2015-05-18 06:00 | 2015-05-18 | 1 | 6 | 135 | 55 | 1
2015-05-18 06:15 | 2015-05-18 | 1 | 6 | 129 | 55 | 1
2015-05-18 06:30 | 2015-05-18 | 1 | 6 | 134 | 55 | 1
2015-05-18 06:45 | 2015-05-18 | 1 | 6 | 138 | 55 | 1
2015-05-18 07:00 | 2015-05-18 | 1 | 7 | 137 | 55 | 1
2015-05-18 07:15 | 2015-05-18 | 1 | 7 | 136 | 55 | 1
2015-05-18 07:30 | 2015-05-18 | 1 | 7 | 132 | 55 | 1
2015-05-18 07:45 | 2015-05-18 | 1 | 7 | 137 | 55 | 1
2015-05-18 08:00 | 2015-05-18 | 1 | 8 | 144 | 55.0667 | 1
2015-05-18 08:15 | 2015-05-18 | 1 | 8 | 151 | 55.3167 | 1
2015-05-18 08:30 | 2015-05-18 | 1 | 8 | 155 | 55.5667 | 1
2015-05-18 08:45 | 2015-05-18 | 1 | 8 | 151 | 55.8167 | 1
2015-05-18 09:00 | 2015-05-18 | 1 | 9 | 157 | 56.0667 | 1
2015-05-18 09:15 | 2015-05-18 | 1 | 9 | 158 | 56.3167 | 1
2015-05-18 09:30 | 2015-05-18 | 1 | 9 | 162 | 56.5667 | 1
2015-05-18 09:45 | 2015-05-18 | 1 | 9 | 166 | 56.8167 | 1
2015-05-18 10:00 | 2015-05-18 | 1 | 10 | 172 | 57.0667 | 1
2015-05-18 10:15 | 2015-05-18 | 1 | 10 | 172 | 57.3167 | 1
2015-05-18 10:30 | 2015-05-18 | 1 | 10 | 171 | 57.5667 | 1
2015-05-18 10:45 | 2015-05-18 | 1 | 10 | 177 | 57.8167 | 1
2015-05-18 11:00 | 2015-05-18 | 1 | 11 | 181 | 58 | 1
2015-05-18 11:15 | 2015-05-18 | 1 | 11 | 188 | 58 | 1
2015-05-18 11:30 | 2015-05-18 | 1 | 11 | 185 | 58 | 1
2015-05-18 11:45 | 2015-05-18 | 1 | 11 | 176 | 58 | 1
2015-05-18 12:00 | 2015-05-18 | 1 | 12 | 179 | 58.0667 | 1
2015-05-18 12:15 | 2015-05-18 | 1 | 12 | 184 | 58.3167 | 1
2015-05-18 12:30 | 2015-05-18 | 1 | 12 | 184 | 58.5667 | 1
2015-05-18 12:45 | 2015-05-18 | 1 | 12 | 179 | 58.8167 | 1
2015-05-18 13:00 | 2015-05-18 | 1 | 13 | 181 | 59 | 1
2015-05-18 13:15 | 2015-05-18 | 1 | 13 | 202 | 59 | 1
2015-05-18 13:30 | 2015-05-18 | 1 | 13 | 187 | 59 | 1
2015-05-18 13:45 | 2015-05-18 | 1 | 13 | 190 | 59 | 1
2015-05-18 14:00 | 2015-05-18 | 1 | 14 | 184 | 59 | 1
2015-05-18 14:15 | 2015-05-18 | 1 | 14 | 196 | 59 | 1
2015-05-18 14:30 | 2015-05-18 | 1 | 14 | 188 | 59 | 1
2015-05-18 14:45 | 2015-05-18 | 1 | 14 | 207 | 59 | 1
2015-05-18 15:00 | 2015-05-18 | 1 | 15 | 202 | 59 | 1
2015-05-18 15:15 | 2015-05-18 | 1 | 15 | 194 | 59 | 1
2015-05-18 15:30 | 2015-05-18 | 1 | 15 | 202 | 59 | 1
2015-05-18 15:45 | 2015-05-18 | 1 | 15 | 196 | 59 | 1
2015-05-18 16:00 | 2015-05-18 | 1 | 16 | 207 | 58.9333 | 1
2015-05-18 16:15 | 2015-05-18 | 1 | 16 | 197 | 58.6833 | 1
2015-05-18 16:30 | 2015-05-18 | 1 | 16 | 191 | 58.4333 | 1
2015-05-18 16:45 | 2015-05-18 | 1 | 16 | 197 | 58.1833 | 1
2015-05-18 17:00 | 2015-05-18 | 1 | 17 | 183 | 57.9333 | 1
2015-05-18 17:15 | 2015-05-18 | 1 | 17 | 200 | 57.6833 | 1
2015-05-18 17:30 | 2015-05-18 | 1 | 17 | 186 | 57.4333 | 1
2015-05-18 17:45 | 2015-05-18 | 1 | 17 | 195 | 57.1833 | 1
2015-05-18 18:00 | 2015-05-18 | 1 | 18 | 181 | 57 | 1
2015-05-18 18:15 | 2015-05-18 | 1 | 18 | 189 | 57 | 1
2015-05-18 18:30 | 2015-05-18 | 1 | 18 | 190 | 57 | 1
2015-05-18 18:45 | 2015-05-18 | 1 | 18 | 183 | 57 | 1
2015-05-18 19:00 | 2015-05-18 | 1 | 19 | 183 | 57 | 1
2015-05-18 19:15 | 2015-05-18 | 1 | 19 | 168 | 57 | 1
2015-05-18 19:30 | 2015-05-18 | 1 | 19 | 169 | 57 | 1
2015-05-18 19:45 | 2015-05-18 | 1 | 19 | 160 | 57 | 1
2015-05-18 20:00 | 2015-05-18 | 1 | 20 | 168 | 57 | 1
2015-05-18 20:15 | 2015-05-18 | 1 | 20 | 166 | 57 | 1
2015-05-18 20:30 | 2015-05-18 | 1 | 20 | 158 | 57 | 1
2015-05-18 20:45 | 2015-05-18 | 1 | 20 | 156 | 57 | 1
2015-05-18 21:00 | 2015-05-18 | 1 | 21 | 162 | 57 | 1
2015-05-18 21:15 | 2015-05-18 | 1 | 21 | 156 | 57 | 1
2015-05-18 21:30 | 2015-05-18 | 1 | 21 | 146 | 57 | 1
2015-05-18 21:45 | 2015-05-18 | 1 | 21 | 145 | 57 | 1
2015-05-18 22:00 | 2015-05-18 | 1 | 22 | 147 | 56.9333 | 1
2015-05-18 22:15 | 2015-05-18 | 1 | 22 | 157 | 56.6833 | 1
2015-05-18 22:30 | 2015-05-18 | 1 | 22 | 149 | 56.4333 | 1
2015-05-18 22:45 | 2015-05-18 | 1 | 22 | 149 | 56.1833 | 1
2015-05-18 23:00 | 2015-05-18 | 1 | 23 | 151 | 56 | 1
2015-05-18 23:15 | 2015-05-18 | 1 | 23 | 149 | 56 | 1
2015-05-18 23:30 | 2015-05-18 | 1 | 23 | 149 | 56 | 1
2015-05-18 23:45 | 2015-05-18 | 1 | 23 | 157 | 56 | 1
2015-05-19 | 2015-05-19 | 2 | 0 | 155 | 56 | 1
2015-05-19 00:15 | 2015-05-19 | 2 | 0 | 145 | 56 | 1
2015-05-19 00:30 | 2015-05-19 | 2 | 0 | 142 | 56 | 1
2015-05-19 00:45 | 2015-05-19 | 2 | 0 | 144 | 56 | 1
2015-05-19 01:00 | 2015-05-19 | 2 | 1 | 153 | 55.8 | 1
2015-05-19 01:15 | 2015-05-19 | 2 | 1 | 149 | 55.05 | 1
2015-05-19 01:30 | 2015-05-19 | 2 | 1 | 145 | 55 | 1
2015-05-19 01:45 | 2015-05-19 | 2 | 1 | 145 | 55 | 1
2015-05-19 02:00 | 2015-05-19 | 2 | 2 | 140 | 55 | 1
2015-05-19 02:15 | 2015-05-19 | 2 | 2 | 150 | 55 | 1
2015-05-19 02:30 | 2015-05-19 | 2 | 2 | 148 | 55 | 1
2015-05-19 02:45 | 2015-05-19 | 2 | 2 | 146 | 55 | 1
2015-05-19 03:00 | 2015-05-19 | 2 | 3 | 141 | 55 | 1
2015-05-19 03:15 | 2015-05-19 | 2 | 3 | 145 | 55 | 1
2015-05-19 03:30 | 2015-05-19 | 2 | 3 | 152 | 55 | 1
2015-05-19 03:45 | 2015-05-19 | 2 | 3 | 146 | 55 | 1
2015-05-19 04:00 | 2015-05-19 | 2 | 4 | 143 | 55.931 | 1
2015-05-19 04:15 | 2015-05-19 | 2 | 4 | 144 | 55.6724 | 1
2015-05-19 04:30 | 2015-05-19 | 2 | 4 | 145 | 55.4138 | 1
2015-05-19 04:45 | 2015-05-19 | 2 | 4 | 145 | 55.1552 | 1
2015-05-19 05:00 | 2015-05-19 | 2 | 5 | 156 | 55 | 1
2015-05-19 05:15 | 2015-05-19 | 2 | 5 | 147 | 55 | 1
2015-05-19 05:30 | 2015-05-19 | 2 | 5 | 141 | 55 | 1
2015-05-19 05:45 | 2015-05-19 | 2 | 5 | 143 | 55 | 1
2015-05-19 06:00 | 2015-05-19 | 2 | 6 | 145 | 55.0667 | 1
2015-05-19 06:15 | 2015-05-19 | 2 | 6 | 158 | 55.3167 | 1
2015-05-19 06:30 | 2015-05-19 | 2 | 6 | 145 | 55.5667 | 1
2015-05-19 06:45 | 2015-05-19 | 2 | 6 | 148 | 55.8167 | 1
2015-05-19 07:00 | 2015-05-19 | 2 | 7 | 143 | 56 | 1
2015-05-19 07:15 | 2015-05-19 | 2 | 7 | 154 | 56 | 1
2015-05-19 07:30 | 2015-05-19 | 2 | 7 | 153 | 56 | 1
2015-05-19 07:45 | 2015-05-19 | 2 | 7 | 145 | 56 | 1
2015-05-19 08:00 | 2015-05-19 | 2 | 8 | 150 | 56 | 1
2015-05-19 08:15 | 2015-05-19 | 2 | 8 | 155 | 56 | 1
2015-05-19 08:30 | 2015-05-19 | 2 | 8 | 167 | 56 | 1
2015-05-19 08:45 | 2015-05-19 | 2 | 8 | 172 | 56 | 1
2015-05-19 09:00 | 2015-05-19 | 2 | 9 | 162 | 56.0667 | 1
2015-05-19 09:15 | 2015-05-19 | 2 | 9 | 162 | 56.3167 | 1
2015-05-19 09:30 | 2015-05-19 | 2 | 9 | 160 | 56.5667 | 1
2015-05-19 09:45 | 2015-05-19 | 2 | 9 | 176 | 56.8167 | 1
2015-05-19 10:00 | 2015-05-19 | 2 | 10 | 176 | 57 | 1
2015-05-19 10:15 | 2015-05-19 | 2 | 10 | 175 | 57.1778 | 1
2015-05-19 10:30 | 2015-05-19 | 2 | 10 | 175 | 57.8444 | 1
2015-05-19 10:45 | 2015-05-19 | 2 | 10 | 178 | 58.5111 | 1
2015-05-19 11:00 | 2015-05-19 | 2 | 11 | 187 | 59.0667 | 1
2015-05-19 11:15 | 2015-05-19 | 2 | 11 | 190 | 59.3167 | 1
2015-05-19 11:30 | 2015-05-19 | 2 | 11 | 172 | 59.5667 | 1
2015-05-19 11:45 | 2015-05-19 | 2 | 11 | 183 | 59.8167 | 1
2015-05-19 12:00 | 2015-05-19 | 2 | 12 | 188 | 60.1333 | 1
2015-05-19 12:15 | 2015-05-19 | 2 | 12 | 213 | 60.6333 | 1
2015-05-19 12:30 | 2015-05-19 | 2 | 12 | 192 | 61.1333 | 1
2015-05-19 12:45 | 2015-05-19 | 2 | 12 | 193 | 61.6333 | 1
2015-05-19 13:00 | 2015-05-19 | 2 | 13 | 187 | 62 | 1
2015-05-19 13:15 | 2015-05-19 | 2 | 13 | 197 | 62 | 1
2015-05-19 13:30 | 2015-05-19 | 2 | 13 | 220 | 62 | 1
2015-05-19 13:45 | 2015-05-19 | 2 | 13 | 198 | 62 | 1
2015-05-19 14:00 | 2015-05-19 | 2 | 14 | 206 | 62 | 1
2015-05-19 14:15 | 2015-05-19 | 2 | 14 | 206 | 62 | 1
2015-05-19 14:30 | 2015-05-19 | 2 | 14 | 217 | 62 | 1
2015-05-19 14:45 | 2015-05-19 | 2 | 14 | 208 | 62 | 1
2015-05-19 15:00 | 2015-05-19 | 2 | 15 | 207 | 61.9333 | 1
2015-05-19 15:15 | 2015-05-19 | 2 | 15 | 215 | 61.6833 | 1
2015-05-19 15:30 | 2015-05-19 | 2 | 15 | 213 | 61.4333 | 1
2015-05-19 15:45 | 2015-05-19 | 2 | 15 | 219 | 61.1833 | 1
2015-05-19 16:00 | 2015-05-19 | 2 | 16 | 219 | 60.9333 | 1
2015-05-19 16:15 | 2015-05-19 | 2 | 16 | 212 | 60.6833 | 1
2015-05-19 16:30 | 2015-05-19 | 2 | 16 | 212 | 60.4333 | 1
2015-05-19 16:45 | 2015-05-19 | 2 | 16 | 215 | 60.1833 | 1
2015-05-19 17:00 | 2015-05-19 | 2 | 17 | 220 | 59.9245 | 1
2015-05-19 17:15 | 2015-05-19 | 2 | 17 | 219 | 59.6415 | 1
2015-05-19 17:30 | 2015-05-19 | 2 | 17 | 212 | 59.3585 | 1
2015-05-19 17:45 | 2015-05-19 | 2 | 17 | 204 | 59.0755 | 1
2015-05-19 18:00 | 2015-05-19 | 2 | 18 | 208 | 57.9333 | 1
2015-05-19 18:15 | 2015-05-19 | 2 | 18 | 202 | 57.6833 | 1
2015-05-19 18:30 | 2015-05-19 | 2 | 18 | 199 | 57.4333 | 1
2015-05-19 18:45 | 2015-05-19 | 2 | 18 | 190 | 57.1833 | 1
2015-05-19 19:00 | 2015-05-19 | 2 | 19 | 190 | 56.9333 | 1
2015-05-19 19:15 | 2015-05-19 | 2 | 19 | 192 | 56.6833 | 1
2015-05-19 19:30 | 2015-05-19 | 2 | 19 | 194 | 56.4333 | 1
2015-05-19 19:45 | 2015-05-19 | 2 | 19 | 183 | 56.1833 | 1
2015-05-19 20:00 | 2015-05-19 | 2 | 20 | 174 | 56.0667 | 1
2015-05-19 20:15 | 2015-05-19 | 2 | 20 | 162 | 56.3167 | 1
2015-05-19 20:30 | 2015-05-19 | 2 | 20 | 158 | 56.5667 | 1
2015-05-19 20:45 | 2015-05-19 | 2 | 20 | 159 | 56.8167 | 1
2015-05-19 21:00 | 2015-05-19 | 2 | 21 | 169 | 56.9333 | 1
2015-05-19 21:15 | 2015-05-19 | 2 | 21 | 152 | 56.6833 | 1
2015-05-19 21:30 | 2015-05-19 | 2 | 21 | 148 | 56.4333 | 1
2015-05-19 21:45 | 2015-05-19 | 2 | 21 | 148 | 56.1833 | 1
2015-05-19 22:00 | 2015-05-19 | 2 | 22 | 154 | 56 | 1
2015-05-19 22:15 | 2015-05-19 | 2 | 22 | 163 | 56 | 1
2015-05-19 22:30 | 2015-05-19 | 2 | 22 | 149 | 56 | 1
2015-05-19 22:45 | 2015-05-19 | 2 | 22 | 150 | 56 | 1
2015-05-19 23:00 | 2015-05-19 | 2 | 23 | 160 | 56 | 1
2015-05-19 23:15 | 2015-05-19 | 2 | 23 | 153 | 56 | 1
2015-05-19 23:30 | 2015-05-19 | 2 | 23 | 148 | 56 | 1
2015-05-19 23:45 | 2015-05-19 | 2 | 23 | 148 | 56 | 1
2015-05-20 | 2015-05-20 | 3 | 0 | 153 | 55.9111 | 1
2015-05-20 00:15 | 2015-05-20 | 3 | 0 | 150 | 55.5778 | 1
2015-05-20 00:30 | 2015-05-20 | 3 | 0 | 143 | 55.2444 | 1
2015-05-20 00:45 | 2015-05-20 | 3 | 0 | 142 | 55.2667 | 1
2015-05-20 01:00 | 2015-05-20 | 3 | 1 | 140 | 56 | 1
2015-05-20 01:15 | 2015-05-20 | 3 | 1 | 143 | 56 | 1
2015-05-20 01:30 | 2015-05-20 | 3 | 1 | 146 | 56 | 1
2015-05-20 01:45 | 2015-05-20 | 3 | 1 | 142 | 56 | 1
2015-05-20 02:00 | 2015-05-20 | 3 | 2 | 141 | 56 | 1
2015-05-20 02:15 | 2015-05-20 | 3 | 2 | 144 | 56 | 1
2015-05-20 02:30 | 2015-05-20 | 3 | 2 | 149 | 56 | 1
2015-05-20 02:45 | 2015-05-20 | 3 | 2 | 143 | 56 | 1
2015-05-20 03:00 | 2015-05-20 | 3 | 3 | 139 | 56 | 1
2015-05-20 03:15 | 2015-05-20 | 3 | 3 | 137 | 56 | 1
2015-05-20 03:30 | 2015-05-20 | 3 | 3 | 136 | 56 | 1
2015-05-20 03:45 | 2015-05-20 | 3 | 3 | 138 | 56 | 1
2015-05-20 04:00 | 2015-05-20 | 3 | 4 | 147 | 55.875 | 1
2015-05-20 04:15 | 2015-05-20 | 3 | 4 | 144 | 55.4062 | 1
2015-05-20 04:30 | 2015-05-20 | 3 | 4 | 141 | 55.0714 | 1
2015-05-20 04:45 | 2015-05-20 | 3 | 4 | 137 | 55.6071 | 1
2015-05-20 05:00 | 2015-05-20 | 3 | 5 | 139 | 56.0667 | 1
2015-05-20 05:15 | 2015-05-20 | 3 | 5 | 139 | 56.3167 | 1
2015-05-20 05:30 | 2015-05-20 | 3 | 5 | 143 | 56.5667 | 1
2015-05-20 05:45 | 2015-05-20 | 3 | 5 | 148 | 56.8167 | 1
2015-05-20 06:00 | 2015-05-20 | 3 | 6 | 136 | 57 | 1
2015-05-20 06:15 | 2015-05-20 | 3 | 6 | 137 | 57 | 1
2015-05-20 06:30 | 2015-05-20 | 3 | 6 | 138 | 57 | 1
2015-05-20 06:45 | 2015-05-20 | 3 | 6 | 144 | 57 | 1
2015-05-20 07:00 | 2015-05-20 | 3 | 7 | 138 | 56.7714 | 1
2015-05-20 07:15 | 2015-05-20 | 3 | 7 | 143 | 55.9143 | 1
2015-05-20 07:30 | 2015-05-20 | 3 | 7 | 138 | 55.0571 | 1
2015-05-20 07:45 | 2015-05-20 | 3 | 7 | 139 | 55.56 | 1
2015-05-20 08:00 | 2015-05-20 | 3 | 8 | 151 | 56 | 1
2015-05-20 08:15 | 2015-05-20 | 3 | 8 | 169 | 56 | 1
2015-05-20 08:30 | 2015-05-20 | 3 | 8 | 162 | 56 | 1
2015-05-20 08:45 | 2015-05-20 | 3 | 8 | 163 | 56 | 1
2015-05-20 09:00 | 2015-05-20 | 3 | 9 | 178 | 56.1333 | 1
2015-05-20 09:15 | 2015-05-20 | 3 | 9 | 175 | 56.6333 | 1
2015-05-20 09:30 | 2015-05-20 | 3 | 9 | 182 | 57.1333 | 1
2015-05-20 09:45 | 2015-05-20 | 3 | 9 | 180 | 57.6333 | 1
2015-05-20 10:00 | 2015-05-20 | 3 | 10 | 182 | 58 | 1
2015-05-20 10:15 | 2015-05-20 | 3 | 10 | 188 | 58 | 1
2015-05-20 10:30 | 2015-05-20 | 3 | 10 | 200 | 58 | 1
2015-05-20 10:45 | 2015-05-20 | 3 | 10 | 201 | 58 | 1
2015-05-20 11:00 | 2015-05-20 | 3 | 11 | 199 | 58.1333 | 1
2015-05-20 11:15 | 2015-05-20 | 3 | 11 | 200 | 58.6333 | 1
2015-05-20 11:30 | 2015-05-20 | 3 | 11 | 198 | 59.1333 | 1
2015-05-20 11:45 | 2015-05-20 | 3 | 11 | 208 | 59.6333 | 1
2015-05-20 12:00 | 2015-05-20 | 3 | 12 | 211 | 60.0667 | 1
2015-05-20 12:15 | 2015-05-20 | 3 | 12 | 219 | 60.3167 | 1
2015-05-20 12:30 | 2015-05-20 | 3 | 12 | 212 | 60.5667 | 1
2015-05-20 12:45 | 2015-05-20 | 3 | 12 | 219 | 60.8167 | 1
2015-05-20 13:00 | 2015-05-20 | 3 | 13 | 214 | 60.9333 | 1
2015-05-20 13:15 | 2015-05-20 | 3 | 13 | 227 | 60.6833 | 1
2015-05-20 13:30 | 2015-05-20 | 3 | 13 | 229 | 60.4333 | 1
2015-05-20 13:45 | 2015-05-20 | 3 | 13 | 214 | 60.1833 | 1
2015-05-20 14:00 | 2015-05-20 | 3 | 14 | 221 | 60 | 1
2015-05-20 14:15 | 2015-05-20 | 3 | 14 | 211 | 60 | 1
2015-05-20 14:30 | 2015-05-20 | 3 | 14 | 235 | 60 | 1
2015-05-20 14:45 | 2015-05-20 | 3 | 14 | 224 | 60 | 1
2015-05-20 15:00 | 2015-05-20 | 3 | 15 | 220 | 60 | 1
2015-05-20 15:15 | 2015-05-20 | 3 | 15 | 223 | 60 | 1
2015-05-20 15:30 | 2015-05-20 | 3 | 15 | 223 | 60 | 1
2015-05-20 15:45 | 2015-05-20 | 3 | 15 | 219 | 60 | 1
2015-05-20 16:00 | 2015-05-20 | 3 | 16 | 226 | 59.9333 | 1
2015-05-20 16:15 | 2015-05-20 | 3 | 16 | 229 | 59.6833 | 1
2015-05-20 16:30 | 2015-05-20 | 3 | 16 | 212 | 59.4333 | 1
2015-05-20 16:45 | 2015-05-20 | 3 | 16 | 224 | 59.1833 | 1
2015-05-20 17:00 | 2015-05-20 | 3 | 17 | 211 | 59 | 1
2015-05-20 17:15 | 2015-05-20 | 3 | 17 | 216 | 59 | 1
2015-05-20 17:30 | 2015-05-20 | 3 | 17 | 228 | 59 | 1
2015-05-20 17:45 | 2015-05-20 | 3 | 17 | 203 | 59 | 1
2015-05-20 18:00 | 2015-05-20 | 3 | 18 | 215 | 58.8667 | 1
2015-05-20 18:15 | 2015-05-20 | 3 | 18 | 197 | 58.3667 | 1
2015-05-20 18:30 | 2015-05-20 | 3 | 18 | 222 | 57.8667 | 1
2015-05-20 18:45 | 2015-05-20 | 3 | 18 | 194 | 57.3667 | 1
2015-05-20 19:00 | 2015-05-20 | 3 | 19 | 187 | 57 | 1
2015-05-20 19:15 | 2015-05-20 | 3 | 19 | 197 | 57 | 1
2015-05-20 19:30 | 2015-05-20 | 3 | 19 | 192 | 57 | 1
2015-05-20 19:45 | 2015-05-20 | 3 | 19 | 182 | 57 | 1
2015-05-20 20:00 | 2015-05-20 | 3 | 20 | 171 | 57 | 1
2015-05-20 20:15 | 2015-05-20 | 3 | 20 | 168 | 57 | 1
2015-05-20 20:30 | 2015-05-20 | 3 | 20 | 167 | 57 | 1
2015-05-20 20:45 | 2015-05-20 | 3 | 20 | 174 | 57 | 1
2015-05-20 21:00 | 2015-05-20 | 3 | 21 | 171 | 57 | 1
2015-05-20 21:15 | 2015-05-20 | 3 | 21 | 156 | 57 | 1
2015-05-20 21:30 | 2015-05-20 | 3 | 21 | 151 | 57 | 1
2015-05-20 21:45 | 2015-05-20 | 3 | 21 | 161 | 57 | 1
2015-05-20 22:00 | 2015-05-20 | 3 | 22 | 165 | 57 | 1
2015-05-20 22:15 | 2015-05-20 | 3 | 22 | 157 | 57 | 1
2015-05-20 22:30 | 2015-05-20 | 3 | 22 | 159 | 57 | 1
2015-05-20 22:45 | 2015-05-20 | 3 | 22 | 161 | 57 | 1
2015-05-20 23:00 | 2015-05-20 | 3 | 23 | 172 | 56.9333 | 1
2015-05-20 23:15 | 2015-05-20 | 3 | 23 | 154 | 56.6833 | 1
2015-05-20 23:30 | 2015-05-20 | 3 | 23 | 150 | 56.4333 | 1
2015-05-20 23:45 | 2015-05-20 | 3 | 23 | 148 | 56.1833 | 1
2015-05-21 | 2015-05-21 | 4 | 0 | 151 | 55.9091 | 1
2015-05-21 00:15 | 2015-05-21 | 4 | 0 | 159 | 55.5682 | 1
2015-05-21 00:30 | 2015-05-21 | 4 | 0 | 148 | 55.2273 | 1
2015-05-21 00:45 | 2015-05-21 | 4 | 0 | 146 | 55.3125 | 1
2015-05-21 01:00 | 2015-05-21 | 4 | 1 | 145 | 56.1481 | 1
2015-05-21 01:15 | 2015-05-21 | 4 | 1 | 155 | 56.7037 | 1
2015-05-21 01:30 | 2015-05-21 | 4 | 1 | 152 | 56.7879 | 1
2015-05-21 01:45 | 2015-05-21 | 4 | 1 | 141 | 56.3333 | 1
2015-05-21 02:00 | 2015-05-21 | 4 | 2 | 141 | 55.8462 | 1
2015-05-21 02:15 | 2015-05-21 | 4 | 2 | 137 | 55.2692 | 1
2015-05-21 02:30 | 2015-05-21 | 4 | 2 | 146 | 55.2353 | 1
2015-05-21 02:45 | 2015-05-21 | 4 | 2 | 144 | 55.6765 | 1
2015-05-21 03:00 | 2015-05-21 | 4 | 3 | 140 | 56 | 1
2015-05-21 03:15 | 2015-05-21 | 4 | 3 | 144 | 56 | 1
2015-05-21 03:30 | 2015-05-21 | 4 | 3 | 150 | 56 | 1
2015-05-21 03:45 | 2015-05-21 | 4 | 3 | 148 | 56 | 1
2015-05-21 04:00 | 2015-05-21 | 4 | 4 | 142 | 56.0909 | 1
2015-05-21 04:15 | 2015-05-21 | 4 | 4 | 144 | 56.4318 | 1
2015-05-21 04:30 | 2015-05-21 | 4 | 4 | 138 | 56.7727 | 1
2015-05-21 04:45 | 2015-05-21 | 4 | 4 | 144 | 57 | 1
2015-05-21 05:00 | 2015-05-21 | 4 | 5 | 142 | 57 | 1
2015-05-21 05:15 | 2015-05-21 | 4 | 5 | 154 | 56.8913 | 1
2015-05-21 05:30 | 2015-05-21 | 4 | 5 | 138 | 56.5652 | 1
2015-05-21 05:45 | 2015-05-21 | 4 | 5 | 140 | 56.2391 | 1
2015-05-21 06:00 | 2015-05-21 | 4 | 6 | 141 | 56 | 1
2015-05-21 06:15 | 2015-05-21 | 4 | 6 | 156 | 56 | 1
2015-05-21 06:30 | 2015-05-21 | 4 | 6 | 140 | 56 | 1
2015-05-21 06:45 | 2015-05-21 | 4 | 6 | 143 | 56 | 1
2015-05-21 07:00 | 2015-05-21 | 4 | 7 | 143 | 55.84 | 1
2015-05-21 07:15 | 2015-05-21 | 4 | 7 | 154 | 55.24 | 1
2015-05-21 07:30 | 2015-05-21 | 4 | 7 | 140 | 55.5143 | 1
2015-05-21 07:45 | 2015-05-21 | 4 | 7 | 149 | 56.3714 | 1
2015-05-21 08:00 | 2015-05-21 | 4 | 8 | 147 | 57.1379 | 1
2015-05-21 08:15 | 2015-05-21 | 4 | 8 | 149 | 57.6552 | 1
2015-05-21 08:30 | 2015-05-21 | 4 | 8 | 157 | 58.1724 | 1
2015-05-21 08:45 | 2015-05-21 | 4 | 8 | 176 | 58.6897 | 1
2015-05-21 09:00 | 2015-05-21 | 4 | 9 | 166 | 59.2759 | 1
2015-05-21 09:15 | 2015-05-21 | 4 | 9 | 174 | 60.3103 | 1
2015-05-21 09:30 | 2015-05-21 | 4 | 9 | 176 | 61.3448 | 1
2015-05-21 09:45 | 2015-05-21 | 4 | 9 | 198 | 62.3793 | 1
2015-05-21 10:00 | 2015-05-21 | 4 | 10 | 203 | 63.0667 | 1
2015-05-21 10:15 | 2015-05-21 | 4 | 10 | 210 | 63.3167 | 1
2015-05-21 10:30 | 2015-05-21 | 4 | 10 | 212 | 63.5667 | 1
2015-05-21 10:45 | 2015-05-21 | 4 | 10 | 202 | 63.8167 | 1
2015-05-21 11:00 | 2015-05-21 | 4 | 11 | 221 | 64 | 1
2015-05-21 11:15 | 2015-05-21 | 4 | 11 | 204 | 64 | 1
2015-05-21 11:30 | 2015-05-21 | 4 | 11 | 210 | 64 | 1
2015-05-21 11:45 | 2015-05-21 | 4 | 11 | 214 | 64.5769 | 1
2015-05-21 12:00 | 2015-05-21 | 4 | 12 | 207 | 64.9333 | 1
2015-05-21 12:15 | 2015-05-21 | 4 | 12 | 230 | 64.6833 | 1
2015-05-21 12:30 | 2015-05-21 | 4 | 12 | 210 | 64.4333 | 1
2015-05-21 12:45 | 2015-05-21 | 4 | 12 | 210 | 64.1833 | 1
2015-05-21 13:00 | 2015-05-21 | 4 | 13 | 219 | 64.1333 | 1
2015-05-21 13:15 | 2015-05-21 | 4 | 13 | 203 | 64.6333 | 1
2015-05-21 13:30 | 2015-05-21 | 4 | 13 | 223 | 65.1333 | 2
2015-05-21 13:45 | 2015-05-21 | 4 | 13 | 217 | 65.6333 | 2
2015-05-21 14:00 | 2015-05-21 | 4 | 14 | 212 | 65.8 | 2
2015-05-21 14:15 | 2015-05-21 | 4 | 14 | 219 | 65.05 | 2
2015-05-21 14:30 | 2015-05-21 | 4 | 14 | 210 | 64.3 | 1
2015-05-21 14:45 | 2015-05-21 | 4 | 14 | 216 | 63.55 | 1
2015-05-21 15:00 | 2015-05-21 | 4 | 15 | 206 | 62.9333 | 1
2015-05-21 15:15 | 2015-05-21 | 4 | 15 | 204 | 62.6833 | 1
2015-05-21 15:30 | 2015-05-21 | 4 | 15 | 201 | 62.4333 | 1
2015-05-21 15:45 | 2015-05-21 | 4 | 15 | 221 | 62.1833 | 1
2015-05-21 16:00 | 2015-05-21 | 4 | 16 | 201 | 62.0851 | 1
2015-05-21 16:15 | 2015-05-21 | 4 | 16 | 199 | 62.4043 | 1
2015-05-21 16:30 | 2015-05-21 | 4 | 16 | 195 | 62.7234 | 1
2015-05-21 16:45 | 2015-05-21 | 4 | 16 | 197 | 62.8462 | 1
2015-05-21 17:00 | 2015-05-21 | 4 | 17 | 215 | 61.9333 | 1
2015-05-21 17:15 | 2015-05-21 | 4 | 17 | 198 | 61.6833 | 1
2015-05-21 17:30 | 2015-05-21 | 4 | 17 | 203 | 61.4333 | 1
2015-05-21 17:45 | 2015-05-21 | 4 | 17 | 203 | 61.1833 | 1
2015-05-21 18:00 | 2015-05-21 | 4 | 18 | 203 | 60.9333 | 1
2015-05-21 18:15 | 2015-05-21 | 4 | 18 | 214 | 60.6833 | 1
2015-05-21 18:30 | 2015-05-21 | 4 | 18 | 199 | 60.4333 | 1
2015-05-21 18:45 | 2015-05-21 | 4 | 18 | 197 | 60.1833 | 1
2015-05-21 19:00 | 2015-05-21 | 4 | 19 | 194 | 59.9333 | 1
2015-05-21 19:15 | 2015-05-21 | 4 | 19 | 194 | 59.6833 | 1
2015-05-21 19:30 | 2015-05-21 | 4 | 19 | 190 | 59.4333 | 1
2015-05-21 19:45 | 2015-05-21 | 4 | 19 | 187 | 59.1833 | 1
2015-05-21 20:00 | 2015-05-21 | 4 | 20 | 185 | 58.9333 | 1
2015-05-21 20:15 | 2015-05-21 | 4 | 20 | 185 | 58.6833 | 1
2015-05-21 20:30 | 2015-05-21 | 4 | 20 | 191 | 58.4333 | 1
2015-05-21 20:45 | 2015-05-21 | 4 | 20 | 179 | 58.1833 | 1
2015-05-21 21:00 | 2015-05-21 | 4 | 21 | 183 | 58 | 1
2015-05-21 21:15 | 2015-05-21 | 4 | 21 | 160 | 58 | 1
2015-05-21 21:30 | 2015-05-21 | 4 | 21 | 158 | 58 | 1
2015-05-21 21:45 | 2015-05-21 | 4 | 21 | 162 | 58 | 1
2015-05-21 22:00 | 2015-05-21 | 4 | 22 | 171 | 57.9333 | 1
2015-05-21 22:15 | 2015-05-21 | 4 | 22 | 154 | 57.6833 | 1
2015-05-21 22:30 | 2015-05-21 | 4 | 22 | 159 | 57.4333 | 1
2015-05-21 22:45 | 2015-05-21 | 4 | 22 | 155 | 57.1833 | 1
2015-05-21 23:00 | 2015-05-21 | 4 | 23 | 168 | 57 | 1
2015-05-21 23:15 | 2015-05-21 | 4 | 23 | 153 | 57 | 1
2015-05-21 23:30 | 2015-05-21 | 4 | 23 | 156 | 57 | 1
2015-05-21 23:45 | 2015-05-21 | 4 | 23 | 146 | 57.4762 | 1
2015-05-22 | 2015-05-22 | 5 | 0 | 156 | 58 | 1
2015-05-22 00:15 | 2015-05-22 | 5 | 0 | 164 | 58 | 1
2015-05-22 00:30 | 2015-05-22 | 5 | 0 | 148 | 58 | 1
2015-05-22 00:45 | 2015-05-22 | 5 | 0 | 147 | 58 | 1
2015-05-22 01:00 | 2015-05-22 | 5 | 1 | 150 | 57.9333 | 1
2015-05-22 01:15 | 2015-05-22 | 5 | 1 | 149 | 57.6833 | 1
2015-05-22 01:30 | 2015-05-22 | 5 | 1 | 162 | 57.4333 | 1
2015-05-22 01:45 | 2015-05-22 | 5 | 1 | 143 | 57.1833 | 1
2015-05-22 02:00 | 2015-05-22 | 5 | 2 | 148 | 57 | 1
2015-05-22 02:15 | 2015-05-22 | 5 | 2 | 142 | 57 | 1
2015-05-22 02:30 | 2015-05-22 | 5 | 2 | 155 | 57 | 1
2015-05-22 02:45 | 2015-05-22 | 5 | 2 | 148 | 57 | 1
2015-05-22 03:00 | 2015-05-22 | 5 | 3 | 148 | 56.9333 | 1
2015-05-22 03:15 | 2015-05-22 | 5 | 3 | 145 | 56.6833 | 1
2015-05-22 03:30 | 2015-05-22 | 5 | 3 | 149 | 56.4333 | 1
2015-05-22 03:45 | 2015-05-22 | 5 | 3 | 157 | 56.1833 | 1
2015-05-22 04:00 | 2015-05-22 | 5 | 4 | 145 | 56 | 1
2015-05-22 04:15 | 2015-05-22 | 5 | 4 | 142 | 56 | 1
2015-05-22 04:30 | 2015-05-22 | 5 | 4 | 142 | 56 | 1
2015-05-22 04:45 | 2015-05-22 | 5 | 4 | 144 | 56 | 1
2015-05-22 05:00 | 2015-05-22 | 5 | 5 | 155 | 56.069 | 1
2015-05-22 05:15 | 2015-05-22 | 5 | 5 | 147 | 56.3276 | 1
2015-05-22 05:30 | 2015-05-22 | 5 | 5 | 146 | 56.5862 | 1
2015-05-22 05:45 | 2015-05-22 | 5 | 5 | 143 | 56.8448 | 1
2015-05-22 06:00 | 2015-05-22 | 5 | 6 | 154 | 57.0667 | 1
2015-05-22 06:15 | 2015-05-22 | 5 | 6 | 140 | 57.3167 | 1
2015-05-22 06:30 | 2015-05-22 | 5 | 6 | 142 | 57.5667 | 1
2015-05-22 06:45 | 2015-05-22 | 5 | 6 | 137 | 57.8167 | 1
2015-05-22 07:00 | 2015-05-22 | 5 | 7 | 140 | 58.069 | 1
2015-05-22 07:15 | 2015-05-22 | 5 | 7 | 150 | 58.3276 | 1
2015-05-22 07:30 | 2015-05-22 | 5 | 7 | 147 | 58.5862 | 1
2015-05-22 07:45 | 2015-05-22 | 5 | 7 | 142 | 58.8448 | 1
2015-05-22 08:00 | 2015-05-22 | 5 | 8 | 146 | 59.0667 | 1
2015-05-22 08:15 | 2015-05-22 | 5 | 8 | 154 | 59.3167 | 1
2015-05-22 08:30 | 2015-05-22 | 5 | 8 | 160 | 59.5667 | 1
2015-05-22 08:45 | 2015-05-22 | 5 | 8 | 151 | 59.8167 | 1
2015-05-22 09:00 | 2015-05-22 | 5 | 9 | 153 | 60.2069 | 1
2015-05-22 09:15 | 2015-05-22 | 5 | 9 | 165 | 60.9828 | 1
2015-05-22 09:30 | 2015-05-22 | 5 | 9 | 183 | 61.7586 | 1
2015-05-22 09:45 | 2015-05-22 | 5 | 9 | 189 | 62.5345 | 1
2015-05-22 10:00 | 2015-05-22 | 5 | 10 | 194 | 62.9333 | 1
2015-05-22 10:15 | 2015-05-22 | 5 | 10 | 190 | 62.6833 | 1
2015-05-22 10:30 | 2015-05-22 | 5 | 10 | 198 | 62.4333 | 1
2015-05-22 10:45 | 2015-05-22 | 5 | 10 | 202 | 62.1833 | 1
2015-05-22 11:00 | 2015-05-22 | 5 | 11 | 199 | 61.8519 | 1
2015-05-22 11:15 | 2015-05-22 | 5 | 11 | 200 | 61.2963 | 1
2015-05-22 11:30 | 2015-05-22 | 5 | 11 | 189 | 61.2121 | 1
2015-05-22 11:45 | 2015-05-22 | 5 | 11 | 192 | 61.6667 | 1
2015-05-22 12:00 | 2015-05-22 | 5 | 12 | 202 | 62 | 1
2015-05-22 12:15 | 2015-05-22 | 5 | 12 | 204 | 62 | 1
2015-05-22 12:30 | 2015-05-22 | 5 | 12 | 187 | 62 | 1
2015-05-22 12:45 | 2015-05-22 | 5 | 12 | 198 | 62 | 1
2015-05-22 13:00 | 2015-05-22 | 5 | 13 | 188 | 61.9333 | 1
2015-05-22 13:15 | 2015-05-22 | 5 | 13 | 197 | 61.6833 | 1
2015-05-22 13:30 | 2015-05-22 | 5 | 13 | 206 | 61.4333 | 1
2015-05-22 13:45 | 2015-05-22 | 5 | 13 | 189 | 61.1833 | 1
2015-05-22 14:00 | 2015-05-22 | 5 | 14 | 203 | 61 | 1
2015-05-22 14:15 | 2015-05-22 | 5 | 14 | 194 | 61 | 1
2015-05-22 14:30 | 2015-05-22 | 5 | 14 | 213 | 61 | 1
2015-05-22 14:45 | 2015-05-22 | 5 | 14 | 209 | 61 | 1
2015-05-22 15:00 | 2015-05-22 | 5 | 15 | 201 | 61 | 1
2015-05-22 15:15 | 2015-05-22 | 5 | 15 | 199 | 61 | 1
2015-05-22 15:30 | 2015-05-22 | 5 | 15 | 208 | 61 | 1
2015-05-22 15:45 | 2015-05-22 | 5 | 15 | 206 | 61 | 1
2015-05-22 16:00 | 2015-05-22 | 5 | 16 | 204 | 61 | 1
2015-05-22 16:15 | 2015-05-22 | 5 | 16 | 197 | 61 | 1
2015-05-22 16:30 | 2015-05-22 | 5 | 16 | 202 | 61 | 1
2015-05-22 16:45 | 2015-05-22 | 5 | 16 | 205 | 61 | 1
2015-05-22 17:00 | 2015-05-22 | 5 | 17 | 216 | 59.9333 | 1
2015-05-22 17:15 | 2015-05-22 | 5 | 17 | 205 | 59.6833 | 1
2015-05-22 17:30 | 2015-05-22 | 5 | 17 | 216 | 59.4333 | 1
2015-05-22 17:45 | 2015-05-22 | 5 | 17 | 202 | 59.1833 | 1
2015-05-22 18:00 | 2015-05-22 | 5 | 18 | 197 | 59 | 1
2015-05-22 18:15 | 2015-05-22 | 5 | 18 | 183 | 59 | 1
2015-05-22 18:30 | 2015-05-22 | 5 | 18 | 189 | 59 | 1
2015-05-22 18:45 | 2015-05-22 | 5 | 18 | 197 | 59 | 1
2015-05-22 19:00 | 2015-05-22 | 5 | 19 | 184 | 58.9333 | 1
2015-05-22 19:15 | 2015-05-22 | 5 | 19 | 180 | 58.6833 | 1
2015-05-22 19:30 | 2015-05-22 | 5 | 19 | 177 | 58.4333 | 1
2015-05-22 19:45 | 2015-05-22 | 5 | 19 | 177 | 58.1833 | 1
2015-05-22 20:00 | 2015-05-22 | 5 | 20 | 180 | 57.9333 | 1
2015-05-22 20:15 | 2015-05-22 | 5 | 20 | 185 | 57.6833 | 1
2015-05-22 20:30 | 2015-05-22 | 5 | 20 | 166 | 57.4333 | 1
2015-05-22 20:45 | 2015-05-22 | 5 | 20 | 165 | 57.1833 | 1
2015-05-22 21:00 | 2015-05-22 | 5 | 21 | 161 | 57.0667 | 1
2015-05-22 21:15 | 2015-05-22 | 5 | 21 | 152 | 57.3167 | 1
2015-05-22 21:30 | 2015-05-22 | 5 | 21 | 145 | 57.5667 | 1
2015-05-22 21:45 | 2015-05-22 | 5 | 21 | 142 | 57.8167 | 1
2015-05-22 22:00 | 2015-05-22 | 5 | 22 | 144 | 57.9184 | 1
2015-05-22 22:15 | 2015-05-22 | 5 | 22 | 140 | 57.6122 | 1
2015-05-22 22:30 | 2015-05-22 | 5 | 22 | 155 | 57.3061 | 1
2015-05-22 22:45 | 2015-05-22 | 5 | 22 | 140 | 57 | 1
2015-05-22 23:00 | 2015-05-22 | 5 | 23 | 141 | 57 | 1
2015-05-22 23:15 | 2015-05-22 | 5 | 23 | 139 | 57 | 1
2015-05-22 23:30 | 2015-05-22 | 5 | 23 | 144 | 57 | 1
2015-05-22 23:45 | 2015-05-22 | 5 | 23 | 152 | 57 | 1
2015-05-23 | 2015-05-23 | 6 | 0 | 143 | 57 | 1
2015-05-23 00:15 | 2015-05-23 | 6 | 0 | 147 | 57 | 1
2015-05-23 00:30 | 2015-05-23 | 6 | 0 | 140 | 56.8125 | 1
2015-05-23 00:45 | 2015-05-23 | 6 | 0 | 138 | 56.3438 | 1
2015-05-23 01:00 | 2015-05-23 | 6 | 1 | 140 | 55.75 | 1
2015-05-23 01:15 | 2015-05-23 | 6 | 1 | 149 | 55.0682 | 1
2015-05-23 01:30 | 2015-05-23 | 6 | 1 | 140 | 55.4091 | 1
2015-05-23 01:45 | 2015-05-23 | 6 | 1 | 139 | 55.75 | 1
2015-05-23 02:00 | 2015-05-23 | 6 | 2 | 137 | 55.7895 | 1
2015-05-23 02:15 | 2015-05-23 | 6 | 2 | 137 | 55 | 1
2015-05-23 02:30 | 2015-05-23 | 6 | 2 | 145 | 55 | 1
2015-05-23 02:45 | 2015-05-23 | 6 | 2 | 151 | 55 | 1
2015-05-23 03:00 | 2015-05-23 | 6 | 3 | 136 | 54.9333 | 1
2015-05-23 03:15 | 2015-05-23 | 6 | 3 | 141 | 54.6833 | 1
2015-05-23 03:30 | 2015-05-23 | 6 | 3 | 140 | 54.4333 | 1
2015-05-23 03:45 | 2015-05-23 | 6 | 3 | 146 | 54.1833 | 1
2015-05-23 04:00 | 2015-05-23 | 6 | 4 | 148 | 54.0833 | 1
2015-05-23 04:15 | 2015-05-23 | 6 | 4 | 140 | 54.3958 | 1
2015-05-23 04:30 | 2015-05-23 | 6 | 4 | 141 | 54.7083 | 1
2015-05-23 04:45 | 2015-05-23 | 6 | 4 | 140 | 54.9167 | 1
2015-05-23 05:00 | 2015-05-23 | 6 | 5 | 144 | 54.0889 | 1
2015-05-23 05:15 | 2015-05-23 | 6 | 5 | 149 | 54.4222 | 1
2015-05-23 05:30 | 2015-05-23 | 6 | 5 | 138 | 54.7556 | 1
2015-05-23 05:45 | 2015-05-23 | 6 | 5 | 138 | 55 | 1
2015-05-23 06:00 | 2015-05-23 | 6 | 6 | 137 | 54.9333 | 1
2015-05-23 06:15 | 2015-05-23 | 6 | 6 | 146 | 54.6833 | 1
2015-05-23 06:30 | 2015-05-23 | 6 | 6 | 146 | 54.4333 | 1
2015-05-23 06:45 | 2015-05-23 | 6 | 6 | 139 | 54.1833 | 1
2015-05-23 07:00 | 2015-05-23 | 6 | 7 | 141 | 54.0667 | 1
2015-05-23 07:15 | 2015-05-23 | 6 | 7 | 139 | 54.3167 | 1
2015-05-23 07:30 | 2015-05-23 | 6 | 7 | 145 | 54.5667 | 1
2015-05-23 07:45 | 2015-05-23 | 6 | 7 | 142 | 54.8167 | 1
2015-05-23 08:00 | 2015-05-23 | 6 | 8 | 134 | 55.0667 | 1
2015-05-23 08:15 | 2015-05-23 | 6 | 8 | 134 | 55.3167 | 1
2015-05-23 08:30 | 2015-05-23 | 6 | 8 | 137 | 55.5667 | 1
2015-05-23 08:45 | 2015-05-23 | 6 | 8 | 147 | 55.8167 | 1
2015-05-23 09:00 | 2015-05-23 | 6 | 9 | 139 | 56.0667 | 1
2015-05-23 09:15 | 2015-05-23 | 6 | 9 | 145 | 56.3167 | 1
2015-05-23 09:30 | 2015-05-23 | 6 | 9 | 151 | 56.5667 | 1
2015-05-23 09:45 | 2015-05-23 | 6 | 9 | 162 | 56.8167 | 1
2015-05-23 10:00 | 2015-05-23 | 6 | 10 | 148 | 57 | 1
2015-05-23 10:15 | 2015-05-23 | 6 | 10 | 148 | 57 | 1
2015-05-23 10:30 | 2015-05-23 | 6 | 10 | 145 | 57 | 1
2015-05-23 10:45 | 2015-05-23 | 6 | 10 | 153 | 57.5417 | 1
2015-05-23 11:00 | 2015-05-23 | 6 | 11 | 170 | 58.0667 | 1
2015-05-23 11:15 | 2015-05-23 | 6 | 11 | 161 | 58.3167 | 1
2015-05-23 11:30 | 2015-05-23 | 6 | 11 | 162 | 58.5667 | 1
2015-05-23 11:45 | 2015-05-23 | 6 | 11 | 157 | 58.8167 | 1
2015-05-23 12:00 | 2015-05-23 | 6 | 12 | 168 | 59 | 1
2015-05-23 12:15 | 2015-05-23 | 6 | 12 | 172 | 59 | 1
2015-05-23 12:30 | 2015-05-23 | 6 | 12 | 160 | 59 | 1
2015-05-23 12:45 | 2015-05-23 | 6 | 12 | 160 | 59 | 1
2015-05-23 13:00 | 2015-05-23 | 6 | 13 | 168 | 59.2 | 1
2015-05-23 13:15 | 2015-05-23 | 6 | 13 | 174 | 59.95 | 1
2015-05-23 13:30 | 2015-05-23 | 6 | 13 | 181 | 60.7 | 1
2015-05-23 13:45 | 2015-05-23 | 6 | 13 | 172 | 61.45 | 1
2015-05-23 14:00 | 2015-05-23 | 6 | 14 | 171 | 61.9333 | 1
2015-05-23 14:15 | 2015-05-23 | 6 | 14 | 172 | 61.6833 | 1
2015-05-23 14:30 | 2015-05-23 | 6 | 14 | 177 | 61.4333 | 1
2015-05-23 14:45 | 2015-05-23 | 6 | 14 | 184 | 61.1833 | 1
2015-05-23 15:00 | 2015-05-23 | 6 | 15 | 170 | 60.9333 | 1
2015-05-23 15:15 | 2015-05-23 | 6 | 15 | 177 | 60.6833 | 1
2015-05-23 15:30 | 2015-05-23 | 6 | 15 | 179 | 60.4333 | 1
2015-05-23 15:45 | 2015-05-23 | 6 | 15 | 191 | 60.1833 | 1
2015-05-23 16:00 | 2015-05-23 | 6 | 16 | 181 | 59.9333 | 1
2015-05-23 16:15 | 2015-05-23 | 6 | 16 | 180 | 59.6833 | 1
2015-05-23 16:30 | 2015-05-23 | 6 | 16 | 189 | 59.4333 | 1
2015-05-23 16:45 | 2015-05-23 | 6 | 16 | 175 | 59.1833 | 1
2015-05-23 17:00 | 2015-05-23 | 6 | 17 | 192 | 58.9333 | 1
2015-05-23 17:15 | 2015-05-23 | 6 | 17 | 187 | 58.6833 | 1
2015-05-23 17:30 | 2015-05-23 | 6 | 17 | 176 | 58.4333 | 1
2015-05-23 17:45 | 2015-05-23 | 6 | 17 | 190 | 58.1833 | 1
2015-05-23 18:00 | 2015-05-23 | 6 | 18 | 171 | 57.9245 | 1
2015-05-23 18:15 | 2015-05-23 | 6 | 18 | 178 | 57.6415 | 1
2015-05-23 18:30 | 2015-05-23 | 6 | 18 | 187 | 57.3585 | 1
2015-05-23 18:45 | 2015-05-23 | 6 | 18 | 177 | 57.0755 | 1
2015-05-23 19:00 | 2015-05-23 | 6 | 19 | 171 | 56 | 1
2015-05-23 19:15 | 2015-05-23 | 6 | 19 | 175 | 56 | 1
2015-05-23 19:30 | 2015-05-23 | 6 | 19 | 181 | 56 | 1
2015-05-23 19:45 | 2015-05-23 | 6 | 19 | 174 | 56 | 1
2015-05-23 20:00 | 2015-05-23 | 6 | 20 | 171 | 55.9333 | 1
2015-05-23 20:15 | 2015-05-23 | 6 | 20 | 166 | 55.6833 | 1
2015-05-23 20:30 | 2015-05-23 | 6 | 20 | 180 | 55.4333 | 1
2015-05-23 20:45 | 2015-05-23 | 6 | 20 | 163 | 55.1833 | 1
2015-05-23 21:00 | 2015-05-23 | 6 | 21 | 166 | 55 | 1
2015-05-23 21:15 | 2015-05-23 | 6 | 21 | 149 | 55 | 1
2015-05-23 21:30 | 2015-05-23 | 6 | 21 | 156 | 55 | 1
2015-05-23 21:45 | 2015-05-23 | 6 | 21 | 151 | 55 | 1
2015-05-23 22:00 | 2015-05-23 | 6 | 22 | 148 | 55 | 1
2015-05-23 22:15 | 2015-05-23 | 6 | 22 | 143 | 55 | 1
2015-05-23 22:30 | 2015-05-23 | 6 | 22 | 142 | 55 | 1
2015-05-23 22:45 | 2015-05-23 | 6 | 22 | 142 | 55 | 1
2015-05-23 23:00 | 2015-05-23 | 6 | 23 | 140 | 54.9333 | 1
2015-05-23 23:15 | 2015-05-23 | 6 | 23 | 136 | 54.6833 | 1
2015-05-23 23:30 | 2015-05-23 | 6 | 23 | 141 | 54.4333 | 1
2015-05-23 23:45 | 2015-05-23 | 6 | 23 | 135 | 54.1833 | 1
2015-05-24 | 2015-05-24 | 7 | 0 | 148 | 54 | 1
2015-05-24 00:15 | 2015-05-24 | 7 | 0 | 136 | 54 | 1
2015-05-24 00:30 | 2015-05-24 | 7 | 0 | 138 | 54 | 1
2015-05-24 00:45 | 2015-05-24 | 7 | 0 | 136 | 54 | 1
2015-05-24 01:00 | 2015-05-24 | 7 | 1 | 138 | 54 | 1
2015-05-24 01:15 | 2015-05-24 | 7 | 1 | 139 | 54 | 1
2015-05-24 01:30 | 2015-05-24 | 7 | 1 | 140 | 54 | 1
2015-05-24 01:45 | 2015-05-24 | 7 | 1 | 136 | 54 | 1
2015-05-24 02:00 | 2015-05-24 | 7 | 2 | 134 | 54 | 1
2015-05-24 02:15 | 2015-05-24 | 7 | 2 | 134 | 53.8367 | 1
2015-05-24 02:30 | 2015-05-24 | 7 | 2 | 139 | 53.5306 | 1
2015-05-24 02:45 | 2015-05-24 | 7 | 2 | 135 | 53.2245 | 1
2015-05-24 03:00 | 2015-05-24 | 7 | 3 | 150 | 52.9333 | 1
2015-05-24 03:15 | 2015-05-24 | 7 | 3 | 133 | 52.6833 | 1
2015-05-24 03:30 | 2015-05-24 | 7 | 3 | 134 | 52.4333 | 1
2015-05-24 03:45 | 2015-05-24 | 7 | 3 | 133 | 52.1833 | 1
2015-05-24 04:00 | 2015-05-24 | 7 | 4 | 136 | 52 | 1
2015-05-24 04:15 | 2015-05-24 | 7 | 4 | 139 | 52 | 1
2015-05-24 04:30 | 2015-05-24 | 7 | 4 | 146 | 52 | 1
2015-05-24 04:45 | 2015-05-24 | 7 | 4 | 137 | 52 | 1
2015-05-24 05:00 | 2015-05-24 | 7 | 5 | 138 | 52.1333 | 1
2015-05-24 05:15 | 2015-05-24 | 7 | 5 | 133 | 52.6333 | 1
2015-05-24 05:30 | 2015-05-24 | 7 | 5 | 139 | 53.1333 | 1
2015-05-24 05:45 | 2015-05-24 | 7 | 5 | 136 | 53.6333 | 1
2015-05-24 06:00 | 2015-05-24 | 7 | 6 | 142 | 54 | 1
2015-05-24 06:15 | 2015-05-24 | 7 | 6 | 135 | 54.2545 | 1
2015-05-24 06:30 | 2015-05-24 | 7 | 6 | 134 | 54.5273 | 1
2015-05-24 06:45 | 2015-05-24 | 7 | 6 | 138 | 54.8 | 1
2015-05-24 07:00 | 2015-05-24 | 7 | 7 | 134 | 55 | 1
2015-05-24 07:15 | 2015-05-24 | 7 | 7 | 145 | 55 | 1
2015-05-24 07:30 | 2015-05-24 | 7 | 7 | 148 | 55 | 1
2015-05-24 07:45 | 2015-05-24 | 7 | 7 | 148 | 55 | 1
2015-05-24 08:00 | 2015-05-24 | 7 | 8 | 150 | 55.0667 | 1
2015-05-24 08:15 | 2015-05-24 | 7 | 8 | 146 | 55.3167 | 1
2015-05-24 08:30 | 2015-05-24 | 7 | 8 | 154 | 55.5667 | 1
2015-05-24 08:45 | 2015-05-24 | 7 | 8 | 150 | 55.8167 | 1
2015-05-24 09:00 | 2015-05-24 | 7 | 9 | 159 | 56.0667 | 1
2015-05-24 09:15 | 2015-05-24 | 7 | 9 | 151 | 56.3167 | 1
2015-05-24 09:30 | 2015-05-24 | 7 | 9 | 157 | 56.5667 | 1
2015-05-24 09:45 | 2015-05-24 | 7 | 9 | 158 | 56.8167 | 1
2015-05-24 10:00 | 2015-05-24 | 7 | 10 | 173 | 57.0667 | 1
2015-05-24 10:15 | 2015-05-24 | 7 | 10 | 176 | 57.3167 | 1
2015-05-24 10:30 | 2015-05-24 | 7 | 10 | 166 | 57.5667 | 1
2015-05-24 10:45 | 2015-05-24 | 7 | 10 | 175 | 57.8167 | 1
2015-05-24 11:00 | 2015-05-24 | 7 | 11 | 178 | 58.2 | 1
2015-05-24 11:15 | 2015-05-24 | 7 | 11 | 182 | 58.95 | 1
2015-05-24 11:30 | 2015-05-24 | 7 | 11 | 186 | 59.7 | 1
2015-05-24 11:45 | 2015-05-24 | 7 | 11 | 177 | 60.45 | 1
2015-05-24 12:00 | 2015-05-24 | 7 | 12 | 181 | 60.9333 | 1
2015-05-24 12:15 | 2015-05-24 | 7 | 12 | 196 | 60.6833 | 1
2015-05-24 12:30 | 2015-05-24 | 7 | 12 | 178 | 60.4333 | 1
2015-05-24 12:45 | 2015-05-24 | 7 | 12 | 187 | 60.1833 | 1
2015-05-24 13:00 | 2015-05-24 | 7 | 13 | 181 | 60 | 1
2015-05-24 13:15 | 2015-05-24 | 7 | 13 | 177 | 60 | 1
2015-05-24 13:30 | 2015-05-24 | 7 | 13 | 194 | 60 | 1
2015-05-24 13:45 | 2015-05-24 | 7 | 13 | 186 | 60 | 1
2015-05-24 14:00 | 2015-05-24 | 7 | 14 | 186 | 59.8667 | 1
2015-05-24 14:15 | 2015-05-24 | 7 | 14 | 189 | 59.3667 | 1
2015-05-24 14:30 | 2015-05-24 | 7 | 14 | 186 | 58.8667 | 1
2015-05-24 14:45 | 2015-05-24 | 7 | 14 | 196 | 58.3667 | 1
2015-05-24 15:00 | 2015-05-24 | 7 | 15 | 192 | 58 | 1
2015-05-24 15:15 | 2015-05-24 | 7 | 15 | 192 | 58 | 1
2015-05-24 15:30 | 2015-05-24 | 7 | 15 | 189 | 58 | 1
2015-05-24 15:45 | 2015-05-24 | 7 | 15 | 199 | 58 | 1
2015-05-24 16:00 | 2015-05-24 | 7 | 16 | 196 | 57.9333 | 1
2015-05-24 16:15 | 2015-05-24 | 7 | 16 | 203 | 57.6833 | 1
2015-05-24 16:30 | 2015-05-24 | 7 | 16 | 194 | 57.4333 | 1
2015-05-24 16:45 | 2015-05-24 | 7 | 16 | 191 | 57.1833 | 1
2015-05-24 17:00 | 2015-05-24 | 7 | 17 | 197 | 56.9333 | 1
2015-05-24 17:15 | 2015-05-24 | 7 | 17 | 195 | 56.6833 | 1
2015-05-24 17:30 | 2015-05-24 | 7 | 17 | 202 | 56.4333 | 1
2015-05-24 17:45 | 2015-05-24 | 7 | 17 | 187 | 56.1833 | 1
2015-05-24 18:00 | 2015-05-24 | 7 | 18 | 201 | 56 | 1
2015-05-24 18:15 | 2015-05-24 | 7 | 18 | 183 | 56 | 1
2015-05-24 18:30 | 2015-05-24 | 7 | 18 | 191 | 56 | 1
2015-05-24 18:45 | 2015-05-24 | 7 | 18 | 179 | 56 | 1
2015-05-24 19:00 | 2015-05-24 | 7 | 19 | 188 | 55.8462 | 1
2015-05-24 19:15 | 2015-05-24 | 7 | 19 | 175 | 55.2692 | 1
2015-05-24 19:30 | 2015-05-24 | 7 | 19 | 162 | 55.2353 | 1
2015-05-24 19:45 | 2015-05-24 | 7 | 19 | 166 | 55.6765 | 1
2015-05-24 20:00 | 2015-05-24 | 7 | 20 | 156 | 56 | 1
2015-05-24 20:15 | 2015-05-24 | 7 | 20 | 172 | 56 | 1
2015-05-24 20:30 | 2015-05-24 | 7 | 20 | 160 | 56 | 1
2015-05-24 20:45 | 2015-05-24 | 7 | 20 | 158 | 56 | 1
2015-05-24 21:00 | 2015-05-24 | 7 | 21 | 152 | 56 | 1
2015-05-24 21:15 | 2015-05-24 | 7 | 21 | 144 | 56 | 1
2015-05-24 21:30 | 2015-05-24 | 7 | 21 | 150 | 56 | 1
2015-05-24 21:45 | 2015-05-24 | 7 | 21 | 149 | 56 | 1
2015-05-24 22:00 | 2015-05-24 | 7 | 22 | 144 | 56 | 1
2015-05-24 22:15 | 2015-05-24 | 7 | 22 | 144 | 56 | 1
2015-05-24 22:30 | 2015-05-24 | 7 | 22 | 141 | 56 | 1
2015-05-24 22:45 | 2015-05-24 | 7 | 22 | 155 | 56 | 1
2015-05-24 23:00 | 2015-05-24 | 7 | 23 | 148 | 56 | 1
2015-05-24 23:15 | 2015-05-24 | 7 | 23 | 140 | 56 | 1
2015-05-24 23:30 | 2015-05-24 | 7 | 23 | 145 | 56 | 1
2015-05-24 23:45 | 2015-05-24 | 7 | 23 | 154 | 56 | 1
2015-05-25 | 2015-05-25 | 0 | 0 | 142 | 55.9333 | 1
2015-05-25 00:15 | 2015-05-25 | 0 | 0 | 140 | 55.6833 | 1
2015-05-25 00:30 | 2015-05-25 | 0 | 0 | 136 | 55.4333 | 1
2015-05-25 00:45 | 2015-05-25 | 0 | 0 | 151 | 55.1833 | 1
2015-05-25 01:00 | 2015-05-25 | 0 | 1 | 142 | 55 | 1
2015-05-25 01:15 | 2015-05-25 | 0 | 1 | 136 | 55 | 1
2015-05-25 01:30 | 2015-05-25 | 0 | 1 | 138 | 55 | 1
2015-05-25 01:45 | 2015-05-25 | 0 | 1 | 136 | 55 | 1
2015-05-25 02:00 | 2015-05-25 | 0 | 2 | 152 | 54.9149 | 1
2015-05-25 02:15 | 2015-05-25 | 0 | 2 | 134 | 54.5957 | 1
2015-05-25 02:30 | 2015-05-25 | 0 | 2 | 136 | 54.2766 | 1
2015-05-25 02:45 | 2015-05-25 | 0 | 2 | 141 | 53.8462 | 1
2015-05-25 03:00 | 2015-05-25 | 0 | 3 | 135 | 53.1905 | 1
2015-05-25 03:15 | 2015-05-25 | 0 | 3 | 148 | 53.9048 | 1
2015-05-25 03:30 | 2015-05-25 | 0 | 3 | 139 | 53.6667 | 1
2015-05-25 03:45 | 2015-05-25 | 0 | 3 | 135 | 53.2821 | 1
2015-05-25 04:00 | 2015-05-25 | 0 | 4 | 135 | 53.0755 | 1
2015-05-25 04:15 | 2015-05-25 | 0 | 4 | 143 | 53.3585 | 1
2015-05-25 04:30 | 2015-05-25 | 0 | 4 | 146 | 53.6415 | 1
2015-05-25 04:45 | 2015-05-25 | 0 | 4 | 134 | 53.9245 | 1
2015-05-25 05:00 | 2015-05-25 | 0 | 5 | 147 | 53.069 | 1
2015-05-25 05:15 | 2015-05-25 | 0 | 5 | 134 | 53.3276 | 1
2015-05-25 05:30 | 2015-05-25 | 0 | 5 | 135 | 53.5862 | 1
2015-05-25 05:45 | 2015-05-25 | 0 | 5 | 130 | 53.8448 | 1
2015-05-25 06:00 | 2015-05-25 | 0 | 6 | 141 | 53.1905 | 1
2015-05-25 06:15 | 2015-05-25 | 0 | 6 | 134 | 53.9048 | 1
2015-05-25 06:30 | 2015-05-25 | 0 | 6 | 130 | 54 | 1
2015-05-25 06:45 | 2015-05-25 | 0 | 6 | 126 | 54 | 1
2015-05-25 07:00 | 2015-05-25 | 0 | 7 | 121 | 53.0667 | 1
2015-05-25 07:15 | 2015-05-25 | 0 | 7 | 125 | 53.3167 | 1
2015-05-25 07:30 | 2015-05-25 | 0 | 7 | 118 | 53.5667 | 1
2015-05-25 07:45 | 2015-05-25 | 0 | 7 | 123 | 53.8167 | 1
2015-05-25 08:00 | 2015-05-25 | 0 | 8 | 131 | 54.1333 | 1
2015-05-25 08:15 | 2015-05-25 | 0 | 8 | 120 | 54.6333 | 1
2015-05-25 08:30 | 2015-05-25 | 0 | 8 | 120 | 55.1333 | 1
2015-05-25 08:45 | 2015-05-25 | 0 | 8 | 117 | 55.6333 | 1
2015-05-25 09:00 | 2015-05-25 | 0 | 9 | 126 | 55.8 | 1
2015-05-25 09:15 | 2015-05-25 | 0 | 9 | 129 | 55.05 | 1
2015-05-25 09:30 | 2015-05-25 | 0 | 9 | 123 | 55.35 | 1
2015-05-25 09:45 | 2015-05-25 | 0 | 9 | 123 | 55.725 | 1
2015-05-25 10:00 | 2015-05-25 | 0 | 10 | 128 | 56.2 | 1
2015-05-25 10:15 | 2015-05-25 | 0 | 10 | 133 | 56.95 | 1
2015-05-25 10:30 | 2015-05-25 | 0 | 10 | 143 | 57.7 | 1
2015-05-25 10:45 | 2015-05-25 | 0 | 10 | 147 | 58.45 | 1
2015-05-25 11:00 | 2015-05-25 | 0 | 11 | 159 | 59.1333 | 1
2015-05-25 11:15 | 2015-05-25 | 0 | 11 | 149 | 59.6333 | 1
2015-05-25 11:30 | 2015-05-25 | 0 | 11 | 158 | 60.1333 | 1
2015-05-25 11:45 | 2015-05-25 | 0 | 11 | 164 | 60.6333 | 1
2015-05-25 12:00 | 2015-05-25 | 0 | 12 | 168 | 61.0667 | 1
2015-05-25 12:15 | 2015-05-25 | 0 | 12 | 166 | 61.3167 | 1
2015-05-25 12:30 | 2015-05-25 | 0 | 12 | 160 | 61.5667 | 1
2015-05-25 12:45 | 2015-05-25 | 0 | 12 | 156 | 61.8167 | 1
2015-05-25 13:00 | 2015-05-25 | 0 | 13 | 166 | 61.9333 | 1
2015-05-25 13:15 | 2015-05-25 | 0 | 13 | 167 | 61.6833 | 1
2015-05-25 13:30 | 2015-05-25 | 0 | 13 | 159 | 61.4333 | 1
2015-05-25 13:45 | 2015-05-25 | 0 | 13 | 157 | 61.1833 | 1
2015-05-25 14:00 | 2015-05-25 | 0 | 14 | 158 | 61.1702 | 1
2015-05-25 14:15 | 2015-05-25 | 0 | 14 | 174 | 61.8085 | 1
2015-05-25 14:30 | 2015-05-25 | 0 | 14 | 161 | 62.4468 | 1
2015-05-25 14:45 | 2015-05-25 | 0 | 14 | 160 | 62.8462 | 1
2015-05-25 15:00 | 2015-05-25 | 0 | 15 | 168 | 61.9333 | 1
2015-05-25 15:15 | 2015-05-25 | 0 | 15 | 165 | 61.6833 | 1
2015-05-25 15:30 | 2015-05-25 | 0 | 15 | 184 | 61.4333 | 1
2015-05-25 15:45 | 2015-05-25 | 0 | 15 | 173 | 61.1833 | 1
2015-05-25 16:00 | 2015-05-25 | 0 | 16 | 178 | 60.8667 | 1
2015-05-25 16:15 | 2015-05-25 | 0 | 16 | 168 | 60.3667 | 1
2015-05-25 16:30 | 2015-05-25 | 0 | 16 | 175 | 59.8667 | 1
2015-05-25 16:45 | 2015-05-25 | 0 | 16 | 182 | 59.3667 | 1
2015-05-25 17:00 | 2015-05-25 | 0 | 17 | 173 | 58.9333 | 1
2015-05-25 17:15 | 2015-05-25 | 0 | 17 | 167 | 58.6833 | 1
2015-05-25 17:30 | 2015-05-25 | 0 | 17 | 172 | 58.4333 | 1
2015-05-25 17:45 | 2015-05-25 | 0 | 17 | 168 | 58.1833 | 1
2015-05-25 18:00 | 2015-05-25 | 0 | 18 | 189 | 57.9333 | 1
2015-05-25 18:15 | 2015-05-25 | 0 | 18 | 162 | 57.6833 | 1
2015-05-25 18:30 | 2015-05-25 | 0 | 18 | 174 | 57.4333 | 1
2015-05-25 18:45 | 2015-05-25 | 0 | 18 | 161 | 57.1833 | 1
2015-05-25 19:00 | 2015-05-25 | 0 | 19 | 175 | 57 | 1
2015-05-25 19:15 | 2015-05-25 | 0 | 19 | 169 | 57 | 1
2015-05-25 19:30 | 2015-05-25 | 0 | 19 | 155 | 57 | 1
2015-05-25 19:45 | 2015-05-25 | 0 | 19 | 160 | 57 | 1
2015-05-25 20:00 | 2015-05-25 | 0 | 20 | 149 | 56.9333 | 1
2015-05-25 20:15 | 2015-05-25 | 0 | 20 | 142 | 56.6833 | 1
2015-05-25 20:30 | 2015-05-25 | 0 | 20 | 154 | 56.4333 | 1
2015-05-25 20:45 | 2015-05-25 | 0 | 20 | 135 | 56.1833 | 1
2015-05-25 21:00 | 2015-05-25 | 0 | 21 | 137 | 56 | 1
2015-05-25 21:15 | 2015-05-25 | 0 | 21 | 130 | 56 | 1
2015-05-25 21:30 | 2015-05-25 | 0 | 21 | 139 | 56 | 1
2015-05-25 21:45 | 2015-05-25 | 0 | 21 | 143 | 56 | 1
2015-05-25 22:00 | 2015-05-25 | 0 | 22 | 130 | 56 | 1
2015-05-25 22:15 | 2015-05-25 | 0 | 22 | 130 | 56 | 1
2015-05-25 22:30 | 2015-05-25 | 0 | 22 | 129 | 56 | 1
2015-05-25 22:45 | 2015-05-25 | 0 | 22 | 144 | 56 | 1
2015-05-25 23:00 | 2015-05-25 | 0 | 23 | 130 | 55.9333 | 1
2015-05-25 23:15 | 2015-05-25 | 0 | 23 | 127 | 55.6833 | 1
2015-05-25 23:30 | 2015-05-25 | 0 | 23 | 128 | 55.4333 | 1
2015-05-25 23:45 | 2015-05-25 | 0 | 23 | 137 | 55.1833 | 1
2015-05-26 | 2015-05-26 | 2 | 0 | 145 | 54.9333 | 1
2015-05-26 00:15 | 2015-05-26 | 2 | 0 | 131 | 54.6833 | 1
2015-05-26 00:30 | 2015-05-26 | 2 | 0 | 142 | 54.4333 | 1
2015-05-26 00:45 | 2015-05-26 | 2 | 0 | 127 | 54.1833 | 1
2015-05-26 01:00 | 2015-05-26 | 2 | 1 | 130 | 54.2105 | 1
2015-05-26 01:15 | 2015-05-26 | 2 | 1 | 129 | 55 | 1
2015-05-26 01:30 | 2015-05-26 | 2 | 1 | 147 | 55 | 1
2015-05-26 01:45 | 2015-05-26 | 2 | 1 | 129 | 55 | 1
2015-05-26 02:00 | 2015-05-26 | 2 | 2 | 131 | 55 | 1
2015-05-26 02:15 | 2015-05-26 | 2 | 2 | 126 | 55 | 1
2015-05-26 02:30 | 2015-05-26 | 2 | 2 | 130 | 55 | 1
2015-05-26 02:45 | 2015-05-26 | 2 | 2 | 129 | 55 | 1
2015-05-26 03:00 | 2015-05-26 | 2 | 3 | 129 | 55 | 1
2015-05-26 03:15 | 2015-05-26 | 2 | 3 | 140 | 55 | 1
2015-05-26 03:30 | 2015-05-26 | 2 | 3 | 126 | 55 | 1
2015-05-26 03:45 | 2015-05-26 | 2 | 3 | 125 | 55 | 1
2015-05-26 04:00 | 2015-05-26 | 2 | 4 | 125 | 55 | 1
2015-05-26 04:15 | 2015-05-26 | 2 | 4 | 126 | 55 | 1
2015-05-26 04:30 | 2015-05-26 | 2 | 4 | 126 | 55 | 1
2015-05-26 04:45 | 2015-05-26 | 2 | 4 | 137 | 55 | 1
2015-05-26 05:00 | 2015-05-26 | 2 | 5 | 127 | 55 | 1
2015-05-26 05:15 | 2015-05-26 | 2 | 5 | 124 | 55 | 1
2015-05-26 05:30 | 2015-05-26 | 2 | 5 | 125 | 55 | 1
2015-05-26 05:45 | 2015-05-26 | 2 | 5 | 125 | 55 | 1
2015-05-26 06:00 | 2015-05-26 | 2 | 6 | 138 | 55.0667 | 1
2015-05-26 06:15 | 2015-05-26 | 2 | 6 | 122 | 55.3167 | 1
2015-05-26 06:30 | 2015-05-26 | 2 | 6 | 126 | 55.5667 | 1
2015-05-26 06:45 | 2015-05-26 | 2 | 6 | 129 | 55.8167 | 1
2015-05-26 07:00 | 2015-05-26 | 2 | 7 | 140 | 56.0667 | 1
2015-05-26 07:15 | 2015-05-26 | 2 | 7 | 125 | 56.3167 | 1
2015-05-26 07:30 | 2015-05-26 | 2 | 7 | 131 | 56.5667 | 1
2015-05-26 07:45 | 2015-05-26 | 2 | 7 | 138 | 56.8167 | 1
2015-05-26 08:00 | 2015-05-26 | 2 | 8 | 156 | 57 | 1
2015-05-26 08:15 | 2015-05-26 | 2 | 8 | 145 | 57 | 1
2015-05-26 08:30 | 2015-05-26 | 2 | 8 | 145 | 57 | 1
2015-05-26 08:45 | 2015-05-26 | 2 | 8 | 144 | 57 | 1
2015-05-26 09:00 | 2015-05-26 | 2 | 9 | 162 | 57 | 1
2015-05-26 09:15 | 2015-05-26 | 2 | 9 | 173 | 57 | 1
2015-05-26 09:30 | 2015-05-26 | 2 | 9 | 174 | 57.3333 | 1
2015-05-26 09:45 | 2015-05-26 | 2 | 9 | 190 | 57.7179 | 1
2015-05-26 10:00 | 2015-05-26 | 2 | 10 | 196 | 58.2069 | 1
2015-05-26 10:15 | 2015-05-26 | 2 | 10 | 230 | 58.9828 | 1
2015-05-26 10:30 | 2015-05-26 | 2 | 10 | 221 | 59.7586 | 1
2015-05-26 10:45 | 2015-05-26 | 2 | 10 | 230 | 60.5345 | 1
2015-05-26 11:00 | 2015-05-26 | 2 | 11 | 215 | 60.1333 | 1
2015-05-26 11:15 | 2015-05-26 | 2 | 11 | 232 | 60.6333 | 1
2015-05-26 11:30 | 2015-05-26 | 2 | 11 | 238 | 61.1333 | 1
2015-05-26 11:45 | 2015-05-26 | 2 | 11 | 223 | 61.6333 | 1
2015-05-26 12:00 | 2015-05-26 | 2 | 12 | 243 | 62.1667 | 1
2015-05-26 12:15 | 2015-05-26 | 2 | 12 | 255 | 62.7917 | 1
2015-05-26 12:30 | 2015-05-26 | 2 | 12 | 232 | 63.4167 | 1
2015-05-26 12:45 | 2015-05-26 | 2 | 12 | 253 | 64 | 1
2015-05-26 13:00 | 2015-05-26 | 2 | 13 | 253 | 64 | 1
2015-05-26 13:15 | 2015-05-26 | 2 | 13 | 252 | 64 | 1
2015-05-26 13:30 | 2015-05-26 | 2 | 13 | 272 | 64 | 1
2015-05-26 13:45 | 2015-05-26 | 2 | 13 | 273 | 64 | 1
2015-05-26 14:00 | 2015-05-26 | 2 | 14 | 283 | 64 | 1
2015-05-26 14:15 | 2015-05-26 | 2 | 14 | 279 | 64 | 1
2015-05-26 14:30 | 2015-05-26 | 2 | 14 | 271 | 64 | 1
2015-05-26 14:45 | 2015-05-26 | 2 | 14 | 272 | 64 | 1
2015-05-26 15:00 | 2015-05-26 | 2 | 15 | 275 | 63.9333 | 1
2015-05-26 15:15 | 2015-05-26 | 2 | 15 | 284 | 63.6833 | 1
2015-05-26 15:30 | 2015-05-26 | 2 | 15 | 271 | 63.4333 | 1
2015-05-26 15:45 | 2015-05-26 | 2 | 15 | 284 | 63.1833 | 1
2015-05-26 16:00 | 2015-05-26 | 2 | 16 | 284 | 62.9333 | 1
2015-05-26 16:15 | 2015-05-26 | 2 | 16 | 285 | 62.6833 | 1
2015-05-26 16:30 | 2015-05-26 | 2 | 16 | 278 | 62.4333 | 1
2015-05-26 16:45 | 2015-05-26 | 2 | 16 | 284 | 62.1833 | 1
2015-05-26 17:00 | 2015-05-26 | 2 | 17 | 272 | 61.7647 | 1
2015-05-26 17:15 | 2015-05-26 | 2 | 17 | 270 | 60.907 | 1
2015-05-26 17:30 | 2015-05-26 | 2 | 17 | 283 | 60.2093 | 1
2015-05-26 17:45 | 2015-05-26 | 2 | 17 | 268 | 59.5116 | 1
2015-05-26 18:00 | 2015-05-26 | 2 | 18 | 275 | 58.9333 | 1
2015-05-26 18:15 | 2015-05-26 | 2 | 18 | 281 | 58.6833 | 1
2015-05-26 18:30 | 2015-05-26 | 2 | 18 | 256 | 58.4333 | 1
2015-05-26 18:45 | 2015-05-26 | 2 | 18 | 271 | 58.1833 | 1
2015-05-26 19:00 | 2015-05-26 | 2 | 19 | 240 | 58 | 1
2015-05-26 19:15 | 2015-05-26 | 2 | 19 | 233 | 58 | 1
2015-05-26 19:30 | 2015-05-26 | 2 | 19 | 230 | 58 | 1
2015-05-26 19:45 | 2015-05-26 | 2 | 19 | 240 | 58 | 1
2015-05-26 20:00 | 2015-05-26 | 2 | 20 | 220 | 57.9333 | 1
2015-05-26 20:15 | 2015-05-26 | 2 | 20 | 216 | 57.6833 | 1
2015-05-26 20:30 | 2015-05-26 | 2 | 20 | 203 | 57.4333 | 1
2015-05-26 20:45 | 2015-05-26 | 2 | 20 | 190 | 57.1833 | 1
2015-05-26 21:00 | 2015-05-26 | 2 | 21 | 194 | 57 | 1
2015-05-26 21:15 | 2015-05-26 | 2 | 21 | 185 | 57 | 1
2015-05-26 21:30 | 2015-05-26 | 2 | 21 | 162 | 57 | 1
2015-05-26 21:45 | 2015-05-26 | 2 | 21 | 170 | 57 | 1
2015-05-26 22:00 | 2015-05-26 | 2 | 22 | 164 | 56.9333 | 1
2015-05-26 22:15 | 2015-05-26 | 2 | 22 | 155 | 56.6833 | 1
2015-05-26 22:30 | 2015-05-26 | 2 | 22 | 164 | 56.4333 | 1
2015-05-26 22:45 | 2015-05-26 | 2 | 22 | 162 | 56.1833 | 1
2015-05-26 23:00 | 2015-05-26 | 2 | 23 | 177 | 56 | 1
2015-05-26 23:15 | 2015-05-26 | 2 | 23 | 163 | 56 | 1
2015-05-26 23:30 | 2015-05-26 | 2 | 23 | 161 | 56 | 1
2015-05-26 23:45 | 2015-05-26 | 2 | 23 | 159 | 56 | 1
2015-05-27 | 2015-05-27 | 3 | 0 | 166 | 56.0667 | 1
2015-05-27 00:15 | 2015-05-27 | 3 | 0 | 168 | 56.3167 | 1
2015-05-27 00:30 | 2015-05-27 | 3 | 0 | 158 | 56.5667 | 1
2015-05-27 00:45 | 2015-05-27 | 3 | 0 | 152 | 56.8167 | 1
2015-05-27 01:00 | 2015-05-27 | 3 | 1 | 160 | 56.9333 | 1
2015-05-27 01:15 | 2015-05-27 | 3 | 1 | 158 | 56.6833 | 1
2015-05-27 01:30 | 2015-05-27 | 3 | 1 | 149 | 56.4333 | 1
2015-05-27 01:45 | 2015-05-27 | 3 | 1 | 149 | 56.1833 | 1
2015-05-27 02:00 | 2015-05-27 | 3 | 2 | 149 | 56 | 1
2015-05-27 02:15 | 2015-05-27 | 3 | 2 | 164 | 56 | 1
2015-05-27 02:30 | 2015-05-27 | 3 | 2 | 146 | 56 | 1
2015-05-27 02:45 | 2015-05-27 | 3 | 2 | 150 | 56 | 1
2015-05-27 03:00 | 2015-05-27 | 3 | 3 | 145 | 55.9333 | 1
2015-05-27 03:15 | 2015-05-27 | 3 | 3 | 157 | 55.6833 | 1
2015-05-27 03:30 | 2015-05-27 | 3 | 3 | 155 | 55.4333 | 1
2015-05-27 03:45 | 2015-05-27 | 3 | 3 | 149 | 55.1833 | 1
2015-05-27 04:00 | 2015-05-27 | 3 | 4 | 148 | 54.9333 | 1
2015-05-27 04:15 | 2015-05-27 | 3 | 4 | 148 | 54.6833 | 1
2015-05-27 04:30 | 2015-05-27 | 3 | 4 | 158 | 54.4333 | 1
2015-05-27 04:45 | 2015-05-27 | 3 | 4 | 144 | 54.1833 | 1
2015-05-27 05:00 | 2015-05-27 | 3 | 5 | 142 | 54 | 1
2015-05-27 05:15 | 2015-05-27 | 3 | 5 | 143 | 54 | 1
2015-05-27 05:30 | 2015-05-27 | 3 | 5 | 148 | 54 | 1
2015-05-27 05:45 | 2015-05-27 | 3 | 5 | 156 | 54 | 1
2015-05-27 06:00 | 2015-05-27 | 3 | 6 | 142 | 54.0667 | 1
2015-05-27 06:15 | 2015-05-27 | 3 | 6 | 146 | 54.3167 | 1
2015-05-27 06:30 | 2015-05-27 | 3 | 6 | 147 | 54.5667 | 1
2015-05-27 06:45 | 2015-05-27 | 3 | 6 | 159 | 54.8167 | 1
2015-05-27 07:00 | 2015-05-27 | 3 | 7 | 146 | 55.2286 | 1
2015-05-27 07:15 | 2015-05-27 | 3 | 7 | 147 | 56.0857 | 1
2015-05-27 07:30 | 2015-05-27 | 3 | 7 | 146 | 56.9429 | 1
2015-05-27 07:45 | 2015-05-27 | 3 | 7 | 161 | 57.56 | 1
2015-05-27 08:00 | 2015-05-27 | 3 | 8 | 154 | 58.0667 | 1
2015-05-27 08:15 | 2015-05-27 | 3 | 8 | 157 | 58.3167 | 1
2015-05-27 08:30 | 2015-05-27 | 3 | 8 | 165 | 58.5667 | 1
2015-05-27 08:45 | 2015-05-27 | 3 | 8 | 159 | 58.8167 | 1
2015-05-27 09:00 | 2015-05-27 | 3 | 9 | 183 | 59.0667 | 1
2015-05-27 09:15 | 2015-05-27 | 3 | 9 | 191 | 59.3167 | 1
2015-05-27 09:30 | 2015-05-27 | 3 | 9 | 191 | 59.5667 | 1
2015-05-27 09:45 | 2015-05-27 | 3 | 9 | 207 | 59.8167 | 1
2015-05-27 10:00 | 2015-05-27 | 3 | 10 | 225 | 60.5714 | 1
2015-05-27 10:15 | 2015-05-27 | 3 | 10 | 244 | 61.4528 | 1
2015-05-27 10:30 | 2015-05-27 | 3 | 10 | 237 | 62.0189 | 1
2015-05-27 10:45 | 2015-05-27 | 3 | 10 | 231 | 62.5849 | 1
2015-05-27 11:00 | 2015-05-27 | 3 | 11 | 248 | 63 | 1
2015-05-27 11:15 | 2015-05-27 | 3 | 11 | 259 | 63 | 1
2015-05-27 11:30 | 2015-05-27 | 3 | 11 | 259 | 63 | 1
2015-05-27 11:45 | 2015-05-27 | 3 | 11 | 265 | 63 | 1
2015-05-27 12:00 | 2015-05-27 | 3 | 12 | 261 | 63.0667 | 1
2015-05-27 12:15 | 2015-05-27 | 3 | 12 | 270 | 63.3167 | 1
2015-05-27 12:30 | 2015-05-27 | 3 | 12 | 281 | 63.5667 | 1
2015-05-27 12:45 | 2015-05-27 | 3 | 12 | 278 | 63.8167 | 1
2015-05-27 13:00 | 2015-05-27 | 3 | 13 | 278 | 63.8667 | 1
2015-05-27 13:15 | 2015-05-27 | 3 | 13 | 266 | 63.3667 | 1
2015-05-27 13:30 | 2015-05-27 | 3 | 13 | 275 | 62.8667 | 1
2015-05-27 13:45 | 2015-05-27 | 3 | 13 | 282 | 62.3667 | 1
2015-05-27 14:00 | 2015-05-27 | 3 | 14 | 279 | 61.9091 | 1
2015-05-27 14:15 | 2015-05-27 | 3 | 14 | 288 | 61.5682 | 1
2015-05-27 14:30 | 2015-05-27 | 3 | 14 | 273 | 61.2273 | 1
2015-05-27 14:45 | 2015-05-27 | 3 | 14 | 293 | 61 | 1
2015-05-27 15:00 | 2015-05-27 | 3 | 15 | 278 | 61 | 1
2015-05-27 15:15 | 2015-05-27 | 3 | 15 | 280 | 61 | 1
2015-05-27 15:30 | 2015-05-27 | 3 | 15 | 295 | 60.4444 | 1
2015-05-27 15:45 | 2015-05-27 | 3 | 15 | 279 | 59.6111 | 1
2015-05-27 16:00 | 2015-05-27 | 3 | 16 | 281 | 58.9333 | 1
2015-05-27 16:15 | 2015-05-27 | 3 | 16 | 278 | 58.6833 | 1
2015-05-27 16:30 | 2015-05-27 | 3 | 16 | 293 | 58.4333 | 1
2015-05-27 16:45 | 2015-05-27 | 3 | 16 | 279 | 58.1833 | 1
2015-05-27 17:00 | 2015-05-27 | 3 | 17 | 276 | 58 | 1
2015-05-27 17:15 | 2015-05-27 | 3 | 17 | 271 | 58 | 1
2015-05-27 17:30 | 2015-05-27 | 3 | 17 | 270 | 58 | 1
2015-05-27 17:45 | 2015-05-27 | 3 | 17 | 269 | 58 | 1
2015-05-27 18:00 | 2015-05-27 | 3 | 18 | 269 | 57.9333 | 1
2015-05-27 18:15 | 2015-05-27 | 3 | 18 | 256 | 57.6833 | 1
2015-05-27 18:30 | 2015-05-27 | 3 | 18 | 243 | 57.4333 | 1
2015-05-27 18:45 | 2015-05-27 | 3 | 18 | 239 | 57.1833 | 1
2015-05-27 19:00 | 2015-05-27 | 3 | 19 | 241 | 56.8621 | 1
2015-05-27 19:15 | 2015-05-27 | 3 | 19 | 237 | 56.3448 | 1
2015-05-27 19:30 | 2015-05-27 | 3 | 19 | 232 | 55.8276 | 1
2015-05-27 19:45 | 2015-05-27 | 3 | 19 | 211 | 55.3103 | 1
2015-05-27 20:00 | 2015-05-27 | 3 | 20 | 221 | 55.9333 | 1
2015-05-27 20:15 | 2015-05-27 | 3 | 20 | 191 | 55.6833 | 1
2015-05-27 20:30 | 2015-05-27 | 3 | 20 | 187 | 55.4333 | 1
2015-05-27 20:45 | 2015-05-27 | 3 | 20 | 193 | 55.1833 | 1
2015-05-27 21:00 | 2015-05-27 | 3 | 21 | 180 | 55 | 1
2015-05-27 21:15 | 2015-05-27 | 3 | 21 | 186 | 55 | 1
2015-05-27 21:30 | 2015-05-27 | 3 | 21 | 183 | 55 | 1
2015-05-27 21:45 | 2015-05-27 | 3 | 21 | 172 | 55 | 1
2015-05-27 22:00 | 2015-05-27 | 3 | 22 | 176 | 54.9333 | 1
2015-05-27 22:15 | 2015-05-27 | 3 | 22 | 168 | 54.6833 | 1
2015-05-27 22:30 | 2015-05-27 | 3 | 22 | 175 | 54.4333 | 1
2015-05-27 22:45 | 2015-05-27 | 3 | 22 | 179 | 54.1833 | 1
2015-05-27 23:00 | 2015-05-27 | 3 | 23 | 186 | 54 | 1
2015-05-27 23:15 | 2015-05-27 | 3 | 23 | 174 | 54 | 1
2015-05-27 23:30 | 2015-05-27 | 3 | 23 | 167 | 54 | 1
2015-05-27 23:45 | 2015-05-27 | 3 | 23 | 174 | 54 | 1
2015-05-28 | 2015-05-28 | 4 | 0 | 163 | 54 | 1
2015-05-28 00:15 | 2015-05-28 | 4 | 0 | 158 | 54 | 1
2015-05-28 00:30 | 2015-05-28 | 4 | 0 | 158 | 54 | 1
2015-05-28 00:45 | 2015-05-28 | 4 | 0 | 156 | 54 | 1
2015-05-28 01:00 | 2015-05-28 | 4 | 1 | 166 | 54 | 1
2015-05-28 01:15 | 2015-05-28 | 4 | 1 | 155 | 54 | 1
2015-05-28 01:30 | 2015-05-28 | 4 | 1 | 156 | 54 | 1
2015-05-28 01:45 | 2015-05-28 | 4 | 1 | 157 | 54 | 1
2015-05-28 02:00 | 2015-05-28 | 4 | 2 | 158 | 54 | 1
2015-05-28 02:15 | 2015-05-28 | 4 | 2 | 152 | 54 | 1
2015-05-28 02:30 | 2015-05-28 | 4 | 2 | 160 | 54 | 1
2015-05-28 02:45 | 2015-05-28 | 4 | 2 | 151 | 54 | 1
2015-05-28 03:00 | 2015-05-28 | 4 | 3 | 147 | 53.9333 | 1
2015-05-28 03:15 | 2015-05-28 | 4 | 3 | 148 | 53.6833 | 1
2015-05-28 03:30 | 2015-05-28 | 4 | 3 | 152 | 53.4333 | 1
2015-05-28 03:45 | 2015-05-28 | 4 | 3 | 164 | 53.1833 | 1
2015-05-28 04:00 | 2015-05-28 | 4 | 4 | 146 | 53 | 1
2015-05-28 04:15 | 2015-05-28 | 4 | 4 | 152 | 53 | 1
2015-05-28 04:30 | 2015-05-28 | 4 | 4 | 149 | 53 | 1
2015-05-28 04:45 | 2015-05-28 | 4 | 4 | 148 | 53 | 1
2015-05-28 05:00 | 2015-05-28 | 4 | 5 | 157 | 53 | 1
2015-05-28 05:15 | 2015-05-28 | 4 | 5 | 157 | 53 | 1
2015-05-28 05:30 | 2015-05-28 | 4 | 5 | 145 | 53 | 1
2015-05-28 05:45 | 2015-05-28 | 4 | 5 | 145 | 53 | 1
2015-05-28 06:00 | 2015-05-28 | 4 | 6 | 148 | 53 | 1
2015-05-28 06:15 | 2015-05-28 | 4 | 6 | 162 | 53 | 1
2015-05-28 06:30 | 2015-05-28 | 4 | 6 | 146 | 53 | 1
2015-05-28 06:45 | 2015-05-28 | 4 | 6 | 159 | 53 | 1
2015-05-28 07:00 | 2015-05-28 | 4 | 7 | 149 | 53.0667 | 1
2015-05-28 07:15 | 2015-05-28 | 4 | 7 | 153 | 53.3167 | 1
2015-05-28 07:30 | 2015-05-28 | 4 | 7 | 143 | 53.5667 | 1
2015-05-28 07:45 | 2015-05-28 | 4 | 7 | 161 | 53.8167 | 1
2015-05-28 08:00 | 2015-05-28 | 4 | 8 | 168 | 54.1333 | 1
2015-05-28 08:15 | 2015-05-28 | 4 | 8 | 166 | 54.6333 | 1
2015-05-28 08:30 | 2015-05-28 | 4 | 8 | 163 | 55.1333 | 1
2015-05-28 08:45 | 2015-05-28 | 4 | 8 | 177 | 55.6333 | 1
2015-05-28 09:00 | 2015-05-28 | 4 | 9 | 195 | 55.9216 | 1
2015-05-28 09:15 | 2015-05-28 | 4 | 9 | 184 | 55.6275 | 1
2015-05-28 09:30 | 2015-05-28 | 4 | 9 | 188 | 55.3333 | 1
2015-05-28 09:45 | 2015-05-28 | 4 | 9 | 213 | 55.0392 | 1
2015-05-28 10:00 | 2015-05-28 | 4 | 10 | 225 | 56.1333 | 1
2015-05-28 10:15 | 2015-05-28 | 4 | 10 | 238 | 56.6333 | 1
2015-05-28 10:30 | 2015-05-28 | 4 | 10 | 219 | 57.1333 | 1
2015-05-28 10:45 | 2015-05-28 | 4 | 10 | 234 | 57.6333 | 1
2015-05-28 11:00 | 2015-05-28 | 4 | 11 | 235 | 58.1333 | 1
2015-05-28 11:15 | 2015-05-28 | 4 | 11 | 242 | 58.6333 | 1
2015-05-28 11:30 | 2015-05-28 | 4 | 11 | 239 | 59.1333 | 1
2015-05-28 11:45 | 2015-05-28 | 4 | 11 | 235 | 59.6333 | 1
2015-05-28 12:00 | 2015-05-28 | 4 | 12 | 249 | 60.069 | 1
2015-05-28 12:15 | 2015-05-28 | 4 | 12 | 250 | 60.3276 | 1
2015-05-28 12:30 | 2015-05-28 | 4 | 12 | 262 | 60.5862 | 1
2015-05-28 12:45 | 2015-05-28 | 4 | 12 | 265 | 60.8448 | 1
2015-05-28 13:00 | 2015-05-28 | 4 | 13 | 252 | 61.9333 | 1
2015-05-28 13:15 | 2015-05-28 | 4 | 13 | 259 | 61.6833 | 1
2015-05-28 13:30 | 2015-05-28 | 4 | 13 | 261 | 61.4333 | 1
2015-05-28 13:45 | 2015-05-28 | 4 | 13 | 261 | 61.1833 | 1
2015-05-28 14:00 | 2015-05-28 | 4 | 14 | 270 | 60.9333 | 1
2015-05-28 14:15 | 2015-05-28 | 4 | 14 | 271 | 60.6833 | 1
2015-05-28 14:30 | 2015-05-28 | 4 | 14 | 272 | 60.4333 | 1
2015-05-28 14:45 | 2015-05-28 | 4 | 14 | 267 | 60.1833 | 1
2015-05-28 15:00 | 2015-05-28 | 4 | 15 | 263 | 59.9333 | 1
2015-05-28 15:15 | 2015-05-28 | 4 | 15 | 265 | 59.6833 | 1
2015-05-28 15:30 | 2015-05-28 | 4 | 15 | 278 | 59.4333 | 1
2015-05-28 15:45 | 2015-05-28 | 4 | 15 | 280 | 59.1833 | 1
2015-05-28 16:00 | 2015-05-28 | 4 | 16 | 277 | 58.9333 | 1
2015-05-28 16:15 | 2015-05-28 | 4 | 16 | 268 | 58.6833 | 1
2015-05-28 16:30 | 2015-05-28 | 4 | 16 | 287 | 58.4333 | 1
2015-05-28 16:45 | 2015-05-28 | 4 | 16 | 269 | 58.1833 | 1
2015-05-28 17:00 | 2015-05-28 | 4 | 17 | 291 | 57.8667 | 1
2015-05-28 17:15 | 2015-05-28 | 4 | 17 | 273 | 57.3667 | 1
2015-05-28 17:30 | 2015-05-28 | 4 | 17 | 273 | 56.8667 | 1
2015-05-28 17:45 | 2015-05-28 | 4 | 17 | 270 | 56.3667 | 1
2015-05-28 18:00 | 2015-05-28 | 4 | 18 | 277 | 55.9333 | 1
2015-05-28 18:15 | 2015-05-28 | 4 | 18 | 260 | 55.6833 | 1
2015-05-28 18:30 | 2015-05-28 | 4 | 18 | 255 | 55.4333 | 1
2015-05-28 18:45 | 2015-05-28 | 4 | 18 | 259 | 55.1833 | 1
2015-05-28 19:00 | 2015-05-28 | 4 | 19 | 238 | 55 | 1
2015-05-28 19:15 | 2015-05-28 | 4 | 19 | 243 | 55 | 1
2015-05-28 19:30 | 2015-05-28 | 4 | 19 | 238 | 55 | 1
2015-05-28 19:45 | 2015-05-28 | 4 | 19 | 217 | 55 | 1
2015-05-28 20:00 | 2015-05-28 | 4 | 20 | 221 | 55 | 1
2015-05-28 20:15 | 2015-05-28 | 4 | 20 | 195 | 55 | 1
2015-05-28 20:30 | 2015-05-28 | 4 | 20 | 186 | 55 | 1
2015-05-28 20:45 | 2015-05-28 | 4 | 20 | 189 | 55 | 1
2015-05-28 21:00 | 2015-05-28 | 4 | 21 | 190 | 54.8667 | 1
2015-05-28 21:15 | 2015-05-28 | 4 | 21 | 160 | 54.3667 | 1
2015-05-28 21:30 | 2015-05-28 | 4 | 21 | 163 | 53.8667 | 1
2015-05-28 21:45 | 2015-05-28 | 4 | 21 | 161 | 53.3667 | 1
2015-05-28 22:00 | 2015-05-28 | 4 | 22 | 166 | 53 | 1
2015-05-28 22:15 | 2015-05-28 | 4 | 22 | 170 | 53 | 1
2015-05-28 22:30 | 2015-05-28 | 4 | 22 | 158 | 53 | 1
2015-05-28 22:45 | 2015-05-28 | 4 | 22 | 163 | 53 | 1
2015-05-28 23:00 | 2015-05-28 | 4 | 23 | 166 | 53.0667 | 1
2015-05-28 23:15 | 2015-05-28 | 4 | 23 | 168 | 53.3167 | 1
2015-05-28 23:30 | 2015-05-28 | 4 | 23 | 165 | 53.5667 | 1
2015-05-28 23:45 | 2015-05-28 | 4 | 23 | 158 | 53.8167 | 1
2015-05-29 | 2015-05-29 | 5 | 0 | 158 | 54 | 1
2015-05-29 00:15 | 2015-05-29 | 5 | 0 | 152 | 54 | 1
2015-05-29 00:30 | 2015-05-29 | 5 | 0 | 160 | 54 | 1
2015-05-29 00:45 | 2015-05-29 | 5 | 0 | 164 | 54 | 1
2015-05-29 01:00 | 2015-05-29 | 5 | 1 | 153 | 54 | 1
2015-05-29 01:15 | 2015-05-29 | 5 | 1 | 163 | 54 | 1
2015-05-29 01:30 | 2015-05-29 | 5 | 1 | 157 | 54 | 1
2015-05-29 01:45 | 2015-05-29 | 5 | 1 | 153 | 54 | 1
2015-05-29 02:00 | 2015-05-29 | 5 | 2 | 159 | 54 | 1
2015-05-29 02:15 | 2015-05-29 | 5 | 2 | 152 | 54 | 1
2015-05-29 02:30 | 2015-05-29 | 5 | 2 | 155 | 54 | 1
2015-05-29 02:45 | 2015-05-29 | 5 | 2 | 159 | 54 | 1
2015-05-29 03:00 | 2015-05-29 | 5 | 3 | 148 | 54 | 1
2015-05-29 03:15 | 2015-05-29 | 5 | 3 | 155 | 54 | 1
2015-05-29 03:30 | 2015-05-29 | 5 | 3 | 151 | 54 | 1
2015-05-29 03:45 | 2015-05-29 | 5 | 3 | 148 | 54 | 1
2015-05-29 04:00 | 2015-05-29 | 5 | 4 | 148 | 54 | 1
2015-05-29 04:15 | 2015-05-29 | 5 | 4 | 149 | 54 | 1
2015-05-29 04:30 | 2015-05-29 | 5 | 4 | 155 | 54 | 1
2015-05-29 04:45 | 2015-05-29 | 5 | 4 | 158 | 54 | 1
2015-05-29 05:00 | 2015-05-29 | 5 | 5 | 144 | 54 | 1
2015-05-29 05:15 | 2015-05-29 | 5 | 5 | 155 | 54 | 1
2015-05-29 05:30 | 2015-05-29 | 5 | 5 | 150 | 54 | 1
2015-05-29 05:45 | 2015-05-29 | 5 | 5 | 145 | 54 | 1
2015-05-29 06:00 | 2015-05-29 | 5 | 6 | 143 | 54 | 1
2015-05-29 06:15 | 2015-05-29 | 5 | 6 | 159 | 54 | 1
2015-05-29 06:30 | 2015-05-29 | 5 | 6 | 146 | 54 | 1
2015-05-29 06:45 | 2015-05-29 | 5 | 6 | 146 | 54 | 1
2015-05-29 07:00 | 2015-05-29 | 5 | 7 | 149 | 54.0667 | 1
2015-05-29 07:15 | 2015-05-29 | 5 | 7 | 148 | 54.3167 | 1
2015-05-29 07:30 | 2015-05-29 | 5 | 7 | 158 | 54.5667 | 1
2015-05-29 07:45 | 2015-05-29 | 5 | 7 | 152 | 54.8167 | 1
2015-05-29 08:00 | 2015-05-29 | 5 | 8 | 154 | 55.0667 | 1
2015-05-29 08:15 | 2015-05-29 | 5 | 8 | 160 | 55.3167 | 1
2015-05-29 08:30 | 2015-05-29 | 5 | 8 | 159 | 55.5667 | 1
2015-05-29 08:45 | 2015-05-29 | 5 | 8 | 165 | 55.8167 | 1
2015-05-29 09:00 | 2015-05-29 | 5 | 9 | 180 | 56.0667 | 1
2015-05-29 09:15 | 2015-05-29 | 5 | 9 | 170 | 56.3167 | 1
2015-05-29 09:30 | 2015-05-29 | 5 | 9 | 169 | 56.5667 | 1
2015-05-29 09:45 | 2015-05-29 | 5 | 9 | 170 | 56.8167 | 1
2015-05-29 10:00 | 2015-05-29 | 5 | 10 | 194 | 57.3019 | 1
2015-05-29 10:15 | 2015-05-29 | 5 | 10 | 212 | 58.434 | 1
2015-05-29 10:30 | 2015-05-29 | 5 | 10 | 218 | 59.566 | 1
2015-05-29 10:45 | 2015-05-29 | 5 | 10 | 230 | 60.6981 | 1
2015-05-29 11:00 | 2015-05-29 | 5 | 11 | 239 | 61.9333 | 1
2015-05-29 11:15 | 2015-05-29 | 5 | 11 | 227 | 61.6833 | 1
2015-05-29 11:30 | 2015-05-29 | 5 | 11 | 234 | 61.4333 | 1
2015-05-29 11:45 | 2015-05-29 | 5 | 11 | 242 | 61.1833 | 1
2015-05-29 12:00 | 2015-05-29 | 5 | 12 | 263 | 60.9333 | 1
2015-05-29 12:15 | 2015-05-29 | 5 | 12 | 271 | 60.6833 | 1
2015-05-29 12:30 | 2015-05-29 | 5 | 12 | 246 | 60.4333 | 1
2015-05-29 12:45 | 2015-05-29 | 5 | 12 | 264 | 60.1833 | 1
2015-05-29 13:00 | 2015-05-29 | 5 | 13 | 263 | 60.0667 | 1
2015-05-29 13:15 | 2015-05-29 | 5 | 13 | 264 | 60.3167 | 1
2015-05-29 13:30 | 2015-05-29 | 5 | 13 | 260 | 60.5667 | 1
2015-05-29 13:45 | 2015-05-29 | 5 | 13 | 275 | 60.8167 | 1
2015-05-29 14:00 | 2015-05-29 | 5 | 14 | 278 | 61 | 1
2015-05-29 14:15 | 2015-05-29 | 5 | 14 | 273 | 61 | 1
2015-05-29 14:30 | 2015-05-29 | 5 | 14 | 270 | 61 | 1
2015-05-29 14:45 | 2015-05-29 | 5 | 14 | 271 | 61 | 1
2015-05-29 15:00 | 2015-05-29 | 5 | 15 | 270 | 60.8667 | 1
2015-05-29 15:15 | 2015-05-29 | 5 | 15 | 278 | 60.3667 | 1
2015-05-29 15:30 | 2015-05-29 | 5 | 15 | 282 | 59.8667 | 1
2015-05-29 15:45 | 2015-05-29 | 5 | 15 | 273 | 59.3667 | 1
2015-05-29 16:00 | 2015-05-29 | 5 | 16 | 279 | 58.8222 | 1
2015-05-29 16:15 | 2015-05-29 | 5 | 16 | 274 | 58.1556 | 1
2015-05-29 16:30 | 2015-05-29 | 5 | 16 | 273 | 57.4889 | 1
2015-05-29 16:45 | 2015-05-29 | 5 | 16 | 274 | 57 | 1
2015-05-29 17:00 | 2015-05-29 | 5 | 17 | 283 | 57 | 1
2015-05-29 17:15 | 2015-05-29 | 5 | 17 | 274 | 57 | 1
2015-05-29 17:30 | 2015-05-29 | 5 | 17 | 269 | 56.6842 | 1
2015-05-29 17:45 | 2015-05-29 | 5 | 17 | 270 | 56.2895 | 1
2015-05-29 18:00 | 2015-05-29 | 5 | 18 | 267 | 55.9333 | 1
2015-05-29 18:15 | 2015-05-29 | 5 | 18 | 275 | 55.6833 | 1
2015-05-29 18:30 | 2015-05-29 | 5 | 18 | 273 | 55.4333 | 1
2015-05-29 18:45 | 2015-05-29 | 5 | 18 | 255 | 55.1833 | 1
2015-05-29 19:00 | 2015-05-29 | 5 | 19 | 247 | 54.9333 | 1
2015-05-29 19:15 | 2015-05-29 | 5 | 19 | 234 | 54.6833 | 1
2015-05-29 19:30 | 2015-05-29 | 5 | 19 | 228 | 54.4333 | 1
2015-05-29 19:45 | 2015-05-29 | 5 | 19 | 215 | 54.1833 | 1
2015-05-29 20:00 | 2015-05-29 | 5 | 20 | 207 | 54 | 1
2015-05-29 20:15 | 2015-05-29 | 5 | 20 | 182 | 54 | 1
2015-05-29 20:30 | 2015-05-29 | 5 | 20 | 183 | 54 | 1
2015-05-29 20:45 | 2015-05-29 | 5 | 20 | 172 | 54 | 1
2015-05-29 21:00 | 2015-05-29 | 5 | 21 | 178 | 54 | 1
2015-05-29 21:15 | 2015-05-29 | 5 | 21 | 166 | 54 | 1
2015-05-29 21:30 | 2015-05-29 | 5 | 21 | 163 | 54 | 1
2015-05-29 21:45 | 2015-05-29 | 5 | 21 | 167 | 54 | 1
2015-05-29 22:00 | 2015-05-29 | 5 | 22 | 153 | 54 | 1
2015-05-29 22:15 | 2015-05-29 | 5 | 22 | 158 | 54 | 1
2015-05-29 22:30 | 2015-05-29 | 5 | 22 | 160 | 54 | 1
2015-05-29 22:45 | 2015-05-29 | 5 | 22 | 157 | 54 | 1
2015-05-29 23:00 | 2015-05-29 | 5 | 23 | 156 | 54 | 1
2015-05-29 23:15 | 2015-05-29 | 5 | 23 | 168 | 54 | 1
2015-05-29 23:30 | 2015-05-29 | 5 | 23 | 155 | 54 | 1
2015-05-29 23:45 | 2015-05-29 | 5 | 23 | 166 | 54 | 1
2015-05-30 | 2015-05-30 | 6 | 0 | 164 | 54 | 1
2015-05-30 00:15 | 2015-05-30 | 6 | 0 | 155 | 53.8913 | 1
2015-05-30 00:30 | 2015-05-30 | 6 | 0 | 159 | 53.5652 | 1
2015-05-30 00:45 | 2015-05-30 | 6 | 0 | 165 | 53.2391 | 1
2015-05-30 01:00 | 2015-05-30 | 6 | 1 | 153 | 53 | 1
2015-05-30 01:15 | 2015-05-30 | 6 | 1 | 154 | 53 | 1
2015-05-30 01:30 | 2015-05-30 | 6 | 1 | 153 | 53 | 1
2015-05-30 01:45 | 2015-05-30 | 6 | 1 | 153 | 53 | 1
2015-05-30 02:00 | 2015-05-30 | 6 | 2 | 166 | 52.9333 | 1
2015-05-30 02:15 | 2015-05-30 | 6 | 2 | 159 | 52.6833 | 1
2015-05-30 02:30 | 2015-05-30 | 6 | 2 | 157 | 52.4333 | 1
2015-05-30 02:45 | 2015-05-30 | 6 | 2 | 153 | 52.1833 | 1
2015-05-30 03:00 | 2015-05-30 | 6 | 3 | 163 | 52.0667 | 1
2015-05-30 03:15 | 2015-05-30 | 6 | 3 | 154 | 52.3167 | 1
2015-05-30 03:30 | 2015-05-30 | 6 | 3 | 150 | 52.5667 | 1
2015-05-30 03:45 | 2015-05-30 | 6 | 3 | 156 | 52.8167 | 1
2015-05-30 04:00 | 2015-05-30 | 6 | 4 | 156 | 53 | 1
2015-05-30 04:15 | 2015-05-30 | 6 | 4 | 151 | 53 | 1
2015-05-30 04:30 | 2015-05-30 | 6 | 4 | 154 | 53 | 1
2015-05-30 04:45 | 2015-05-30 | 6 | 4 | 152 | 53 | 1
2015-05-30 05:00 | 2015-05-30 | 6 | 5 | 171 | 53 | 1
2015-05-30 05:15 | 2015-05-30 | 6 | 5 | 154 | 53 | 1
2015-05-30 05:30 | 2015-05-30 | 6 | 5 | 152 | 53 | 1
2015-05-30 05:45 | 2015-05-30 | 6 | 5 | 150 | 53 | 1
2015-05-30 06:00 | 2015-05-30 | 6 | 6 | 154 | 53.0667 | 1
2015-05-30 06:15 | 2015-05-30 | 6 | 6 | 150 | 53.3167 | 1
2015-05-30 06:30 | 2015-05-30 | 6 | 6 | 160 | 53.5667 | 1
2015-05-30 06:45 | 2015-05-30 | 6 | 6 | 165 | 53.8167 | 1
2015-05-30 07:00 | 2015-05-30 | 6 | 7 | 154 | 54.0667 | 1
2015-05-30 07:15 | 2015-05-30 | 6 | 7 | 157 | 54.3167 | 1
2015-05-30 07:30 | 2015-05-30 | 6 | 7 | 156 | 54.5667 | 1
2015-05-30 07:45 | 2015-05-30 | 6 | 7 | 154 | 54.8167 | 1
2015-05-30 08:00 | 2015-05-30 | 6 | 8 | 146 | 55 | 1
2015-05-30 08:15 | 2015-05-30 | 6 | 8 | 152 | 55 | 1
2015-05-30 08:30 | 2015-05-30 | 6 | 8 | 146 | 55 | 1
2015-05-30 08:45 | 2015-05-30 | 6 | 8 | 160 | 55 | 1
2015-05-30 09:00 | 2015-05-30 | 6 | 9 | 159 | 55.1333 | 1
2015-05-30 09:15 | 2015-05-30 | 6 | 9 | 178 | 55.6333 | 1
2015-05-30 09:30 | 2015-05-30 | 6 | 9 | 193 | 56.1333 | 1
2015-05-30 09:45 | 2015-05-30 | 6 | 9 | 185 | 56.6333 | 1
2015-05-30 10:00 | 2015-05-30 | 6 | 10 | 186 | 57.2581 | 1
2015-05-30 10:15 | 2015-05-30 | 6 | 10 | 190 | 58.2258 | 1
2015-05-30 10:30 | 2015-05-30 | 6 | 10 | 203 | 59.1034 | 1
2015-05-30 10:45 | 2015-05-30 | 6 | 10 | 199 | 59.6207 | 1
2015-05-30 11:00 | 2015-05-30 | 6 | 11 | 212 | 60.0667 | 1
2015-05-30 11:15 | 2015-05-30 | 6 | 11 | 211 | 60.3167 | 1
2015-05-30 11:30 | 2015-05-30 | 6 | 11 | 213 | 60.5667 | 1
2015-05-30 11:45 | 2015-05-30 | 6 | 11 | 213 | 60.8167 | 1
2015-05-30 12:00 | 2015-05-30 | 6 | 12 | 221 | 61.1333 | 1
2015-05-30 12:15 | 2015-05-30 | 6 | 12 | 222 | 61.6333 | 1
2015-05-30 12:30 | 2015-05-30 | 6 | 12 | 224 | 62.1333 | 1
2015-05-30 12:45 | 2015-05-30 | 6 | 12 | 230 | 62.6333 | 1
2015-05-30 13:00 | 2015-05-30 | 6 | 13 | 234 | 63 | 1
2015-05-30 13:15 | 2015-05-30 | 6 | 13 | 236 | 63 | 1
2015-05-30 13:30 | 2015-05-30 | 6 | 13 | 250 | 63 | 1
2015-05-30 13:45 | 2015-05-30 | 6 | 13 | 238 | 63 | 1
2015-05-30 14:00 | 2015-05-30 | 6 | 14 | 248 | 63 | 1
2015-05-30 14:15 | 2015-05-30 | 6 | 14 | 242 | 63 | 1
2015-05-30 14:30 | 2015-05-30 | 6 | 14 | 244 | 63 | 1
2015-05-30 14:45 | 2015-05-30 | 6 | 14 | 244 | 63 | 1
2015-05-30 15:00 | 2015-05-30 | 6 | 15 | 242 | 62.8667 | 1
2015-05-30 15:15 | 2015-05-30 | 6 | 15 | 237 | 62.3667 | 1
2015-05-30 15:30 | 2015-05-30 | 6 | 15 | 175 | 61.8667 | 1
2015-05-30 15:45 | 2015-05-30 | 6 | 15 | 176 | 61.3667 | 1
2015-05-30 16:00 | 2015-05-30 | 6 | 16 | 171 | 60.8667 | 1
2015-05-30 16:15 | 2015-05-30 | 6 | 16 | 180 | 60.3667 | 1
2015-05-30 16:30 | 2015-05-30 | 6 | 16 | 183 | 59.8667 | 1
2015-05-30 16:45 | 2015-05-30 | 6 | 16 | 181 | 59.3667 | 1
2015-05-30 17:00 | 2015-05-30 | 6 | 17 | 192 | 58.8667 | 1
2015-05-30 17:15 | 2015-05-30 | 6 | 17 | 187 | 58.3667 | 1
2015-05-30 17:30 | 2015-05-30 | 6 | 17 | 186 | 57.8667 | 1
2015-05-30 17:45 | 2015-05-30 | 6 | 17 | 198 | 57.3667 | 1
2015-05-30 18:00 | 2015-05-30 | 6 | 18 | 185 | 56.5556 | 1
2015-05-30 18:15 | 2015-05-30 | 6 | 18 | 190 | 55 | 1
2015-05-30 18:30 | 2015-05-30 | 6 | 18 | 192 | 55 | 1
2015-05-30 18:45 | 2015-05-30 | 6 | 18 | 184 | 55 | 1
2015-05-30 19:00 | 2015-05-30 | 6 | 19 | 188 | 55 | 1
2015-05-30 19:15 | 2015-05-30 | 6 | 19 | 186 | 55 | 1
2015-05-30 19:30 | 2015-05-30 | 6 | 19 | 186 | 55 | 1
2015-05-30 19:45 | 2015-05-30 | 6 | 19 | 182 | 55 | 1
2015-05-30 20:00 | 2015-05-30 | 6 | 20 | 172 | 55 | 1
2015-05-30 20:15 | 2015-05-30 | 6 | 20 | 172 | 55 | 1
2015-05-30 20:30 | 2015-05-30 | 6 | 20 | 159 | 55 | 1
2015-05-30 20:45 | 2015-05-30 | 6 | 20 | 161 | 55 | 1
2015-05-30 21:00 | 2015-05-30 | 6 | 21 | 164 | 54.9333 | 1
2015-05-30 21:15 | 2015-05-30 | 6 | 21 | 152 | 54.6833 | 1
2015-05-30 21:30 | 2015-05-30 | 6 | 21 | 159 | 54.4333 | 1
2015-05-30 21:45 | 2015-05-30 | 6 | 21 | 155 | 54.1833 | 1
2015-05-30 22:00 | 2015-05-30 | 6 | 22 | 152 | 54 | 1
2015-05-30 22:15 | 2015-05-30 | 6 | 22 | 157 | 54 | 1
2015-05-30 22:30 | 2015-05-30 | 6 | 22 | 158 | 54 | 1
2015-05-30 22:45 | 2015-05-30 | 6 | 22 | 154 | 54 | 1
2015-05-30 23:00 | 2015-05-30 | 6 | 23 | 154 | 54 | 1
2015-05-30 23:15 | 2015-05-30 | 6 | 23 | 151 | 54 | 1
2015-05-30 23:30 | 2015-05-30 | 6 | 23 | 146 | 54 | 1
2015-05-30 23:45 | 2015-05-30 | 6 | 23 | 146 | 54 | 1
2015-05-31 | 2015-05-31 | 7 | 0 | 145 | 54 | 1
2015-05-31 00:15 | 2015-05-31 | 7 | 0 | 143 | 54 | 1
2015-05-31 00:30 | 2015-05-31 | 7 | 0 | 151 | 54 | 1
2015-05-31 00:45 | 2015-05-31 | 7 | 0 | 145 | 54 | 1
2015-05-31 01:00 | 2015-05-31 | 7 | 1 | 144 | 54 | 1
2015-05-31 01:15 | 2015-05-31 | 7 | 1 | 146 | 54 | 1
2015-05-31 01:30 | 2015-05-31 | 7 | 1 | 145 | 54 | 1
2015-05-31 01:45 | 2015-05-31 | 7 | 1 | 154 | 54 | 1
2015-05-31 02:00 | 2015-05-31 | 7 | 2 | 148 | 54 | 1
2015-05-31 02:15 | 2015-05-31 | 7 | 2 | 154 | 54 | 1
2015-05-31 02:30 | 2015-05-31 | 7 | 2 | 148 | 53.7222 | 1
2015-05-31 02:45 | 2015-05-31 | 7 | 2 | 147 | 53.3056 | 1
2015-05-31 03:00 | 2015-05-31 | 7 | 3 | 147 | 53.069 | 1
2015-05-31 03:15 | 2015-05-31 | 7 | 3 | 149 | 53.3276 | 1
2015-05-31 03:30 | 2015-05-31 | 7 | 3 | 145 | 53.5862 | 1
2015-05-31 03:45 | 2015-05-31 | 7 | 3 | 145 | 53.8448 | 1
2015-05-31 04:00 | 2015-05-31 | 7 | 4 | 144 | 53 | 1
2015-05-31 04:15 | 2015-05-31 | 7 | 4 | 156 | 53 | 1
2015-05-31 04:30 | 2015-05-31 | 7 | 4 | 154 | 53 | 1
2015-05-31 04:45 | 2015-05-31 | 7 | 4 | 144 | 53 | 1
2015-05-31 05:00 | 2015-05-31 | 7 | 5 | 152 | 53 | 1
2015-05-31 05:15 | 2015-05-31 | 7 | 5 | 153 | 53 | 1
2015-05-31 05:30 | 2015-05-31 | 7 | 5 | 147 | 53 | 1
2015-05-31 05:45 | 2015-05-31 | 7 | 5 | 153 | 53 | 1
2015-05-31 06:00 | 2015-05-31 | 7 | 6 | 150 | 53.0667 | 1
2015-05-31 06:15 | 2015-05-31 | 7 | 6 | 143 | 53.3167 | 1
2015-05-31 06:30 | 2015-05-31 | 7 | 6 | 151 | 53.5667 | 1
2015-05-31 06:45 | 2015-05-31 | 7 | 6 | 146 | 53.8167 | 1
2015-05-31 07:00 | 2015-05-31 | 7 | 7 | 160 | 54.2 | 1
2015-05-31 07:15 | 2015-05-31 | 7 | 7 | 172 | 54.95 | 1
2015-05-31 07:30 | 2015-05-31 | 7 | 7 | 157 | 55.7 | 1
2015-05-31 07:45 | 2015-05-31 | 7 | 7 | 159 | 56.45 | 1
2015-05-31 08:00 | 2015-05-31 | 7 | 8 | 155 | 57 | 1
2015-05-31 08:15 | 2015-05-31 | 7 | 8 | 161 | 57.5882 | 1
2015-05-31 08:30 | 2015-05-31 | 7 | 8 | 164 | 58.4706 | 1
2015-05-31 08:45 | 2015-05-31 | 7 | 8 | 156 | 59.3529 | 1
2015-05-31 09:00 | 2015-05-31 | 7 | 9 | 171 | 60 | 1
2015-05-31 09:15 | 2015-05-31 | 7 | 9 | 167 | 60 | 1
2015-05-31 09:30 | 2015-05-31 | 7 | 9 | 170 | 60 | 1
2015-05-31 09:45 | 2015-05-31 | 7 | 9 | 171 | 60 | 1
2015-05-31 10:00 | 2015-05-31 | 7 | 10 | 168 | 60.2 | 1
2015-05-31 10:15 | 2015-05-31 | 7 | 10 | 180 | 60.95 | 1
2015-05-31 10:30 | 2015-05-31 | 7 | 10 | 167 | 61.7 | 1
2015-05-31 10:45 | 2015-05-31 | 7 | 10 | 169 | 62.45 | 1
2015-05-31 11:00 | 2015-05-31 | 7 | 11 | 174 | 63.0667 | 1
2015-05-31 11:15 | 2015-05-31 | 7 | 11 | 164 | 63.3167 | 1
2015-05-31 11:30 | 2015-05-31 | 7 | 11 | 180 | 63.5667 | 1
2015-05-31 11:45 | 2015-05-31 | 7 | 11 | 166 | 63.8167 | 1
2015-05-31 12:00 | 2015-05-31 | 7 | 12 | 170 | 64.0667 | 1
2015-05-31 12:15 | 2015-05-31 | 7 | 12 | 171 | 64.3167 | 1
2015-05-31 12:30 | 2015-05-31 | 7 | 12 | 166 | 64.5667 | 1
2015-05-31 12:45 | 2015-05-31 | 7 | 12 | 173 | 64.8167 | 1
2015-05-31 13:00 | 2015-05-31 | 7 | 13 | 167 | 65 | 1
2015-05-31 13:15 | 2015-05-31 | 7 | 13 | 175 | 65 | 1
2015-05-31 13:30 | 2015-05-31 | 7 | 13 | 170 | 65 | 1
2015-05-31 13:45 | 2015-05-31 | 7 | 13 | 174 | 65 | 1
2015-05-31 14:00 | 2015-05-31 | 7 | 14 | 178 | 64.9333 | 1
2015-05-31 14:15 | 2015-05-31 | 7 | 14 | 175 | 64.6833 | 1
2015-05-31 14:30 | 2015-05-31 | 7 | 14 | 174 | 64.4333 | 1
2015-05-31 14:45 | 2015-05-31 | 7 | 14 | 179 | 64.1833 | 1
2015-05-31 15:00 | 2015-05-31 | 7 | 15 | 176 | 64.0667 | 1
2015-05-31 15:15 | 2015-05-31 | 7 | 15 | 179 | 64.3167 | 1
2015-05-31 15:30 | 2015-05-31 | 7 | 15 | 182 | 64.5667 | 1
2015-05-31 15:45 | 2015-05-31 | 7 | 15 | 179 | 64.8167 | 1
2015-05-31 16:00 | 2015-05-31 | 7 | 16 | 184 | 64.8667 | 1
2015-05-31 16:15 | 2015-05-31 | 7 | 16 | 188 | 64.3667 | 1
2015-05-31 16:30 | 2015-05-31 | 7 | 16 | 183 | 63.8667 | 1
2015-05-31 16:45 | 2015-05-31 | 7 | 16 | 180 | 63.3667 | 1
2015-05-31 17:00 | 2015-05-31 | 7 | 17 | 190 | 62.8667 | 1
2015-05-31 17:15 | 2015-05-31 | 7 | 17 | 186 | 62.3667 | 1
2015-05-31 17:30 | 2015-05-31 | 7 | 17 | 185 | 61.8667 | 1
2015-05-31 17:45 | 2015-05-31 | 7 | 17 | 197 | 61.3667 | 1
2015-05-31 18:00 | 2015-05-31 | 7 | 18 | 185 | 60.8667 | 1
2015-05-31 18:15 | 2015-05-31 | 7 | 18 | 188 | 60.3667 | 1
2015-05-31 18:30 | 2015-05-31 | 7 | 18 | 189 | 59.8667 | 1
2015-05-31 18:45 | 2015-05-31 | 7 | 18 | 186 | 59.3667 | 1
2015-05-31 19:00 | 2015-05-31 | 7 | 19 | 186 | 58.9333 | 1
2015-05-31 19:15 | 2015-05-31 | 7 | 19 | 181 | 58.6833 | 1
2015-05-31 19:30 | 2015-05-31 | 7 | 19 | 182 | 58.4333 | 1
2015-05-31 19:45 | 2015-05-31 | 7 | 19 | 171 | 58.1833 | 1
2015-05-31 20:00 | 2015-05-31 | 7 | 20 | 176 | 58.0667 | 1
2015-05-31 20:15 | 2015-05-31 | 7 | 20 | 168 | 58.3167 | 1
2015-05-31 20:30 | 2015-05-31 | 7 | 20 | 174 | 58.5667 | 1
2015-05-31 20:45 | 2015-05-31 | 7 | 20 | 176 | 58.8167 | 1
2015-05-31 21:00 | 2015-05-31 | 7 | 21 | 164 | 59 | 1
2015-05-31 21:15 | 2015-05-31 | 7 | 21 | 171 | 59 | 1
2015-05-31 21:30 | 2015-05-31 | 7 | 21 | 150 | 59 | 1
2015-05-31 21:45 | 2015-05-31 | 7 | 21 | 154 | 59 | 1
2015-05-31 22:00 | 2015-05-31 | 7 | 22 | 140 | 59.0667 | 1
2015-05-31 22:15 | 2015-05-31 | 7 | 22 | 143 | 59.3167 | 1
2015-05-31 22:30 | 2015-05-31 | 7 | 22 | 143 | 59.5667 | 1
2015-05-31 22:45 | 2015-05-31 | 7 | 22 | 141 | 59.8167 | 1
2015-05-31 23:00 | 2015-05-31 | 7 | 23 | 137 | 59.84 | 1
2015-05-31 23:15 | 2015-05-31 | 7 | 23 | 140 | 59.24 | 1
2015-05-31 23:30 | 2015-05-31 | 7 | 23 | 141 | 59 | 1
2015-05-31 23:45 | 2015-05-31 | 7 | 23 | 140 | 59 | 1
2015-06-01 | 2015-06-01 | 1 | 0 | 136 | 59 | 1
2015-06-01 00:15 | 2015-06-01 | 1 | 0 | 131 | 59 | 1
2015-06-01 00:30 | 2015-06-01 | 1 | 0 | 136 | 59 | 1
2015-06-01 00:45 | 2015-06-01 | 1 | 0 | 133 | 59 | 1
2015-06-01 01:00 | 2015-06-01 | 1 | 1 | 133 | 59 | 1
2015-06-01 01:15 | 2015-06-01 | 1 | 1 | 135 | 59 | 1
2015-06-01 01:30 | 2015-06-01 | 1 | 1 | 135 | 59 | 1
2015-06-01 01:45 | 2015-06-01 | 1 | 1 | 132 | 59 | 1
2015-06-01 02:00 | 2015-06-01 | 1 | 2 | 137 | 59 | 1
2015-06-01 02:15 | 2015-06-01 | 1 | 2 | 132 | 59 | 1
2015-06-01 02:30 | 2015-06-01 | 1 | 2 | 133 | 59 | 1
2015-06-01 02:45 | 2015-06-01 | 1 | 2 | 133 | 59 | 1
2015-06-01 03:00 | 2015-06-01 | 1 | 3 | 137 | 59 | 1
2015-06-01 03:15 | 2015-06-01 | 1 | 3 | 132 | 59 | 1
2015-06-01 03:30 | 2015-06-01 | 1 | 3 | 133 | 59 | 1
2015-06-01 03:45 | 2015-06-01 | 1 | 3 | 130 | 59 | 1
2015-06-01 04:00 | 2015-06-01 | 1 | 4 | 132 | 59 | 1
2015-06-01 04:15 | 2015-06-01 | 1 | 4 | 131 | 59 | 1
2015-06-01 04:30 | 2015-06-01 | 1 | 4 | 130 | 59 | 1
2015-06-01 04:45 | 2015-06-01 | 1 | 4 | 136 | 59 | 1
2015-06-01 05:00 | 2015-06-01 | 1 | 5 | 130 | 59 | 1
2015-06-01 05:15 | 2015-06-01 | 1 | 5 | 131 | 59 | 1
2015-06-01 05:30 | 2015-06-01 | 1 | 5 | 131 | 59 | 1
2015-06-01 05:45 | 2015-06-01 | 1 | 5 | 131 | 59 | 1
2015-06-01 06:00 | 2015-06-01 | 1 | 6 | 132 | 59.0667 | 1
2015-06-01 06:15 | 2015-06-01 | 1 | 6 | 131 | 59.3167 | 1
2015-06-01 06:30 | 2015-06-01 | 1 | 6 | 131 | 59.5667 | 1
2015-06-01 06:45 | 2015-06-01 | 1 | 6 | 132 | 59.8167 | 1
2015-06-01 07:00 | 2015-06-01 | 1 | 7 | 132 | 60.1333 | 1
2015-06-01 07:15 | 2015-06-01 | 1 | 7 | 135 | 60.6333 | 1
2015-06-01 07:30 | 2015-06-01 | 1 | 7 | 127 | 61.1333 | 1
2015-06-01 07:45 | 2015-06-01 | 1 | 7 | 133 | 61.6333 | 1
2015-06-01 08:00 | 2015-06-01 | 1 | 8 | 137 | 62.1333 | 1
2015-06-01 08:15 | 2015-06-01 | 1 | 8 | 144 | 62.6333 | 1
2015-06-01 08:30 | 2015-06-01 | 1 | 8 | 151 | 63.1333 | 1
2015-06-01 08:45 | 2015-06-01 | 1 | 8 | 164 | 63.6333 | 1
2015-06-01 09:00 | 2015-06-01 | 1 | 9 | 190 | 64 | 1
2015-06-01 09:15 | 2015-06-01 | 1 | 9 | 189 | 64 | 1
2015-06-01 09:30 | 2015-06-01 | 1 | 9 | 191 | 64.5 | 1
2015-06-01 09:45 | 2015-06-01 | 1 | 9 | 196 | 65.4375 | 2
2015-06-01 10:00 | 2015-06-01 | 1 | 10 | 188 | 65.0667 | 2
2015-06-01 10:15 | 2015-06-01 | 1 | 10 | 194 | 65.3167 | 2
2015-06-01 10:30 | 2015-06-01 | 1 | 10 | 195 | 65.5667 | 2
2015-06-01 10:45 | 2015-06-01 | 1 | 10 | 192 | 65.8167 | 2
2015-06-01 11:00 | 2015-06-01 | 1 | 11 | 202 | 66.2667 | 2
2015-06-01 11:15 | 2015-06-01 | 1 | 11 | 194 | 67.2667 | 2
2015-06-01 11:30 | 2015-06-01 | 1 | 11 | 197 | 68.2667 | 2
2015-06-01 11:45 | 2015-06-01 | 1 | 11 | 193 | 69.2667 | 2
2015-06-01 12:00 | 2015-06-01 | 1 | 12 | 206 | 70.0667 | 3
2015-06-01 12:15 | 2015-06-01 | 1 | 12 | 195 | 70.3167 | 3
2015-06-01 12:30 | 2015-06-01 | 1 | 12 | 197 | 70.5667 | 3
2015-06-01 12:45 | 2015-06-01 | 1 | 12 | 197 | 70.8167 | 3
2015-06-01 13:00 | 2015-06-01 | 1 | 13 | 199 | 71.0667 | 3
2015-06-01 13:15 | 2015-06-01 | 1 | 13 | 199 | 71.3167 | 3
2015-06-01 13:30 | 2015-06-01 | 1 | 13 | 205 | 71.5667 | 3
2015-06-01 13:45 | 2015-06-01 | 1 | 13 | 203 | 71.8167 | 3
2015-06-01 14:00 | 2015-06-01 | 1 | 14 | 204 | 71.9333 | 3
2015-06-01 14:15 | 2015-06-01 | 1 | 14 | 213 | 71.6833 | 3
2015-06-01 14:30 | 2015-06-01 | 1 | 14 | 210 | 71.4333 | 3
2015-06-01 14:45 | 2015-06-01 | 1 | 14 | 209 | 71.1833 | 3
2015-06-01 15:00 | 2015-06-01 | 1 | 15 | 208 | 70.8667 | 3
2015-06-01 15:15 | 2015-06-01 | 1 | 15 | 211 | 70.3667 | 3
2015-06-01 15:30 | 2015-06-01 | 1 | 15 | 207 | 69.8667 | 2
2015-06-01 15:45 | 2015-06-01 | 1 | 15 | 224 | 69.3667 | 2
2015-06-01 16:00 | 2015-06-01 | 1 | 16 | 213 | 68.9024 | 2
2015-06-01 16:15 | 2015-06-01 | 1 | 16 | 219 | 68.5366 | 2
2015-06-01 16:30 | 2015-06-01 | 1 | 16 | 216 | 68.1707 | 2
2015-06-01 16:45 | 2015-06-01 | 1 | 16 | 214 | 67.5789 | 2
2015-06-01 17:00 | 2015-06-01 | 1 | 17 | 220 | 66.9333 | 2
2015-06-01 17:15 | 2015-06-01 | 1 | 17 | 221 | 66.6833 | 2
2015-06-01 17:30 | 2015-06-01 | 1 | 17 | 215 | 66.4333 | 2
2015-06-01 17:45 | 2015-06-01 | 1 | 17 | 218 | 66.1833 | 2
2015-06-01 18:00 | 2015-06-01 | 1 | 18 | 223 | 65.7838 | 2
2015-06-01 18:15 | 2015-06-01 | 1 | 18 | 210 | 64.973 | 1
2015-06-01 18:30 | 2015-06-01 | 1 | 18 | 218 | 64.1622 | 1
2015-06-01 18:45 | 2015-06-01 | 1 | 18 | 208 | 64 | 1
2015-06-01 19:00 | 2015-06-01 | 1 | 19 | 217 | 63.8667 | 1
2015-06-01 19:15 | 2015-06-01 | 1 | 19 | 206 | 63.3667 | 1
2015-06-01 19:30 | 2015-06-01 | 1 | 19 | 209 | 62.8667 | 1
2015-06-01 19:45 | 2015-06-01 | 1 | 19 | 211 | 62.3667 | 1
2015-06-01 20:00 | 2015-06-01 | 1 | 20 | 203 | 61.875 | 1
2015-06-01 20:15 | 2015-06-01 | 1 | 20 | 204 | 61.4062 | 1
2015-06-01 20:30 | 2015-06-01 | 1 | 20 | 193 | 61 | 1
2015-06-01 20:45 | 2015-06-01 | 1 | 20 | 189 | 61 | 1
2015-06-01 21:00 | 2015-06-01 | 1 | 21 | 186 | 60.9333 | 1
2015-06-01 21:15 | 2015-06-01 | 1 | 21 | 177 | 60.6833 | 1
2015-06-01 21:30 | 2015-06-01 | 1 | 21 | 176 | 60.4333 | 1
2015-06-01 21:45 | 2015-06-01 | 1 | 21 | 184 | 60.1833 | 1
2015-06-01 22:00 | 2015-06-01 | 1 | 22 | 183 | 60 | 1
2015-06-01 22:15 | 2015-06-01 | 1 | 22 | 197 | 60 | 1
2015-06-01 22:30 | 2015-06-01 | 1 | 22 | 186 | 60 | 1
2015-06-01 22:45 | 2015-06-01 | 1 | 22 | 187 | 60 | 1
2015-06-01 23:00 | 2015-06-01 | 1 | 23 | 180 | 59.9333 | 1
2015-06-01 23:15 | 2015-06-01 | 1 | 23 | 171 | 59.6833 | 1
2015-06-01 23:30 | 2015-06-01 | 1 | 23 | 166 | 59.4333 | 1
2015-06-01 23:45 | 2015-06-01 | 1 | 23 | 160 | 59.1833 | 1
2015-06-02 | 2015-06-02 | 2 | 0 | 163 | 59 | 1
2015-06-02 00:15 | 2015-06-02 | 2 | 0 | 156 | 59 | 1
2015-06-02 00:30 | 2015-06-02 | 2 | 0 | 163 | 59 | 1
2015-06-02 00:45 | 2015-06-02 | 2 | 0 | 154 | 59 | 1
2015-06-02 01:00 | 2015-06-02 | 2 | 1 | 152 | 58.8431 | 1
2015-06-02 01:15 | 2015-06-02 | 2 | 1 | 159 | 58.2549 | 1
2015-06-02 01:30 | 2015-06-02 | 2 | 1 | 139 | 57.6667 | 1
2015-06-02 01:45 | 2015-06-02 | 2 | 1 | 141 | 57.0784 | 1
2015-06-02 02:00 | 2015-06-02 | 2 | 2 | 138 | 57 | 1
2015-06-02 02:15 | 2015-06-02 | 2 | 2 | 134 | 57 | 1
2015-06-02 02:30 | 2015-06-02 | 2 | 2 | 133 | 57 | 1
2015-06-02 02:45 | 2015-06-02 | 2 | 2 | 135 | 57 | 1
2015-06-02 03:00 | 2015-06-02 | 2 | 3 | 136 | 57 | 1
2015-06-02 03:15 | 2015-06-02 | 2 | 3 | 140 | 57 | 1
2015-06-02 03:30 | 2015-06-02 | 2 | 3 | 133 | 57 | 1
2015-06-02 03:45 | 2015-06-02 | 2 | 3 | 131 | 57 | 1
2015-06-02 04:00 | 2015-06-02 | 2 | 4 | 132 | 57 | 1
2015-06-02 04:15 | 2015-06-02 | 2 | 4 | 135 | 57 | 1
2015-06-02 04:30 | 2015-06-02 | 2 | 4 | 132 | 57 | 1
2015-06-02 04:45 | 2015-06-02 | 2 | 4 | 132 | 57 | 1
2015-06-02 05:00 | 2015-06-02 | 2 | 5 | 138 | 57 | 1
2015-06-02 05:15 | 2015-06-02 | 2 | 5 | 143 | 57 | 1
2015-06-02 05:30 | 2015-06-02 | 2 | 5 | 133 | 57 | 1
2015-06-02 05:45 | 2015-06-02 | 2 | 5 | 138 | 57 | 1
2015-06-02 06:00 | 2015-06-02 | 2 | 6 | 139 | 58.1333 | 1
2015-06-02 06:15 | 2015-06-02 | 2 | 6 | 138 | 58.6333 | 1
2015-06-02 06:30 | 2015-06-02 | 2 | 6 | 145 | 59.1333 | 1
2015-06-02 06:45 | 2015-06-02 | 2 | 6 | 135 | 59.6333 | 1
2015-06-02 07:00 | 2015-06-02 | 2 | 7 | 141 | 60.0667 | 1
2015-06-02 07:15 | 2015-06-02 | 2 | 7 | 140 | 60.3167 | 1
2015-06-02 07:30 | 2015-06-02 | 2 | 7 | 145 | 60.5667 | 1
2015-06-02 07:45 | 2015-06-02 | 2 | 7 | 153 | 60.8167 | 1
2015-06-02 08:00 | 2015-06-02 | 2 | 8 | 149 | 61 | 1
2015-06-02 08:15 | 2015-06-02 | 2 | 8 | 153 | 61 | 1
2015-06-02 08:30 | 2015-06-02 | 2 | 8 | 155 | 61 | 1
2015-06-02 08:45 | 2015-06-02 | 2 | 8 | 173 | 61 | 1
2015-06-02 09:00 | 2015-06-02 | 2 | 9 | 169 | 61 | 1
2015-06-02 09:15 | 2015-06-02 | 2 | 9 | 182 | 61 | 1
2015-06-02 09:30 | 2015-06-02 | 2 | 9 | 192 | 61 | 1
2015-06-02 09:45 | 2015-06-02 | 2 | 9 | 186 | 61 | 1
2015-06-02 10:00 | 2015-06-02 | 2 | 10 | 190 | 61.0667 | 1
2015-06-02 10:15 | 2015-06-02 | 2 | 10 | 188 | 61.3167 | 1
2015-06-02 10:30 | 2015-06-02 | 2 | 10 | 189 | 61.5667 | 1
2015-06-02 10:45 | 2015-06-02 | 2 | 10 | 175 | 61.8167 | 1
2015-06-02 11:00 | 2015-06-02 | 2 | 11 | 181 | 61.8667 | 1
2015-06-02 11:15 | 2015-06-02 | 2 | 11 | 184 | 61.3667 | 1
2015-06-02 11:30 | 2015-06-02 | 2 | 11 | 190 | 61.1333 | 1
2015-06-02 11:45 | 2015-06-02 | 2 | 11 | 191 | 61.6333 | 1
2015-06-02 12:00 | 2015-06-02 | 2 | 12 | 197 | 62.087 | 1
2015-06-02 12:15 | 2015-06-02 | 2 | 12 | 196 | 62.413 | 1
2015-06-02 12:30 | 2015-06-02 | 2 | 12 | 196 | 62.7391 | 1
2015-06-02 12:45 | 2015-06-02 | 2 | 12 | 196 | 63 | 1
2015-06-02 13:00 | 2015-06-02 | 2 | 13 | 199 | 63.1333 | 1
2015-06-02 13:15 | 2015-06-02 | 2 | 13 | 201 | 63.6333 | 1
2015-06-02 13:30 | 2015-06-02 | 2 | 13 | 202 | 64.1333 | 1
2015-06-02 13:45 | 2015-06-02 | 2 | 13 | 200 | 64.6333 | 1
2015-06-02 14:00 | 2015-06-02 | 2 | 14 | 199 | 64.9333 | 1
2015-06-02 14:15 | 2015-06-02 | 2 | 14 | 200 | 64.6833 | 1
2015-06-02 14:30 | 2015-06-02 | 2 | 14 | 203 | 64.4333 | 1
2015-06-02 14:45 | 2015-06-02 | 2 | 14 | 224 | 64.1833 | 1
2015-06-02 15:00 | 2015-06-02 | 2 | 15 | 267 | 64 | 1
2015-06-02 15:15 | 2015-06-02 | 2 | 15 | 251 | 64 | 1
2015-06-02 15:30 | 2015-06-02 | 2 | 15 | 260 | 64 | 1
2015-06-02 15:45 | 2015-06-02 | 2 | 15 | 251 | 64 | 1
2015-06-02 16:00 | 2015-06-02 | 2 | 16 | 243 | 63.8667 | 1
2015-06-02 16:15 | 2015-06-02 | 2 | 16 | 247 | 63.3667 | 1
2015-06-02 16:30 | 2015-06-02 | 2 | 16 | 236 | 62.8667 | 1
2015-06-02 16:45 | 2015-06-02 | 2 | 16 | 246 | 62.3667 | 1
2015-06-02 17:00 | 2015-06-02 | 2 | 17 | 235 | 61.8667 | 1
2015-06-02 17:15 | 2015-06-02 | 2 | 17 | 242 | 61.3667 | 1
2015-06-02 17:30 | 2015-06-02 | 2 | 17 | 239 | 60.8667 | 1
2015-06-02 17:45 | 2015-06-02 | 2 | 17 | 237 | 60.3667 | 1
2015-06-02 18:00 | 2015-06-02 | 2 | 18 | 235 | 59.9333 | 1
2015-06-02 18:15 | 2015-06-02 | 2 | 18 | 228 | 59.6833 | 1
2015-06-02 18:30 | 2015-06-02 | 2 | 18 | 236 | 59.4333 | 1
2015-06-02 18:45 | 2015-06-02 | 2 | 18 | 226 | 59.1833 | 1
2015-06-02 19:00 | 2015-06-02 | 2 | 19 | 217 | 58.9333 | 1
2015-06-02 19:15 | 2015-06-02 | 2 | 19 | 222 | 58.6833 | 1
2015-06-02 19:30 | 2015-06-02 | 2 | 19 | 220 | 58.4333 | 1
2015-06-02 19:45 | 2015-06-02 | 2 | 19 | 214 | 58.1833 | 1
2015-06-02 20:00 | 2015-06-02 | 2 | 20 | 210 | 57.9333 | 1
2015-06-02 20:15 | 2015-06-02 | 2 | 20 | 208 | 57.6833 | 1
2015-06-02 20:30 | 2015-06-02 | 2 | 20 | 203 | 57.4333 | 1
2015-06-02 20:45 | 2015-06-02 | 2 | 20 | 201 | 57.1833 | 1
2015-06-02 21:00 | 2015-06-02 | 2 | 21 | 203 | 57 | 1
2015-06-02 21:15 | 2015-06-02 | 2 | 21 | 206 | 57 | 1
2015-06-02 21:30 | 2015-06-02 | 2 | 21 | 198 | 57 | 1
2015-06-02 21:45 | 2015-06-02 | 2 | 21 | 191 | 57 | 1
2015-06-02 22:00 | 2015-06-02 | 2 | 22 | 185 | 57 | 1
2015-06-02 22:15 | 2015-06-02 | 2 | 22 | 183 | 57 | 1
2015-06-02 22:30 | 2015-06-02 | 2 | 22 | 183 | 57 | 1
2015-06-02 22:45 | 2015-06-02 | 2 | 22 | 185 | 57 | 1
2015-06-02 23:00 | 2015-06-02 | 2 | 23 | 190 | 56.84 | 1
2015-06-02 23:15 | 2015-06-02 | 2 | 23 | 184 | 56.24 | 1
2015-06-02 23:30 | 2015-06-02 | 2 | 23 | 167 | 55.64 | 1
2015-06-02 23:45 | 2015-06-02 | 2 | 23 | 166 | 55.04 | 1
2015-06-03 | 2015-06-03 | 3 | 0 | 157 | 56 | 1
2015-06-03 00:15 | 2015-06-03 | 3 | 0 | 171 | 56 | 1
2015-06-03 00:30 | 2015-06-03 | 3 | 0 | 152 | 56 | 1
2015-06-03 00:45 | 2015-06-03 | 3 | 0 | 150 | 56 | 1
2015-06-03 01:00 | 2015-06-03 | 3 | 1 | 153 | 56 | 1
2015-06-03 01:15 | 2015-06-03 | 3 | 1 | 155 | 56 | 1
2015-06-03 01:30 | 2015-06-03 | 3 | 1 | 149 | 56 | 1
2015-06-03 01:45 | 2015-06-03 | 3 | 1 | 148 | 56 | 1
2015-06-03 02:00 | 2015-06-03 | 3 | 2 | 149 | 56 | 1
2015-06-03 02:15 | 2015-06-03 | 3 | 2 | 146 | 56 | 1
2015-06-03 02:30 | 2015-06-03 | 3 | 2 | 164 | 56 | 1
2015-06-03 02:45 | 2015-06-03 | 3 | 2 | 150 | 56 | 1
2015-06-03 03:00 | 2015-06-03 | 3 | 3 | 153 | 55.931 | 1
2015-06-03 03:15 | 2015-06-03 | 3 | 3 | 149 | 55.6724 | 1
2015-06-03 03:30 | 2015-06-03 | 3 | 3 | 145 | 55.4138 | 1
2015-06-03 03:45 | 2015-06-03 | 3 | 3 | 145 | 55.1552 | 1
2015-06-03 04:00 | 2015-06-03 | 3 | 4 | 146 | 55 | 1
2015-06-03 04:15 | 2015-06-03 | 3 | 4 | 155 | 55 | 1
2015-06-03 04:30 | 2015-06-03 | 3 | 4 | 144 | 55 | 1
2015-06-03 04:45 | 2015-06-03 | 3 | 4 | 145 | 55 | 1
2015-06-03 05:00 | 2015-06-03 | 3 | 5 | 143 | 55.1333 | 1
2015-06-03 05:15 | 2015-06-03 | 3 | 5 | 142 | 55.6333 | 1
2015-06-03 05:30 | 2015-06-03 | 3 | 5 | 154 | 56.1333 | 1
2015-06-03 05:45 | 2015-06-03 | 3 | 5 | 145 | 56.6333 | 1
2015-06-03 06:00 | 2015-06-03 | 3 | 6 | 141 | 57 | 1
2015-06-03 06:15 | 2015-06-03 | 3 | 6 | 141 | 57 | 1
2015-06-03 06:30 | 2015-06-03 | 3 | 6 | 153 | 57 | 1
2015-06-03 06:45 | 2015-06-03 | 3 | 6 | 147 | 57 | 1
2015-06-03 07:00 | 2015-06-03 | 3 | 7 | 149 | 56.2 | 1
2015-06-03 07:15 | 2015-06-03 | 3 | 7 | 152 | 56.95 | 1
2015-06-03 07:30 | 2015-06-03 | 3 | 7 | 146 | 57.7 | 1
2015-06-03 07:45 | 2015-06-03 | 3 | 7 | 151 | 58.45 | 1
2015-06-03 08:00 | 2015-06-03 | 3 | 8 | 159 | 59.0667 | 1
2015-06-03 08:15 | 2015-06-03 | 3 | 8 | 174 | 59.3167 | 1
2015-06-03 08:30 | 2015-06-03 | 3 | 8 | 177 | 59.5667 | 1
2015-06-03 08:45 | 2015-06-03 | 3 | 8 | 184 | 59.8167 | 1
2015-06-03 09:00 | 2015-06-03 | 3 | 9 | 194 | 60.0889 | 1
2015-06-03 09:15 | 2015-06-03 | 3 | 9 | 204 | 60.4222 | 1
2015-06-03 09:30 | 2015-06-03 | 3 | 9 | 203 | 60.7556 | 1
2015-06-03 09:45 | 2015-06-03 | 3 | 9 | 211 | 61 | 1
2015-06-03 10:00 | 2015-06-03 | 3 | 10 | 206 | 61.1333 | 1
2015-06-03 10:15 | 2015-06-03 | 3 | 10 | 212 | 61.6333 | 1
2015-06-03 10:30 | 2015-06-03 | 3 | 10 | 232 | 62.1333 | 1
2015-06-03 10:45 | 2015-06-03 | 3 | 10 | 217 | 62.6333 | 1
2015-06-03 11:00 | 2015-06-03 | 3 | 11 | 218 | 63 | 1
2015-06-03 11:15 | 2015-06-03 | 3 | 11 | 232 | 63 | 1
2015-06-03 11:30 | 2015-06-03 | 3 | 11 | 219 | 63 | 1
2015-06-03 11:45 | 2015-06-03 | 3 | 11 | 219 | 63 | 1
2015-06-03 12:00 | 2015-06-03 | 3 | 12 | 241 | 63.1333 | 1
2015-06-03 12:15 | 2015-06-03 | 3 | 12 | 223 | 63.6333 | 1
2015-06-03 12:30 | 2015-06-03 | 3 | 12 | 225 | 64.1333 | 1
2015-06-03 12:45 | 2015-06-03 | 3 | 12 | 232 | 64.6333 | 1
2015-06-03 13:00 | 2015-06-03 | 3 | 13 | 224 | 64.7333 | 1
2015-06-03 13:15 | 2015-06-03 | 3 | 13 | 251 | 63.7333 | 1
2015-06-03 13:30 | 2015-06-03 | 3 | 13 | 238 | 62.7333 | 1
2015-06-03 13:45 | 2015-06-03 | 3 | 13 | 240 | 61.7333 | 1
2015-06-03 14:00 | 2015-06-03 | 3 | 14 | 257 | 61 | 1
2015-06-03 14:15 | 2015-06-03 | 3 | 14 | 229 | 61 | 1
2015-06-03 14:30 | 2015-06-03 | 3 | 14 | 229 | 61 | 1
2015-06-03 14:45 | 2015-06-03 | 3 | 14 | 236 | 60.55 | 1
2015-06-03 15:00 | 2015-06-03 | 3 | 15 | 230 | 60 | 1
2015-06-03 15:15 | 2015-06-03 | 3 | 15 | 237 | 60 | 1
2015-06-03 15:30 | 2015-06-03 | 3 | 15 | 234 | 60 | 1
2015-06-03 15:45 | 2015-06-03 | 3 | 15 | 224 | 60 | 1
2015-06-03 16:00 | 2015-06-03 | 3 | 16 | 241 | 60 | 1
2015-06-03 16:15 | 2015-06-03 | 3 | 16 | 221 | 60 | 1
2015-06-03 16:30 | 2015-06-03 | 3 | 16 | 229 | 60 | 1
2015-06-03 16:45 | 2015-06-03 | 3 | 16 | 228 | 60 | 1
2015-06-03 17:00 | 2015-06-03 | 3 | 17 | 220 | 59.9333 | 1
2015-06-03 17:15 | 2015-06-03 | 3 | 17 | 236 | 59.6833 | 1
2015-06-03 17:30 | 2015-06-03 | 3 | 17 | 225 | 59.4333 | 1
2015-06-03 17:45 | 2015-06-03 | 3 | 17 | 227 | 59.1833 | 1
2015-06-03 18:00 | 2015-06-03 | 3 | 18 | 225 | 58.7241 | 1
2015-06-03 18:15 | 2015-06-03 | 3 | 18 | 211 | 57.6897 | 1
2015-06-03 18:30 | 2015-06-03 | 3 | 18 | 218 | 57.1613 | 1
2015-06-03 18:45 | 2015-06-03 | 3 | 18 | 208 | 57.6452 | 1
2015-06-03 19:00 | 2015-06-03 | 3 | 19 | 208 | 57.9333 | 1
2015-06-03 19:15 | 2015-06-03 | 3 | 19 | 199 | 57.6833 | 1
2015-06-03 19:30 | 2015-06-03 | 3 | 19 | 194 | 57.4333 | 1
2015-06-03 19:45 | 2015-06-03 | 3 | 19 | 201 | 57.1833 | 1
2015-06-03 20:00 | 2015-06-03 | 3 | 20 | 199 | 57 | 1
2015-06-03 20:15 | 2015-06-03 | 3 | 20 | 192 | 57 | 1
2015-06-03 20:30 | 2015-06-03 | 3 | 20 | 181 | 57 | 1
2015-06-03 20:45 | 2015-06-03 | 3 | 20 | 170 | 57 | 1
2015-06-03 21:00 | 2015-06-03 | 3 | 21 | 179 | 56.8621 | 1
2015-06-03 21:15 | 2015-06-03 | 3 | 21 | 178 | 56.3448 | 1
2015-06-03 21:30 | 2015-06-03 | 3 | 21 | 157 | 55.8276 | 1
2015-06-03 21:45 | 2015-06-03 | 3 | 21 | 158 | 55.3103 | 1
2015-06-03 22:00 | 2015-06-03 | 3 | 22 | 153 | 55.907 | 1
2015-06-03 22:15 | 2015-06-03 | 3 | 22 | 171 | 55.5581 | 1
2015-06-03 22:30 | 2015-06-03 | 3 | 22 | 154 | 55.2093 | 1
2015-06-03 22:45 | 2015-06-03 | 3 | 22 | 156 | 55.3529 | 1
2015-06-03 23:00 | 2015-06-03 | 3 | 23 | 158 | 55.9091 | 1
2015-06-03 23:15 | 2015-06-03 | 3 | 23 | 160 | 55.5682 | 1
2015-06-03 23:30 | 2015-06-03 | 3 | 23 | 168 | 55.2273 | 1
2015-06-03 23:45 | 2015-06-03 | 3 | 23 | 156 | 55 | 1
2015-06-04 | 2015-06-04 | 4 | 0 | 156 | 55 | 1
2015-06-04 00:15 | 2015-06-04 | 4 | 0 | 152 | 55 | 1
2015-06-04 00:30 | 2015-06-04 | 4 | 0 | 163 | 55 | 1
2015-06-04 00:45 | 2015-06-04 | 4 | 0 | 157 | 55 | 1
2015-06-04 01:00 | 2015-06-04 | 4 | 1 | 155 | 55 | 1
2015-06-04 01:15 | 2015-06-04 | 4 | 1 | 151 | 55 | 1
2015-06-04 01:30 | 2015-06-04 | 4 | 1 | 153 | 55 | 1
2015-06-04 01:45 | 2015-06-04 | 4 | 1 | 149 | 55 | 1
2015-06-04 02:00 | 2015-06-04 | 4 | 2 | 151 | 55 | 1
2015-06-04 02:15 | 2015-06-04 | 4 | 2 | 163 | 55 | 1
2015-06-04 02:30 | 2015-06-04 | 4 | 2 | 149 | 55 | 1
2015-06-04 02:45 | 2015-06-04 | 4 | 2 | 149 | 55 | 1
2015-06-04 03:00 | 2015-06-04 | 4 | 3 | 150 | 54.9333 | 1
2015-06-04 03:15 | 2015-06-04 | 4 | 3 | 155 | 54.6833 | 1
2015-06-04 03:30 | 2015-06-04 | 4 | 3 | 151 | 54.4333 | 1
2015-06-04 03:45 | 2015-06-04 | 4 | 3 | 145 | 54.1833 | 1
2015-06-04 04:00 | 2015-06-04 | 4 | 4 | 144 | 54 | 1
2015-06-04 04:15 | 2015-06-04 | 4 | 4 | 144 | 54 | 1
2015-06-04 04:30 | 2015-06-04 | 4 | 4 | 152 | 54 | 1
2015-06-04 04:45 | 2015-06-04 | 4 | 4 | 155 | 54 | 1
2015-06-04 05:00 | 2015-06-04 | 4 | 5 | 148 | 54 | 1
2015-06-04 05:15 | 2015-06-04 | 4 | 5 | 150 | 54 | 1
2015-06-04 05:30 | 2015-06-04 | 4 | 5 | 143 | 54 | 1
2015-06-04 05:45 | 2015-06-04 | 4 | 5 | 157 | 54 | 1
2015-06-04 06:00 | 2015-06-04 | 4 | 6 | 151 | 54.1333 | 1
2015-06-04 06:15 | 2015-06-04 | 4 | 6 | 150 | 54.6333 | 1
2015-06-04 06:30 | 2015-06-04 | 4 | 6 | 144 | 55.1333 | 1
2015-06-04 06:45 | 2015-06-04 | 4 | 6 | 144 | 55.6333 | 1
2015-06-04 07:00 | 2015-06-04 | 4 | 7 | 148 | 56.1 | 1
2015-06-04 07:15 | 2015-06-04 | 4 | 7 | 151 | 56.475 | 1
2015-06-04 07:30 | 2015-06-04 | 4 | 7 | 160 | 56.85 | 1
2015-06-04 07:45 | 2015-06-04 | 4 | 7 | 151 | 57.45 | 1
2015-06-04 08:00 | 2015-06-04 | 4 | 8 | 170 | 58.2 | 1
2015-06-04 08:15 | 2015-06-04 | 4 | 8 | 179 | 58.95 | 1
2015-06-04 08:30 | 2015-06-04 | 4 | 8 | 173 | 59.7 | 1
2015-06-04 08:45 | 2015-06-04 | 4 | 8 | 195 | 60.45 | 1
2015-06-04 09:00 | 2015-06-04 | 4 | 9 | 184 | 61.1333 | 1
2015-06-04 09:15 | 2015-06-04 | 4 | 9 | 183 | 61.6333 | 1
2015-06-04 09:30 | 2015-06-04 | 4 | 9 | 194 | 62.1333 | 1
2015-06-04 09:45 | 2015-06-04 | 4 | 9 | 199 | 62.6333 | 1
2015-06-04 10:00 | 2015-06-04 | 4 | 10 | 211 | 63.2 | 1
2015-06-04 10:15 | 2015-06-04 | 4 | 10 | 189 | 63.95 | 1
2015-06-04 10:30 | 2015-06-04 | 4 | 10 | 220 | 64.7 | 1
2015-06-04 10:45 | 2015-06-04 | 4 | 10 | 225 | 65.45 | 2
2015-06-04 11:00 | 2015-06-04 | 4 | 11 | 218 | 66.1333 | 2
2015-06-04 11:15 | 2015-06-04 | 4 | 11 | 241 | 66.6333 | 2
2015-06-04 11:30 | 2015-06-04 | 4 | 11 | 228 | 67.1333 | 2
2015-06-04 11:45 | 2015-06-04 | 4 | 11 | 228 | 67.6333 | 2
2015-06-04 12:00 | 2015-06-04 | 4 | 12 | 229 | 67.9333 | 2
2015-06-04 12:15 | 2015-06-04 | 4 | 12 | 229 | 67.6833 | 2
2015-06-04 12:30 | 2015-06-04 | 4 | 12 | 249 | 67.4333 | 2
2015-06-04 12:45 | 2015-06-04 | 4 | 12 | 242 | 67.1833 | 2
2015-06-04 13:00 | 2015-06-04 | 4 | 13 | 238 | 66.9333 | 2
2015-06-04 13:15 | 2015-06-04 | 4 | 13 | 235 | 66.6833 | 2
2015-06-04 13:30 | 2015-06-04 | 4 | 13 | 238 | 66.4333 | 2
2015-06-04 13:45 | 2015-06-04 | 4 | 13 | 235 | 66.1833 | 2
2015-06-04 14:00 | 2015-06-04 | 4 | 14 | 240 | 65.9333 | 2
2015-06-04 14:15 | 2015-06-04 | 4 | 14 | 246 | 65.6833 | 2
2015-06-04 14:30 | 2015-06-04 | 4 | 14 | 243 | 65.4333 | 2
2015-06-04 14:45 | 2015-06-04 | 4 | 14 | 239 | 65.1833 | 2
2015-06-04 15:00 | 2015-06-04 | 4 | 15 | 251 | 65 | 1
2015-06-04 15:15 | 2015-06-04 | 4 | 15 | 251 | 65 | 1
2015-06-04 15:30 | 2015-06-04 | 4 | 15 | 243 | 65 | 1
2015-06-04 15:45 | 2015-06-04 | 4 | 15 | 259 | 65 | 1
2015-06-04 16:00 | 2015-06-04 | 4 | 16 | 249 | 64.8667 | 1
2015-06-04 16:15 | 2015-06-04 | 4 | 16 | 251 | 64.3667 | 1
2015-06-04 16:30 | 2015-06-04 | 4 | 16 | 251 | 63.8667 | 1
2015-06-04 16:45 | 2015-06-04 | 4 | 16 | 252 | 63.3667 | 1
2015-06-04 17:00 | 2015-06-04 | 4 | 17 | 259 | 62.8667 | 1
2015-06-04 17:15 | 2015-06-04 | 4 | 17 | 248 | 62.3667 | 1
2015-06-04 17:30 | 2015-06-04 | 4 | 17 | 255 | 61.8667 | 1
2015-06-04 17:45 | 2015-06-04 | 4 | 17 | 253 | 61.3667 | 1
2015-06-04 18:00 | 2015-06-04 | 4 | 18 | 245 | 60.8667 | 1
2015-06-04 18:15 | 2015-06-04 | 4 | 18 | 252 | 60.3667 | 1
2015-06-04 18:30 | 2015-06-04 | 4 | 18 | 250 | 59.8667 | 1
2015-06-04 18:45 | 2015-06-04 | 4 | 18 | 243 | 59.3667 | 1
2015-06-04 19:00 | 2015-06-04 | 4 | 19 | 253 | 58.8 | 1
2015-06-04 19:15 | 2015-06-04 | 4 | 19 | 238 | 58.05 | 1
2015-06-04 19:30 | 2015-06-04 | 4 | 19 | 232 | 57.3 | 1
2015-06-04 19:45 | 2015-06-04 | 4 | 19 | 231 | 56.55 | 1
2015-06-04 20:00 | 2015-06-04 | 4 | 20 | 225 | 56.0667 | 1
2015-06-04 20:15 | 2015-06-04 | 4 | 20 | 222 | 56.3167 | 1
2015-06-04 20:30 | 2015-06-04 | 4 | 20 | 214 | 56.5667 | 1
2015-06-04 20:45 | 2015-06-04 | 4 | 20 | 219 | 56.8167 | 1
2015-06-04 21:00 | 2015-06-04 | 4 | 21 | 213 | 57 | 1
2015-06-04 21:15 | 2015-06-04 | 4 | 21 | 191 | 57 | 1
2015-06-04 21:30 | 2015-06-04 | 4 | 21 | 198 | 57 | 1
2015-06-04 21:45 | 2015-06-04 | 4 | 21 | 182 | 57 | 1
2015-06-04 22:00 | 2015-06-04 | 4 | 22 | 197 | 56.9333 | 1
2015-06-04 22:15 | 2015-06-04 | 4 | 22 | 186 | 56.6833 | 1
2015-06-04 22:30 | 2015-06-04 | 4 | 22 | 185 | 56.4333 | 1
2015-06-04 22:45 | 2015-06-04 | 4 | 22 | 185 | 56.1833 | 1
2015-06-04 23:00 | 2015-06-04 | 4 | 23 | 191 | 56.0667 | 1
2015-06-04 23:15 | 2015-06-04 | 4 | 23 | 190 | 56.3167 | 1
2015-06-04 23:30 | 2015-06-04 | 4 | 23 | 196 | 56.5667 | 1
2015-06-04 23:45 | 2015-06-04 | 4 | 23 | 188 | 56.8167 | 1
2015-06-05 | 2015-06-05 | 5 | 0 | 181 | 56.9333 | 1
2015-06-05 00:15 | 2015-06-05 | 5 | 0 | 181 | 56.6833 | 1
2015-06-05 00:30 | 2015-06-05 | 5 | 0 | 178 | 56.4333 | 1
2015-06-05 00:45 | 2015-06-05 | 5 | 0 | 160 | 56.1833 | 1
2015-06-05 01:00 | 2015-06-05 | 5 | 1 | 160 | 56 | 1
2015-06-05 01:15 | 2015-06-05 | 5 | 1 | 159 | 56 | 1
2015-06-05 01:30 | 2015-06-05 | 5 | 1 | 153 | 56 | 1
2015-06-05 01:45 | 2015-06-05 | 5 | 1 | 152 | 56 | 1
2015-06-05 02:00 | 2015-06-05 | 5 | 2 | 150 | 55.9333 | 1
2015-06-05 02:15 | 2015-06-05 | 5 | 2 | 162 | 55.6833 | 1
2015-06-05 02:30 | 2015-06-05 | 5 | 2 | 155 | 55.4333 | 1
2015-06-05 02:45 | 2015-06-05 | 5 | 2 | 150 | 55.1833 | 1
2015-06-05 03:00 | 2015-06-05 | 5 | 3 | 157 | 55 | 1
2015-06-05 03:15 | 2015-06-05 | 5 | 3 | 151 | 55 | 1
2015-06-05 03:30 | 2015-06-05 | 5 | 3 | 147 | 55 | 1
2015-06-05 03:45 | 2015-06-05 | 5 | 3 | 148 | 55 | 1
2015-06-05 04:00 | 2015-06-05 | 5 | 4 | 147 | 55 | 1
2015-06-05 04:15 | 2015-06-05 | 5 | 4 | 156 | 55 | 1
2015-06-05 04:30 | 2015-06-05 | 5 | 4 | 159 | 55 | 1
2015-06-05 04:45 | 2015-06-05 | 5 | 4 | 145 | 55 | 1
2015-06-05 05:00 | 2015-06-05 | 5 | 5 | 146 | 55.0667 | 1
2015-06-05 05:15 | 2015-06-05 | 5 | 5 | 146 | 55.3167 | 1
2015-06-05 05:30 | 2015-06-05 | 5 | 5 | 163 | 55.5667 | 1
2015-06-05 05:45 | 2015-06-05 | 5 | 5 | 153 | 55.8167 | 1
2015-06-05 06:00 | 2015-06-05 | 5 | 6 | 146 | 56.1333 | 1
2015-06-05 06:15 | 2015-06-05 | 5 | 6 | 148 | 56.6333 | 1
2015-06-05 06:30 | 2015-06-05 | 5 | 6 | 144 | 57.1333 | 1
2015-06-05 06:45 | 2015-06-05 | 5 | 6 | 163 | 57.6333 | 1
2015-06-05 07:00 | 2015-06-05 | 5 | 7 | 152 | 58.2667 | 1
2015-06-05 07:15 | 2015-06-05 | 5 | 7 | 150 | 59.2667 | 1
2015-06-05 07:30 | 2015-06-05 | 5 | 7 | 148 | 60.2667 | 1
2015-06-05 07:45 | 2015-06-05 | 5 | 7 | 154 | 61 | 1
2015-06-05 08:00 | 2015-06-05 | 5 | 8 | 172 | 61.1333 | 1
2015-06-05 08:15 | 2015-06-05 | 5 | 8 | 165 | 61.6333 | 1
2015-06-05 08:30 | 2015-06-05 | 5 | 8 | 176 | 62.1333 | 1
2015-06-05 08:45 | 2015-06-05 | 5 | 8 | 185 | 62.6333 | 1
2015-06-05 09:00 | 2015-06-05 | 5 | 9 | 192 | 63.0667 | 1
2015-06-05 09:15 | 2015-06-05 | 5 | 9 | 231 | 63.3167 | 1
2015-06-05 09:30 | 2015-06-05 | 5 | 9 | 216 | 63.5667 | 1
2015-06-05 09:45 | 2015-06-05 | 5 | 9 | 220 | 63.8167 | 1
2015-06-05 10:00 | 2015-06-05 | 5 | 10 | 218 | 64.2 | 1
2015-06-05 10:15 | 2015-06-05 | 5 | 10 | 222 | 64.95 | 1
2015-06-05 10:30 | 2015-06-05 | 5 | 10 | 242 | 65.7 | 2
2015-06-05 10:45 | 2015-06-05 | 5 | 10 | 250 | 66.45 | 2
2015-06-05 11:00 | 2015-06-05 | 5 | 11 | 235 | 67 | 2
2015-06-05 11:15 | 2015-06-05 | 5 | 11 | 243 | 67 | 2
2015-06-05 11:30 | 2015-06-05 | 5 | 11 | 240 | 67 | 2
2015-06-05 11:45 | 2015-06-05 | 5 | 11 | 238 | 67 | 2
2015-06-05 12:00 | 2015-06-05 | 5 | 12 | 237 | 67.2667 | 2
2015-06-05 12:15 | 2015-06-05 | 5 | 12 | 246 | 68.2667 | 2
2015-06-05 12:30 | 2015-06-05 | 5 | 12 | 252 | 69.2667 | 2
2015-06-05 12:45 | 2015-06-05 | 5 | 12 | 248 | 70.2667 | 3
2015-06-05 13:00 | 2015-06-05 | 5 | 13 | 235 | 71 | 3
2015-06-05 13:15 | 2015-06-05 | 5 | 13 | 246 | 71 | 3
2015-06-05 13:30 | 2015-06-05 | 5 | 13 | 256 | 71 | 3
2015-06-05 13:45 | 2015-06-05 | 5 | 13 | 254 | 71 | 3
2015-06-05 14:00 | 2015-06-05 | 5 | 14 | 259 | 71 | 3
2015-06-05 14:15 | 2015-06-05 | 5 | 14 | 262 | 71 | 3
2015-06-05 14:30 | 2015-06-05 | 5 | 14 | 256 | 71 | 3
2015-06-05 14:45 | 2015-06-05 | 5 | 14 | 259 | 71 | 3
2015-06-05 15:00 | 2015-06-05 | 5 | 15 | 258 | 70.8 | 3
2015-06-05 15:15 | 2015-06-05 | 5 | 15 | 264 | 70.05 | 3
2015-06-05 15:30 | 2015-06-05 | 5 | 15 | 264 | 69.3 | 2
2015-06-05 15:45 | 2015-06-05 | 5 | 15 | 268 | 68.55 | 2
2015-06-05 16:00 | 2015-06-05 | 5 | 16 | 279 | 67.8 | 2
2015-06-05 16:15 | 2015-06-05 | 5 | 16 | 269 | 67.05 | 2
2015-06-05 16:30 | 2015-06-05 | 5 | 16 | 267 | 66.3 | 2
2015-06-05 16:45 | 2015-06-05 | 5 | 16 | 269 | 65.55 | 2
2015-06-05 17:00 | 2015-06-05 | 5 | 17 | 271 | 65 | 1
2015-06-05 17:15 | 2015-06-05 | 5 | 17 | 278 | 65 | 1
2015-06-05 17:30 | 2015-06-05 | 5 | 17 | 260 | 65 | 1
2015-06-05 17:45 | 2015-06-05 | 5 | 17 | 256 | 65 | 1
2015-06-05 18:00 | 2015-06-05 | 5 | 18 | 254 | 64.9333 | 1
2015-06-05 18:15 | 2015-06-05 | 5 | 18 | 251 | 64.6833 | 1
2015-06-05 18:30 | 2015-06-05 | 5 | 18 | 253 | 64.4333 | 1
2015-06-05 18:45 | 2015-06-05 | 5 | 18 | 248 | 64.1833 | 1
2015-06-05 19:00 | 2015-06-05 | 5 | 19 | 252 | 63.6667 | 1
2015-06-05 19:15 | 2015-06-05 | 5 | 19 | 243 | 62.4167 | 1
2015-06-05 19:30 | 2015-06-05 | 5 | 19 | 232 | 61.1667 | 1
2015-06-05 19:45 | 2015-06-05 | 5 | 19 | 239 | 60.4583 | 1
2015-06-05 20:00 | 2015-06-05 | 5 | 20 | 229 | 60 | 1
2015-06-05 20:15 | 2015-06-05 | 5 | 20 | 224 | 60 | 1
2015-06-05 20:30 | 2015-06-05 | 5 | 20 | 231 | 60 | 1
2015-06-05 20:45 | 2015-06-05 | 5 | 20 | 222 | 60 | 1
2015-06-05 21:00 | 2015-06-05 | 5 | 21 | 216 | 59.9333 | 1
2015-06-05 21:15 | 2015-06-05 | 5 | 21 | 205 | 59.6833 | 1
2015-06-05 21:30 | 2015-06-05 | 5 | 21 | 190 | 59.4333 | 1
2015-06-05 21:45 | 2015-06-05 | 5 | 21 | 190 | 59.1833 | 1
2015-06-05 22:00 | 2015-06-05 | 5 | 22 | 194 | 58.9333 | 1
2015-06-05 22:15 | 2015-06-05 | 5 | 22 | 189 | 58.6833 | 1
2015-06-05 22:30 | 2015-06-05 | 5 | 22 | 194 | 58.4333 | 1
2015-06-05 22:45 | 2015-06-05 | 5 | 22 | 181 | 58.1833 | 1
2015-06-05 23:00 | 2015-06-05 | 5 | 23 | 188 | 58 | 1
2015-06-05 23:15 | 2015-06-05 | 5 | 23 | 184 | 58 | 1
2015-06-05 23:30 | 2015-06-05 | 5 | 23 | 180 | 58 | 1
2015-06-05 23:45 | 2015-06-05 | 5 | 23 | 187 | 58 | 1
2015-06-06 | 2015-06-06 | 6 | 0 | 183 | 57.9259 | 1
2015-06-06 00:15 | 2015-06-06 | 6 | 0 | 187 | 57.6481 | 1
2015-06-06 00:30 | 2015-06-06 | 6 | 0 | 191 | 57.3704 | 1
2015-06-06 00:45 | 2015-06-06 | 6 | 0 | 184 | 57.0926 | 1
2015-06-06 01:00 | 2015-06-06 | 6 | 1 | 181 | 58 | 1
2015-06-06 01:15 | 2015-06-06 | 6 | 1 | 182 | 58 | 1
2015-06-06 01:30 | 2015-06-06 | 6 | 1 | 178 | 58 | 1
2015-06-06 01:45 | 2015-06-06 | 6 | 1 | 178 | 58 | 1
2015-06-06 02:00 | 2015-06-06 | 6 | 2 | 173 | 58 | 1
2015-06-06 02:15 | 2015-06-06 | 6 | 2 | 188 | 58 | 1
2015-06-06 02:30 | 2015-06-06 | 6 | 2 | 174 | 58 | 1
2015-06-06 02:45 | 2015-06-06 | 6 | 2 | 170 | 58 | 1
2015-06-06 03:00 | 2015-06-06 | 6 | 3 | 160 | 57.8 | 1
2015-06-06 03:15 | 2015-06-06 | 6 | 3 | 162 | 57.05 | 1
2015-06-06 03:30 | 2015-06-06 | 6 | 3 | 158 | 57.35 | 1
2015-06-06 03:45 | 2015-06-06 | 6 | 3 | 153 | 57.725 | 1
2015-06-06 04:00 | 2015-06-06 | 6 | 4 | 166 | 58 | 1
2015-06-06 04:15 | 2015-06-06 | 6 | 4 | 160 | 58 | 1
2015-06-06 04:30 | 2015-06-06 | 6 | 4 | 150 | 58 | 1
2015-06-06 04:45 | 2015-06-06 | 6 | 4 | 151 | 58 | 1
2015-06-06 05:00 | 2015-06-06 | 6 | 5 | 151 | 58.0667 | 1
2015-06-06 05:15 | 2015-06-06 | 6 | 5 | 156 | 58.3167 | 1
2015-06-06 05:30 | 2015-06-06 | 6 | 5 | 158 | 58.5667 | 1
2015-06-06 05:45 | 2015-06-06 | 6 | 5 | 150 | 58.8167 | 1
2015-06-06 06:00 | 2015-06-06 | 6 | 6 | 149 | 59 | 1
2015-06-06 06:15 | 2015-06-06 | 6 | 6 | 149 | 59 | 1
2015-06-06 06:30 | 2015-06-06 | 6 | 6 | 150 | 59 | 1
2015-06-06 06:45 | 2015-06-06 | 6 | 6 | 154 | 59 | 1
2015-06-06 07:00 | 2015-06-06 | 6 | 7 | 159 | 59.5714 | 1
2015-06-06 07:15 | 2015-06-06 | 6 | 7 | 154 | 61.1087 | 1
2015-06-06 07:30 | 2015-06-06 | 6 | 7 | 148 | 61.4348 | 1
2015-06-06 07:45 | 2015-06-06 | 6 | 7 | 155 | 61.7609 | 1
2015-06-06 08:00 | 2015-06-06 | 6 | 8 | 150 | 62.2 | 1
2015-06-06 08:15 | 2015-06-06 | 6 | 8 | 175 | 62.95 | 1
2015-06-06 08:30 | 2015-06-06 | 6 | 8 | 176 | 63.7 | 1
2015-06-06 08:45 | 2015-06-06 | 6 | 8 | 169 | 64 | 1
2015-06-06 09:00 | 2015-06-06 | 6 | 9 | 181 | 64.1333 | 1
2015-06-06 09:15 | 2015-06-06 | 6 | 9 | 179 | 64.6333 | 1
2015-06-06 09:30 | 2015-06-06 | 6 | 9 | 192 | 65.1333 | 2
2015-06-06 09:45 | 2015-06-06 | 6 | 9 | 184 | 65.6333 | 2
2015-06-06 10:00 | 2015-06-06 | 6 | 10 | 183 | 66 | 2
2015-06-06 10:15 | 2015-06-06 | 6 | 10 | 189 | 66 | 2
2015-06-06 10:30 | 2015-06-06 | 6 | 10 | 184 | 66 | 2
2015-06-06 10:45 | 2015-06-06 | 6 | 10 | 190 | 66 | 2
2015-06-06 11:00 | 2015-06-06 | 6 | 11 | 187 | 66.1333 | 2
2015-06-06 11:15 | 2015-06-06 | 6 | 11 | 190 | 66.6333 | 2
2015-06-06 11:30 | 2015-06-06 | 6 | 11 | 201 | 67.1333 | 2
2015-06-06 11:45 | 2015-06-06 | 6 | 11 | 210 | 67.6333 | 2
2015-06-06 12:00 | 2015-06-06 | 6 | 12 | 206 | 68.1333 | 2
2015-06-06 12:15 | 2015-06-06 | 6 | 12 | 202 | 68.6333 | 2
2015-06-06 12:30 | 2015-06-06 | 6 | 12 | 199 | 69.1333 | 2
2015-06-06 12:45 | 2015-06-06 | 6 | 12 | 198 | 69.6333 | 2
2015-06-06 13:00 | 2015-06-06 | 6 | 13 | 213 | 70.1333 | 3
2015-06-06 13:15 | 2015-06-06 | 6 | 13 | 211 | 70.6333 | 3
2015-06-06 13:30 | 2015-06-06 | 6 | 13 | 202 | 71.1333 | 3
2015-06-06 13:45 | 2015-06-06 | 6 | 13 | 211 | 71.6333 | 3
2015-06-06 14:00 | 2015-06-06 | 6 | 14 | 213 | 72 | 3
2015-06-06 14:15 | 2015-06-06 | 6 | 14 | 219 | 72 | 3
2015-06-06 14:30 | 2015-06-06 | 6 | 14 | 207 | 72 | 3
2015-06-06 14:45 | 2015-06-06 | 6 | 14 | 223 | 72 | 3
2015-06-06 15:00 | 2015-06-06 | 6 | 15 | 214 | 71.8667 | 3
2015-06-06 15:15 | 2015-06-06 | 6 | 15 | 222 | 71.3667 | 3
2015-06-06 15:30 | 2015-06-06 | 6 | 15 | 213 | 70.8667 | 3
2015-06-06 15:45 | 2015-06-06 | 6 | 15 | 226 | 70.3667 | 3
2015-06-06 16:00 | 2015-06-06 | 6 | 16 | 216 | 69.9333 | 2
2015-06-06 16:15 | 2015-06-06 | 6 | 16 | 223 | 69.6833 | 2
2015-06-06 16:30 | 2015-06-06 | 6 | 16 | 222 | 69.4333 | 2
2015-06-06 16:45 | 2015-06-06 | 6 | 16 | 227 | 69.1833 | 2
2015-06-06 17:00 | 2015-06-06 | 6 | 17 | 222 | 68.7333 | 2
2015-06-06 17:15 | 2015-06-06 | 6 | 17 | 227 | 67.7333 | 2
2015-06-06 17:30 | 2015-06-06 | 6 | 17 | 224 | 66.7333 | 2
2015-06-06 17:45 | 2015-06-06 | 6 | 17 | 227 | 65.7333 | 2
2015-06-06 18:00 | 2015-06-06 | 6 | 18 | 223 | 64.8 | 1
2015-06-06 18:15 | 2015-06-06 | 6 | 18 | 214 | 64.05 | 1
2015-06-06 18:30 | 2015-06-06 | 6 | 18 | 219 | 63.3 | 1
2015-06-06 18:45 | 2015-06-06 | 6 | 18 | 225 | 62.55 | 1
2015-06-06 19:00 | 2015-06-06 | 6 | 19 | 215 | 61.9333 | 1
2015-06-06 19:15 | 2015-06-06 | 6 | 19 | 215 | 61.6833 | 1
2015-06-06 19:30 | 2015-06-06 | 6 | 19 | 210 | 61.4333 | 1
2015-06-06 19:45 | 2015-06-06 | 6 | 19 | 218 | 61.1833 | 1
2015-06-06 20:00 | 2015-06-06 | 6 | 20 | 206 | 60.9333 | 1
2015-06-06 20:15 | 2015-06-06 | 6 | 20 | 210 | 60.6833 | 1
2015-06-06 20:30 | 2015-06-06 | 6 | 20 | 207 | 60.4333 | 1
2015-06-06 20:45 | 2015-06-06 | 6 | 20 | 210 | 60.1833 | 1
2015-06-06 21:00 | 2015-06-06 | 6 | 21 | 191 | 59.9333 | 1
2015-06-06 21:15 | 2015-06-06 | 6 | 21 | 196 | 59.6833 | 1
2015-06-06 21:30 | 2015-06-06 | 6 | 21 | 190 | 59.4333 | 1
2015-06-06 21:45 | 2015-06-06 | 6 | 21 | 199 | 59.1833 | 1
2015-06-06 22:00 | 2015-06-06 | 6 | 22 | 185 | 58.9333 | 1
2015-06-06 22:15 | 2015-06-06 | 6 | 22 | 190 | 58.6833 | 1
2015-06-06 22:30 | 2015-06-06 | 6 | 22 | 189 | 58.4333 | 1
2015-06-06 22:45 | 2015-06-06 | 6 | 22 | 185 | 58.1833 | 1
2015-06-06 23:00 | 2015-06-06 | 6 | 23 | 190 | 58 | 1
2015-06-06 23:15 | 2015-06-06 | 6 | 23 | 189 | 58 | 1
2015-06-06 23:30 | 2015-06-06 | 6 | 23 | 179 | 58 | 1
2015-06-06 23:45 | 2015-06-06 | 6 | 23 | 181 | 58 | 1
2015-06-07 | 2015-06-07 | 7 | 0 | 194 | 57.9333 | 1
2015-06-07 00:15 | 2015-06-07 | 7 | 0 | 179 | 57.6833 | 1
2015-06-07 00:30 | 2015-06-07 | 7 | 0 | 188 | 57.4333 | 1
2015-06-07 00:45 | 2015-06-07 | 7 | 0 | 192 | 57.1833 | 1
2015-06-07 01:00 | 2015-06-07 | 7 | 1 | 175 | 57 | 1
2015-06-07 01:15 | 2015-06-07 | 7 | 1 | 187 | 57 | 1
2015-06-07 01:30 | 2015-06-07 | 7 | 1 | 182 | 57 | 1
2015-06-07 01:45 | 2015-06-07 | 7 | 1 | 179 | 57 | 1
2015-06-07 02:00 | 2015-06-07 | 7 | 2 | 181 | 58 | 1
2015-06-07 02:15 | 2015-06-07 | 7 | 2 | 176 | 58 | 1
2015-06-07 02:30 | 2015-06-07 | 7 | 2 | 186 | 58 | 1
2015-06-07 02:45 | 2015-06-07 | 7 | 2 | 172 | 58 | 1
2015-06-07 03:00 | 2015-06-07 | 7 | 3 | 180 | 58 | 1
2015-06-07 03:15 | 2015-06-07 | 7 | 3 | 182 | 58 | 1
2015-06-07 03:30 | 2015-06-07 | 7 | 3 | 178 | 58 | 1
2015-06-07 03:45 | 2015-06-07 | 7 | 3 | 181 | 58 | 1
2015-06-07 04:00 | 2015-06-07 | 7 | 4 | 175 | 58.0667 | 1
2015-06-07 04:15 | 2015-06-07 | 7 | 4 | 187 | 58.3167 | 1
2015-06-07 04:30 | 2015-06-07 | 7 | 4 | 176 | 58.5667 | 1
2015-06-07 04:45 | 2015-06-07 | 7 | 4 | 183 | 58.8167 | 1
2015-06-07 05:00 | 2015-06-07 | 7 | 5 | 179 | 59.0667 | 1
2015-06-07 05:15 | 2015-06-07 | 7 | 5 | 185 | 59.3167 | 1
2015-06-07 05:30 | 2015-06-07 | 7 | 5 | 176 | 59.5667 | 1
2015-06-07 05:45 | 2015-06-07 | 7 | 5 | 178 | 59.8167 | 1
2015-06-07 06:00 | 2015-06-07 | 7 | 6 | 181 | 60 | 1
2015-06-07 06:15 | 2015-06-07 | 7 | 6 | 177 | 60 | 1
2015-06-07 06:30 | 2015-06-07 | 7 | 6 | 178 | 60 | 1
2015-06-07 06:45 | 2015-06-07 | 7 | 6 | 179 | 60 | 1
2015-06-07 07:00 | 2015-06-07 | 7 | 7 | 192 | 60.0755 | 1
2015-06-07 07:15 | 2015-06-07 | 7 | 7 | 190 | 60.3585 | 1
2015-06-07 07:30 | 2015-06-07 | 7 | 7 | 194 | 60.6415 | 1
2015-06-07 07:45 | 2015-06-07 | 7 | 7 | 189 | 60.9245 | 1
2015-06-07 08:00 | 2015-06-07 | 7 | 8 | 200 | 61.1333 | 1
2015-06-07 08:15 | 2015-06-07 | 7 | 8 | 186 | 61.6333 | 1
2015-06-07 08:30 | 2015-06-07 | 7 | 8 | 196 | 62.1333 | 1
2015-06-07 08:45 | 2015-06-07 | 7 | 8 | 191 | 62.6333 | 1
2015-06-07 09:00 | 2015-06-07 | 7 | 9 | 196 | 63.0667 | 1
2015-06-07 09:15 | 2015-06-07 | 7 | 9 | 194 | 63.3167 | 1
2015-06-07 09:30 | 2015-06-07 | 7 | 9 | 192 | 63.5667 | 1
2015-06-07 09:45 | 2015-06-07 | 7 | 9 | 200 | 63.8167 | 1
2015-06-07 10:00 | 2015-06-07 | 7 | 10 | 203 | 64.1333 | 1
2015-06-07 10:15 | 2015-06-07 | 7 | 10 | 212 | 64.6333 | 1
2015-06-07 10:30 | 2015-06-07 | 7 | 10 | 203 | 65.1333 | 2
2015-06-07 10:45 | 2015-06-07 | 7 | 10 | 201 | 65.6333 | 2
2015-06-07 11:00 | 2015-06-07 | 7 | 11 | 208 | 66.2 | 2
2015-06-07 11:15 | 2015-06-07 | 7 | 11 | 210 | 66.95 | 2
2015-06-07 11:30 | 2015-06-07 | 7 | 11 | 214 | 67.7 | 2
2015-06-07 11:45 | 2015-06-07 | 7 | 11 | 209 | 68.45 | 2
2015-06-07 12:00 | 2015-06-07 | 7 | 12 | 210 | 69 | 2
2015-06-07 12:15 | 2015-06-07 | 7 | 12 | 211 | 69 | 2
2015-06-07 12:30 | 2015-06-07 | 7 | 12 | 214 | 69 | 2
2015-06-07 12:45 | 2015-06-07 | 7 | 12 | 215 | 69 | 2
2015-06-07 13:00 | 2015-06-07 | 7 | 13 | 223 | 68.9333 | 2
2015-06-07 13:15 | 2015-06-07 | 7 | 13 | 217 | 68.6833 | 2
2015-06-07 13:30 | 2015-06-07 | 7 | 13 | 229 | 68.4333 | 2
2015-06-07 13:45 | 2015-06-07 | 7 | 13 | 219 | 68.1833 | 2
2015-06-07 14:00 | 2015-06-07 | 7 | 14 | 235 | 67.9333 | 2
2015-06-07 14:15 | 2015-06-07 | 7 | 14 | 224 | 67.6833 | 2
2015-06-07 14:30 | 2015-06-07 | 7 | 14 | 243 | 67.4333 | 2
2015-06-07 14:45 | 2015-06-07 | 7 | 14 | 234 | 67.1833 | 2
2015-06-07 15:00 | 2015-06-07 | 7 | 15 | 249 | 66.9333 | 2
2015-06-07 15:15 | 2015-06-07 | 7 | 15 | 236 | 66.6833 | 2
2015-06-07 15:30 | 2015-06-07 | 7 | 15 | 255 | 66.4333 | 2
2015-06-07 15:45 | 2015-06-07 | 7 | 15 | 251 | 66.1833 | 2
2015-06-07 16:00 | 2015-06-07 | 7 | 16 | 256 | 65.8 | 2
2015-06-07 16:15 | 2015-06-07 | 7 | 16 | 259 | 65.05 | 2
2015-06-07 16:30 | 2015-06-07 | 7 | 16 | 259 | 64.3 | 1
2015-06-07 16:45 | 2015-06-07 | 7 | 16 | 256 | 63.55 | 1
2015-06-07 17:00 | 2015-06-07 | 7 | 17 | 269 | 62.9333 | 1
2015-06-07 17:15 | 2015-06-07 | 7 | 17 | 257 | 62.6833 | 1
2015-06-07 17:30 | 2015-06-07 | 7 | 17 | 258 | 62.4333 | 1
2015-06-07 17:45 | 2015-06-07 | 7 | 17 | 254 | 62.1833 | 1
2015-06-07 18:00 | 2015-06-07 | 7 | 18 | 243 | 61.8667 | 1
2015-06-07 18:15 | 2015-06-07 | 7 | 18 | 255 | 61.3667 | 1
2015-06-07 18:30 | 2015-06-07 | 7 | 18 | 244 | 60.8667 | 1
2015-06-07 18:45 | 2015-06-07 | 7 | 18 | 257 | 60.3667 | 1
2015-06-07 19:00 | 2015-06-07 | 7 | 19 | 234 | 59.8 | 1
2015-06-07 19:15 | 2015-06-07 | 7 | 19 | 240 | 59.05 | 1
2015-06-07 19:30 | 2015-06-07 | 7 | 19 | 233 | 58.3 | 1
2015-06-07 19:45 | 2015-06-07 | 7 | 19 | 239 | 57.55 | 1
2015-06-07 20:00 | 2015-06-07 | 7 | 20 | 230 | 56.9333 | 1
2015-06-07 20:15 | 2015-06-07 | 7 | 20 | 243 | 56.6833 | 1
2015-06-07 20:30 | 2015-06-07 | 7 | 20 | 224 | 56.4333 | 1
2015-06-07 20:45 | 2015-06-07 | 7 | 20 | 219 | 56.1833 | 1
2015-06-07 21:00 | 2015-06-07 | 7 | 21 | 217 | 56 | 1
2015-06-07 21:15 | 2015-06-07 | 7 | 21 | 213 | 56 | 1
2015-06-07 21:30 | 2015-06-07 | 7 | 21 | 198 | 56 | 1
2015-06-07 21:45 | 2015-06-07 | 7 | 21 | 203 | 56 | 1
2015-06-07 22:00 | 2015-06-07 | 7 | 22 | 205 | 56 | 1
2015-06-07 22:15 | 2015-06-07 | 7 | 22 | 206 | 56 | 1
2015-06-07 22:30 | 2015-06-07 | 7 | 22 | 200 | 56 | 1
2015-06-07 22:45 | 2015-06-07 | 7 | 22 | 203 | 56 | 1
2015-06-07 23:00 | 2015-06-07 | 7 | 23 | 197 | 55.9333 | 1
2015-06-07 23:15 | 2015-06-07 | 7 | 23 | 199 | 55.6833 | 1
2015-06-07 23:30 | 2015-06-07 | 7 | 23 | 204 | 55.4333 | 1
2015-06-07 23:45 | 2015-06-07 | 7 | 23 | 210 | 55.1833 | 1
2015-06-08 | 2015-06-08 | 1 | 0 | 195 | 55.0667 | 1
2015-06-08 00:15 | 2015-06-08 | 1 | 0 | 196 | 55.3167 | 1
2015-06-08 00:30 | 2015-06-08 | 1 | 0 | 193 | 55.5667 | 1
2015-06-08 00:45 | 2015-06-08 | 1 | 0 | 195 | 55.8167 | 1
2015-06-08 01:00 | 2015-06-08 | 1 | 1 | 195 | 55.9333 | 1
2015-06-08 01:15 | 2015-06-08 | 1 | 1 | 190 | 55.6833 | 1
2015-06-08 01:30 | 2015-06-08 | 1 | 1 | 199 | 55.4333 | 1
2015-06-08 01:45 | 2015-06-08 | 1 | 1 | 200 | 55.1833 | 1
2015-06-08 02:00 | 2015-06-08 | 1 | 2 | 187 | 55 | 1
2015-06-08 02:15 | 2015-06-08 | 1 | 2 | 189 | 55 | 1
2015-06-08 02:30 | 2015-06-08 | 1 | 2 | 199 | 55 | 1
2015-06-08 02:45 | 2015-06-08 | 1 | 2 | 182 | 55 | 1
2015-06-08 03:00 | 2015-06-08 | 1 | 3 | 194 | 55 | 1
2015-06-08 03:15 | 2015-06-08 | 1 | 3 | 187 | 55 | 1
2015-06-08 03:30 | 2015-06-08 | 1 | 3 | 194 | 55 | 1
2015-06-08 03:45 | 2015-06-08 | 1 | 3 | 199 | 55 | 1
2015-06-08 04:00 | 2015-06-08 | 1 | 4 | 185 | 55 | 1
2015-06-08 04:15 | 2015-06-08 | 1 | 4 | 180 | 55 | 1
2015-06-08 04:30 | 2015-06-08 | 1 | 4 | 186 | 55 | 1
2015-06-08 04:45 | 2015-06-08 | 1 | 4 | 191 | 55 | 1
2015-06-08 05:00 | 2015-06-08 | 1 | 5 | 182 | 55.0667 | 1
2015-06-08 05:15 | 2015-06-08 | 1 | 5 | 179 | 55.3167 | 1
2015-06-08 05:30 | 2015-06-08 | 1 | 5 | 188 | 55.5667 | 1
2015-06-08 05:45 | 2015-06-08 | 1 | 5 | 187 | 55.8167 | 1
2015-06-08 06:00 | 2015-06-08 | 1 | 6 | 181 | 56.3333 | 1
2015-06-08 06:15 | 2015-06-08 | 1 | 6 | 189 | 57.5833 | 1
2015-06-08 06:30 | 2015-06-08 | 1 | 6 | 192 | 58.8333 | 1
2015-06-08 06:45 | 2015-06-08 | 1 | 6 | 183 | 60.0833 | 1
2015-06-08 07:00 | 2015-06-08 | 1 | 7 | 188 | 61.2667 | 1
2015-06-08 07:15 | 2015-06-08 | 1 | 7 | 195 | 62.2667 | 1
2015-06-08 07:30 | 2015-06-08 | 1 | 7 | 193 | 63.2667 | 1
2015-06-08 07:45 | 2015-06-08 | 1 | 7 | 199 | 64.2667 | 1
2015-06-08 08:00 | 2015-06-08 | 1 | 8 | 195 | 65.1333 | 2
2015-06-08 08:15 | 2015-06-08 | 1 | 8 | 205 | 65.6333 | 2
2015-06-08 08:30 | 2015-06-08 | 1 | 8 | 204 | 66.1333 | 2
2015-06-08 08:45 | 2015-06-08 | 1 | 8 | 213 | 66.6333 | 2
2015-06-08 09:00 | 2015-06-08 | 1 | 9 | 224 | 67.3333 | 2
2015-06-08 09:15 | 2015-06-08 | 1 | 9 | 224 | 68.5833 | 2
2015-06-08 09:30 | 2015-06-08 | 1 | 9 | 230 | 69.8333 | 2
2015-06-08 09:45 | 2015-06-08 | 1 | 9 | 234 | 71.0833 | 3
2015-06-08 10:00 | 2015-06-08 | 1 | 10 | 241 | 72 | 3
2015-06-08 10:15 | 2015-06-08 | 1 | 10 | 247 | 72 | 3
2015-06-08 10:30 | 2015-06-08 | 1 | 10 | 259 | 72 | 3
2015-06-08 10:45 | 2015-06-08 | 1 | 10 | 254 | 72 | 3
2015-06-08 11:00 | 2015-06-08 | 1 | 11 | 275 | 72.2 | 3
2015-06-08 11:15 | 2015-06-08 | 1 | 11 | 263 | 72.95 | 3
2015-06-08 11:30 | 2015-06-08 | 1 | 11 | 284 | 73.7 | 3
2015-06-08 11:45 | 2015-06-08 | 1 | 11 | 277 | 74.45 | 3
2015-06-08 12:00 | 2015-06-08 | 1 | 12 | 287 | 75.5333 | 4
2015-06-08 12:15 | 2015-06-08 | 1 | 12 | 286 | 77.5333 | 4
2015-06-08 12:30 | 2015-06-08 | 1 | 12 | 296 | 79.5333 | 4
2015-06-08 12:45 | 2015-06-08 | 1 | 12 | 294 | 81.5333 | 5
2015-06-08 13:00 | 2015-06-08 | 1 | 13 | 294 | 82.8667 | 5
2015-06-08 13:15 | 2015-06-08 | 1 | 13 | 299 | 82.3667 | 5
2015-06-08 13:30 | 2015-06-08 | 1 | 13 | 291 | 81.8667 | 5
2015-06-08 13:45 | 2015-06-08 | 1 | 13 | 302 | 81.3667 | 5
2015-06-08 14:00 | 2015-06-08 | 1 | 14 | 298 | 80.9333 | 5
2015-06-08 14:15 | 2015-06-08 | 1 | 14 | 294 | 80.6833 | 5
2015-06-08 14:30 | 2015-06-08 | 1 | 14 | 303 | 80.4333 | 5
2015-06-08 14:45 | 2015-06-08 | 1 | 14 | 298 | 80.1833 | 5
2015-06-08 15:00 | 2015-06-08 | 1 | 15 | 307 | 80.1333 | 5
2015-06-08 15:15 | 2015-06-08 | 1 | 15 | 315 | 80.6333 | 5
2015-06-08 15:30 | 2015-06-08 | 1 | 15 | 321 | 81.1333 | 5
2015-06-08 15:45 | 2015-06-08 | 1 | 15 | 322 | 81.6333 | 5
2015-06-08 16:00 | 2015-06-08 | 1 | 16 | 320 | 81.8667 | 5
2015-06-08 16:15 | 2015-06-08 | 1 | 16 | 321 | 81.3667 | 5
2015-06-08 16:30 | 2015-06-08 | 1 | 16 | 318 | 80.8667 | 5
2015-06-08 16:45 | 2015-06-08 | 1 | 16 | 315 | 80.3667 | 5
2015-06-08 17:00 | 2015-06-08 | 1 | 17 | 316 | 79.7333 | 4
2015-06-08 17:15 | 2015-06-08 | 1 | 17 | 316 | 78.7333 | 4
2015-06-08 17:30 | 2015-06-08 | 1 | 17 | 314 | 77.7333 | 4
2015-06-08 17:45 | 2015-06-08 | 1 | 17 | 318 | 76.7333 | 4
2015-06-08 18:00 | 2015-06-08 | 1 | 18 | 316 | 75.5333 | 4
2015-06-08 18:15 | 2015-06-08 | 1 | 18 | 317 | 73.7833 | 3
2015-06-08 18:30 | 2015-06-08 | 1 | 18 | 316 | 72.0333 | 3
2015-06-08 18:45 | 2015-06-08 | 1 | 18 | 310 | 70.2833 | 3
2015-06-08 19:00 | 2015-06-08 | 1 | 19 | 305 | 68.5333 | 2
2015-06-08 19:15 | 2015-06-08 | 1 | 19 | 289 | 66.7833 | 2
2015-06-08 19:30 | 2015-06-08 | 1 | 19 | 286 | 65.0333 | 2
2015-06-08 19:45 | 2015-06-08 | 1 | 19 | 280 | 63.2833 | 1
2015-06-08 20:00 | 2015-06-08 | 1 | 20 | 282 | 61.9333 | 1
2015-06-08 20:15 | 2015-06-08 | 1 | 20 | 279 | 61.6833 | 1
2015-06-08 20:30 | 2015-06-08 | 1 | 20 | 264 | 61.4333 | 1
2015-06-08 20:45 | 2015-06-08 | 1 | 20 | 272 | 61.1833 | 1
2015-06-08 21:00 | 2015-06-08 | 1 | 21 | 259 | 60.9333 | 1
2015-06-08 21:15 | 2015-06-08 | 1 | 21 | 253 | 60.6833 | 1
2015-06-08 21:30 | 2015-06-08 | 1 | 21 | 239 | 60.4333 | 1
2015-06-08 21:45 | 2015-06-08 | 1 | 21 | 231 | 60.1833 | 1
2015-06-08 22:00 | 2015-06-08 | 1 | 22 | 236 | 59.8667 | 1
2015-06-08 22:15 | 2015-06-08 | 1 | 22 | 227 | 59.3667 | 1
2015-06-08 22:30 | 2015-06-08 | 1 | 22 | 234 | 58.8667 | 1
2015-06-08 22:45 | 2015-06-08 | 1 | 22 | 217 | 58.3667 | 1
2015-06-08 23:00 | 2015-06-08 | 1 | 23 | 234 | 57.9333 | 1
2015-06-08 23:15 | 2015-06-08 | 1 | 23 | 219 | 57.6833 | 1
2015-06-08 23:30 | 2015-06-08 | 1 | 23 | 217 | 57.4333 | 1
2015-06-08 23:45 | 2015-06-08 | 1 | 23 | 206 | 57.1833 | 1
2015-06-09 | 2015-06-09 | 2 | 0 | 207 | 56.9333 | 1
2015-06-09 00:15 | 2015-06-09 | 2 | 0 | 209 | 56.6833 | 1
2015-06-09 00:30 | 2015-06-09 | 2 | 0 | 204 | 56.4333 | 1
2015-06-09 00:45 | 2015-06-09 | 2 | 0 | 210 | 56.1833 | 1
2015-06-09 01:00 | 2015-06-09 | 2 | 1 | 203 | 55.9333 | 1
2015-06-09 01:15 | 2015-06-09 | 2 | 1 | 204 | 55.6833 | 1
2015-06-09 01:30 | 2015-06-09 | 2 | 1 | 202 | 55.4333 | 1
2015-06-09 01:45 | 2015-06-09 | 2 | 1 | 202 | 55.1833 | 1
2015-06-09 02:00 | 2015-06-09 | 2 | 2 | 209 | 55 | 1
2015-06-09 02:15 | 2015-06-09 | 2 | 2 | 194 | 55 | 1
2015-06-09 02:30 | 2015-06-09 | 2 | 2 | 199 | 55 | 1
2015-06-09 02:45 | 2015-06-09 | 2 | 2 | 197 | 55 | 1
2015-06-09 03:00 | 2015-06-09 | 2 | 3 | 195 | 55 | 1
2015-06-09 03:15 | 2015-06-09 | 2 | 3 | 194 | 55 | 1
2015-06-09 03:30 | 2015-06-09 | 2 | 3 | 194 | 55 | 1
2015-06-09 03:45 | 2015-06-09 | 2 | 3 | 187 | 55 | 1
2015-06-09 04:00 | 2015-06-09 | 2 | 4 | 194 | 54.9333 | 1
2015-06-09 04:15 | 2015-06-09 | 2 | 4 | 189 | 54.6833 | 1
2015-06-09 04:30 | 2015-06-09 | 2 | 4 | 185 | 54.4333 | 1
2015-06-09 04:45 | 2015-06-09 | 2 | 4 | 183 | 54.1833 | 1
2015-06-09 05:00 | 2015-06-09 | 2 | 5 | 188 | 54.1333 | 1
2015-06-09 05:15 | 2015-06-09 | 2 | 5 | 189 | 54.6333 | 1
2015-06-09 05:30 | 2015-06-09 | 2 | 5 | 180 | 55.1333 | 1
2015-06-09 05:45 | 2015-06-09 | 2 | 5 | 187 | 55.6333 | 1
2015-06-09 06:00 | 2015-06-09 | 2 | 6 | 188 | 56.3333 | 1
2015-06-09 06:15 | 2015-06-09 | 2 | 6 | 179 | 57.5833 | 1
2015-06-09 06:30 | 2015-06-09 | 2 | 6 | 188 | 58.8333 | 1
2015-06-09 06:45 | 2015-06-09 | 2 | 6 | 190 | 60.0833 | 1
2015-06-09 07:00 | 2015-06-09 | 2 | 7 | 191 | 61.1333 | 1
2015-06-09 07:15 | 2015-06-09 | 2 | 7 | 190 | 61.6333 | 1
2015-06-09 07:30 | 2015-06-09 | 2 | 7 | 195 | 62.1333 | 1
2015-06-09 07:45 | 2015-06-09 | 2 | 7 | 192 | 62.6333 | 1
2015-06-09 08:00 | 2015-06-09 | 2 | 8 | 211 | 63.2 | 1
2015-06-09 08:15 | 2015-06-09 | 2 | 8 | 196 | 63.95 | 1
2015-06-09 08:30 | 2015-06-09 | 2 | 8 | 208 | 64.7 | 1
2015-06-09 08:45 | 2015-06-09 | 2 | 8 | 223 | 65.45 | 2
2015-06-09 09:00 | 2015-06-09 | 2 | 9 | 218 | 66.0667 | 2
2015-06-09 09:15 | 2015-06-09 | 2 | 9 | 232 | 66.3167 | 2
2015-06-09 09:30 | 2015-06-09 | 2 | 9 | 242 | 66.5667 | 2
2015-06-09 09:45 | 2015-06-09 | 2 | 9 | 250 | 66.8167 | 2
2015-06-09 10:00 | 2015-06-09 | 2 | 10 | 245 | 67.0667 | 2
2015-06-09 10:15 | 2015-06-09 | 2 | 10 | 248 | 67.3167 | 2
2015-06-09 10:30 | 2015-06-09 | 2 | 10 | 255 | 67.5667 | 2
2015-06-09 10:45 | 2015-06-09 | 2 | 10 | 257 | 67.8167 | 2
2015-06-09 11:00 | 2015-06-09 | 2 | 11 | 250 | 68.1333 | 2
2015-06-09 11:15 | 2015-06-09 | 2 | 11 | 250 | 68.6333 | 2
2015-06-09 11:30 | 2015-06-09 | 2 | 11 | 248 | 69.1333 | 2
2015-06-09 11:45 | 2015-06-09 | 2 | 11 | 250 | 69.6333 | 2
2015-06-09 12:00 | 2015-06-09 | 2 | 12 | 258 | 70.2667 | 3
2015-06-09 12:15 | 2015-06-09 | 2 | 12 | 250 | 71.2667 | 3
2015-06-09 12:30 | 2015-06-09 | 2 | 12 | 261 | 72.2667 | 3
2015-06-09 12:45 | 2015-06-09 | 2 | 12 | 253 | 73.2667 | 3
2015-06-09 13:00 | 2015-06-09 | 2 | 13 | 266 | 74.0952 | 3
2015-06-09 13:15 | 2015-06-09 | 2 | 13 | 261 | 74.4524 | 3
2015-06-09 13:30 | 2015-06-09 | 2 | 13 | 270 | 74.8095 | 3
2015-06-09 13:45 | 2015-06-09 | 2 | 13 | 263 | 74.6111 | 3
2015-06-09 14:00 | 2015-06-09 | 2 | 14 | 277 | 73.9333 | 3
2015-06-09 14:15 | 2015-06-09 | 2 | 14 | 269 | 73.6833 | 3
2015-06-09 14:30 | 2015-06-09 | 2 | 14 | 285 | 73.4333 | 3
2015-06-09 14:45 | 2015-06-09 | 2 | 14 | 279 | 73.1833 | 3
2015-06-09 15:00 | 2015-06-09 | 2 | 15 | 267 | 72.3793 | 3
2015-06-09 15:15 | 2015-06-09 | 2 | 15 | 278 | 70.0517 | 3
2015-06-09 15:30 | 2015-06-09 | 2 | 15 | 284 | 67.7241 | 2
2015-06-09 15:45 | 2015-06-09 | 2 | 15 | 293 | 65.3966 | 2
2015-06-09 16:00 | 2015-06-09 | 2 | 16 | 277 | 66.0667 | 2
2015-06-09 16:15 | 2015-06-09 | 2 | 16 | 284 | 66.3167 | 2
2015-06-09 16:30 | 2015-06-09 | 2 | 16 | 292 | 66.5667 | 2
2015-06-09 16:45 | 2015-06-09 | 2 | 16 | 278 | 66.8167 | 2
2015-06-09 17:00 | 2015-06-09 | 2 | 17 | 267 | 66.9333 | 2
2015-06-09 17:15 | 2015-06-09 | 2 | 17 | 265 | 66.6833 | 2
2015-06-09 17:30 | 2015-06-09 | 2 | 17 | 262 | 66.4333 | 2
2015-06-09 17:45 | 2015-06-09 | 2 | 17 | 258 | 66.1833 | 2
2015-06-09 18:00 | 2015-06-09 | 2 | 18 | 253 | 66.0667 | 2
2015-06-09 18:15 | 2015-06-09 | 2 | 18 | 245 | 66.3167 | 2
2015-06-09 18:30 | 2015-06-09 | 2 | 18 | 238 | 66.5667 | 2
2015-06-09 18:45 | 2015-06-09 | 2 | 18 | 249 | 66.8167 | 2
2015-06-09 19:00 | 2015-06-09 | 2 | 19 | 233 | 66.9333 | 2
2015-06-09 19:15 | 2015-06-09 | 2 | 19 | 232 | 66.6833 | 2
2015-06-09 19:30 | 2015-06-09 | 2 | 19 | 234 | 66.4333 | 2
2015-06-09 19:45 | 2015-06-09 | 2 | 19 | 226 | 66.1833 | 2
2015-06-09 20:00 | 2015-06-09 | 2 | 20 | 227 | 66 | 2
2015-06-09 20:15 | 2015-06-09 | 2 | 20 | 228 | 66 | 2
2015-06-09 20:30 | 2015-06-09 | 2 | 20 | 232 | 66 | 2
2015-06-09 20:45 | 2015-06-09 | 2 | 20 | 232 | 66 | 2
2015-06-09 21:00 | 2015-06-09 | 2 | 21 | 220 | 65.8667 | 2
2015-06-09 21:15 | 2015-06-09 | 2 | 21 | 215 | 65.3667 | 2
2015-06-09 21:30 | 2015-06-09 | 2 | 21 | 211 | 64.8667 | 1
2015-06-09 21:45 | 2015-06-09 | 2 | 21 | 215 | 64.3667 | 1
2015-06-09 22:00 | 2015-06-09 | 2 | 22 | 214 | 64 | 1
2015-06-09 22:15 | 2015-06-09 | 2 | 22 | 210 | 64 | 1
2015-06-09 22:30 | 2015-06-09 | 2 | 22 | 211 | 64 | 1
2015-06-09 22:45 | 2015-06-09 | 2 | 22 | 215 | 64 | 1
2015-06-09 23:00 | 2015-06-09 | 2 | 23 | 214 | 64.0667 | 1
2015-06-09 23:15 | 2015-06-09 | 2 | 23 | 221 | 64.3167 | 1
2015-06-09 23:30 | 2015-06-09 | 2 | 23 | 210 | 64.5667 | 1
2015-06-09 23:45 | 2015-06-09 | 2 | 23 | 209 | 64.8167 | 1
2015-06-10 | 2015-06-10 | 3 | 0 | 219 | 64.931 | 1
2015-06-10 00:15 | 2015-06-10 | 3 | 0 | 200 | 64.6724 | 1
2015-06-10 00:30 | 2015-06-10 | 3 | 0 | 208 | 64.4138 | 1
2015-06-10 00:45 | 2015-06-10 | 3 | 0 | 203 | 64.1552 | 1
2015-06-10 01:00 | 2015-06-10 | 3 | 1 | 202 | 63 | 1
2015-06-10 01:15 | 2015-06-10 | 3 | 1 | 202 | 63 | 1
2015-06-10 01:30 | 2015-06-10 | 3 | 1 | 201 | 63 | 1
2015-06-10 01:45 | 2015-06-10 | 3 | 1 | 203 | 63 | 1
2015-06-10 02:00 | 2015-06-10 | 3 | 2 | 202 | 62.8 | 1
2015-06-10 02:15 | 2015-06-10 | 3 | 2 | 197 | 62.05 | 1
2015-06-10 02:30 | 2015-06-10 | 3 | 2 | 205 | 61.3 | 1
2015-06-10 02:45 | 2015-06-10 | 3 | 2 | 199 | 60.55 | 1
2015-06-10 03:00 | 2015-06-10 | 3 | 3 | 205 | 59.8667 | 1
2015-06-10 03:15 | 2015-06-10 | 3 | 3 | 202 | 59.3667 | 1
2015-06-10 03:30 | 2015-06-10 | 3 | 3 | 196 | 58.8667 | 1
2015-06-10 03:45 | 2015-06-10 | 3 | 3 | 206 | 58.3667 | 1
2015-06-10 04:00 | 2015-06-10 | 3 | 4 | 192 | 58.0667 | 1
2015-06-10 04:15 | 2015-06-10 | 3 | 4 | 202 | 58.3167 | 1
2015-06-10 04:30 | 2015-06-10 | 3 | 4 | 203 | 58.5667 | 1
2015-06-10 04:45 | 2015-06-10 | 3 | 4 | 204 | 58.8167 | 1
2015-06-10 05:00 | 2015-06-10 | 3 | 5 | 198 | 59.0667 | 1
2015-06-10 05:15 | 2015-06-10 | 3 | 5 | 194 | 59.3167 | 1
2015-06-10 05:30 | 2015-06-10 | 3 | 5 | 198 | 59.5667 | 1
2015-06-10 05:45 | 2015-06-10 | 3 | 5 | 190 | 59.8167 | 1
2015-06-10 06:00 | 2015-06-10 | 3 | 6 | 197 | 60 | 1
2015-06-10 06:15 | 2015-06-10 | 3 | 6 | 188 | 60 | 1
2015-06-10 06:30 | 2015-06-10 | 3 | 6 | 192 | 60 | 1
2015-06-10 06:45 | 2015-06-10 | 3 | 6 | 195 | 60 | 1
2015-06-10 07:00 | 2015-06-10 | 3 | 7 | 187 | 60.0667 | 1
2015-06-10 07:15 | 2015-06-10 | 3 | 7 | 188 | 60.3167 | 1
2015-06-10 07:30 | 2015-06-10 | 3 | 7 | 190 | 60.5667 | 1
2015-06-10 07:45 | 2015-06-10 | 3 | 7 | 188 | 60.8167 | 1
2015-06-10 08:00 | 2015-06-10 | 3 | 8 | 196 | 61.1333 | 1
2015-06-10 08:15 | 2015-06-10 | 3 | 8 | 205 | 61.6333 | 1
2015-06-10 08:30 | 2015-06-10 | 3 | 8 | 197 | 62.1333 | 1
2015-06-10 08:45 | 2015-06-10 | 3 | 8 | 199 | 62.6333 | 1
2015-06-10 09:00 | 2015-06-10 | 3 | 9 | 214 | 63.1333 | 1
2015-06-10 09:15 | 2015-06-10 | 3 | 9 | 216 | 63.6333 | 1
2015-06-10 09:30 | 2015-06-10 | 3 | 9 | 223 | 64.1333 | 1
2015-06-10 09:45 | 2015-06-10 | 3 | 9 | 222 | 64.6333 | 1
2015-06-10 10:00 | 2015-06-10 | 3 | 10 | 225 | 65.0667 | 2
2015-06-10 10:15 | 2015-06-10 | 3 | 10 | 223 | 65.3167 | 2
2015-06-10 10:30 | 2015-06-10 | 3 | 10 | 223 | 65.5667 | 2
2015-06-10 10:45 | 2015-06-10 | 3 | 10 | 219 | 65.8167 | 2
2015-06-10 11:00 | 2015-06-10 | 3 | 11 | 222 | 66.0667 | 2
2015-06-10 11:15 | 2015-06-10 | 3 | 11 | 228 | 66.3167 | 2
2015-06-10 11:30 | 2015-06-10 | 3 | 11 | 229 | 66.5667 | 2
2015-06-10 11:45 | 2015-06-10 | 3 | 11 | 227 | 66.8167 | 2
2015-06-10 12:00 | 2015-06-10 | 3 | 12 | 231 | 66.7333 | 2
2015-06-10 12:15 | 2015-06-10 | 3 | 12 | 220 | 65.7333 | 2
2015-06-10 12:30 | 2015-06-10 | 3 | 12 | 221 | 64.7333 | 1
2015-06-10 12:45 | 2015-06-10 | 3 | 12 | 225 | 63.7333 | 1
2015-06-10 13:00 | 2015-06-10 | 3 | 13 | 218 | 62.9333 | 1
2015-06-10 13:15 | 2015-06-10 | 3 | 13 | 229 | 62.6833 | 1
2015-06-10 13:30 | 2015-06-10 | 3 | 13 | 222 | 62.4333 | 1
2015-06-10 13:45 | 2015-06-10 | 3 | 13 | 223 | 62.1833 | 1
2015-06-10 14:00 | 2015-06-10 | 3 | 14 | 225 | 61.9333 | 1
2015-06-10 14:15 | 2015-06-10 | 3 | 14 | 225 | 61.6833 | 1
2015-06-10 14:30 | 2015-06-10 | 3 | 14 | 223 | 61.4333 | 1
2015-06-10 14:45 | 2015-06-10 | 3 | 14 | 223 | 61.1833 | 1
2015-06-10 15:00 | 2015-06-10 | 3 | 15 | 228 | 61.2 | 1
2015-06-10 15:15 | 2015-06-10 | 3 | 15 | 226 | 61.95 | 1
2015-06-10 15:30 | 2015-06-10 | 3 | 15 | 222 | 62.7 | 1
2015-06-10 15:45 | 2015-06-10 | 3 | 15 | 219 | 63.45 | 1
2015-06-10 16:00 | 2015-06-10 | 3 | 16 | 228 | 63.9333 | 1
2015-06-10 16:15 | 2015-06-10 | 3 | 16 | 230 | 63.6833 | 1
2015-06-10 16:30 | 2015-06-10 | 3 | 16 | 229 | 63.4333 | 1
2015-06-10 16:45 | 2015-06-10 | 3 | 16 | 238 | 63.1833 | 1
2015-06-10 17:00 | 2015-06-10 | 3 | 17 | 229 | 62.9333 | 1
2015-06-10 17:15 | 2015-06-10 | 3 | 17 | 231 | 62.6833 | 1
2015-06-10 17:30 | 2015-06-10 | 3 | 17 | 222 | 62.4333 | 1
2015-06-10 17:45 | 2015-06-10 | 3 | 17 | 221 | 62.1833 | 1
2015-06-10 18:00 | 2015-06-10 | 3 | 18 | 222 | 61.8667 | 1
2015-06-10 18:15 | 2015-06-10 | 3 | 18 | 215 | 61.3667 | 1
2015-06-10 18:30 | 2015-06-10 | 3 | 18 | 210 | 60.8667 | 1
2015-06-10 18:45 | 2015-06-10 | 3 | 18 | 203 | 60.3667 | 1
2015-06-10 19:00 | 2015-06-10 | 3 | 19 | 211 | 59.8 | 1
2015-06-10 19:15 | 2015-06-10 | 3 | 19 | 203 | 59.05 | 1
2015-06-10 19:30 | 2015-06-10 | 3 | 19 | 200 | 58.3 | 1
2015-06-10 19:45 | 2015-06-10 | 3 | 19 | 203 | 57.55 | 1
2015-06-10 20:00 | 2015-06-10 | 3 | 20 | 199 | 57 | 1
2015-06-10 20:15 | 2015-06-10 | 3 | 20 | 201 | 57 | 1
2015-06-10 20:30 | 2015-06-10 | 3 | 20 | 195 | 57 | 1
2015-06-10 20:45 | 2015-06-10 | 3 | 20 | 196 | 57 | 1
2015-06-10 21:00 | 2015-06-10 | 3 | 21 | 197 | 57 | 1
2015-06-10 21:15 | 2015-06-10 | 3 | 21 | 185 | 57 | 1
2015-06-10 21:30 | 2015-06-10 | 3 | 21 | 185 | 57 | 1
2015-06-10 21:45 | 2015-06-10 | 3 | 21 | 187 | 57 | 1
2015-06-10 22:00 | 2015-06-10 | 3 | 22 | 178 | 57 | 1
2015-06-10 22:15 | 2015-06-10 | 3 | 22 | 189 | 57 | 1
2015-06-10 22:30 | 2015-06-10 | 3 | 22 | 186 | 57 | 1
2015-06-10 22:45 | 2015-06-10 | 3 | 22 | 179 | 57 | 1
2015-06-10 23:00 | 2015-06-10 | 3 | 23 | 184 | 56.9333 | 1
2015-06-10 23:15 | 2015-06-10 | 3 | 23 | 183 | 56.6833 | 1
2015-06-10 23:30 | 2015-06-10 | 3 | 23 | 177 | 56.4333 | 1
2015-06-10 23:45 | 2015-06-10 | 3 | 23 | 177 | 56.1833 | 1
2015-06-11 | 2015-06-11 | 4 | 0 | 170 | 56 | 1
2015-06-11 00:15 | 2015-06-11 | 4 | 0 | 181 | 56 | 1
2015-06-11 00:30 | 2015-06-11 | 4 | 0 | 169 | 56 | 1
2015-06-11 00:45 | 2015-06-11 | 4 | 0 | 172 | 56 | 1
2015-06-11 01:00 | 2015-06-11 | 4 | 1 | 168 | 55.8571 | 1
2015-06-11 01:15 | 2015-06-11 | 4 | 1 | 165 | 55.3214 | 1
2015-06-11 01:30 | 2015-06-11 | 4 | 1 | 164 | 55 | 1
2015-06-11 01:45 | 2015-06-11 | 4 | 1 | 164 | 55 | 1
2015-06-11 02:00 | 2015-06-11 | 4 | 2 | 167 | 55 | 1
2015-06-11 02:15 | 2015-06-11 | 4 | 2 | 167 | 55 | 1
2015-06-11 02:30 | 2015-06-11 | 4 | 2 | 166 | 55 | 1
2015-06-11 02:45 | 2015-06-11 | 4 | 2 | 160 | 55 | 1
2015-06-11 03:00 | 2015-06-11 | 4 | 3 | 167 | 55 | 1
2015-06-11 03:15 | 2015-06-11 | 4 | 3 | 164 | 55 | 1
2015-06-11 03:30 | 2015-06-11 | 4 | 3 | 163 | 55 | 1
2015-06-11 03:45 | 2015-06-11 | 4 | 3 | 159 | 55 | 1
2015-06-11 04:00 | 2015-06-11 | 4 | 4 | 163 | 55 | 1
2015-06-11 04:15 | 2015-06-11 | 4 | 4 | 163 | 55 | 1
2015-06-11 04:30 | 2015-06-11 | 4 | 4 | 163 | 55 | 1
2015-06-11 04:45 | 2015-06-11 | 4 | 4 | 164 | 55 | 1
2015-06-11 05:00 | 2015-06-11 | 4 | 5 | 163 | 55.0667 | 1
2015-06-11 05:15 | 2015-06-11 | 4 | 5 | 164 | 55.3167 | 1
2015-06-11 05:30 | 2015-06-11 | 4 | 5 | 162 | 55.5667 | 1
2015-06-11 05:45 | 2015-06-11 | 4 | 5 | 161 | 55.8167 | 1
2015-06-11 06:00 | 2015-06-11 | 4 | 6 | 165 | 56.069 | 1
2015-06-11 06:15 | 2015-06-11 | 4 | 6 | 170 | 56.3276 | 1
2015-06-11 06:30 | 2015-06-11 | 4 | 6 | 166 | 56.5862 | 1
2015-06-11 06:45 | 2015-06-11 | 4 | 6 | 168 | 56.8448 | 1
2015-06-11 07:00 | 2015-06-11 | 4 | 7 | 166 | 58.0851 | 1
2015-06-11 07:15 | 2015-06-11 | 4 | 7 | 169 | 58.4043 | 1
2015-06-11 07:30 | 2015-06-11 | 4 | 7 | 167 | 58.7234 | 1
2015-06-11 07:45 | 2015-06-11 | 4 | 7 | 163 | 59 | 1
2015-06-11 08:00 | 2015-06-11 | 4 | 8 | 170 | 59.1379 | 1
2015-06-11 08:15 | 2015-06-11 | 4 | 8 | 179 | 59.6552 | 1
2015-06-11 08:30 | 2015-06-11 | 4 | 8 | 183 | 60.1724 | 1
2015-06-11 08:45 | 2015-06-11 | 4 | 8 | 183 | 60.6897 | 1
2015-06-11 09:00 | 2015-06-11 | 4 | 9 | 186 | 61 | 1
2015-06-11 09:15 | 2015-06-11 | 4 | 9 | 200 | 61.625 | 1
2015-06-11 09:30 | 2015-06-11 | 4 | 9 | 203 | 62.5625 | 1
2015-06-11 09:45 | 2015-06-11 | 4 | 9 | 207 | 63.4211 | 1
2015-06-11 10:00 | 2015-06-11 | 4 | 10 | 216 | 64.2667 | 1
2015-06-11 10:15 | 2015-06-11 | 4 | 10 | 218 | 65.2667 | 2
2015-06-11 10:30 | 2015-06-11 | 4 | 10 | 224 | 66.2667 | 2
2015-06-11 10:45 | 2015-06-11 | 4 | 10 | 220 | 67.2667 | 2
2015-06-11 11:00 | 2015-06-11 | 4 | 11 | 226 | 68.1333 | 2
2015-06-11 11:15 | 2015-06-11 | 4 | 11 | 225 | 68.6333 | 2
2015-06-11 11:30 | 2015-06-11 | 4 | 11 | 225 | 69.1333 | 2
2015-06-11 11:45 | 2015-06-11 | 4 | 11 | 214 | 69.6333 | 2
2015-06-11 12:00 | 2015-06-11 | 4 | 12 | 228 | 70.0667 | 3
2015-06-11 12:15 | 2015-06-11 | 4 | 12 | 224 | 70.3167 | 3
2015-06-11 12:30 | 2015-06-11 | 4 | 12 | 235 | 70.5667 | 3
2015-06-11 12:45 | 2015-06-11 | 4 | 12 | 213 | 70.8167 | 3
2015-06-11 13:00 | 2015-06-11 | 4 | 13 | 232 | 70.9333 | 3
2015-06-11 13:15 | 2015-06-11 | 4 | 13 | 219 | 70.6833 | 3
2015-06-11 13:30 | 2015-06-11 | 4 | 13 | 232 | 70.4333 | 3
2015-06-11 13:45 | 2015-06-11 | 4 | 13 | 232 | 70.1833 | 3
2015-06-11 14:00 | 2015-06-11 | 4 | 14 | 233 | 69.8667 | 2
2015-06-11 14:15 | 2015-06-11 | 4 | 14 | 234 | 69.3667 | 2
2015-06-11 14:30 | 2015-06-11 | 4 | 14 | 246 | 68.8667 | 2
2015-06-11 14:45 | 2015-06-11 | 4 | 14 | 236 | 68.3667 | 2
2015-06-11 15:00 | 2015-06-11 | 4 | 15 | 248 | 68 | 2
2015-06-11 15:15 | 2015-06-11 | 4 | 15 | 239 | 68 | 2
2015-06-11 15:30 | 2015-06-11 | 4 | 15 | 247 | 68 | 2
2015-06-11 15:45 | 2015-06-11 | 4 | 15 | 255 | 68 | 2
2015-06-11 16:00 | 2015-06-11 | 4 | 16 | 249 | 67.9333 | 2
2015-06-11 16:15 | 2015-06-11 | 4 | 16 | 253 | 67.6833 | 2
2015-06-11 16:30 | 2015-06-11 | 4 | 16 | 249 | 67.4333 | 2
2015-06-11 16:45 | 2015-06-11 | 4 | 16 | 244 | 67.1833 | 2
2015-06-11 17:00 | 2015-06-11 | 4 | 17 | 252 | 66.7333 | 2
2015-06-11 17:15 | 2015-06-11 | 4 | 17 | 250 | 65.7333 | 2
2015-06-11 17:30 | 2015-06-11 | 4 | 17 | 249 | 64.7333 | 1
2015-06-11 17:45 | 2015-06-11 | 4 | 17 | 239 | 63.7333 | 1
2015-06-11 18:00 | 2015-06-11 | 4 | 18 | 243 | 62.7333 | 1
2015-06-11 18:15 | 2015-06-11 | 4 | 18 | 242 | 61.7333 | 1
2015-06-11 18:30 | 2015-06-11 | 4 | 18 | 242 | 60.7333 | 1
2015-06-11 18:45 | 2015-06-11 | 4 | 18 | 233 | 59.7333 | 1
2015-06-11 19:00 | 2015-06-11 | 4 | 19 | 230 | 58.8667 | 1
2015-06-11 19:15 | 2015-06-11 | 4 | 19 | 234 | 58.3667 | 1
2015-06-11 19:30 | 2015-06-11 | 4 | 19 | 222 | 57.8667 | 1
2015-06-11 19:45 | 2015-06-11 | 4 | 19 | 229 | 57.3667 | 1
2015-06-11 20:00 | 2015-06-11 | 4 | 20 | 225 | 57 | 1
2015-06-11 20:15 | 2015-06-11 | 4 | 20 | 230 | 57 | 1
2015-06-11 20:30 | 2015-06-11 | 4 | 20 | 211 | 57 | 1
2015-06-11 20:45 | 2015-06-11 | 4 | 20 | 214 | 57 | 1
2015-06-11 21:00 | 2015-06-11 | 4 | 21 | 209 | 56.9333 | 1
2015-06-11 21:15 | 2015-06-11 | 4 | 21 | 201 | 56.6833 | 1
2015-06-11 21:30 | 2015-06-11 | 4 | 21 | 205 | 56.4333 | 1
2015-06-11 21:45 | 2015-06-11 | 4 | 21 | 198 | 56.1833 | 1
2015-06-11 22:00 | 2015-06-11 | 4 | 22 | 190 | 56 | 1
2015-06-11 22:15 | 2015-06-11 | 4 | 22 | 195 | 56 | 1
2015-06-11 22:30 | 2015-06-11 | 4 | 22 | 190 | 56 | 1
2015-06-11 22:45 | 2015-06-11 | 4 | 22 | 191 | 56 | 1
2015-06-11 23:00 | 2015-06-11 | 4 | 23 | 191 | 56 | 1
2015-06-11 23:15 | 2015-06-11 | 4 | 23 | 188 | 56 | 1
2015-06-11 23:30 | 2015-06-11 | 4 | 23 | 183 | 56 | 1
2015-06-11 23:45 | 2015-06-11 | 4 | 23 | 185 | 56 | 1
2015-06-12 | 2015-06-12 | 5 | 0 | 175 | 55.9333 | 1
2015-06-12 00:15 | 2015-06-12 | 5 | 0 | 181 | 55.6833 | 1
2015-06-12 00:30 | 2015-06-12 | 5 | 0 | 176 | 55.4333 | 1
2015-06-12 00:45 | 2015-06-12 | 5 | 0 | 176 | 55.1833 | 1
2015-06-12 01:00 | 2015-06-12 | 5 | 1 | 172 | 55 | 1
2015-06-12 01:15 | 2015-06-12 | 5 | 1 | 170 | 55 | 1
2015-06-12 01:30 | 2015-06-12 | 5 | 1 | 176 | 55 | 1
2015-06-12 01:45 | 2015-06-12 | 5 | 1 | 175 | 55 | 1
2015-06-12 02:00 | 2015-06-12 | 5 | 2 | 166 | 55 | 1
2015-06-12 02:15 | 2015-06-12 | 5 | 2 | 167 | 55 | 1
2015-06-12 02:30 | 2015-06-12 | 5 | 2 | 174 | 55 | 1
2015-06-12 02:45 | 2015-06-12 | 5 | 2 | 169 | 55 | 1
2015-06-12 03:00 | 2015-06-12 | 5 | 3 | 162 | 55 | 1
2015-06-12 03:15 | 2015-06-12 | 5 | 3 | 169 | 55 | 1
2015-06-12 03:30 | 2015-06-12 | 5 | 3 | 168 | 55 | 1
2015-06-12 03:45 | 2015-06-12 | 5 | 3 | 164 | 55 | 1
2015-06-12 04:00 | 2015-06-12 | 5 | 4 | 167 | 55 | 1
2015-06-12 04:15 | 2015-06-12 | 5 | 4 | 167 | 55 | 1
2015-06-12 04:30 | 2015-06-12 | 5 | 4 | 165 | 55 | 1
2015-06-12 04:45 | 2015-06-12 | 5 | 4 | 163 | 55 | 1
2015-06-12 05:00 | 2015-06-12 | 5 | 5 | 170 | 55.0667 | 1
2015-06-12 05:15 | 2015-06-12 | 5 | 5 | 168 | 55.3167 | 1
2015-06-12 05:30 | 2015-06-12 | 5 | 5 | 162 | 55.5667 | 1
2015-06-12 05:45 | 2015-06-12 | 5 | 5 | 164 | 55.8167 | 1
2015-06-12 06:00 | 2015-06-12 | 5 | 6 | 166 | 56.2667 | 1
2015-06-12 06:15 | 2015-06-12 | 5 | 6 | 165 | 57.2667 | 1
2015-06-12 06:30 | 2015-06-12 | 5 | 6 | 162 | 58.2667 | 1
2015-06-12 06:45 | 2015-06-12 | 5 | 6 | 170 | 59.2667 | 1
2015-06-12 07:00 | 2015-06-12 | 5 | 7 | 167 | 60.2 | 1
2015-06-12 07:15 | 2015-06-12 | 5 | 7 | 169 | 60.95 | 1
2015-06-12 07:30 | 2015-06-12 | 5 | 7 | 171 | 61.7 | 1
2015-06-12 07:45 | 2015-06-12 | 5 | 7 | 177 | 62.45 | 1
2015-06-12 08:00 | 2015-06-12 | 5 | 8 | 179 | 63.0667 | 1
2015-06-12 08:15 | 2015-06-12 | 5 | 8 | 185 | 63.3167 | 1
2015-06-12 08:30 | 2015-06-12 | 5 | 8 | 197 | 63.5667 | 1
2015-06-12 08:45 | 2015-06-12 | 5 | 8 | 194 | 63.8167 | 1
2015-06-12 09:00 | 2015-06-12 | 5 | 9 | 205 | 64.3333 | 1
2015-06-12 09:15 | 2015-06-12 | 5 | 9 | 202 | 65.5833 | 2
2015-06-12 09:30 | 2015-06-12 | 5 | 9 | 216 | 66.8333 | 2
2015-06-12 09:45 | 2015-06-12 | 5 | 9 | 216 | 68.0833 | 2
2015-06-12 10:00 | 2015-06-12 | 5 | 10 | 218 | 69.2 | 2
2015-06-12 10:15 | 2015-06-12 | 5 | 10 | 242 | 69.95 | 2
2015-06-12 10:30 | 2015-06-12 | 5 | 10 | 231 | 70.7 | 3
2015-06-12 10:45 | 2015-06-12 | 5 | 10 | 227 | 71.45 | 3
2015-06-12 11:00 | 2015-06-12 | 5 | 11 | 234 | 71.8667 | 3
2015-06-12 11:15 | 2015-06-12 | 5 | 11 | 238 | 71.3667 | 3
2015-06-12 11:30 | 2015-06-12 | 5 | 11 | 254 | 70.8667 | 3
2015-06-12 11:45 | 2015-06-12 | 5 | 11 | 244 | 70.3667 | 3
2015-06-12 12:00 | 2015-06-12 | 5 | 12 | 261 | 70 | 2
2015-06-12 12:15 | 2015-06-12 | 5 | 12 | 242 | 70 | 2
2015-06-12 12:30 | 2015-06-12 | 5 | 12 | 253 | 70 | 2
2015-06-12 12:45 | 2015-06-12 | 5 | 12 | 254 | 70 | 2
2015-06-12 13:00 | 2015-06-12 | 5 | 13 | 267 | 70.0667 | 3
2015-06-12 13:15 | 2015-06-12 | 5 | 13 | 249 | 70.3167 | 3
2015-06-12 13:30 | 2015-06-12 | 5 | 13 | 264 | 70.5667 | 3
2015-06-12 13:45 | 2015-06-12 | 5 | 13 | 265 | 70.8167 | 3
2015-06-12 14:00 | 2015-06-12 | 5 | 14 | 260 | 71.0667 | 3
2015-06-12 14:15 | 2015-06-12 | 5 | 14 | 276 | 71.3167 | 3
2015-06-12 14:30 | 2015-06-12 | 5 | 14 | 265 | 71.5667 | 3
2015-06-12 14:45 | 2015-06-12 | 5 | 14 | 273 | 71.8167 | 3
2015-06-12 15:00 | 2015-06-12 | 5 | 15 | 271 | 72.0667 | 3
2015-06-12 15:15 | 2015-06-12 | 5 | 15 | 280 | 72.3167 | 3
2015-06-12 15:30 | 2015-06-12 | 5 | 15 | 269 | 72.5667 | 3
2015-06-12 15:45 | 2015-06-12 | 5 | 15 | 273 | 72.8167 | 3
2015-06-12 16:00 | 2015-06-12 | 5 | 16 | 277 | 72.8667 | 3
2015-06-12 16:15 | 2015-06-12 | 5 | 16 | 273 | 72.3667 | 3
2015-06-12 16:30 | 2015-06-12 | 5 | 16 | 269 | 71.8667 | 3
2015-06-12 16:45 | 2015-06-12 | 5 | 16 | 275 | 71.3667 | 3
2015-06-12 17:00 | 2015-06-12 | 5 | 17 | 278 | 70.7333 | 3
2015-06-12 17:15 | 2015-06-12 | 5 | 17 | 277 | 69.7333 | 2
2015-06-12 17:30 | 2015-06-12 | 5 | 17 | 267 | 68.7333 | 2
2015-06-12 17:45 | 2015-06-12 | 5 | 17 | 271 | 67.7333 | 2
2015-06-12 18:00 | 2015-06-12 | 5 | 18 | 267 | 66.8667 | 2
2015-06-12 18:15 | 2015-06-12 | 5 | 18 | 266 | 66.3667 | 2
2015-06-12 18:30 | 2015-06-12 | 5 | 18 | 255 | 65.8667 | 2
2015-06-12 18:45 | 2015-06-12 | 5 | 18 | 266 | 65.3667 | 2
2015-06-12 19:00 | 2015-06-12 | 5 | 19 | 250 | 64.8667 | 1
2015-06-12 19:15 | 2015-06-12 | 5 | 19 | 261 | 64.3667 | 1
2015-06-12 19:30 | 2015-06-12 | 5 | 19 | 248 | 63.8667 | 1
2015-06-12 19:45 | 2015-06-12 | 5 | 19 | 246 | 63.3667 | 1
2015-06-12 20:00 | 2015-06-12 | 5 | 20 | 234 | 62.8667 | 1
2015-06-12 20:15 | 2015-06-12 | 5 | 20 | 242 | 62.3667 | 1
2015-06-12 20:30 | 2015-06-12 | 5 | 20 | 223 | 61.8667 | 1
2015-06-12 20:45 | 2015-06-12 | 5 | 20 | 226 | 61.3667 | 1
2015-06-12 21:00 | 2015-06-12 | 5 | 21 | 228 | 60.9333 | 1
2015-06-12 21:15 | 2015-06-12 | 5 | 21 | 204 | 60.6833 | 1
2015-06-12 21:30 | 2015-06-12 | 5 | 21 | 204 | 60.4333 | 1
2015-06-12 21:45 | 2015-06-12 | 5 | 21 | 198 | 60.1833 | 1
2015-06-12 22:00 | 2015-06-12 | 5 | 22 | 204 | 60 | 1
2015-06-12 22:15 | 2015-06-12 | 5 | 22 | 204 | 60 | 1
2015-06-12 22:30 | 2015-06-12 | 5 | 22 | 194 | 60 | 1
2015-06-12 22:45 | 2015-06-12 | 5 | 22 | 194 | 60 | 1
2015-06-12 23:00 | 2015-06-12 | 5 | 23 | 192 | 59.9333 | 1
2015-06-12 23:15 | 2015-06-12 | 5 | 23 | 189 | 59.6833 | 1
2015-06-12 23:30 | 2015-06-12 | 5 | 23 | 190 | 59.4333 | 1
2015-06-12 23:45 | 2015-06-12 | 5 | 23 | 200 | 59.1833 | 1
2015-06-13 | 2015-06-13 | 6 | 0 | 183 | 58.9333 | 1
2015-06-13 00:15 | 2015-06-13 | 6 | 0 | 193 | 58.6833 | 1
2015-06-13 00:30 | 2015-06-13 | 6 | 0 | 196 | 58.4333 | 1
2015-06-13 00:45 | 2015-06-13 | 6 | 0 | 189 | 58.1833 | 1
2015-06-13 01:00 | 2015-06-13 | 6 | 1 | 197 | 57.9333 | 1
2015-06-13 01:15 | 2015-06-13 | 6 | 1 | 192 | 57.6833 | 1
2015-06-13 01:30 | 2015-06-13 | 6 | 1 | 182 | 57.4333 | 1
2015-06-13 01:45 | 2015-06-13 | 6 | 1 | 181 | 57.1833 | 1
2015-06-13 02:00 | 2015-06-13 | 6 | 2 | 179 | 57 | 1
2015-06-13 02:15 | 2015-06-13 | 6 | 2 | 189 | 57 | 1
2015-06-13 02:30 | 2015-06-13 | 6 | 2 | 185 | 57 | 1
2015-06-13 02:45 | 2015-06-13 | 6 | 2 | 172 | 57 | 1
2015-06-13 03:00 | 2015-06-13 | 6 | 3 | 172 | 57 | 1
2015-06-13 03:15 | 2015-06-13 | 6 | 3 | 186 | 57 | 1
2015-06-13 03:30 | 2015-06-13 | 6 | 3 | 184 | 57 | 1
2015-06-13 03:45 | 2015-06-13 | 6 | 3 | 174 | 57 | 1
2015-06-13 04:00 | 2015-06-13 | 6 | 4 | 176 | 56.8596 | 1
2015-06-13 04:15 | 2015-06-13 | 6 | 4 | 170 | 56.3333 | 1
2015-06-13 04:30 | 2015-06-13 | 6 | 4 | 174 | 55.807 | 1
2015-06-13 04:45 | 2015-06-13 | 6 | 4 | 186 | 55.2807 | 1
2015-06-13 05:00 | 2015-06-13 | 6 | 5 | 183 | 57.0667 | 1
2015-06-13 05:15 | 2015-06-13 | 6 | 5 | 170 | 57.3167 | 1
2015-06-13 05:30 | 2015-06-13 | 6 | 5 | 167 | 57.5667 | 1
2015-06-13 05:45 | 2015-06-13 | 6 | 5 | 180 | 57.8167 | 1
2015-06-13 06:00 | 2015-06-13 | 6 | 6 | 188 | 58.2667 | 1
2015-06-13 06:15 | 2015-06-13 | 6 | 6 | 167 | 59.2667 | 1
2015-06-13 06:30 | 2015-06-13 | 6 | 6 | 173 | 60.2667 | 1
2015-06-13 06:45 | 2015-06-13 | 6 | 6 | 190 | 61.2667 | 1
2015-06-13 07:00 | 2015-06-13 | 6 | 7 | 176 | 62.0667 | 1
2015-06-13 07:15 | 2015-06-13 | 6 | 7 | 173 | 62.3167 | 1
2015-06-13 07:30 | 2015-06-13 | 6 | 7 | 177 | 62.5667 | 1
2015-06-13 07:45 | 2015-06-13 | 6 | 7 | 189 | 62.8167 | 1
2015-06-13 08:00 | 2015-06-13 | 6 | 8 | 170 | 63.0667 | 1
2015-06-13 08:15 | 2015-06-13 | 6 | 8 | 171 | 63.3167 | 1
2015-06-13 08:30 | 2015-06-13 | 6 | 8 | 174 | 63.5667 | 1
2015-06-13 08:45 | 2015-06-13 | 6 | 8 | 178 | 63.8167 | 1
2015-06-13 09:00 | 2015-06-13 | 6 | 9 | 186 | 64.0667 | 1
2015-06-13 09:15 | 2015-06-13 | 6 | 9 | 178 | 64.3167 | 1
2015-06-13 09:30 | 2015-06-13 | 6 | 9 | 176 | 64.5667 | 1
2015-06-13 09:45 | 2015-06-13 | 6 | 9 | 189 | 64.8167 | 1
2015-06-13 10:00 | 2015-06-13 | 6 | 10 | 191 | 65.1333 | 2
2015-06-13 10:15 | 2015-06-13 | 6 | 10 | 181 | 65.6333 | 2
2015-06-13 10:30 | 2015-06-13 | 6 | 10 | 190 | 66.1333 | 2
2015-06-13 10:45 | 2015-06-13 | 6 | 10 | 203 | 66.6333 | 2
2015-06-13 11:00 | 2015-06-13 | 6 | 11 | 201 | 67.1333 | 2
2015-06-13 11:15 | 2015-06-13 | 6 | 11 | 190 | 67.6333 | 2
2015-06-13 11:30 | 2015-06-13 | 6 | 11 | 191 | 68.1333 | 2
2015-06-13 11:45 | 2015-06-13 | 6 | 11 | 190 | 68.6333 | 2
2015-06-13 12:00 | 2015-06-13 | 6 | 12 | 214 | 69.1333 | 2
2015-06-13 12:15 | 2015-06-13 | 6 | 12 | 204 | 69.6333 | 2
2015-06-13 12:30 | 2015-06-13 | 6 | 12 | 196 | 70.1333 | 3
2015-06-13 12:45 | 2015-06-13 | 6 | 12 | 209 | 70.6333 | 3
2015-06-13 13:00 | 2015-06-13 | 6 | 13 | 199 | 71.1333 | 3
2015-06-13 13:15 | 2015-06-13 | 6 | 13 | 219 | 71.6333 | 3
2015-06-13 13:30 | 2015-06-13 | 6 | 13 | 217 | 72.1333 | 3
2015-06-13 13:45 | 2015-06-13 | 6 | 13 | 226 | 72.6333 | 3
2015-06-13 14:00 | 2015-06-13 | 6 | 14 | 214 | 72.9333 | 3
2015-06-13 14:15 | 2015-06-13 | 6 | 14 | 227 | 72.6833 | 3
2015-06-13 14:30 | 2015-06-13 | 6 | 14 | 215 | 72.4333 | 3
2015-06-13 14:45 | 2015-06-13 | 6 | 14 | 237 | 72.1833 | 3
2015-06-13 15:00 | 2015-06-13 | 6 | 15 | 225 | 72.3077 | 3
2015-06-13 15:15 | 2015-06-13 | 6 | 15 | 237 | 73.4615 | 3
2015-06-13 15:30 | 2015-06-13 | 6 | 15 | 228 | 74.6154 | 3
2015-06-13 15:45 | 2015-06-13 | 6 | 15 | 236 | 74.0476 | 3
2015-06-13 16:00 | 2015-06-13 | 6 | 16 | 228 | 72.5556 | 3
2015-06-13 16:15 | 2015-06-13 | 6 | 16 | 231 | 71.6078 | 3
2015-06-13 16:30 | 2015-06-13 | 6 | 16 | 235 | 71.0196 | 3
2015-06-13 16:45 | 2015-06-13 | 6 | 16 | 229 | 70.4314 | 3
2015-06-13 17:00 | 2015-06-13 | 6 | 17 | 250 | 69.8667 | 2
2015-06-13 17:15 | 2015-06-13 | 6 | 17 | 226 | 69.3667 | 2
2015-06-13 17:30 | 2015-06-13 | 6 | 17 | 241 | 68.8667 | 2
2015-06-13 17:45 | 2015-06-13 | 6 | 17 | 223 | 68.3667 | 2
2015-06-13 18:00 | 2015-06-13 | 6 | 18 | 232 | 67.5333 | 2
2015-06-13 18:15 | 2015-06-13 | 6 | 18 | 215 | 65.7833 | 2
2015-06-13 18:30 | 2015-06-13 | 6 | 18 | 227 | 64.0333 | 1
2015-06-13 18:45 | 2015-06-13 | 6 | 18 | 234 | 62.2833 | 1
2015-06-13 19:00 | 2015-06-13 | 6 | 19 | 239 | 60.9333 | 1
2015-06-13 19:15 | 2015-06-13 | 6 | 19 | 216 | 60.6833 | 1
2015-06-13 19:30 | 2015-06-13 | 6 | 19 | 235 | 60.4333 | 1
2015-06-13 19:45 | 2015-06-13 | 6 | 19 | 219 | 60.1833 | 1
2015-06-13 20:00 | 2015-06-13 | 6 | 20 | 208 | 59.9333 | 1
2015-06-13 20:15 | 2015-06-13 | 6 | 20 | 222 | 59.6833 | 1
2015-06-13 20:30 | 2015-06-13 | 6 | 20 | 199 | 59.4333 | 1
2015-06-13 20:45 | 2015-06-13 | 6 | 20 | 196 | 59.1833 | 1
2015-06-13 21:00 | 2015-06-13 | 6 | 21 | 203 | 58.9333 | 1
2015-06-13 21:15 | 2015-06-13 | 6 | 21 | 210 | 58.6833 | 1
2015-06-13 21:30 | 2015-06-13 | 6 | 21 | 192 | 58.4333 | 1
2015-06-13 21:45 | 2015-06-13 | 6 | 21 | 189 | 58.1833 | 1
2015-06-13 22:00 | 2015-06-13 | 6 | 22 | 182 | 57.9333 | 1
2015-06-13 22:15 | 2015-06-13 | 6 | 22 | 186 | 57.6833 | 1
2015-06-13 22:30 | 2015-06-13 | 6 | 22 | 194 | 57.4333 | 1
2015-06-13 22:45 | 2015-06-13 | 6 | 22 | 185 | 57.1833 | 1
2015-06-13 23:00 | 2015-06-13 | 6 | 23 | 180 | 57 | 1
2015-06-13 23:15 | 2015-06-13 | 6 | 23 | 180 | 57 | 1
2015-06-13 23:30 | 2015-06-13 | 6 | 23 | 192 | 57 | 1
2015-06-13 23:45 | 2015-06-13 | 6 | 23 | 177 | 57 | 1
2015-06-14 | 2015-06-14 | 7 | 0 | 176 | 56.9333 | 1
2015-06-14 00:15 | 2015-06-14 | 7 | 0 | 170 | 56.6833 | 1
2015-06-14 00:30 | 2015-06-14 | 7 | 0 | 171 | 56.4333 | 1
2015-06-14 00:45 | 2015-06-14 | 7 | 0 | 185 | 56.1833 | 1
2015-06-14 01:00 | 2015-06-14 | 7 | 1 | 172 | 55.9333 | 1
2015-06-14 01:15 | 2015-06-14 | 7 | 1 | 167 | 55.6833 | 1
2015-06-14 01:30 | 2015-06-14 | 7 | 1 | 159 | 55.4333 | 1
2015-06-14 01:45 | 2015-06-14 | 7 | 1 | 189 | 55.1833 | 1
2015-06-14 02:00 | 2015-06-14 | 7 | 2 | 168 | 54.9333 | 1
2015-06-14 02:15 | 2015-06-14 | 7 | 2 | 156 | 54.6833 | 1
2015-06-14 02:30 | 2015-06-14 | 7 | 2 | 160 | 54.4333 | 1
2015-06-14 02:45 | 2015-06-14 | 7 | 2 | 152 | 54.1833 | 1
2015-06-14 03:00 | 2015-06-14 | 7 | 3 | 166 | 54 | 1
2015-06-14 03:15 | 2015-06-14 | 7 | 3 | 158 | 54 | 1
2015-06-14 03:30 | 2015-06-14 | 7 | 3 | 153 | 54 | 1
2015-06-14 03:45 | 2015-06-14 | 7 | 3 | 154 | 54 | 1
2015-06-14 04:00 | 2015-06-14 | 7 | 4 | 167 | 54 | 1
2015-06-14 04:15 | 2015-06-14 | 7 | 4 | 159 | 54 | 1
2015-06-14 04:30 | 2015-06-14 | 7 | 4 | 170 | 54 | 1
2015-06-14 04:45 | 2015-06-14 | 7 | 4 | 163 | 54 | 1
2015-06-14 05:00 | 2015-06-14 | 7 | 5 | 173 | 54.1333 | 1
2015-06-14 05:15 | 2015-06-14 | 7 | 5 | 172 | 54.6333 | 1
2015-06-14 05:30 | 2015-06-14 | 7 | 5 | 161 | 55.1333 | 1
2015-06-14 05:45 | 2015-06-14 | 7 | 5 | 159 | 55.6333 | 1
2015-06-14 06:00 | 2015-06-14 | 7 | 6 | 157 | 56.2 | 1
2015-06-14 06:15 | 2015-06-14 | 7 | 6 | 173 | 56.95 | 1
2015-06-14 06:30 | 2015-06-14 | 7 | 6 | 185 | 57.7 | 1
2015-06-14 06:45 | 2015-06-14 | 7 | 6 | 172 | 58.45 | 1
2015-06-14 07:00 | 2015-06-14 | 7 | 7 | 172 | 59.0667 | 1
2015-06-14 07:15 | 2015-06-14 | 7 | 7 | 180 | 59.3167 | 1
2015-06-14 07:30 | 2015-06-14 | 7 | 7 | 186 | 59.5667 | 1
2015-06-14 07:45 | 2015-06-14 | 7 | 7 | 176 | 59.8167 | 1
2015-06-14 08:00 | 2015-06-14 | 7 | 8 | 175 | 60.2 | 1
2015-06-14 08:15 | 2015-06-14 | 7 | 8 | 174 | 60.95 | 1
2015-06-14 08:30 | 2015-06-14 | 7 | 8 | 183 | 61.7 | 1
2015-06-14 08:45 | 2015-06-14 | 7 | 8 | 204 | 62.45 | 1
2015-06-14 09:00 | 2015-06-14 | 7 | 9 | 199 | 63.2 | 1
2015-06-14 09:15 | 2015-06-14 | 7 | 9 | 193 | 63.95 | 1
2015-06-14 09:30 | 2015-06-14 | 7 | 9 | 189 | 64.7 | 1
2015-06-14 09:45 | 2015-06-14 | 7 | 9 | 204 | 65.45 | 2
2015-06-14 10:00 | 2015-06-14 | 7 | 10 | 199 | 66.0667 | 2
2015-06-14 10:15 | 2015-06-14 | 7 | 10 | 198 | 66.3167 | 2
2015-06-14 10:30 | 2015-06-14 | 7 | 10 | 198 | 66.5667 | 2
2015-06-14 10:45 | 2015-06-14 | 7 | 10 | 200 | 66.8167 | 2
2015-06-14 11:00 | 2015-06-14 | 7 | 11 | 216 | 66.9333 | 2
2015-06-14 11:15 | 2015-06-14 | 7 | 11 | 207 | 66.6833 | 2
2015-06-14 11:30 | 2015-06-14 | 7 | 11 | 204 | 66.4333 | 2
2015-06-14 11:45 | 2015-06-14 | 7 | 11 | 207 | 66.1833 | 2
2015-06-14 12:00 | 2015-06-14 | 7 | 12 | 209 | 65.9333 | 2
2015-06-14 12:15 | 2015-06-14 | 7 | 12 | 229 | 65.6833 | 2
2015-06-14 12:30 | 2015-06-14 | 7 | 12 | 212 | 65.4333 | 2
2015-06-14 12:45 | 2015-06-14 | 7 | 12 | 215 | 65.1833 | 2
2015-06-14 13:00 | 2015-06-14 | 7 | 13 | 215 | 65 | 1
2015-06-14 13:15 | 2015-06-14 | 7 | 13 | 221 | 65 | 1
2015-06-14 13:30 | 2015-06-14 | 7 | 13 | 232 | 65 | 1
2015-06-14 13:45 | 2015-06-14 | 7 | 13 | 229 | 65 | 1
2015-06-14 14:00 | 2015-06-14 | 7 | 14 | 213 | 64.9333 | 1
2015-06-14 14:15 | 2015-06-14 | 7 | 14 | 225 | 64.6833 | 1
2015-06-14 14:30 | 2015-06-14 | 7 | 14 | 230 | 64.4333 | 1
2015-06-14 14:45 | 2015-06-14 | 7 | 14 | 231 | 64.1833 | 1
2015-06-14 15:00 | 2015-06-14 | 7 | 15 | 226 | 64 | 1
2015-06-14 15:15 | 2015-06-14 | 7 | 15 | 222 | 64 | 1
2015-06-14 15:30 | 2015-06-14 | 7 | 15 | 232 | 64 | 1
2015-06-14 15:45 | 2015-06-14 | 7 | 15 | 238 | 64 | 1
2015-06-14 16:00 | 2015-06-14 | 7 | 16 | 248 | 63.8 | 1
2015-06-14 16:15 | 2015-06-14 | 7 | 16 | 226 | 63.05 | 1
2015-06-14 16:30 | 2015-06-14 | 7 | 16 | 240 | 62.3 | 1
2015-06-14 16:45 | 2015-06-14 | 7 | 16 | 228 | 61.55 | 1
2015-06-14 17:00 | 2015-06-14 | 7 | 17 | 252 | 60.8 | 1
2015-06-14 17:15 | 2015-06-14 | 7 | 17 | 236 | 60.05 | 1
2015-06-14 17:30 | 2015-06-14 | 7 | 17 | 238 | 59.3 | 1
2015-06-14 17:45 | 2015-06-14 | 7 | 17 | 237 | 58.55 | 1
2015-06-14 18:00 | 2015-06-14 | 7 | 18 | 238 | 57.8667 | 1
2015-06-14 18:15 | 2015-06-14 | 7 | 18 | 246 | 57.3667 | 1
2015-06-14 18:30 | 2015-06-14 | 7 | 18 | 237 | 56.8667 | 1
2015-06-14 18:45 | 2015-06-14 | 7 | 18 | 223 | 56.3667 | 1
2015-06-14 19:00 | 2015-06-14 | 7 | 19 | 235 | 55.8667 | 1
2015-06-14 19:15 | 2015-06-14 | 7 | 19 | 220 | 55.3667 | 1
2015-06-14 19:30 | 2015-06-14 | 7 | 19 | 228 | 54.8667 | 1
2015-06-14 19:45 | 2015-06-14 | 7 | 19 | 226 | 54.3667 | 1
2015-06-14 20:00 | 2015-06-14 | 7 | 20 | 212 | 54.0667 | 1
2015-06-14 20:15 | 2015-06-14 | 7 | 20 | 210 | 54.3167 | 1
2015-06-14 20:30 | 2015-06-14 | 7 | 20 | 199 | 54.5667 | 1
2015-06-14 20:45 | 2015-06-14 | 7 | 20 | 217 | 54.8167 | 1
2015-06-14 21:00 | 2015-06-14 | 7 | 21 | 198 | 55.0667 | 1
2015-06-14 21:15 | 2015-06-14 | 7 | 21 | 185 | 55.3167 | 1
2015-06-14 21:30 | 2015-06-14 | 7 | 21 | 193 | 55.5667 | 1
2015-06-14 21:45 | 2015-06-14 | 7 | 21 | 178 | 55.8167 | 1
2015-06-14 22:00 | 2015-06-14 | 7 | 22 | 171 | 55.9333 | 1
2015-06-14 22:15 | 2015-06-14 | 7 | 22 | 163 | 55.6833 | 1
2015-06-14 22:30 | 2015-06-14 | 7 | 22 | 186 | 55.4333 | 1
2015-06-14 22:45 | 2015-06-14 | 7 | 22 | 172 | 55.1833 | 1
2015-06-14 23:00 | 2015-06-14 | 7 | 23 | 168 | 55 | 1
2015-06-14 23:15 | 2015-06-14 | 7 | 23 | 164 | 55 | 1
2015-06-14 23:30 | 2015-06-14 | 7 | 23 | 164 | 55 | 1
2015-06-14 23:45 | 2015-06-14 | 7 | 23 | 180 | 55 | 1
2015-06-15 | 2015-06-15 | 1 | 0 | 169 | 54.9333 | 1
2015-06-15 00:15 | 2015-06-15 | 1 | 0 | 161 | 54.6833 | 1
2015-06-15 00:30 | 2015-06-15 | 1 | 0 | 161 | 54.4333 | 1
2015-06-15 00:45 | 2015-06-15 | 1 | 0 | 163 | 54.1833 | 1
2015-06-15 01:00 | 2015-06-15 | 1 | 1 | 179 | 53.9333 | 1
2015-06-15 01:15 | 2015-06-15 | 1 | 1 | 163 | 53.6833 | 1
2015-06-15 01:30 | 2015-06-15 | 1 | 1 | 163 | 53.4333 | 1
2015-06-15 01:45 | 2015-06-15 | 1 | 1 | 164 | 53.1833 | 1
2015-06-15 02:00 | 2015-06-15 | 1 | 2 | 162 | 53.0667 | 1
2015-06-15 02:15 | 2015-06-15 | 1 | 2 | 178 | 53.3167 | 1
2015-06-15 02:30 | 2015-06-15 | 1 | 2 | 157 | 53.5667 | 1
2015-06-15 02:45 | 2015-06-15 | 1 | 2 | 166 | 53.8167 | 1
2015-06-15 03:00 | 2015-06-15 | 1 | 3 | 159 | 53.9333 | 1
2015-06-15 03:15 | 2015-06-15 | 1 | 3 | 157 | 53.6833 | 1
2015-06-15 03:30 | 2015-06-15 | 1 | 3 | 174 | 53.4333 | 1
2015-06-15 03:45 | 2015-06-15 | 1 | 3 | 161 | 53.1833 | 1
2015-06-15 04:00 | 2015-06-15 | 1 | 4 | 162 | 53 | 1
2015-06-15 04:15 | 2015-06-15 | 1 | 4 | 159 | 53 | 1
2015-06-15 04:30 | 2015-06-15 | 1 | 4 | 163 | 53 | 1
2015-06-15 04:45 | 2015-06-15 | 1 | 4 | 175 | 53 | 1
2015-06-15 05:00 | 2015-06-15 | 1 | 5 | 160 | 53 | 1
2015-06-15 05:15 | 2015-06-15 | 1 | 5 | 157 | 53 | 1
2015-06-15 05:30 | 2015-06-15 | 1 | 5 | 157 | 53 | 1
2015-06-15 05:45 | 2015-06-15 | 1 | 5 | 168 | 53 | 1
2015-06-15 06:00 | 2015-06-15 | 1 | 6 | 169 | 53 | 1
2015-06-15 06:15 | 2015-06-15 | 1 | 6 | 157 | 53 | 1
2015-06-15 06:30 | 2015-06-15 | 1 | 6 | 159 | 53 | 1
2015-06-15 06:45 | 2015-06-15 | 1 | 6 | 154 | 53 | 1
2015-06-15 07:00 | 2015-06-15 | 1 | 7 | 159 | 53.069 | 1
2015-06-15 07:15 | 2015-06-15 | 1 | 7 | 171 | 53.3276 | 1
2015-06-15 07:30 | 2015-06-15 | 1 | 7 | 157 | 53.5862 | 1
2015-06-15 07:45 | 2015-06-15 | 1 | 7 | 169 | 53.8448 | 1
2015-06-15 08:00 | 2015-06-15 | 1 | 8 | 166 | 54.0667 | 1
2015-06-15 08:15 | 2015-06-15 | 1 | 8 | 183 | 54.3167 | 1
2015-06-15 08:30 | 2015-06-15 | 1 | 8 | 187 | 54.5667 | 1
2015-06-15 08:45 | 2015-06-15 | 1 | 8 | 177 | 54.8167 | 1
2015-06-15 09:00 | 2015-06-15 | 1 | 9 | 182 | 55.0667 | 1
2015-06-15 09:15 | 2015-06-15 | 1 | 9 | 187 | 55.3167 | 1
2015-06-15 09:30 | 2015-06-15 | 1 | 9 | 204 | 55.5667 | 1
2015-06-15 09:45 | 2015-06-15 | 1 | 9 | 242 | 55.8167 | 1
2015-06-15 10:00 | 2015-06-15 | 1 | 10 | 219 | 56.1333 | 1
2015-06-15 10:15 | 2015-06-15 | 1 | 10 | 223 | 56.6333 | 1
2015-06-15 10:30 | 2015-06-15 | 1 | 10 | 222 | 57.1333 | 1
2015-06-15 10:45 | 2015-06-15 | 1 | 10 | 223 | 57.6333 | 1
2015-06-15 11:00 | 2015-06-15 | 1 | 11 | 238 | 58.0667 | 1
2015-06-15 11:15 | 2015-06-15 | 1 | 11 | 227 | 58.3167 | 1
2015-06-15 11:30 | 2015-06-15 | 1 | 11 | 226 | 58.5667 | 1
2015-06-15 11:45 | 2015-06-15 | 1 | 11 | 241 | 58.8167 | 1
2015-06-15 12:00 | 2015-06-15 | 1 | 12 | 228 | 59 | 1
2015-06-15 12:15 | 2015-06-15 | 1 | 12 | 250 | 59 | 1
2015-06-15 12:30 | 2015-06-15 | 1 | 12 | 238 | 59 | 1
2015-06-15 12:45 | 2015-06-15 | 1 | 12 | 229 | 59 | 1
2015-06-15 13:00 | 2015-06-15 | 1 | 13 | 225 | 58.9333 | 1
2015-06-15 13:15 | 2015-06-15 | 1 | 13 | 233 | 58.6833 | 1
2015-06-15 13:30 | 2015-06-15 | 1 | 13 | 241 | 58.4333 | 1
2015-06-15 13:45 | 2015-06-15 | 1 | 13 | 236 | 58.1833 | 1
2015-06-15 14:00 | 2015-06-15 | 1 | 14 | 235 | 58 | 1
2015-06-15 14:15 | 2015-06-15 | 1 | 14 | 244 | 58 | 1
2015-06-15 14:30 | 2015-06-15 | 1 | 14 | 254 | 58 | 1
2015-06-15 14:45 | 2015-06-15 | 1 | 14 | 235 | 58 | 1
2015-06-15 15:00 | 2015-06-15 | 1 | 15 | 235 | 58.0667 | 1
2015-06-15 15:15 | 2015-06-15 | 1 | 15 | 243 | 58.3167 | 1
2015-06-15 15:30 | 2015-06-15 | 1 | 15 | 248 | 58.5667 | 1
2015-06-15 15:45 | 2015-06-15 | 1 | 15 | 247 | 58.8167 | 1
2015-06-15 16:00 | 2015-06-15 | 1 | 16 | 250 | 59 | 1
2015-06-15 16:15 | 2015-06-15 | 1 | 16 | 239 | 59 | 1
2015-06-15 16:30 | 2015-06-15 | 1 | 16 | 249 | 59 | 1
2015-06-15 16:45 | 2015-06-15 | 1 | 16 | 247 | 59 | 1
2015-06-15 17:00 | 2015-06-15 | 1 | 17 | 259 | 58.8667 | 1
2015-06-15 17:15 | 2015-06-15 | 1 | 17 | 251 | 58.3667 | 1
2015-06-15 17:30 | 2015-06-15 | 1 | 17 | 243 | 57.8667 | 1
2015-06-15 17:45 | 2015-06-15 | 1 | 17 | 239 | 57.3667 | 1
2015-06-15 18:00 | 2015-06-15 | 1 | 18 | 257 | 56.9333 | 1
2015-06-15 18:15 | 2015-06-15 | 1 | 18 | 241 | 56.6833 | 1
2015-06-15 18:30 | 2015-06-15 | 1 | 18 | 235 | 56.4333 | 1
2015-06-15 18:45 | 2015-06-15 | 1 | 18 | 234 | 56.1833 | 1
2015-06-15 19:00 | 2015-06-15 | 1 | 19 | 238 | 56 | 1
2015-06-15 19:15 | 2015-06-15 | 1 | 19 | 238 | 56 | 1
2015-06-15 19:30 | 2015-06-15 | 1 | 19 | 220 | 56 | 1
2015-06-15 19:45 | 2015-06-15 | 1 | 19 | 220 | 56 | 1
2015-06-15 20:00 | 2015-06-15 | 1 | 20 | 212 | 56 | 1
2015-06-15 20:15 | 2015-06-15 | 1 | 20 | 223 | 56 | 1
2015-06-15 20:30 | 2015-06-15 | 1 | 20 | 210 | 56 | 1
2015-06-15 20:45 | 2015-06-15 | 1 | 20 | 197 | 56 | 1
2015-06-15 21:00 | 2015-06-15 | 1 | 21 | 198 | 55.9333 | 1
2015-06-15 21:15 | 2015-06-15 | 1 | 21 | 196 | 55.6833 | 1
2015-06-15 21:30 | 2015-06-15 | 1 | 21 | 195 | 55.4333 | 1
2015-06-15 21:45 | 2015-06-15 | 1 | 21 | 180 | 55.1833 | 1
2015-06-15 22:00 | 2015-06-15 | 1 | 22 | 185 | 55 | 1
2015-06-15 22:15 | 2015-06-15 | 1 | 22 | 180 | 55 | 1
2015-06-15 22:30 | 2015-06-15 | 1 | 22 | 192 | 55 | 1
2015-06-15 22:45 | 2015-06-15 | 1 | 22 | 189 | 55 | 1
2015-06-15 23:00 | 2015-06-15 | 1 | 23 | 180 | 55 | 1
2015-06-15 23:15 | 2015-06-15 | 1 | 23 | 174 | 55 | 1
2015-06-15 23:30 | 2015-06-15 | 1 | 23 | 168 | 55 | 1
2015-06-15 23:45 | 2015-06-15 | 1 | 23 | 174 | 55 | 1
2015-06-16 | 2015-06-16 | 2 | 0 | 175 | 54.931 | 1
2015-06-16 00:15 | 2015-06-16 | 2 | 0 | 161 | 54.6724 | 1
2015-06-16 00:30 | 2015-06-16 | 2 | 0 | 161 | 54.4138 | 1
2015-06-16 00:45 | 2015-06-16 | 2 | 0 | 158 | 54.1552 | 1
2015-06-16 01:00 | 2015-06-16 | 2 | 1 | 161 | 54 | 1
2015-06-16 01:15 | 2015-06-16 | 2 | 1 | 169 | 54 | 1
2015-06-16 01:30 | 2015-06-16 | 2 | 1 | 166 | 54 | 1
2015-06-16 01:45 | 2015-06-16 | 2 | 1 | 154 | 54 | 1
2015-06-16 02:00 | 2015-06-16 | 2 | 2 | 151 | 54 | 1
2015-06-16 02:15 | 2015-06-16 | 2 | 2 | 154 | 54 | 1
2015-06-16 02:30 | 2015-06-16 | 2 | 2 | 153 | 54 | 1
2015-06-16 02:45 | 2015-06-16 | 2 | 2 | 159 | 54 | 1
2015-06-16 03:00 | 2015-06-16 | 2 | 3 | 138 | 54 | 1
2015-06-16 03:15 | 2015-06-16 | 2 | 3 | 150 | 54 | 1
2015-06-16 03:30 | 2015-06-16 | 2 | 3 | 155 | 54 | 1
2015-06-16 03:45 | 2015-06-16 | 2 | 3 | 167 | 54 | 1
2015-06-16 04:00 | 2015-06-16 | 2 | 4 | 137 | 54 | 1
2015-06-16 04:15 | 2015-06-16 | 2 | 4 | 143 | 54 | 1
2015-06-16 04:30 | 2015-06-16 | 2 | 4 | 136 | 54 | 1
2015-06-16 04:45 | 2015-06-16 | 2 | 4 | 139 | 54 | 1
2015-06-16 05:00 | 2015-06-16 | 2 | 5 | 148 | 54 | 1
2015-06-16 05:15 | 2015-06-16 | 2 | 5 | 143 | 54 | 1
2015-06-16 05:30 | 2015-06-16 | 2 | 5 | 137 | 54 | 1
2015-06-16 05:45 | 2015-06-16 | 2 | 5 | 137 | 54 | 1
2015-06-16 06:00 | 2015-06-16 | 2 | 6 | 139 | 54.0667 | 1
2015-06-16 06:15 | 2015-06-16 | 2 | 6 | 152 | 54.3167 | 1
2015-06-16 06:30 | 2015-06-16 | 2 | 6 | 149 | 54.5667 | 1
2015-06-16 06:45 | 2015-06-16 | 2 | 6 | 154 | 54.8167 | 1
2015-06-16 07:00 | 2015-06-16 | 2 | 7 | 139 | 55.0667 | 1
2015-06-16 07:15 | 2015-06-16 | 2 | 7 | 155 | 55.3167 | 1
2015-06-16 07:30 | 2015-06-16 | 2 | 7 | 158 | 55.5667 | 1
2015-06-16 07:45 | 2015-06-16 | 2 | 7 | 170 | 55.8167 | 1
2015-06-16 08:00 | 2015-06-16 | 2 | 8 | 174 | 55.0877 | 1
2015-06-16 08:15 | 2015-06-16 | 2 | 8 | 174 | 56.4035 | 1
2015-06-16 08:30 | 2015-06-16 | 2 | 8 | 174 | 57.7193 | 1
2015-06-16 08:45 | 2015-06-16 | 2 | 8 | 187 | 59.0351 | 1
2015-06-16 09:00 | 2015-06-16 | 2 | 9 | 201 | 60.2 | 1
2015-06-16 09:15 | 2015-06-16 | 2 | 9 | 189 | 60.95 | 1
2015-06-16 09:30 | 2015-06-16 | 2 | 9 | 213 | 61.7 | 1
2015-06-16 09:45 | 2015-06-16 | 2 | 9 | 203 | 62.45 | 1
2015-06-16 10:00 | 2015-06-16 | 2 | 10 | 214 | 63.0667 | 1
2015-06-16 10:15 | 2015-06-16 | 2 | 10 | 234 | 63.3167 | 1
2015-06-16 10:30 | 2015-06-16 | 2 | 10 | 218 | 63.5667 | 1
2015-06-16 10:45 | 2015-06-16 | 2 | 10 | 214 | 63.8167 | 1
2015-06-16 11:00 | 2015-06-16 | 2 | 11 | 176 | 63.9333 | 1
2015-06-16 11:15 | 2015-06-16 | 2 | 11 | 188 | 63.6833 | 1
2015-06-16 11:30 | 2015-06-16 | 2 | 11 | 200 | 63.4333 | 1
2015-06-16 11:45 | 2015-06-16 | 2 | 11 | 208 | 63.1833 | 1
2015-06-16 12:00 | 2015-06-16 | 2 | 12 | 200 | 63.0667 | 1
2015-06-16 12:15 | 2015-06-16 | 2 | 12 | 195 | 63.3167 | 1
2015-06-16 12:30 | 2015-06-16 | 2 | 12 | 194 | 63.5667 | 1
2015-06-16 12:45 | 2015-06-16 | 2 | 12 | 219 | 63.8167 | 1
2015-06-16 13:00 | 2015-06-16 | 2 | 13 | 245 | 64 | 1
2015-06-16 13:15 | 2015-06-16 | 2 | 13 | 228 | 64 | 1
2015-06-16 13:30 | 2015-06-16 | 2 | 13 | 240 | 64 | 1
2015-06-16 13:45 | 2015-06-16 | 2 | 13 | 226 | 64 | 1
2015-06-16 14:00 | 2015-06-16 | 2 | 14 | 243 | 63.9333 | 1
2015-06-16 14:15 | 2015-06-16 | 2 | 14 | 235 | 63.6833 | 1
2015-06-16 14:30 | 2015-06-16 | 2 | 14 | 229 | 63.4333 | 1
2015-06-16 14:45 | 2015-06-16 | 2 | 14 | 227 | 63.1833 | 1
2015-06-16 15:00 | 2015-06-16 | 2 | 15 | 228 | 63 | 1
2015-06-16 15:15 | 2015-06-16 | 2 | 15 | 237 | 63 | 1
2015-06-16 15:30 | 2015-06-16 | 2 | 15 | 246 | 63 | 1
2015-06-16 15:45 | 2015-06-16 | 2 | 15 | 233 | 63 | 1
2015-06-16 16:00 | 2015-06-16 | 2 | 16 | 237 | 62.9333 | 1
2015-06-16 16:15 | 2015-06-16 | 2 | 16 | 242 | 62.6833 | 1
2015-06-16 16:30 | 2015-06-16 | 2 | 16 | 240 | 62.4333 | 1
2015-06-16 16:45 | 2015-06-16 | 2 | 16 | 245 | 62.1833 | 1
2015-06-16 17:00 | 2015-06-16 | 2 | 17 | 250 | 61.8 | 1
2015-06-16 17:15 | 2015-06-16 | 2 | 17 | 243 | 61.05 | 1
2015-06-16 17:30 | 2015-06-16 | 2 | 17 | 237 | 60.3 | 1
2015-06-16 17:45 | 2015-06-16 | 2 | 17 | 231 | 59.55 | 1
2015-06-16 18:00 | 2015-06-16 | 2 | 18 | 248 | 58.7949 | 1
2015-06-16 18:15 | 2015-06-16 | 2 | 18 | 228 | 58.0256 | 1
2015-06-16 18:30 | 2015-06-16 | 2 | 18 | 247 | 57.2564 | 1
2015-06-16 18:45 | 2015-06-16 | 2 | 18 | 230 | 57 | 1
2015-06-16 19:00 | 2015-06-16 | 2 | 19 | 231 | 56.8667 | 1
2015-06-16 19:15 | 2015-06-16 | 2 | 19 | 225 | 56.3667 | 1
2015-06-16 19:30 | 2015-06-16 | 2 | 19 | 218 | 55.8667 | 1
2015-06-16 19:45 | 2015-06-16 | 2 | 19 | 224 | 55.3667 | 1
2015-06-16 20:00 | 2015-06-16 | 2 | 20 | 208 | 54.9333 | 1
2015-06-16 20:15 | 2015-06-16 | 2 | 20 | 212 | 54.6833 | 1
2015-06-16 20:30 | 2015-06-16 | 2 | 20 | 218 | 54.4333 | 1
2015-06-16 20:45 | 2015-06-16 | 2 | 20 | 206 | 54.1833 | 1
2015-06-16 21:00 | 2015-06-16 | 2 | 21 | 200 | 54 | 1
2015-06-16 21:15 | 2015-06-16 | 2 | 21 | 191 | 54 | 1
2015-06-16 21:30 | 2015-06-16 | 2 | 21 | 189 | 54 | 1
2015-06-16 21:45 | 2015-06-16 | 2 | 21 | 191 | 54 | 1
2015-06-16 22:00 | 2015-06-16 | 2 | 22 | 202 | 54 | 1
2015-06-16 22:15 | 2015-06-16 | 2 | 22 | 184 | 54 | 1
2015-06-16 22:30 | 2015-06-16 | 2 | 22 | 176 | 54 | 1
2015-06-16 22:45 | 2015-06-16 | 2 | 22 | 179 | 54 | 1
2015-06-16 23:00 | 2015-06-16 | 2 | 23 | 188 | 53.9333 | 1
2015-06-16 23:15 | 2015-06-16 | 2 | 23 | 174 | 53.6833 | 1
2015-06-16 23:30 | 2015-06-16 | 2 | 23 | 164 | 53.4333 | 1
2015-06-16 23:45 | 2015-06-16 | 2 | 23 | 160 | 53.1833 | 1
2015-06-17 | 2015-06-17 | 3 | 0 | 161 | 53 | 1
2015-06-17 00:15 | 2015-06-17 | 3 | 0 | 176 | 53 | 1
2015-06-17 00:30 | 2015-06-17 | 3 | 0 | 163 | 53 | 1
2015-06-17 00:45 | 2015-06-17 | 3 | 0 | 157 | 53 | 1
2015-06-17 01:00 | 2015-06-17 | 3 | 1 | 162 | 53 | 1
2015-06-17 01:15 | 2015-06-17 | 3 | 1 | 167 | 53 | 1
2015-06-17 01:30 | 2015-06-17 | 3 | 1 | 167 | 53 | 1
2015-06-17 01:45 | 2015-06-17 | 3 | 1 | 155 | 53 | 1
2015-06-17 02:00 | 2015-06-17 | 3 | 2 | 154 | 52.9333 | 1
2015-06-17 02:15 | 2015-06-17 | 3 | 2 | 154 | 52.6833 | 1
2015-06-17 02:30 | 2015-06-17 | 3 | 2 | 166 | 52.4333 | 1
2015-06-17 02:45 | 2015-06-17 | 3 | 2 | 154 | 52.1833 | 1
2015-06-17 03:00 | 2015-06-17 | 3 | 3 | 147 | 52.0667 | 1
2015-06-17 03:15 | 2015-06-17 | 3 | 3 | 153 | 52.3167 | 1
2015-06-17 03:30 | 2015-06-17 | 3 | 3 | 151 | 52.5667 | 1
2015-06-17 03:45 | 2015-06-17 | 3 | 3 | 166 | 52.8167 | 1
2015-06-17 04:00 | 2015-06-17 | 3 | 4 | 143 | 53 | 1
2015-06-17 04:15 | 2015-06-17 | 3 | 4 | 135 | 53 | 1
2015-06-17 04:30 | 2015-06-17 | 3 | 4 | 131 | 53 | 1
2015-06-17 04:45 | 2015-06-17 | 3 | 4 | 149 | 53 | 1
2015-06-17 05:00 | 2015-06-17 | 3 | 5 | 134 | 53.0667 | 1
2015-06-17 05:15 | 2015-06-17 | 3 | 5 | 131 | 53.3167 | 1
2015-06-17 05:30 | 2015-06-17 | 3 | 5 | 132 | 53.5667 | 1
2015-06-17 05:45 | 2015-06-17 | 3 | 5 | 131 | 53.8167 | 1
2015-06-17 06:00 | 2015-06-17 | 3 | 6 | 148 | 54.069 | 1
2015-06-17 06:15 | 2015-06-17 | 3 | 6 | 137 | 54.3276 | 1
2015-06-17 06:30 | 2015-06-17 | 3 | 6 | 153 | 54.5862 | 1
2015-06-17 06:45 | 2015-06-17 | 3 | 6 | 152 | 54.8448 | 1
2015-06-17 07:00 | 2015-06-17 | 3 | 7 | 152 | 55.25 | 1
2015-06-17 07:15 | 2015-06-17 | 3 | 7 | 165 | 56.1875 | 1
2015-06-17 07:30 | 2015-06-17 | 3 | 7 | 148 | 57.0714 | 1
2015-06-17 07:45 | 2015-06-17 | 3 | 7 | 151 | 57.6071 | 1
2015-06-17 08:00 | 2015-06-17 | 3 | 8 | 163 | 58.1333 | 1
2015-06-17 08:15 | 2015-06-17 | 3 | 8 | 175 | 58.6333 | 1
2015-06-17 08:30 | 2015-06-17 | 3 | 8 | 191 | 59.1333 | 1
2015-06-17 08:45 | 2015-06-17 | 3 | 8 | 210 | 59.6333 | 1
2015-06-17 09:00 | 2015-06-17 | 3 | 9 | 207 | 60.2 | 1
2015-06-17 09:15 | 2015-06-17 | 3 | 9 | 210 | 60.95 | 1
2015-06-17 09:30 | 2015-06-17 | 3 | 9 | 213 | 61.7 | 1
2015-06-17 09:45 | 2015-06-17 | 3 | 9 | 227 | 62.45 | 1
2015-06-17 10:00 | 2015-06-17 | 3 | 10 | 233 | 63.1333 | 1
2015-06-17 10:15 | 2015-06-17 | 3 | 10 | 234 | 63.6333 | 1
2015-06-17 10:30 | 2015-06-17 | 3 | 10 | 237 | 64.1333 | 1
2015-06-17 10:45 | 2015-06-17 | 3 | 10 | 231 | 64.6333 | 1
2015-06-17 11:00 | 2015-06-17 | 3 | 11 | 244 | 65.069 | 2
2015-06-17 11:15 | 2015-06-17 | 3 | 11 | 240 | 65.3276 | 2
2015-06-17 11:30 | 2015-06-17 | 3 | 11 | 235 | 65.5862 | 2
2015-06-17 11:45 | 2015-06-17 | 3 | 11 | 242 | 65.8448 | 2
2015-06-17 12:00 | 2015-06-17 | 3 | 12 | 228 | 65.9333 | 2
2015-06-17 12:15 | 2015-06-17 | 3 | 12 | 241 | 65.6833 | 2
2015-06-17 12:30 | 2015-06-17 | 3 | 12 | 239 | 65.4333 | 2
2015-06-17 12:45 | 2015-06-17 | 3 | 12 | 254 | 65.1833 | 2
2015-06-17 13:00 | 2015-06-17 | 3 | 13 | 243 | 64.5 | 1
2015-06-17 13:15 | 2015-06-17 | 3 | 13 | 246 | 64 | 1
2015-06-17 13:30 | 2015-06-17 | 3 | 13 | 251 | 64 | 1
2015-06-17 13:45 | 2015-06-17 | 3 | 13 | 259 | 64 | 1
2015-06-17 14:00 | 2015-06-17 | 3 | 14 | 260 | 63.8667 | 1
2015-06-17 14:15 | 2015-06-17 | 3 | 14 | 284 | 63.3667 | 1
2015-06-17 14:30 | 2015-06-17 | 3 | 14 | 261 | 62.8667 | 1
2015-06-17 14:45 | 2015-06-17 | 3 | 14 | 277 | 62.3667 | 1
2015-06-17 15:00 | 2015-06-17 | 3 | 15 | 273 | 62 | 1
2015-06-17 15:15 | 2015-06-17 | 3 | 15 | 261 | 62 | 1
2015-06-17 15:30 | 2015-06-17 | 3 | 15 | 259 | 62 | 1
2015-06-17 15:45 | 2015-06-17 | 3 | 15 | 274 | 62 | 1
2015-06-17 16:00 | 2015-06-17 | 3 | 16 | 262 | 61.8667 | 1
2015-06-17 16:15 | 2015-06-17 | 3 | 16 | 259 | 61.3667 | 1
2015-06-17 16:30 | 2015-06-17 | 3 | 16 | 265 | 60.8667 | 1
2015-06-17 16:45 | 2015-06-17 | 3 | 16 | 255 | 60.3667 | 1
2015-06-17 17:00 | 2015-06-17 | 3 | 17 | 259 | 59.8667 | 1
2015-06-17 17:15 | 2015-06-17 | 3 | 17 | 258 | 59.3667 | 1
2015-06-17 17:30 | 2015-06-17 | 3 | 17 | 268 | 58.8667 | 1
2015-06-17 17:45 | 2015-06-17 | 3 | 17 | 252 | 58.3667 | 1
2015-06-17 18:00 | 2015-06-17 | 3 | 18 | 254 | 57.9333 | 1
2015-06-17 18:15 | 2015-06-17 | 3 | 18 | 243 | 57.6833 | 1
2015-06-17 18:30 | 2015-06-17 | 3 | 18 | 252 | 57.4333 | 1
2015-06-17 18:45 | 2015-06-17 | 3 | 18 | 259 | 57.1833 | 1
2015-06-17 19:00 | 2015-06-17 | 3 | 19 | 244 | 56.9333 | 1
2015-06-17 19:15 | 2015-06-17 | 3 | 19 | 249 | 56.6833 | 1
2015-06-17 19:30 | 2015-06-17 | 3 | 19 | 243 | 56.4333 | 1
2015-06-17 19:45 | 2015-06-17 | 3 | 19 | 233 | 56.1833 | 1
2015-06-17 20:00 | 2015-06-17 | 3 | 20 | 224 | 56 | 1
2015-06-17 20:15 | 2015-06-17 | 3 | 20 | 222 | 56 | 1
2015-06-17 20:30 | 2015-06-17 | 3 | 20 | 232 | 56 | 1
2015-06-17 20:45 | 2015-06-17 | 3 | 20 | 214 | 56 | 1
2015-06-17 21:00 | 2015-06-17 | 3 | 21 | 213 | 56 | 1
2015-06-17 21:15 | 2015-06-17 | 3 | 21 | 201 | 56 | 1
2015-06-17 21:30 | 2015-06-17 | 3 | 21 | 209 | 56 | 1
2015-06-17 21:45 | 2015-06-17 | 3 | 21 | 199 | 56 | 1
2015-06-17 22:00 | 2015-06-17 | 3 | 22 | 191 | 55.9333 | 1
2015-06-17 22:15 | 2015-06-17 | 3 | 22 | 200 | 55.6833 | 1
2015-06-17 22:30 | 2015-06-17 | 3 | 22 | 203 | 55.4333 | 1
2015-06-17 22:45 | 2015-06-17 | 3 | 22 | 210 | 55.1833 | 1
2015-06-17 23:00 | 2015-06-17 | 3 | 23 | 190 | 54.9333 | 1
2015-06-17 23:15 | 2015-06-17 | 3 | 23 | 188 | 54.6833 | 1
2015-06-17 23:30 | 2015-06-17 | 3 | 23 | 176 | 54.4333 | 1
2015-06-17 23:45 | 2015-06-17 | 3 | 23 | 182 | 54.1833 | 1
2015-06-18 | 2015-06-18 | 4 | 0 | 172 | 54 | 1
2015-06-18 00:15 | 2015-06-18 | 4 | 0 | 163 | 54 | 1
2015-06-18 00:30 | 2015-06-18 | 4 | 0 | 158 | 54 | 1
2015-06-18 00:45 | 2015-06-18 | 4 | 0 | 178 | 54 | 1
2015-06-18 01:00 | 2015-06-18 | 4 | 1 | 167 | 54 | 1
2015-06-18 01:15 | 2015-06-18 | 4 | 1 | 169 | 54 | 1
2015-06-18 01:30 | 2015-06-18 | 4 | 1 | 158 | 54 | 1
2015-06-18 01:45 | 2015-06-18 | 4 | 1 | 158 | 54 | 1
2015-06-18 02:00 | 2015-06-18 | 4 | 2 | 173 | 54 | 1
2015-06-18 02:15 | 2015-06-18 | 4 | 2 | 151 | 54 | 1
2015-06-18 02:30 | 2015-06-18 | 4 | 2 | 151 | 54 | 1
2015-06-18 02:45 | 2015-06-18 | 4 | 2 | 159 | 54 | 1
2015-06-18 03:00 | 2015-06-18 | 4 | 3 | 163 | 53.9333 | 1
2015-06-18 03:15 | 2015-06-18 | 4 | 3 | 150 | 53.6833 | 1
2015-06-18 03:30 | 2015-06-18 | 4 | 3 | 148 | 53.4333 | 1
2015-06-18 03:45 | 2015-06-18 | 4 | 3 | 149 | 53.1833 | 1
2015-06-18 04:00 | 2015-06-18 | 4 | 4 | 165 | 53 | 1
2015-06-18 04:15 | 2015-06-18 | 4 | 4 | 145 | 53 | 1
2015-06-18 04:30 | 2015-06-18 | 4 | 4 | 141 | 53 | 1
2015-06-18 04:45 | 2015-06-18 | 4 | 4 | 130 | 53 | 1
2015-06-18 05:00 | 2015-06-18 | 4 | 5 | 141 | 53.1333 | 1
2015-06-18 05:15 | 2015-06-18 | 4 | 5 | 141 | 53.6333 | 1
2015-06-18 05:30 | 2015-06-18 | 4 | 5 | 134 | 54.1333 | 1
2015-06-18 05:45 | 2015-06-18 | 4 | 5 | 140 | 54.6333 | 1
2015-06-18 06:00 | 2015-06-18 | 4 | 6 | 130 | 55.1333 | 1
2015-06-18 06:15 | 2015-06-18 | 4 | 6 | 130 | 55.6333 | 1
2015-06-18 06:30 | 2015-06-18 | 4 | 6 | 152 | 56.1333 | 1
2015-06-18 06:45 | 2015-06-18 | 4 | 6 | 147 | 56.6333 | 1
2015-06-18 07:00 | 2015-06-18 | 4 | 7 | 158 | 57.1333 | 1
2015-06-18 07:15 | 2015-06-18 | 4 | 7 | 163 | 57.6333 | 1
2015-06-18 07:30 | 2015-06-18 | 4 | 7 | 167 | 58.1333 | 1
2015-06-18 07:45 | 2015-06-18 | 4 | 7 | 177 | 58.6333 | 1
2015-06-18 08:00 | 2015-06-18 | 4 | 8 | 185 | 59.0667 | 1
2015-06-18 08:15 | 2015-06-18 | 4 | 8 | 187 | 59.3167 | 1
2015-06-18 08:30 | 2015-06-18 | 4 | 8 | 183 | 59.5667 | 1
2015-06-18 08:45 | 2015-06-18 | 4 | 8 | 182 | 59.8167 | 1
2015-06-18 09:00 | 2015-06-18 | 4 | 9 | 202 | 60.0667 | 1
2015-06-18 09:15 | 2015-06-18 | 4 | 9 | 201 | 60.3167 | 1
2015-06-18 09:30 | 2015-06-18 | 4 | 9 | 204 | 60.5667 | 1
2015-06-18 09:45 | 2015-06-18 | 4 | 9 | 223 | 60.8167 | 1
2015-06-18 10:00 | 2015-06-18 | 4 | 10 | 215 | 61.1333 | 1
2015-06-18 10:15 | 2015-06-18 | 4 | 10 | 241 | 61.6333 | 1
2015-06-18 10:30 | 2015-06-18 | 4 | 10 | 216 | 62.1333 | 1
2015-06-18 10:45 | 2015-06-18 | 4 | 10 | 221 | 62.6333 | 1
2015-06-18 11:00 | 2015-06-18 | 4 | 11 | 236 | 63.1333 | 1
2015-06-18 11:15 | 2015-06-18 | 4 | 11 | 230 | 63.6333 | 1
2015-06-18 11:30 | 2015-06-18 | 4 | 11 | 247 | 64.1333 | 1
2015-06-18 11:45 | 2015-06-18 | 4 | 11 | 240 | 64.6333 | 1
2015-06-18 12:00 | 2015-06-18 | 4 | 12 | 232 | 65.0667 | 2
2015-06-18 12:15 | 2015-06-18 | 4 | 12 | 246 | 65.3167 | 2
2015-06-18 12:30 | 2015-06-18 | 4 | 12 | 240 | 65.5667 | 2
2015-06-18 12:45 | 2015-06-18 | 4 | 12 | 246 | 65.8167 | 2
2015-06-18 13:00 | 2015-06-18 | 4 | 13 | 234 | 66 | 2
2015-06-18 13:15 | 2015-06-18 | 4 | 13 | 242 | 66 | 2
2015-06-18 13:30 | 2015-06-18 | 4 | 13 | 250 | 66 | 2
2015-06-18 13:45 | 2015-06-18 | 4 | 13 | 254 | 66 | 2
2015-06-18 14:00 | 2015-06-18 | 4 | 14 | 256 | 66.0667 | 2
2015-06-18 14:15 | 2015-06-18 | 4 | 14 | 243 | 66.3167 | 2
2015-06-18 14:30 | 2015-06-18 | 4 | 14 | 254 | 66.5667 | 2
2015-06-18 14:45 | 2015-06-18 | 4 | 14 | 239 | 66.8167 | 2
2015-06-18 15:00 | 2015-06-18 | 4 | 15 | 259 | 66.9333 | 2
2015-06-18 15:15 | 2015-06-18 | 4 | 15 | 246 | 66.6833 | 2
2015-06-18 15:30 | 2015-06-18 | 4 | 15 | 250 | 66.4333 | 2
2015-06-18 15:45 | 2015-06-18 | 4 | 15 | 249 | 66.1833 | 2
2015-06-18 16:00 | 2015-06-18 | 4 | 16 | 257 | 66.0667 | 2
2015-06-18 16:15 | 2015-06-18 | 4 | 16 | 248 | 66.3167 | 2
2015-06-18 16:30 | 2015-06-18 | 4 | 16 | 237 | 66.5667 | 2
2015-06-18 16:45 | 2015-06-18 | 4 | 16 | 247 | 66.8167 | 2
2015-06-18 17:00 | 2015-06-18 | 4 | 17 | 241 | 66.8 | 2
2015-06-18 17:15 | 2015-06-18 | 4 | 17 | 259 | 66.05 | 2
2015-06-18 17:30 | 2015-06-18 | 4 | 17 | 240 | 65.3 | 2
2015-06-18 17:45 | 2015-06-18 | 4 | 17 | 245 | 64.55 | 1
2015-06-18 18:00 | 2015-06-18 | 4 | 18 | 235 | 63.8 | 1
2015-06-18 18:15 | 2015-06-18 | 4 | 18 | 240 | 63.05 | 1
2015-06-18 18:30 | 2015-06-18 | 4 | 18 | 233 | 62.3 | 1
2015-06-18 18:45 | 2015-06-18 | 4 | 18 | 230 | 61.55 | 1
2015-06-18 19:00 | 2015-06-18 | 4 | 19 | 247 | 60.8 | 1
2015-06-18 19:15 | 2015-06-18 | 4 | 19 | 226 | 60.05 | 1
2015-06-18 19:30 | 2015-06-18 | 4 | 19 | 221 | 59.3 | 1
2015-06-18 19:45 | 2015-06-18 | 4 | 19 | 223 | 58.55 | 1
2015-06-18 20:00 | 2015-06-18 | 4 | 20 | 230 | 58 | 1
2015-06-18 20:15 | 2015-06-18 | 4 | 20 | 216 | 58 | 1
2015-06-18 20:30 | 2015-06-18 | 4 | 20 | 219 | 58 | 1
2015-06-18 20:45 | 2015-06-18 | 4 | 20 | 202 | 58 | 1
2015-06-18 21:00 | 2015-06-18 | 4 | 21 | 205 | 57.8667 | 1
2015-06-18 21:15 | 2015-06-18 | 4 | 21 | 189 | 57.3667 | 1
2015-06-18 21:30 | 2015-06-18 | 4 | 21 | 199 | 56.8667 | 1
2015-06-18 21:45 | 2015-06-18 | 4 | 21 | 177 | 56.3667 | 1
2015-06-18 22:00 | 2015-06-18 | 4 | 22 | 188 | 56 | 1
2015-06-18 22:15 | 2015-06-18 | 4 | 22 | 172 | 56 | 1
2015-06-18 22:30 | 2015-06-18 | 4 | 22 | 188 | 56 | 1
2015-06-18 22:45 | 2015-06-18 | 4 | 22 | 186 | 56 | 1
2015-06-18 23:00 | 2015-06-18 | 4 | 23 | 184 | 55.8667 | 1
2015-06-18 23:15 | 2015-06-18 | 4 | 23 | 175 | 55.3667 | 1
2015-06-18 23:30 | 2015-06-18 | 4 | 23 | 174 | 54.8667 | 1
2015-06-18 23:45 | 2015-06-18 | 4 | 23 | 173 | 54.3667 | 1
2015-06-19 | 2015-06-19 | 5 | 0 | 180 | 53.9333 | 1
2015-06-19 00:15 | 2015-06-19 | 5 | 0 | 169 | 53.6833 | 1
2015-06-19 00:30 | 2015-06-19 | 5 | 0 | 171 | 53.4333 | 1
2015-06-19 00:45 | 2015-06-19 | 5 | 0 | 167 | 53.1833 | 1
2015-06-19 01:00 | 2015-06-19 | 5 | 1 | 176 | 53 | 1
2015-06-19 01:15 | 2015-06-19 | 5 | 1 | 180 | 53 | 1
2015-06-19 01:30 | 2015-06-19 | 5 | 1 | 177 | 53 | 1
2015-06-19 01:45 | 2015-06-19 | 5 | 1 | 165 | 53 | 1
2015-06-19 02:00 | 2015-06-19 | 5 | 2 | 159 | 52.9333 | 1
2015-06-19 02:15 | 2015-06-19 | 5 | 2 | 158 | 52.6833 | 1
2015-06-19 02:30 | 2015-06-19 | 5 | 2 | 156 | 52.4333 | 1
2015-06-19 02:45 | 2015-06-19 | 5 | 2 | 164 | 52.1833 | 1
2015-06-19 03:00 | 2015-06-19 | 5 | 3 | 156 | 52 | 1
2015-06-19 03:15 | 2015-06-19 | 5 | 3 | 159 | 52 | 1
2015-06-19 03:30 | 2015-06-19 | 5 | 3 | 154 | 51.8387 | 1
2015-06-19 03:45 | 2015-06-19 | 5 | 3 | 158 | 51.3548 | 1
2015-06-19 04:00 | 2015-06-19 | 5 | 4 | 156 | 51 | 1
2015-06-19 04:15 | 2015-06-19 | 5 | 4 | 168 | 51 | 1
2015-06-19 04:30 | 2015-06-19 | 5 | 4 | 146 | 51 | 1
2015-06-19 04:45 | 2015-06-19 | 5 | 4 | 146 | 51 | 1
2015-06-19 05:00 | 2015-06-19 | 5 | 5 | 144 | 51.2 | 1
2015-06-19 05:15 | 2015-06-19 | 5 | 5 | 147 | 51.95 | 1
2015-06-19 05:30 | 2015-06-19 | 5 | 5 | 145 | 52.7 | 1
2015-06-19 05:45 | 2015-06-19 | 5 | 5 | 143 | 53.45 | 1
2015-06-19 06:00 | 2015-06-19 | 5 | 6 | 148 | 54.1333 | 1
2015-06-19 06:15 | 2015-06-19 | 5 | 6 | 140 | 54.6333 | 1
2015-06-19 06:30 | 2015-06-19 | 5 | 6 | 146 | 55.1333 | 1
2015-06-19 06:45 | 2015-06-19 | 5 | 6 | 156 | 55.6333 | 1
2015-06-19 07:00 | 2015-06-19 | 5 | 7 | 166 | 56.2 | 1
2015-06-19 07:15 | 2015-06-19 | 5 | 7 | 170 | 56.95 | 1
2015-06-19 07:30 | 2015-06-19 | 5 | 7 | 164 | 57.7 | 1
2015-06-19 07:45 | 2015-06-19 | 5 | 7 | 167 | 58.45 | 1
2015-06-19 08:00 | 2015-06-19 | 5 | 8 | 170 | 59.1333 | 1
2015-06-19 08:15 | 2015-06-19 | 5 | 8 | 175 | 59.6333 | 1
2015-06-19 08:30 | 2015-06-19 | 5 | 8 | 181 | 60.1333 | 1
2015-06-19 08:45 | 2015-06-19 | 5 | 8 | 191 | 60.6333 | 1
2015-06-19 09:00 | 2015-06-19 | 5 | 9 | 204 | 61.1333 | 1
2015-06-19 09:15 | 2015-06-19 | 5 | 9 | 194 | 61.6333 | 1
2015-06-19 09:30 | 2015-06-19 | 5 | 9 | 196 | 62.1333 | 1
2015-06-19 09:45 | 2015-06-19 | 5 | 9 | 210 | 62.6333 | 1
2015-06-19 10:00 | 2015-06-19 | 5 | 10 | 207 | 63.1333 | 1
2015-06-19 10:15 | 2015-06-19 | 5 | 10 | 210 | 63.6333 | 1
2015-06-19 10:30 | 2015-06-19 | 5 | 10 | 206 | 64.1333 | 1
2015-06-19 10:45 | 2015-06-19 | 5 | 10 | 213 | 64.6333 | 1
2015-06-19 11:00 | 2015-06-19 | 5 | 11 | 225 | 65.0667 | 2
2015-06-19 11:15 | 2015-06-19 | 5 | 11 | 207 | 65.3167 | 2
2015-06-19 11:30 | 2015-06-19 | 5 | 11 | 216 | 65.5667 | 2
2015-06-19 11:45 | 2015-06-19 | 5 | 11 | 217 | 65.8167 | 2
2015-06-19 12:00 | 2015-06-19 | 5 | 12 | 218 | 66 | 2
2015-06-19 12:15 | 2015-06-19 | 5 | 12 | 238 | 66 | 2
2015-06-19 12:30 | 2015-06-19 | 5 | 12 | 227 | 66 | 2
2015-06-19 12:45 | 2015-06-19 | 5 | 12 | 223 | 66 | 2
2015-06-19 13:00 | 2015-06-19 | 5 | 13 | 235 | 66.0667 | 2
2015-06-19 13:15 | 2015-06-19 | 5 | 13 | 226 | 66.3167 | 2
2015-06-19 13:30 | 2015-06-19 | 5 | 13 | 242 | 66.5667 | 2
2015-06-19 13:45 | 2015-06-19 | 5 | 13 | 237 | 66.8167 | 2
2015-06-19 14:00 | 2015-06-19 | 5 | 14 | 239 | 66.9333 | 2
2015-06-19 14:15 | 2015-06-19 | 5 | 14 | 237 | 66.6833 | 2
2015-06-19 14:30 | 2015-06-19 | 5 | 14 | 247 | 66.4333 | 2
2015-06-19 14:45 | 2015-06-19 | 5 | 14 | 241 | 66.1833 | 2
2015-06-19 15:00 | 2015-06-19 | 5 | 15 | 246 | 66.0667 | 2
2015-06-19 15:15 | 2015-06-19 | 5 | 15 | 238 | 66.3167 | 2
2015-06-19 15:30 | 2015-06-19 | 5 | 15 | 246 | 66.5667 | 2
2015-06-19 15:45 | 2015-06-19 | 5 | 15 | 244 | 66.8167 | 2
2015-06-19 16:00 | 2015-06-19 | 5 | 16 | 248 | 66.8667 | 2
2015-06-19 16:15 | 2015-06-19 | 5 | 16 | 243 | 66.3667 | 2
2015-06-19 16:30 | 2015-06-19 | 5 | 16 | 247 | 65.8667 | 2
2015-06-19 16:45 | 2015-06-19 | 5 | 16 | 234 | 65.3667 | 2
2015-06-19 17:00 | 2015-06-19 | 5 | 17 | 236 | 64.8 | 1
2015-06-19 17:15 | 2015-06-19 | 5 | 17 | 244 | 64.05 | 1
2015-06-19 17:30 | 2015-06-19 | 5 | 17 | 259 | 63.3 | 1
2015-06-19 17:45 | 2015-06-19 | 5 | 17 | 240 | 62.55 | 1
2015-06-19 18:00 | 2015-06-19 | 5 | 18 | 246 | 61.8667 | 1
2015-06-19 18:15 | 2015-06-19 | 5 | 18 | 230 | 61.3667 | 1
2015-06-19 18:30 | 2015-06-19 | 5 | 18 | 244 | 60.8667 | 1
2015-06-19 18:45 | 2015-06-19 | 5 | 18 | 240 | 60.3667 | 1
2015-06-19 19:00 | 2015-06-19 | 5 | 19 | 230 | 59.8 | 1
2015-06-19 19:15 | 2015-06-19 | 5 | 19 | 227 | 59.05 | 1
2015-06-19 19:30 | 2015-06-19 | 5 | 19 | 224 | 58.3 | 1
2015-06-19 19:45 | 2015-06-19 | 5 | 19 | 218 | 57.55 | 1
2015-06-19 20:00 | 2015-06-19 | 5 | 20 | 211 | 57 | 1
2015-06-19 20:15 | 2015-06-19 | 5 | 20 | 223 | 57 | 1
2015-06-19 20:30 | 2015-06-19 | 5 | 20 | 216 | 57 | 1
2015-06-19 20:45 | 2015-06-19 | 5 | 20 | 209 | 57 | 1
2015-06-19 21:00 | 2015-06-19 | 5 | 21 | 205 | 57 | 1
2015-06-19 21:15 | 2015-06-19 | 5 | 21 | 194 | 57 | 1
2015-06-19 21:30 | 2015-06-19 | 5 | 21 | 186 | 57 | 1
2015-06-19 21:45 | 2015-06-19 | 5 | 21 | 197 | 57 | 1
2015-06-19 22:00 | 2015-06-19 | 5 | 22 | 178 | 56.9333 | 1
2015-06-19 22:15 | 2015-06-19 | 5 | 22 | 178 | 56.6833 | 1
2015-06-19 22:30 | 2015-06-19 | 5 | 22 | 173 | 56.4333 | 1
2015-06-19 22:45 | 2015-06-19 | 5 | 22 | 186 | 56.1833 | 1
2015-06-19 23:00 | 2015-06-19 | 5 | 23 | 176 | 55.9333 | 1
2015-06-19 23:15 | 2015-06-19 | 5 | 23 | 179 | 55.6833 | 1
2015-06-19 23:30 | 2015-06-19 | 5 | 23 | 163 | 55.4333 | 1
2015-06-19 23:45 | 2015-06-19 | 5 | 23 | 175 | 55.1833 | 1
2015-06-20 | 2015-06-20 | 6 | 0 | 170 | 54.9333 | 1
2015-06-20 00:15 | 2015-06-20 | 6 | 0 | 183 | 54.6833 | 1
2015-06-20 00:30 | 2015-06-20 | 6 | 0 | 164 | 54.4333 | 1
2015-06-20 00:45 | 2015-06-20 | 6 | 0 | 166 | 54.1833 | 1
2015-06-20 01:00 | 2015-06-20 | 6 | 1 | 156 | 54 | 1
2015-06-20 01:15 | 2015-06-20 | 6 | 1 | 160 | 54 | 1
2015-06-20 01:30 | 2015-06-20 | 6 | 1 | 174 | 54 | 1
2015-06-20 01:45 | 2015-06-20 | 6 | 1 | 157 | 54 | 1
2015-06-20 02:00 | 2015-06-20 | 6 | 2 | 163 | 53.9333 | 1
2015-06-20 02:15 | 2015-06-20 | 6 | 2 | 153 | 53.6833 | 1
2015-06-20 02:30 | 2015-06-20 | 6 | 2 | 169 | 53.4333 | 1
2015-06-20 02:45 | 2015-06-20 | 6 | 2 | 150 | 53.1833 | 1
2015-06-20 03:00 | 2015-06-20 | 6 | 3 | 152 | 53 | 1
2015-06-20 03:15 | 2015-06-20 | 6 | 3 | 148 | 53 | 1
2015-06-20 03:30 | 2015-06-20 | 6 | 3 | 150 | 53 | 1
2015-06-20 03:45 | 2015-06-20 | 6 | 3 | 162 | 53 | 1
2015-06-20 04:00 | 2015-06-20 | 6 | 4 | 152 | 53 | 1
2015-06-20 04:15 | 2015-06-20 | 6 | 4 | 148 | 53 | 1
2015-06-20 04:30 | 2015-06-20 | 6 | 4 | 146 | 53 | 1
2015-06-20 04:45 | 2015-06-20 | 6 | 4 | 146 | 53 | 1
2015-06-20 05:00 | 2015-06-20 | 6 | 5 | 145 | 53 | 1
2015-06-20 05:15 | 2015-06-20 | 6 | 5 | 159 | 53 | 1
2015-06-20 05:30 | 2015-06-20 | 6 | 5 | 147 | 53 | 1
2015-06-20 05:45 | 2015-06-20 | 6 | 5 | 144 | 53 | 1
2015-06-20 06:00 | 2015-06-20 | 6 | 6 | 143 | 53.2 | 1
2015-06-20 06:15 | 2015-06-20 | 6 | 6 | 144 | 53.95 | 1
2015-06-20 06:30 | 2015-06-20 | 6 | 6 | 148 | 54.7 | 1
2015-06-20 06:45 | 2015-06-20 | 6 | 6 | 149 | 55.45 | 1
2015-06-20 07:00 | 2015-06-20 | 6 | 7 | 141 | 56.0667 | 1
2015-06-20 07:15 | 2015-06-20 | 6 | 7 | 142 | 56.3167 | 1
2015-06-20 07:30 | 2015-06-20 | 6 | 7 | 142 | 56.5667 | 1
2015-06-20 07:45 | 2015-06-20 | 6 | 7 | 143 | 56.8167 | 1
2015-06-20 08:00 | 2015-06-20 | 6 | 8 | 145 | 57.2667 | 1
2015-06-20 08:15 | 2015-06-20 | 6 | 8 | 147 | 58.2667 | 1
2015-06-20 08:30 | 2015-06-20 | 6 | 8 | 161 | 59.2667 | 1
2015-06-20 08:45 | 2015-06-20 | 6 | 8 | 156 | 60.2667 | 1
2015-06-20 09:00 | 2015-06-20 | 6 | 9 | 150 | 61.0667 | 1
2015-06-20 09:15 | 2015-06-20 | 6 | 9 | 154 | 61.3167 | 1
2015-06-20 09:30 | 2015-06-20 | 6 | 9 | 165 | 61.5667 | 1
2015-06-20 09:45 | 2015-06-20 | 6 | 9 | 159 | 61.8167 | 1
2015-06-20 10:00 | 2015-06-20 | 6 | 10 | 164 | 62.2667 | 1
2015-06-20 10:15 | 2015-06-20 | 6 | 10 | 164 | 63.2667 | 1
2015-06-20 10:30 | 2015-06-20 | 6 | 10 | 160 | 64.2667 | 1
2015-06-20 10:45 | 2015-06-20 | 6 | 10 | 177 | 65.2667 | 2
2015-06-20 11:00 | 2015-06-20 | 6 | 11 | 180 | 66.1333 | 2
2015-06-20 11:15 | 2015-06-20 | 6 | 11 | 176 | 66.6333 | 2
2015-06-20 11:30 | 2015-06-20 | 6 | 11 | 169 | 67.1333 | 2
2015-06-20 11:45 | 2015-06-20 | 6 | 11 | 190 | 67.6333 | 2
2015-06-20 12:00 | 2015-06-20 | 6 | 12 | 192 | 68 | 2
2015-06-20 12:15 | 2015-06-20 | 6 | 12 | 172 | 68 | 2
2015-06-20 12:30 | 2015-06-20 | 6 | 12 | 198 | 68 | 2
2015-06-20 12:45 | 2015-06-20 | 6 | 12 | 174 | 68 | 2
2015-06-20 13:00 | 2015-06-20 | 6 | 13 | 195 | 68 | 2
2015-06-20 13:15 | 2015-06-20 | 6 | 13 | 188 | 68 | 2
2015-06-20 13:30 | 2015-06-20 | 6 | 13 | 180 | 68 | 2
2015-06-20 13:45 | 2015-06-20 | 6 | 13 | 184 | 68 | 2
2015-06-20 14:00 | 2015-06-20 | 6 | 14 | 184 | 67.8667 | 2
2015-06-20 14:15 | 2015-06-20 | 6 | 14 | 212 | 67.3667 | 2
2015-06-20 14:30 | 2015-06-20 | 6 | 14 | 195 | 66.8667 | 2
2015-06-20 14:45 | 2015-06-20 | 6 | 14 | 202 | 66.3667 | 2
2015-06-20 15:00 | 2015-06-20 | 6 | 15 | 187 | 66.0667 | 2
2015-06-20 15:15 | 2015-06-20 | 6 | 15 | 195 | 66.3167 | 2
2015-06-20 15:30 | 2015-06-20 | 6 | 15 | 216 | 66.5667 | 2
2015-06-20 15:45 | 2015-06-20 | 6 | 15 | 200 | 66.8167 | 2
2015-06-20 16:00 | 2015-06-20 | 6 | 16 | 205 | 66.9333 | 2
2015-06-20 16:15 | 2015-06-20 | 6 | 16 | 193 | 66.6833 | 2
2015-06-20 16:30 | 2015-06-20 | 6 | 16 | 194 | 66.4333 | 2
2015-06-20 16:45 | 2015-06-20 | 6 | 16 | 216 | 66.1833 | 2
2015-06-20 17:00 | 2015-06-20 | 6 | 17 | 196 | 65.8 | 2
2015-06-20 17:15 | 2015-06-20 | 6 | 17 | 200 | 65.05 | 2
2015-06-20 17:30 | 2015-06-20 | 6 | 17 | 195 | 64.3 | 1
2015-06-20 17:45 | 2015-06-20 | 6 | 17 | 209 | 63.55 | 1
2015-06-20 18:00 | 2015-06-20 | 6 | 18 | 211 | 62.6 | 1
2015-06-20 18:15 | 2015-06-20 | 6 | 18 | 201 | 61.1 | 1
2015-06-20 18:30 | 2015-06-20 | 6 | 18 | 204 | 59.6 | 1
2015-06-20 18:45 | 2015-06-20 | 6 | 18 | 201 | 58.1 | 1
2015-06-20 19:00 | 2015-06-20 | 6 | 19 | 211 | 56.8667 | 1
2015-06-20 19:15 | 2015-06-20 | 6 | 19 | 198 | 56.3667 | 1
2015-06-20 19:30 | 2015-06-20 | 6 | 19 | 194 | 55.8667 | 1
2015-06-20 19:45 | 2015-06-20 | 6 | 19 | 196 | 55.3667 | 1
2015-06-20 20:00 | 2015-06-20 | 6 | 20 | 191 | 55 | 1
2015-06-20 20:15 | 2015-06-20 | 6 | 20 | 201 | 55 | 1
2015-06-20 20:30 | 2015-06-20 | 6 | 20 | 192 | 55 | 1
2015-06-20 20:45 | 2015-06-20 | 6 | 20 | 184 | 55 | 1
2015-06-20 21:00 | 2015-06-20 | 6 | 21 | 175 | 54.9333 | 1
2015-06-20 21:15 | 2015-06-20 | 6 | 21 | 188 | 54.6833 | 1
2015-06-20 21:30 | 2015-06-20 | 6 | 21 | 191 | 54.4333 | 1
2015-06-20 21:45 | 2015-06-20 | 6 | 21 | 176 | 54.1833 | 1
2015-06-20 22:00 | 2015-06-20 | 6 | 22 | 175 | 54.0667 | 1
2015-06-20 22:15 | 2015-06-20 | 6 | 22 | 167 | 54.3167 | 1
2015-06-20 22:30 | 2015-06-20 | 6 | 22 | 188 | 54.5667 | 1
2015-06-20 22:45 | 2015-06-20 | 6 | 22 | 172 | 54.8167 | 1
2015-06-20 23:00 | 2015-06-20 | 6 | 23 | 178 | 55 | 1
2015-06-20 23:15 | 2015-06-20 | 6 | 23 | 179 | 55 | 1
2015-06-20 23:30 | 2015-06-20 | 6 | 23 | 178 | 55 | 1
2015-06-20 23:45 | 2015-06-20 | 6 | 23 | 183 | 55 | 1
2015-06-21 | 2015-06-21 | 7 | 0 | 175 | 55 | 1
2015-06-21 00:15 | 2015-06-21 | 7 | 0 | 161 | 55 | 1
2015-06-21 00:30 | 2015-06-21 | 7 | 0 | 172 | 55 | 1
2015-06-21 00:45 | 2015-06-21 | 7 | 0 | 180 | 55 | 1
2015-06-21 01:00 | 2015-06-21 | 7 | 1 | 167 | 55 | 1
2015-06-21 01:15 | 2015-06-21 | 7 | 1 | 161 | 55 | 1
2015-06-21 01:30 | 2015-06-21 | 7 | 1 | 164 | 55 | 1
2015-06-21 01:45 | 2015-06-21 | 7 | 1 | 163 | 55 | 1
2015-06-21 02:00 | 2015-06-21 | 7 | 2 | 174 | 55 | 1
2015-06-21 02:15 | 2015-06-21 | 7 | 2 | 164 | 55 | 1
2015-06-21 02:30 | 2015-06-21 | 7 | 2 | 160 | 55 | 1
2015-06-21 02:45 | 2015-06-21 | 7 | 2 | 161 | 55 | 1
2015-06-21 03:00 | 2015-06-21 | 7 | 3 | 173 | 55 | 1
2015-06-21 03:15 | 2015-06-21 | 7 | 3 | 165 | 55 | 1
2015-06-21 03:30 | 2015-06-21 | 7 | 3 | 156 | 55 | 1
2015-06-21 03:45 | 2015-06-21 | 7 | 3 | 159 | 55 | 1
2015-06-21 04:00 | 2015-06-21 | 7 | 4 | 160 | 55 | 1
2015-06-21 04:15 | 2015-06-21 | 7 | 4 | 170 | 55 | 1
2015-06-21 04:30 | 2015-06-21 | 7 | 4 | 154 | 55 | 1
2015-06-21 04:45 | 2015-06-21 | 7 | 4 | 151 | 55 | 1
2015-06-21 05:00 | 2015-06-21 | 7 | 5 | 149 | 55.0667 | 1
2015-06-21 05:15 | 2015-06-21 | 7 | 5 | 152 | 55.3167 | 1
2015-06-21 05:30 | 2015-06-21 | 7 | 5 | 155 | 55.5667 | 1
2015-06-21 05:45 | 2015-06-21 | 7 | 5 | 160 | 55.8167 | 1
2015-06-21 06:00 | 2015-06-21 | 7 | 6 | 152 | 56.0667 | 1
2015-06-21 06:15 | 2015-06-21 | 7 | 6 | 148 | 56.3167 | 1
2015-06-21 06:30 | 2015-06-21 | 7 | 6 | 158 | 56.5667 | 1
2015-06-21 06:45 | 2015-06-21 | 7 | 6 | 177 | 56.8167 | 1
2015-06-21 07:00 | 2015-06-21 | 7 | 7 | 166 | 57 | 1
2015-06-21 07:15 | 2015-06-21 | 7 | 7 | 163 | 57 | 1
2015-06-21 07:30 | 2015-06-21 | 7 | 7 | 158 | 57.6667 | 1
2015-06-21 07:45 | 2015-06-21 | 7 | 7 | 156 | 58.4359 | 1
2015-06-21 08:00 | 2015-06-21 | 7 | 8 | 171 | 59.0667 | 1
2015-06-21 08:15 | 2015-06-21 | 7 | 8 | 166 | 59.3167 | 1
2015-06-21 08:30 | 2015-06-21 | 7 | 8 | 181 | 59.5667 | 1
2015-06-21 08:45 | 2015-06-21 | 7 | 8 | 169 | 59.8167 | 1
2015-06-21 09:00 | 2015-06-21 | 7 | 9 | 167 | 60 | 1
2015-06-21 09:15 | 2015-06-21 | 7 | 9 | 179 | 60 | 1
2015-06-21 09:30 | 2015-06-21 | 7 | 9 | 176 | 60 | 1
2015-06-21 09:45 | 2015-06-21 | 7 | 9 | 175 | 60 | 1
2015-06-21 10:00 | 2015-06-21 | 7 | 10 | 172 | 60.2 | 1
2015-06-21 10:15 | 2015-06-21 | 7 | 10 | 173 | 60.95 | 1
2015-06-21 10:30 | 2015-06-21 | 7 | 10 | 191 | 61.7 | 1
2015-06-21 10:45 | 2015-06-21 | 7 | 10 | 181 | 62.45 | 1
2015-06-21 11:00 | 2015-06-21 | 7 | 11 | 185 | 63 | 1
2015-06-21 11:15 | 2015-06-21 | 7 | 11 | 179 | 63 | 1
2015-06-21 11:30 | 2015-06-21 | 7 | 11 | 190 | 63 | 1
2015-06-21 11:45 | 2015-06-21 | 7 | 11 | 207 | 63 | 1
2015-06-21 12:00 | 2015-06-21 | 7 | 12 | 191 | 63.0667 | 1
2015-06-21 12:15 | 2015-06-21 | 7 | 12 | 187 | 63.3167 | 1
2015-06-21 12:30 | 2015-06-21 | 7 | 12 | 189 | 63.5667 | 1
2015-06-21 12:45 | 2015-06-21 | 7 | 12 | 189 | 63.8167 | 1
2015-06-21 13:00 | 2015-06-21 | 7 | 13 | 203 | 64.0667 | 1
2015-06-21 13:15 | 2015-06-21 | 7 | 13 | 191 | 64.3167 | 1
2015-06-21 13:30 | 2015-06-21 | 7 | 13 | 190 | 64.5667 | 1
2015-06-21 13:45 | 2015-06-21 | 7 | 13 | 187 | 64.8167 | 1
2015-06-21 14:00 | 2015-06-21 | 7 | 14 | 203 | 65.0667 | 2
2015-06-21 14:15 | 2015-06-21 | 7 | 14 | 193 | 65.3167 | 2
2015-06-21 14:30 | 2015-06-21 | 7 | 14 | 187 | 65.5667 | 2
2015-06-21 14:45 | 2015-06-21 | 7 | 14 | 192 | 65.8167 | 2
2015-06-21 15:00 | 2015-06-21 | 7 | 15 | 194 | 65.8667 | 2
2015-06-21 15:15 | 2015-06-21 | 7 | 15 | 209 | 65.3667 | 2
2015-06-21 15:30 | 2015-06-21 | 7 | 15 | 201 | 64.8667 | 1
2015-06-21 15:45 | 2015-06-21 | 7 | 15 | 204 | 64.3667 | 1
2015-06-21 16:00 | 2015-06-21 | 7 | 16 | 194 | 63.9333 | 1
2015-06-21 16:15 | 2015-06-21 | 7 | 16 | 199 | 63.6833 | 1
2015-06-21 16:30 | 2015-06-21 | 7 | 16 | 216 | 63.4333 | 1
2015-06-21 16:45 | 2015-06-21 | 7 | 16 | 203 | 63.1833 | 1
2015-06-21 17:00 | 2015-06-21 | 7 | 17 | 207 | 62.8667 | 1
2015-06-21 17:15 | 2015-06-21 | 7 | 17 | 211 | 62.3667 | 1
2015-06-21 17:30 | 2015-06-21 | 7 | 17 | 213 | 61.8667 | 1
2015-06-21 17:45 | 2015-06-21 | 7 | 17 | 220 | 61.3667 | 1
2015-06-21 18:00 | 2015-06-21 | 7 | 18 | 204 | 60.8667 | 1
2015-06-21 18:15 | 2015-06-21 | 7 | 18 | 199 | 60.3667 | 1
2015-06-21 18:30 | 2015-06-21 | 7 | 18 | 204 | 59.8667 | 1
2015-06-21 18:45 | 2015-06-21 | 7 | 18 | 201 | 59.3667 | 1
2015-06-21 19:00 | 2015-06-21 | 7 | 19 | 213 | 58.8667 | 1
2015-06-21 19:15 | 2015-06-21 | 7 | 19 | 199 | 58.3667 | 1
2015-06-21 19:30 | 2015-06-21 | 7 | 19 | 197 | 57.8667 | 1
2015-06-21 19:45 | 2015-06-21 | 7 | 19 | 197 | 57.3667 | 1
2015-06-21 20:00 | 2015-06-21 | 7 | 20 | 200 | 57 | 1
2015-06-21 20:15 | 2015-06-21 | 7 | 20 | 200 | 57 | 1
2015-06-21 20:30 | 2015-06-21 | 7 | 20 | 194 | 57 | 1
2015-06-21 20:45 | 2015-06-21 | 7 | 20 | 178 | 57 | 1
2015-06-21 21:00 | 2015-06-21 | 7 | 21 | 188 | 56.814 | 1
2015-06-21 21:15 | 2015-06-21 | 7 | 21 | 188 | 56.1163 | 1
2015-06-21 21:30 | 2015-06-21 | 7 | 21 | 174 | 55.4186 | 1
2015-06-21 21:45 | 2015-06-21 | 7 | 21 | 163 | 55.3529 | 1
2015-06-21 22:00 | 2015-06-21 | 7 | 22 | 157 | 56 | 1
2015-06-21 22:15 | 2015-06-21 | 7 | 22 | 170 | 56 | 1
2015-06-21 22:30 | 2015-06-21 | 7 | 22 | 165 | 56 | 1
2015-06-21 22:45 | 2015-06-21 | 7 | 22 | 157 | 56 | 1
2015-06-21 23:00 | 2015-06-21 | 7 | 23 | 159 | 56.0667 | 1
2015-06-21 23:15 | 2015-06-21 | 7 | 23 | 160 | 56.3167 | 1
2015-06-21 23:30 | 2015-06-21 | 7 | 23 | 164 | 56.5667 | 1
2015-06-21 23:45 | 2015-06-21 | 7 | 23 | 171 | 56.8167 | 1
2015-06-22 | 2015-06-22 | 1 | 0 | 168 | 56.9333 | 1
2015-06-22 00:15 | 2015-06-22 | 1 | 0 | 159 | 56.6833 | 1
2015-06-22 00:30 | 2015-06-22 | 1 | 0 | 158 | 56.4333 | 1
2015-06-22 00:45 | 2015-06-22 | 1 | 0 | 159 | 56.1833 | 1
2015-06-22 01:00 | 2015-06-22 | 1 | 1 | 164 | 56 | 1
2015-06-22 01:15 | 2015-06-22 | 1 | 1 | 166 | 56 | 1
2015-06-22 01:30 | 2015-06-22 | 1 | 1 | 155 | 56 | 1
2015-06-22 01:45 | 2015-06-22 | 1 | 1 | 149 | 56 | 1
2015-06-22 02:00 | 2015-06-22 | 1 | 2 | 149 | 56 | 1
2015-06-22 02:15 | 2015-06-22 | 1 | 2 | 143 | 56 | 1
2015-06-22 02:30 | 2015-06-22 | 1 | 2 | 150 | 56 | 1
2015-06-22 02:45 | 2015-06-22 | 1 | 2 | 136 | 56 | 1
2015-06-22 03:00 | 2015-06-22 | 1 | 3 | 145 | 56 | 1
2015-06-22 03:15 | 2015-06-22 | 1 | 3 | 134 | 56 | 1
2015-06-22 03:30 | 2015-06-22 | 1 | 3 | 137 | 56 | 1
2015-06-22 03:45 | 2015-06-22 | 1 | 3 | 138 | 56 | 1
2015-06-22 04:00 | 2015-06-22 | 1 | 4 | 144 | 55.9 | 1
2015-06-22 04:15 | 2015-06-22 | 1 | 4 | 136 | 55.525 | 1
2015-06-22 04:30 | 2015-06-22 | 1 | 4 | 138 | 55.15 | 1
2015-06-22 04:45 | 2015-06-22 | 1 | 4 | 134 | 55 | 1
2015-06-22 05:00 | 2015-06-22 | 1 | 5 | 135 | 55 | 1
2015-06-22 05:15 | 2015-06-22 | 1 | 5 | 142 | 55 | 1
2015-06-22 05:30 | 2015-06-22 | 1 | 5 | 153 | 55 | 1
2015-06-22 05:45 | 2015-06-22 | 1 | 5 | 148 | 55 | 1
2015-06-22 06:00 | 2015-06-22 | 1 | 6 | 152 | 55 | 1
2015-06-22 06:15 | 2015-06-22 | 1 | 6 | 150 | 55 | 1
2015-06-22 06:30 | 2015-06-22 | 1 | 6 | 149 | 55 | 1
2015-06-22 06:45 | 2015-06-22 | 1 | 6 | 151 | 55 | 1
2015-06-22 07:00 | 2015-06-22 | 1 | 7 | 156 | 55.0667 | 1
2015-06-22 07:15 | 2015-06-22 | 1 | 7 | 160 | 55.3167 | 1
2015-06-22 07:30 | 2015-06-22 | 1 | 7 | 165 | 55.5667 | 1
2015-06-22 07:45 | 2015-06-22 | 1 | 7 | 156 | 55.8167 | 1
2015-06-22 08:00 | 2015-06-22 | 1 | 8 | 156 | 56.2069 | 1
2015-06-22 08:15 | 2015-06-22 | 1 | 8 | 167 | 56.9828 | 1
2015-06-22 08:30 | 2015-06-22 | 1 | 8 | 176 | 57.7586 | 1
2015-06-22 08:45 | 2015-06-22 | 1 | 8 | 186 | 58.5345 | 1
2015-06-22 09:00 | 2015-06-22 | 1 | 9 | 183 | 59.0667 | 1
2015-06-22 09:15 | 2015-06-22 | 1 | 9 | 200 | 59.3167 | 1
2015-06-22 09:30 | 2015-06-22 | 1 | 9 | 190 | 59.5667 | 1
2015-06-22 09:45 | 2015-06-22 | 1 | 9 | 211 | 59.8167 | 1
2015-06-22 10:00 | 2015-06-22 | 1 | 10 | 210 | 60 | 1
2015-06-22 10:15 | 2015-06-22 | 1 | 10 | 217 | 60 | 1
2015-06-22 10:30 | 2015-06-22 | 1 | 10 | 211 | 60 | 1
2015-06-22 10:45 | 2015-06-22 | 1 | 10 | 202 | 60 | 1
2015-06-22 11:00 | 2015-06-22 | 1 | 11 | 199 | 60.0667 | 1
2015-06-22 11:15 | 2015-06-22 | 1 | 11 | 208 | 60.3167 | 1
2015-06-22 11:30 | 2015-06-22 | 1 | 11 | 221 | 60.5667 | 1
2015-06-22 11:45 | 2015-06-22 | 1 | 11 | 213 | 60.8167 | 1
2015-06-22 12:00 | 2015-06-22 | 1 | 12 | 217 | 61.0667 | 1
2015-06-22 12:15 | 2015-06-22 | 1 | 12 | 213 | 61.3167 | 1
2015-06-22 12:30 | 2015-06-22 | 1 | 12 | 232 | 61.5667 | 1
2015-06-22 12:45 | 2015-06-22 | 1 | 12 | 211 | 61.8167 | 1
2015-06-22 13:00 | 2015-06-22 | 1 | 13 | 218 | 62 | 1
2015-06-22 13:15 | 2015-06-22 | 1 | 13 | 219 | 62 | 1
2015-06-22 13:30 | 2015-06-22 | 1 | 13 | 225 | 62 | 1
2015-06-22 13:45 | 2015-06-22 | 1 | 13 | 225 | 62 | 1
2015-06-22 14:00 | 2015-06-22 | 1 | 14 | 220 | 62.1333 | 1
2015-06-22 14:15 | 2015-06-22 | 1 | 14 | 219 | 62.6333 | 1
2015-06-22 14:30 | 2015-06-22 | 1 | 14 | 220 | 63.1333 | 1
2015-06-22 14:45 | 2015-06-22 | 1 | 14 | 219 | 63.6333 | 1
2015-06-22 15:00 | 2015-06-22 | 1 | 15 | 225 | 63.8667 | 1
2015-06-22 15:15 | 2015-06-22 | 1 | 15 | 229 | 63.3667 | 1
2015-06-22 15:30 | 2015-06-22 | 1 | 15 | 216 | 62.8667 | 1
2015-06-22 15:45 | 2015-06-22 | 1 | 15 | 219 | 62.3667 | 1
2015-06-22 16:00 | 2015-06-22 | 1 | 16 | 216 | 61.9333 | 1
2015-06-22 16:15 | 2015-06-22 | 1 | 16 | 235 | 61.6833 | 1
2015-06-22 16:30 | 2015-06-22 | 1 | 16 | 234 | 61.4333 | 1
2015-06-22 16:45 | 2015-06-22 | 1 | 16 | 220 | 61.1833 | 1
2015-06-22 17:00 | 2015-06-22 | 1 | 17 | 221 | 60.9333 | 1
2015-06-22 17:15 | 2015-06-22 | 1 | 17 | 228 | 60.6833 | 1
2015-06-22 17:30 | 2015-06-22 | 1 | 17 | 237 | 60.4333 | 1
2015-06-22 17:45 | 2015-06-22 | 1 | 17 | 217 | 60.1833 | 1
2015-06-22 18:00 | 2015-06-22 | 1 | 18 | 226 | 59.9333 | 1
2015-06-22 18:15 | 2015-06-22 | 1 | 18 | 217 | 59.6833 | 1
2015-06-22 18:30 | 2015-06-22 | 1 | 18 | 227 | 59.4333 | 1
2015-06-22 18:45 | 2015-06-22 | 1 | 18 | 226 | 59.1833 | 1
2015-06-22 19:00 | 2015-06-22 | 1 | 19 | 211 | 58.9333 | 1
2015-06-22 19:15 | 2015-06-22 | 1 | 19 | 217 | 58.6833 | 1
2015-06-22 19:30 | 2015-06-22 | 1 | 19 | 215 | 58.4333 | 1
2015-06-22 19:45 | 2015-06-22 | 1 | 19 | 209 | 58.1833 | 1
2015-06-22 20:00 | 2015-06-22 | 1 | 20 | 223 | 57.9333 | 1
2015-06-22 20:15 | 2015-06-22 | 1 | 20 | 200 | 57.6833 | 1
2015-06-22 20:30 | 2015-06-22 | 1 | 20 | 202 | 57.4333 | 1
2015-06-22 20:45 | 2015-06-22 | 1 | 20 | 196 | 57.1833 | 1
2015-06-22 21:00 | 2015-06-22 | 1 | 21 | 209 | 57 | 1
2015-06-22 21:15 | 2015-06-22 | 1 | 21 | 182 | 57 | 1
2015-06-22 21:30 | 2015-06-22 | 1 | 21 | 177 | 57 | 1
2015-06-22 21:45 | 2015-06-22 | 1 | 21 | 190 | 57 | 1
2015-06-22 22:00 | 2015-06-22 | 1 | 22 | 194 | 56.9333 | 1
2015-06-22 22:15 | 2015-06-22 | 1 | 22 | 185 | 56.6833 | 1
2015-06-22 22:30 | 2015-06-22 | 1 | 22 | 181 | 56.4333 | 1
2015-06-22 22:45 | 2015-06-22 | 1 | 22 | 174 | 56.1833 | 1
2015-06-22 23:00 | 2015-06-22 | 1 | 23 | 182 | 56.0667 | 1
2015-06-22 23:15 | 2015-06-22 | 1 | 23 | 177 | 56.3167 | 1
2015-06-22 23:30 | 2015-06-22 | 1 | 23 | 177 | 56.5667 | 1
2015-06-22 23:45 | 2015-06-22 | 1 | 23 | 172 | 56.8167 | 1
2015-06-23 | 2015-06-23 | 2 | 0 | 162 | 56.9333 | 1
2015-06-23 00:15 | 2015-06-23 | 2 | 0 | 177 | 56.6833 | 1
2015-06-23 00:30 | 2015-06-23 | 2 | 0 | 173 | 56.4333 | 1
2015-06-23 00:45 | 2015-06-23 | 2 | 0 | 162 | 56.1833 | 1
2015-06-23 01:00 | 2015-06-23 | 2 | 1 | 160 | 55.9333 | 1
2015-06-23 01:15 | 2015-06-23 | 2 | 1 | 160 | 55.6833 | 1
2015-06-23 01:30 | 2015-06-23 | 2 | 1 | 162 | 55.4333 | 1
2015-06-23 01:45 | 2015-06-23 | 2 | 1 | 166 | 55.1833 | 1
2015-06-23 02:00 | 2015-06-23 | 2 | 2 | 155 | 55 | 1
2015-06-23 02:15 | 2015-06-23 | 2 | 2 | 150 | 55 | 1
2015-06-23 02:30 | 2015-06-23 | 2 | 2 | 159 | 55 | 1
2015-06-23 02:45 | 2015-06-23 | 2 | 2 | 157 | 55 | 1
2015-06-23 03:00 | 2015-06-23 | 2 | 3 | 149 | 54.9333 | 1
2015-06-23 03:15 | 2015-06-23 | 2 | 3 | 150 | 54.6833 | 1
2015-06-23 03:30 | 2015-06-23 | 2 | 3 | 148 | 54.4333 | 1
2015-06-23 03:45 | 2015-06-23 | 2 | 3 | 148 | 54.1833 | 1
2015-06-23 04:00 | 2015-06-23 | 2 | 4 | 158 | 54 | 1
2015-06-23 04:15 | 2015-06-23 | 2 | 4 | 155 | 54 | 1
2015-06-23 04:30 | 2015-06-23 | 2 | 4 | 146 | 54 | 1
2015-06-23 04:45 | 2015-06-23 | 2 | 4 | 141 | 54 | 1
2015-06-23 05:00 | 2015-06-23 | 2 | 5 | 135 | 54.1333 | 1
2015-06-23 05:15 | 2015-06-23 | 2 | 5 | 133 | 54.6333 | 1
2015-06-23 05:30 | 2015-06-23 | 2 | 5 | 145 | 55.1333 | 1
2015-06-23 05:45 | 2015-06-23 | 2 | 5 | 138 | 55.6333 | 1
2015-06-23 06:00 | 2015-06-23 | 2 | 6 | 136 | 56.1333 | 1
2015-06-23 06:15 | 2015-06-23 | 2 | 6 | 129 | 56.6333 | 1
2015-06-23 06:30 | 2015-06-23 | 2 | 6 | 143 | 57.1333 | 1
2015-06-23 06:45 | 2015-06-23 | 2 | 6 | 152 | 57.6333 | 1
2015-06-23 07:00 | 2015-06-23 | 2 | 7 | 164 | 58.1333 | 1
2015-06-23 07:15 | 2015-06-23 | 2 | 7 | 155 | 58.6333 | 1
2015-06-23 07:30 | 2015-06-23 | 2 | 7 | 158 | 59.1333 | 1
2015-06-23 07:45 | 2015-06-23 | 2 | 7 | 156 | 59.6333 | 1
2015-06-23 08:00 | 2015-06-23 | 2 | 8 | 177 | 60.2 | 1
2015-06-23 08:15 | 2015-06-23 | 2 | 8 | 178 | 60.95 | 1
2015-06-23 08:30 | 2015-06-23 | 2 | 8 | 187 | 61.7 | 1
2015-06-23 08:45 | 2015-06-23 | 2 | 8 | 190 | 62.45 | 1
2015-06-23 09:00 | 2015-06-23 | 2 | 9 | 188 | 63.1333 | 1
2015-06-23 09:15 | 2015-06-23 | 2 | 9 | 186 | 63.6333 | 1
2015-06-23 09:30 | 2015-06-23 | 2 | 9 | 210 | 64.1333 | 1
2015-06-23 09:45 | 2015-06-23 | 2 | 9 | 205 | 64.6333 | 1
2015-06-23 10:00 | 2015-06-23 | 2 | 10 | 200 | 65.1333 | 2
2015-06-23 10:15 | 2015-06-23 | 2 | 10 | 209 | 65.6333 | 2
2015-06-23 10:30 | 2015-06-23 | 2 | 10 | 219 | 66.1333 | 2
2015-06-23 10:45 | 2015-06-23 | 2 | 10 | 215 | 66.6333 | 2
2015-06-23 11:00 | 2015-06-23 | 2 | 11 | 215 | 67.0667 | 2
2015-06-23 11:15 | 2015-06-23 | 2 | 11 | 209 | 67.3167 | 2
2015-06-23 11:30 | 2015-06-23 | 2 | 11 | 215 | 67.5667 | 2
2015-06-23 11:45 | 2015-06-23 | 2 | 11 | 226 | 67.8167 | 2
2015-06-23 12:00 | 2015-06-23 | 2 | 12 | 224 | 68 | 2
2015-06-23 12:15 | 2015-06-23 | 2 | 12 | 220 | 68 | 2
2015-06-23 12:30 | 2015-06-23 | 2 | 12 | 218 | 68 | 2
2015-06-23 12:45 | 2015-06-23 | 2 | 12 | 217 | 68 | 2
2015-06-23 13:00 | 2015-06-23 | 2 | 13 | 231 | 67.8667 | 2
2015-06-23 13:15 | 2015-06-23 | 2 | 13 | 234 | 67.3667 | 2
2015-06-23 13:30 | 2015-06-23 | 2 | 13 | 232 | 66.8667 | 2
2015-06-23 13:45 | 2015-06-23 | 2 | 13 | 231 | 66.3667 | 2
2015-06-23 14:00 | 2015-06-23 | 2 | 14 | 231 | 65.9333 | 2
2015-06-23 14:15 | 2015-06-23 | 2 | 14 | 249 | 65.6833 | 2
2015-06-23 14:30 | 2015-06-23 | 2 | 14 | 245 | 65.4333 | 2
2015-06-23 14:45 | 2015-06-23 | 2 | 14 | 233 | 65.1833 | 2
2015-06-23 15:00 | 2015-06-23 | 2 | 15 | 233 | 65.0667 | 2
2015-06-23 15:15 | 2015-06-23 | 2 | 15 | 239 | 65.3167 | 2
2015-06-23 15:30 | 2015-06-23 | 2 | 15 | 256 | 65.5667 | 2
2015-06-23 15:45 | 2015-06-23 | 2 | 15 | 253 | 65.8167 | 2
2015-06-23 16:00 | 2015-06-23 | 2 | 16 | 251 | 65.9333 | 2
2015-06-23 16:15 | 2015-06-23 | 2 | 16 | 254 | 65.6833 | 2
2015-06-23 16:30 | 2015-06-23 | 2 | 16 | 251 | 65.4333 | 2
2015-06-23 16:45 | 2015-06-23 | 2 | 16 | 268 | 65.1833 | 2
2015-06-23 17:00 | 2015-06-23 | 2 | 17 | 254 | 64.8667 | 1
2015-06-23 17:15 | 2015-06-23 | 2 | 17 | 261 | 64.3667 | 1
2015-06-23 17:30 | 2015-06-23 | 2 | 17 | 245 | 63.8667 | 1
2015-06-23 17:45 | 2015-06-23 | 2 | 17 | 244 | 63.3667 | 1
2015-06-23 18:00 | 2015-06-23 | 2 | 18 | 250 | 62.9333 | 1
2015-06-23 18:15 | 2015-06-23 | 2 | 18 | 249 | 62.6833 | 1
2015-06-23 18:30 | 2015-06-23 | 2 | 18 | 230 | 62.4333 | 1
2015-06-23 18:45 | 2015-06-23 | 2 | 18 | 237 | 62.1833 | 1
2015-06-23 19:00 | 2015-06-23 | 2 | 19 | 231 | 61.8667 | 1
2015-06-23 19:15 | 2015-06-23 | 2 | 19 | 236 | 61.3667 | 1
2015-06-23 19:30 | 2015-06-23 | 2 | 19 | 229 | 60.8667 | 1
2015-06-23 19:45 | 2015-06-23 | 2 | 19 | 221 | 60.3667 | 1
2015-06-23 20:00 | 2015-06-23 | 2 | 20 | 218 | 59.9333 | 1
2015-06-23 20:15 | 2015-06-23 | 2 | 20 | 216 | 59.6833 | 1
2015-06-23 20:30 | 2015-06-23 | 2 | 20 | 226 | 59.4333 | 1
2015-06-23 20:45 | 2015-06-23 | 2 | 20 | 205 | 59.1833 | 1
2015-06-23 21:00 | 2015-06-23 | 2 | 21 | 206 | 58.8667 | 1
2015-06-23 21:15 | 2015-06-23 | 2 | 21 | 195 | 58.3667 | 1
2015-06-23 21:30 | 2015-06-23 | 2 | 21 | 198 | 57.8667 | 1
2015-06-23 21:45 | 2015-06-23 | 2 | 21 | 202 | 57.3667 | 1
2015-06-23 22:00 | 2015-06-23 | 2 | 22 | 183 | 56.9333 | 1
2015-06-23 22:15 | 2015-06-23 | 2 | 22 | 184 | 56.6833 | 1
2015-06-23 22:30 | 2015-06-23 | 2 | 22 | 190 | 56.4333 | 1
2015-06-23 22:45 | 2015-06-23 | 2 | 22 | 189 | 56.1833 | 1
2015-06-23 23:00 | 2015-06-23 | 2 | 23 | 184 | 55.931 | 1
2015-06-23 23:15 | 2015-06-23 | 2 | 23 | 165 | 55.6724 | 1
2015-06-23 23:30 | 2015-06-23 | 2 | 23 | 170 | 55.4138 | 1
2015-06-23 23:45 | 2015-06-23 | 2 | 23 | 165 | 55.1552 | 1
2015-06-24 | 2015-06-24 | 3 | 0 | 184 | 56 | 1
2015-06-24 00:15 | 2015-06-24 | 3 | 0 | 164 | 56 | 1
2015-06-24 00:30 | 2015-06-24 | 3 | 0 | 163 | 56 | 1
2015-06-24 00:45 | 2015-06-24 | 3 | 0 | 170 | 56 | 1
2015-06-24 01:00 | 2015-06-24 | 3 | 1 | 171 | 55.9333 | 1
2015-06-24 01:15 | 2015-06-24 | 3 | 1 | 163 | 55.6833 | 1
2015-06-24 01:30 | 2015-06-24 | 3 | 1 | 164 | 55.4333 | 1
2015-06-24 01:45 | 2015-06-24 | 3 | 1 | 158 | 55.1833 | 1
2015-06-24 02:00 | 2015-06-24 | 3 | 2 | 157 | 55.0667 | 1
2015-06-24 02:15 | 2015-06-24 | 3 | 2 | 163 | 55.3167 | 1
2015-06-24 02:30 | 2015-06-24 | 3 | 2 | 157 | 55.5667 | 1
2015-06-24 02:45 | 2015-06-24 | 3 | 2 | 150 | 55.8167 | 1
2015-06-24 03:00 | 2015-06-24 | 3 | 3 | 151 | 55.9333 | 1
2015-06-24 03:15 | 2015-06-24 | 3 | 3 | 151 | 55.6833 | 1
2015-06-24 03:30 | 2015-06-24 | 3 | 3 | 150 | 55.4333 | 1
2015-06-24 03:45 | 2015-06-24 | 3 | 3 | 165 | 55.1833 | 1
2015-06-24 04:00 | 2015-06-24 | 3 | 4 | 149 | 55 | 1
2015-06-24 04:15 | 2015-06-24 | 3 | 4 | 148 | 55 | 1
2015-06-24 04:30 | 2015-06-24 | 3 | 4 | 143 | 55 | 1
2015-06-24 04:45 | 2015-06-24 | 3 | 4 | 149 | 55 | 1
2015-06-24 05:00 | 2015-06-24 | 3 | 5 | 147 | 54.0667 | 1
2015-06-24 05:15 | 2015-06-24 | 3 | 5 | 153 | 54.3167 | 1
2015-06-24 05:30 | 2015-06-24 | 3 | 5 | 149 | 54.5667 | 1
2015-06-24 05:45 | 2015-06-24 | 3 | 5 | 145 | 54.8167 | 1
2015-06-24 06:00 | 2015-06-24 | 3 | 6 | 138 | 55.2 | 1
2015-06-24 06:15 | 2015-06-24 | 3 | 6 | 142 | 55.95 | 1
2015-06-24 06:30 | 2015-06-24 | 3 | 6 | 150 | 56.7 | 1
2015-06-24 06:45 | 2015-06-24 | 3 | 6 | 159 | 57.45 | 1
2015-06-24 07:00 | 2015-06-24 | 3 | 7 | 152 | 58.1333 | 1
2015-06-24 07:15 | 2015-06-24 | 3 | 7 | 154 | 58.6333 | 1
2015-06-24 07:30 | 2015-06-24 | 3 | 7 | 151 | 59.1333 | 1
2015-06-24 07:45 | 2015-06-24 | 3 | 7 | 154 | 59.6333 | 1
2015-06-24 08:00 | 2015-06-24 | 3 | 8 | 163 | 60.2667 | 1
2015-06-24 08:15 | 2015-06-24 | 3 | 8 | 167 | 61.2667 | 1
2015-06-24 08:30 | 2015-06-24 | 3 | 8 | 168 | 62.2667 | 1
2015-06-24 08:45 | 2015-06-24 | 3 | 8 | 176 | 63.2667 | 1
2015-06-24 09:00 | 2015-06-24 | 3 | 9 | 190 | 64.2 | 1
2015-06-24 09:15 | 2015-06-24 | 3 | 9 | 179 | 64.95 | 1
2015-06-24 09:30 | 2015-06-24 | 3 | 9 | 199 | 65.7 | 2
2015-06-24 09:45 | 2015-06-24 | 3 | 9 | 199 | 66.45 | 2
2015-06-24 10:00 | 2015-06-24 | 3 | 10 | 192 | 67.1333 | 2
2015-06-24 10:15 | 2015-06-24 | 3 | 10 | 202 | 67.6333 | 2
2015-06-24 10:30 | 2015-06-24 | 3 | 10 | 203 | 68.1333 | 2
2015-06-24 10:45 | 2015-06-24 | 3 | 10 | 209 | 68.6333 | 2
2015-06-24 11:00 | 2015-06-24 | 3 | 11 | 226 | 69.0667 | 2
2015-06-24 11:15 | 2015-06-24 | 3 | 11 | 207 | 69.3167 | 2
2015-06-24 11:30 | 2015-06-24 | 3 | 11 | 216 | 69.5667 | 2
2015-06-24 11:45 | 2015-06-24 | 3 | 11 | 218 | 69.8167 | 2
2015-06-24 12:00 | 2015-06-24 | 3 | 12 | 219 | 70 | 2
2015-06-24 12:15 | 2015-06-24 | 3 | 12 | 240 | 70 | 2
2015-06-24 12:30 | 2015-06-24 | 3 | 12 | 223 | 70 | 2
2015-06-24 12:45 | 2015-06-24 | 3 | 12 | 222 | 70 | 2
2015-06-24 13:00 | 2015-06-24 | 3 | 13 | 225 | 69.9333 | 2
2015-06-24 13:15 | 2015-06-24 | 3 | 13 | 235 | 69.6833 | 2
2015-06-24 13:30 | 2015-06-24 | 3 | 13 | 244 | 69.4333 | 2
2015-06-24 13:45 | 2015-06-24 | 3 | 13 | 248 | 69.1833 | 2
2015-06-24 14:00 | 2015-06-24 | 3 | 14 | 238 | 68.9333 | 2
2015-06-24 14:15 | 2015-06-24 | 3 | 14 | 250 | 68.6833 | 2
2015-06-24 14:30 | 2015-06-24 | 3 | 14 | 259 | 68.4333 | 2
2015-06-24 14:45 | 2015-06-24 | 3 | 14 | 272 | 68.1833 | 2
2015-06-24 15:00 | 2015-06-24 | 3 | 15 | 254 | 67.9333 | 2
2015-06-24 15:15 | 2015-06-24 | 3 | 15 | 262 | 67.6833 | 2
2015-06-24 15:30 | 2015-06-24 | 3 | 15 | 257 | 67.4333 | 2
2015-06-24 15:45 | 2015-06-24 | 3 | 15 | 285 | 67.1833 | 2
2015-06-24 16:00 | 2015-06-24 | 3 | 16 | 272 | 66.8667 | 2
2015-06-24 16:15 | 2015-06-24 | 3 | 16 | 269 | 66.3667 | 2
2015-06-24 16:30 | 2015-06-24 | 3 | 16 | 259 | 65.8667 | 2
2015-06-24 16:45 | 2015-06-24 | 3 | 16 | 263 | 65.3667 | 2
2015-06-24 17:00 | 2015-06-24 | 3 | 17 | 263 | 64.8667 | 1
2015-06-24 17:15 | 2015-06-24 | 3 | 17 | 285 | 64.3667 | 1
2015-06-24 17:30 | 2015-06-24 | 3 | 17 | 262 | 63.8667 | 1
2015-06-24 17:45 | 2015-06-24 | 3 | 17 | 264 | 63.3667 | 1
2015-06-24 18:00 | 2015-06-24 | 3 | 18 | 245 | 62.8667 | 1
2015-06-24 18:15 | 2015-06-24 | 3 | 18 | 265 | 62.3667 | 1
2015-06-24 18:30 | 2015-06-24 | 3 | 18 | 251 | 61.8667 | 1
2015-06-24 18:45 | 2015-06-24 | 3 | 18 | 253 | 61.3667 | 1
2015-06-24 19:00 | 2015-06-24 | 3 | 19 | 245 | 60.9333 | 1
2015-06-24 19:15 | 2015-06-24 | 3 | 19 | 239 | 60.6833 | 1
2015-06-24 19:30 | 2015-06-24 | 3 | 19 | 243 | 60.4333 | 1
2015-06-24 19:45 | 2015-06-24 | 3 | 19 | 253 | 60.1833 | 1
2015-06-24 20:00 | 2015-06-24 | 3 | 20 | 229 | 59.9333 | 1
2015-06-24 20:15 | 2015-06-24 | 3 | 20 | 228 | 59.6833 | 1
2015-06-24 20:30 | 2015-06-24 | 3 | 20 | 222 | 59.4333 | 1
2015-06-24 20:45 | 2015-06-24 | 3 | 20 | 227 | 59.1833 | 1
2015-06-24 21:00 | 2015-06-24 | 3 | 21 | 216 | 59 | 1
2015-06-24 21:15 | 2015-06-24 | 3 | 21 | 201 | 59 | 1
2015-06-24 21:30 | 2015-06-24 | 3 | 21 | 198 | 59 | 1
2015-06-24 21:45 | 2015-06-24 | 3 | 21 | 200 | 59 | 1
2015-06-24 22:00 | 2015-06-24 | 3 | 22 | 207 | 59 | 1
2015-06-24 22:15 | 2015-06-24 | 3 | 22 | 198 | 59 | 1
2015-06-24 22:30 | 2015-06-24 | 3 | 22 | 192 | 59 | 1
2015-06-24 22:45 | 2015-06-24 | 3 | 22 | 200 | 59 | 1
2015-06-24 23:00 | 2015-06-24 | 3 | 23 | 200 | 59 | 1
2015-06-24 23:15 | 2015-06-24 | 3 | 23 | 204 | 59 | 1
2015-06-24 23:30 | 2015-06-24 | 3 | 23 | 191 | 59 | 1
2015-06-24 23:45 | 2015-06-24 | 3 | 23 | 183 | 59 | 1
2015-06-25 | 2015-06-25 | 4 | 0 | 190 | 58.9333 | 1
2015-06-25 00:15 | 2015-06-25 | 4 | 0 | 200 | 58.6833 | 1
2015-06-25 00:30 | 2015-06-25 | 4 | 0 | 182 | 58.4333 | 1
2015-06-25 00:45 | 2015-06-25 | 4 | 0 | 180 | 58.1833 | 1
2015-06-25 01:00 | 2015-06-25 | 4 | 1 | 176 | 57.9333 | 1
2015-06-25 01:15 | 2015-06-25 | 4 | 1 | 173 | 57.6833 | 1
2015-06-25 01:30 | 2015-06-25 | 4 | 1 | 193 | 57.4333 | 1
2015-06-25 01:45 | 2015-06-25 | 4 | 1 | 178 | 57.1833 | 1
2015-06-25 02:00 | 2015-06-25 | 4 | 2 | 183 | 57 | 1
2015-06-25 02:15 | 2015-06-25 | 4 | 2 | 172 | 57 | 1
2015-06-25 02:30 | 2015-06-25 | 4 | 2 | 188 | 57 | 1
2015-06-25 02:45 | 2015-06-25 | 4 | 2 | 177 | 57 | 1
2015-06-25 03:00 | 2015-06-25 | 4 | 3 | 170 | 57 | 1
2015-06-25 03:15 | 2015-06-25 | 4 | 3 | 163 | 57 | 1
2015-06-25 03:30 | 2015-06-25 | 4 | 3 | 177 | 57 | 1
2015-06-25 03:45 | 2015-06-25 | 4 | 3 | 186 | 57 | 1
2015-06-25 04:00 | 2015-06-25 | 4 | 4 | 170 | 57 | 1
2015-06-25 04:15 | 2015-06-25 | 4 | 4 | 174 | 57 | 1
2015-06-25 04:30 | 2015-06-25 | 4 | 4 | 164 | 57 | 1
2015-06-25 04:45 | 2015-06-25 | 4 | 4 | 181 | 57 | 1
2015-06-25 05:00 | 2015-06-25 | 4 | 5 | 172 | 57.1333 | 1
2015-06-25 05:15 | 2015-06-25 | 4 | 5 | 172 | 57.6333 | 1
2015-06-25 05:30 | 2015-06-25 | 4 | 5 | 160 | 58.1333 | 1
2015-06-25 05:45 | 2015-06-25 | 4 | 5 | 164 | 58.6333 | 1
2015-06-25 06:00 | 2015-06-25 | 4 | 6 | 179 | 59.2667 | 1
2015-06-25 06:15 | 2015-06-25 | 4 | 6 | 170 | 60.2667 | 1
2015-06-25 06:30 | 2015-06-25 | 4 | 6 | 166 | 61.2667 | 1
2015-06-25 06:45 | 2015-06-25 | 4 | 6 | 176 | 62.2667 | 1
2015-06-25 07:00 | 2015-06-25 | 4 | 7 | 171 | 63.0667 | 1
2015-06-25 07:15 | 2015-06-25 | 4 | 7 | 196 | 63.3167 | 1
2015-06-25 07:30 | 2015-06-25 | 4 | 7 | 184 | 63.5667 | 1
2015-06-25 07:45 | 2015-06-25 | 4 | 7 | 179 | 63.8167 | 1
2015-06-25 08:00 | 2015-06-25 | 4 | 8 | 182 | 64.1333 | 1
2015-06-25 08:15 | 2015-06-25 | 4 | 8 | 191 | 64.6333 | 1
2015-06-25 08:30 | 2015-06-25 | 4 | 8 | 213 | 65.1333 | 2
2015-06-25 08:45 | 2015-06-25 | 4 | 8 | 198 | 65.6333 | 2
2015-06-25 09:00 | 2015-06-25 | 4 | 9 | 201 | 66.2 | 2
2015-06-25 09:15 | 2015-06-25 | 4 | 9 | 201 | 66.95 | 2
2015-06-25 09:30 | 2015-06-25 | 4 | 9 | 202 | 67.7 | 2
2015-06-25 09:45 | 2015-06-25 | 4 | 9 | 227 | 68.45 | 2
2015-06-25 10:00 | 2015-06-25 | 4 | 10 | 217 | 69.2 | 2
2015-06-25 10:15 | 2015-06-25 | 4 | 10 | 221 | 69.95 | 2
2015-06-25 10:30 | 2015-06-25 | 4 | 10 | 223 | 70.7 | 3
2015-06-25 10:45 | 2015-06-25 | 4 | 10 | 239 | 71.45 | 3
2015-06-25 11:00 | 2015-06-25 | 4 | 11 | 236 | 72.1333 | 3
2015-06-25 11:15 | 2015-06-25 | 4 | 11 | 230 | 72.6333 | 3
2015-06-25 11:30 | 2015-06-25 | 4 | 11 | 248 | 73.1333 | 3
2015-06-25 11:45 | 2015-06-25 | 4 | 11 | 238 | 73.6333 | 3
2015-06-25 12:00 | 2015-06-25 | 4 | 12 | 263 | 74.1333 | 3
2015-06-25 12:15 | 2015-06-25 | 4 | 12 | 259 | 74.6333 | 3
2015-06-25 12:30 | 2015-06-25 | 4 | 12 | 258 | 75.1333 | 4
2015-06-25 12:45 | 2015-06-25 | 4 | 12 | 252 | 75.6333 | 4
2015-06-25 13:00 | 2015-06-25 | 4 | 13 | 267 | 75.8667 | 4
2015-06-25 13:15 | 2015-06-25 | 4 | 13 | 270 | 75.3667 | 4
2015-06-25 13:30 | 2015-06-25 | 4 | 13 | 290 | 74.8667 | 3
2015-06-25 13:45 | 2015-06-25 | 4 | 13 | 263 | 74.3667 | 3
2015-06-25 14:00 | 2015-06-25 | 4 | 14 | 275 | 74 | 3
2015-06-25 14:15 | 2015-06-25 | 4 | 14 | 263 | 74 | 3
2015-06-25 14:30 | 2015-06-25 | 4 | 14 | 279 | 74 | 3
2015-06-25 14:45 | 2015-06-25 | 4 | 14 | 298 | 74 | 3
2015-06-25 15:00 | 2015-06-25 | 4 | 15 | 287 | 73.9333 | 3
2015-06-25 15:15 | 2015-06-25 | 4 | 15 | 292 | 73.6833 | 3
2015-06-25 15:30 | 2015-06-25 | 4 | 15 | 285 | 73.4333 | 3
2015-06-25 15:45 | 2015-06-25 | 4 | 15 | 284 | 73.1833 | 3
2015-06-25 16:00 | 2015-06-25 | 4 | 16 | 302 | 72.8667 | 3
2015-06-25 16:15 | 2015-06-25 | 4 | 16 | 280 | 72.3667 | 3
2015-06-25 16:30 | 2015-06-25 | 4 | 16 | 289 | 71.8667 | 3
2015-06-25 16:45 | 2015-06-25 | 4 | 16 | 270 | 71.3667 | 3
2015-06-25 17:00 | 2015-06-25 | 4 | 17 | 278 | 70.8 | 3
2015-06-25 17:15 | 2015-06-25 | 4 | 17 | 287 | 70.05 | 3
2015-06-25 17:30 | 2015-06-25 | 4 | 17 | 286 | 69.3 | 2
2015-06-25 17:45 | 2015-06-25 | 4 | 17 | 278 | 68.55 | 2
2015-06-25 18:00 | 2015-06-25 | 4 | 18 | 280 | 67.8667 | 2
2015-06-25 18:15 | 2015-06-25 | 4 | 18 | 270 | 67.3667 | 2
2015-06-25 18:30 | 2015-06-25 | 4 | 18 | 276 | 66.8667 | 2
2015-06-25 18:45 | 2015-06-25 | 4 | 18 | 283 | 66.3667 | 2
2015-06-25 19:00 | 2015-06-25 | 4 | 19 | 269 | 65.8 | 2
2015-06-25 19:15 | 2015-06-25 | 4 | 19 | 264 | 65.05 | 2
2015-06-25 19:30 | 2015-06-25 | 4 | 19 | 261 | 64.3 | 1
2015-06-25 19:45 | 2015-06-25 | 4 | 19 | 257 | 63.55 | 1
2015-06-25 20:00 | 2015-06-25 | 4 | 20 | 256 | 62.9333 | 1
2015-06-25 20:15 | 2015-06-25 | 4 | 20 | 262 | 62.6833 | 1
2015-06-25 20:30 | 2015-06-25 | 4 | 20 | 237 | 62.4333 | 1
2015-06-25 20:45 | 2015-06-25 | 4 | 20 | 237 | 62.1833 | 1
2015-06-25 21:00 | 2015-06-25 | 4 | 21 | 238 | 62 | 1
2015-06-25 21:15 | 2015-06-25 | 4 | 21 | 213 | 62 | 1
2015-06-25 21:30 | 2015-06-25 | 4 | 21 | 231 | 62 | 1
2015-06-25 21:45 | 2015-06-25 | 4 | 21 | 206 | 62 | 1
2015-06-25 22:00 | 2015-06-25 | 4 | 22 | 213 | 61.9333 | 1
2015-06-25 22:15 | 2015-06-25 | 4 | 22 | 209 | 61.6833 | 1
2015-06-25 22:30 | 2015-06-25 | 4 | 22 | 226 | 61.4333 | 1
2015-06-25 22:45 | 2015-06-25 | 4 | 22 | 218 | 61.1833 | 1
2015-06-25 23:00 | 2015-06-25 | 4 | 23 | 212 | 61 | 1
2015-06-25 23:15 | 2015-06-25 | 4 | 23 | 208 | 61 | 1
2015-06-25 23:30 | 2015-06-25 | 4 | 23 | 208 | 61 | 1
2015-06-25 23:45 | 2015-06-25 | 4 | 23 | 219 | 61 | 1
2015-06-26 | 2015-06-26 | 5 | 0 | 205 | 60.8667 | 1
2015-06-26 00:15 | 2015-06-26 | 5 | 0 | 202 | 60.3667 | 1
2015-06-26 00:30 | 2015-06-26 | 5 | 0 | 198 | 59.8667 | 1
2015-06-26 00:45 | 2015-06-26 | 5 | 0 | 211 | 59.3667 | 1
2015-06-26 01:00 | 2015-06-26 | 5 | 1 | 200 | 59 | 1
2015-06-26 01:15 | 2015-06-26 | 5 | 1 | 192 | 59 | 1
2015-06-26 01:30 | 2015-06-26 | 5 | 1 | 194 | 59 | 1
2015-06-26 01:45 | 2015-06-26 | 5 | 1 | 189 | 59 | 1
2015-06-26 02:00 | 2015-06-26 | 5 | 2 | 208 | 59 | 1
2015-06-26 02:15 | 2015-06-26 | 5 | 2 | 185 | 59 | 1
2015-06-26 02:30 | 2015-06-26 | 5 | 2 | 184 | 59 | 1
2015-06-26 02:45 | 2015-06-26 | 5 | 2 | 182 | 59 | 1
2015-06-26 03:00 | 2015-06-26 | 5 | 3 | 187 | 58.8667 | 1
2015-06-26 03:15 | 2015-06-26 | 5 | 3 | 193 | 58.3667 | 1
2015-06-26 03:30 | 2015-06-26 | 5 | 3 | 185 | 57.8667 | 1
2015-06-26 03:45 | 2015-06-26 | 5 | 3 | 177 | 57.3667 | 1
2015-06-26 04:00 | 2015-06-26 | 5 | 4 | 175 | 56.9333 | 1
2015-06-26 04:15 | 2015-06-26 | 5 | 4 | 193 | 56.6833 | 1
2015-06-26 04:30 | 2015-06-26 | 5 | 4 | 185 | 56.4333 | 1
2015-06-26 04:45 | 2015-06-26 | 5 | 4 | 175 | 56.1833 | 1
2015-06-26 05:00 | 2015-06-26 | 5 | 5 | 177 | 56.0667 | 1
2015-06-26 05:15 | 2015-06-26 | 5 | 5 | 180 | 56.3167 | 1
2015-06-26 05:30 | 2015-06-26 | 5 | 5 | 186 | 56.5667 | 1
2015-06-26 05:45 | 2015-06-26 | 5 | 5 | 176 | 56.8167 | 1
2015-06-26 06:00 | 2015-06-26 | 5 | 6 | 182 | 57.2 | 1
2015-06-26 06:15 | 2015-06-26 | 5 | 6 | 171 | 57.95 | 1
2015-06-26 06:30 | 2015-06-26 | 5 | 6 | 186 | 58.7 | 1
2015-06-26 06:45 | 2015-06-26 | 5 | 6 | 186 | 59.45 | 1
2015-06-26 07:00 | 2015-06-26 | 5 | 7 | 179 | 60.2 | 1
2015-06-26 07:15 | 2015-06-26 | 5 | 7 | 179 | 60.95 | 1
2015-06-26 07:30 | 2015-06-26 | 5 | 7 | 176 | 61.7 | 1
2015-06-26 07:45 | 2015-06-26 | 5 | 7 | 192 | 62.45 | 1
2015-06-26 08:00 | 2015-06-26 | 5 | 8 | 202 | 63.2 | 1
2015-06-26 08:15 | 2015-06-26 | 5 | 8 | 190 | 63.95 | 1
2015-06-26 08:30 | 2015-06-26 | 5 | 8 | 201 | 64.7 | 1
2015-06-26 08:45 | 2015-06-26 | 5 | 8 | 200 | 65.45 | 2
2015-06-26 09:00 | 2015-06-26 | 5 | 9 | 211 | 66.2 | 2
2015-06-26 09:15 | 2015-06-26 | 5 | 9 | 212 | 66.95 | 2
2015-06-26 09:30 | 2015-06-26 | 5 | 9 | 207 | 67.7 | 2
2015-06-26 09:45 | 2015-06-26 | 5 | 9 | 217 | 68.45 | 2
2015-06-26 10:00 | 2015-06-26 | 5 | 10 | 225 | 69.2 | 2
2015-06-26 10:15 | 2015-06-26 | 5 | 10 | 237 | 69.95 | 2
2015-06-26 10:30 | 2015-06-26 | 5 | 10 | 229 | 70.7 | 3
2015-06-26 10:45 | 2015-06-26 | 5 | 10 | 237 | 71.45 | 3
2015-06-26 11:00 | 2015-06-26 | 5 | 11 | 246 | 72 | 3
2015-06-26 11:15 | 2015-06-26 | 5 | 11 | 244 | 72 | 3
2015-06-26 11:30 | 2015-06-26 | 5 | 11 | 275 | 71.9259 | 3
2015-06-26 11:45 | 2015-06-26 | 5 | 11 | 258 | 70.8148 | 3
2015-06-26 12:00 | 2015-06-26 | 5 | 12 | 258 | 70.0667 | 3
2015-06-26 12:15 | 2015-06-26 | 5 | 12 | 253 | 70.3167 | 3
2015-06-26 12:30 | 2015-06-26 | 5 | 12 | 256 | 70.5667 | 3
2015-06-26 12:45 | 2015-06-26 | 5 | 12 | 273 | 70.8167 | 3
2015-06-26 13:00 | 2015-06-26 | 5 | 13 | 271 | 71 | 3
2015-06-26 13:15 | 2015-06-26 | 5 | 13 | 274 | 71 | 3
2015-06-26 13:30 | 2015-06-26 | 5 | 13 | 270 | 71 | 3
2015-06-26 13:45 | 2015-06-26 | 5 | 13 | 261 | 71 | 3
2015-06-26 14:00 | 2015-06-26 | 5 | 14 | 275 | 71 | 3
2015-06-26 14:15 | 2015-06-26 | 5 | 14 | 289 | 71 | 3
2015-06-26 14:30 | 2015-06-26 | 5 | 14 | 289 | 71 | 3
2015-06-26 14:45 | 2015-06-26 | 5 | 14 | 271 | 71 | 3
2015-06-26 15:00 | 2015-06-26 | 5 | 15 | 268 | 70.8667 | 3
2015-06-26 15:15 | 2015-06-26 | 5 | 15 | 271 | 70.3667 | 3
2015-06-26 15:30 | 2015-06-26 | 5 | 15 | 277 | 69.8667 | 2
2015-06-26 15:45 | 2015-06-26 | 5 | 15 | 269 | 69.3667 | 2
2015-06-26 16:00 | 2015-06-26 | 5 | 16 | 270 | 68.9333 | 2
2015-06-26 16:15 | 2015-06-26 | 5 | 16 | 275 | 68.6833 | 2
2015-06-26 16:30 | 2015-06-26 | 5 | 16 | 277 | 68.4333 | 2
2015-06-26 16:45 | 2015-06-26 | 5 | 16 | 270 | 68.1833 | 2
2015-06-26 17:00 | 2015-06-26 | 5 | 17 | 276 | 67.8 | 2
2015-06-26 17:15 | 2015-06-26 | 5 | 17 | 271 | 67.05 | 2
2015-06-26 17:30 | 2015-06-26 | 5 | 17 | 270 | 66.3 | 2
2015-06-26 17:45 | 2015-06-26 | 5 | 17 | 261 | 65.55 | 2
2015-06-26 18:00 | 2015-06-26 | 5 | 18 | 265 | 64.8667 | 1
2015-06-26 18:15 | 2015-06-26 | 5 | 18 | 265 | 64.3667 | 1
2015-06-26 18:30 | 2015-06-26 | 5 | 18 | 263 | 63.8667 | 1
2015-06-26 18:45 | 2015-06-26 | 5 | 18 | 265 | 63.3667 | 1
2015-06-26 19:00 | 2015-06-26 | 5 | 19 | 255 | 62.8667 | 1
2015-06-26 19:15 | 2015-06-26 | 5 | 19 | 257 | 62.3667 | 1
2015-06-26 19:30 | 2015-06-26 | 5 | 19 | 252 | 61.8667 | 1
2015-06-26 19:45 | 2015-06-26 | 5 | 19 | 245 | 61.3667 | 1
2015-06-26 20:00 | 2015-06-26 | 5 | 20 | 254 | 61 | 1
2015-06-26 20:15 | 2015-06-26 | 5 | 20 | 241 | 61 | 1
2015-06-26 20:30 | 2015-06-26 | 5 | 20 | 229 | 61 | 1
2015-06-26 20:45 | 2015-06-26 | 5 | 20 | 225 | 61 | 1
2015-06-26 21:00 | 2015-06-26 | 5 | 21 | 218 | 61 | 1
2015-06-26 21:15 | 2015-06-26 | 5 | 21 | 209 | 60.8723 | 1
2015-06-26 21:30 | 2015-06-26 | 5 | 21 | 200 | 60.5532 | 1
2015-06-26 21:45 | 2015-06-26 | 5 | 21 | 200 | 60.234 | 1
2015-06-26 22:00 | 2015-06-26 | 5 | 22 | 198 | 60 | 1
2015-06-26 22:15 | 2015-06-26 | 5 | 22 | 195 | 60 | 1
2015-06-26 22:30 | 2015-06-26 | 5 | 22 | 196 | 60 | 1
2015-06-26 22:45 | 2015-06-26 | 5 | 22 | 192 | 60 | 1
2015-06-26 23:00 | 2015-06-26 | 5 | 23 | 192 | 59.9333 | 1
2015-06-26 23:15 | 2015-06-26 | 5 | 23 | 191 | 59.6833 | 1
2015-06-26 23:30 | 2015-06-26 | 5 | 23 | 186 | 59.4333 | 1
2015-06-26 23:45 | 2015-06-26 | 5 | 23 | 193 | 59.1833 | 1
2015-06-27 | 2015-06-27 | 6 | 0 | 183 | 59 | 1
2015-06-27 00:15 | 2015-06-27 | 6 | 0 | 181 | 59 | 1
2015-06-27 00:30 | 2015-06-27 | 6 | 0 | 181 | 59 | 1
2015-06-27 00:45 | 2015-06-27 | 6 | 0 | 195 | 59 | 1
2015-06-27 01:00 | 2015-06-27 | 6 | 1 | 178 | 58.8545 | 1
2015-06-27 01:15 | 2015-06-27 | 6 | 1 | 179 | 58.3091 | 1
2015-06-27 01:30 | 2015-06-27 | 6 | 1 | 177 | 57.7636 | 1
2015-06-27 01:45 | 2015-06-27 | 6 | 1 | 175 | 57.2182 | 1
2015-06-27 02:00 | 2015-06-27 | 6 | 2 | 185 | 58.0667 | 1
2015-06-27 02:15 | 2015-06-27 | 6 | 2 | 173 | 58.3167 | 1
2015-06-27 02:30 | 2015-06-27 | 6 | 2 | 175 | 58.5667 | 1
2015-06-27 02:45 | 2015-06-27 | 6 | 2 | 178 | 58.8167 | 1
2015-06-27 03:00 | 2015-06-27 | 6 | 3 | 174 | 59 | 1
2015-06-27 03:15 | 2015-06-27 | 6 | 3 | 179 | 59 | 1
2015-06-27 03:30 | 2015-06-27 | 6 | 3 | 175 | 59 | 1
2015-06-27 03:45 | 2015-06-27 | 6 | 3 | 170 | 59 | 1
2015-06-27 04:00 | 2015-06-27 | 6 | 4 | 160 | 59 | 1
2015-06-27 04:15 | 2015-06-27 | 6 | 4 | 168 | 59 | 1
2015-06-27 04:30 | 2015-06-27 | 6 | 4 | 170 | 59 | 1
2015-06-27 04:45 | 2015-06-27 | 6 | 4 | 173 | 59 | 1
2015-06-27 05:00 | 2015-06-27 | 6 | 5 | 161 | 59 | 1
2015-06-27 05:15 | 2015-06-27 | 6 | 5 | 165 | 59 | 1
2015-06-27 05:30 | 2015-06-27 | 6 | 5 | 172 | 59 | 1
2015-06-27 05:45 | 2015-06-27 | 6 | 5 | 166 | 59 | 1
2015-06-27 06:00 | 2015-06-27 | 6 | 6 | 171 | 59.1333 | 1
2015-06-27 06:15 | 2015-06-27 | 6 | 6 | 154 | 59.6333 | 1
2015-06-27 06:30 | 2015-06-27 | 6 | 6 | 165 | 60.1333 | 1
2015-06-27 06:45 | 2015-06-27 | 6 | 6 | 169 | 60.6333 | 1
2015-06-27 07:00 | 2015-06-27 | 6 | 7 | 178 | 61.0667 | 1
2015-06-27 07:15 | 2015-06-27 | 6 | 7 | 165 | 61.3167 | 1
2015-06-27 07:30 | 2015-06-27 | 6 | 7 | 166 | 61.5667 | 1
2015-06-27 07:45 | 2015-06-27 | 6 | 7 | 172 | 61.8167 | 1
2015-06-27 08:00 | 2015-06-27 | 6 | 8 | 170 | 62.2 | 1
2015-06-27 08:15 | 2015-06-27 | 6 | 8 | 170 | 62.95 | 1
2015-06-27 08:30 | 2015-06-27 | 6 | 8 | 177 | 63.7 | 1
2015-06-27 08:45 | 2015-06-27 | 6 | 8 | 181 | 64.45 | 1
2015-06-27 09:00 | 2015-06-27 | 6 | 9 | 167 | 65.1333 | 2
2015-06-27 09:15 | 2015-06-27 | 6 | 9 | 176 | 65.6333 | 2
2015-06-27 09:30 | 2015-06-27 | 6 | 9 | 169 | 66.1333 | 2
2015-06-27 09:45 | 2015-06-27 | 6 | 9 | 192 | 66.6333 | 2
2015-06-27 10:00 | 2015-06-27 | 6 | 10 | 190 | 67.0667 | 2
2015-06-27 10:15 | 2015-06-27 | 6 | 10 | 188 | 67.3167 | 2
2015-06-27 10:30 | 2015-06-27 | 6 | 10 | 192 | 67.5667 | 2
2015-06-27 10:45 | 2015-06-27 | 6 | 10 | 205 | 67.8167 | 2
2015-06-27 11:00 | 2015-06-27 | 6 | 11 | 208 | 68.2 | 2
2015-06-27 11:15 | 2015-06-27 | 6 | 11 | 211 | 68.95 | 2
2015-06-27 11:30 | 2015-06-27 | 6 | 11 | 212 | 69.7 | 2
2015-06-27 11:45 | 2015-06-27 | 6 | 11 | 227 | 70.45 | 3
2015-06-27 12:00 | 2015-06-27 | 6 | 12 | 228 | 71.0667 | 3
2015-06-27 12:15 | 2015-06-27 | 6 | 12 | 226 | 71.3167 | 3
2015-06-27 12:30 | 2015-06-27 | 6 | 12 | 236 | 71.5667 | 3
2015-06-27 12:45 | 2015-06-27 | 6 | 12 | 233 | 71.8167 | 3
2015-06-27 13:00 | 2015-06-27 | 6 | 13 | 238 | 72.1333 | 3
2015-06-27 13:15 | 2015-06-27 | 6 | 13 | 262 | 72.6333 | 3
2015-06-27 13:30 | 2015-06-27 | 6 | 13 | 245 | 73.1333 | 3
2015-06-27 13:45 | 2015-06-27 | 6 | 13 | 249 | 73.6333 | 3
2015-06-27 14:00 | 2015-06-27 | 6 | 14 | 249 | 73.9333 | 3
2015-06-27 14:15 | 2015-06-27 | 6 | 14 | 248 | 73.6833 | 3
2015-06-27 14:30 | 2015-06-27 | 6 | 14 | 247 | 73.4333 | 3
2015-06-27 14:45 | 2015-06-27 | 6 | 14 | 254 | 73.1833 | 3
2015-06-27 15:00 | 2015-06-27 | 6 | 15 | 248 | 72.9333 | 3
2015-06-27 15:15 | 2015-06-27 | 6 | 15 | 260 | 72.6833 | 3
2015-06-27 15:30 | 2015-06-27 | 6 | 15 | 260 | 72.4333 | 3
2015-06-27 15:45 | 2015-06-27 | 6 | 15 | 269 | 72.1833 | 3
2015-06-27 16:00 | 2015-06-27 | 6 | 16 | 259 | 72 | 3
2015-06-27 16:15 | 2015-06-27 | 6 | 16 | 270 | 72 | 3
2015-06-27 16:30 | 2015-06-27 | 6 | 16 | 265 | 72 | 3
2015-06-27 16:45 | 2015-06-27 | 6 | 16 | 258 | 72 | 3
2015-06-27 17:00 | 2015-06-27 | 6 | 17 | 274 | 71.9333 | 3
2015-06-27 17:15 | 2015-06-27 | 6 | 17 | 258 | 71.6833 | 3
2015-06-27 17:30 | 2015-06-27 | 6 | 17 | 270 | 71.4333 | 3
2015-06-27 17:45 | 2015-06-27 | 6 | 17 | 259 | 71.1833 | 3
2015-06-27 18:00 | 2015-06-27 | 6 | 18 | 269 | 70.8 | 3
2015-06-27 18:15 | 2015-06-27 | 6 | 18 | 249 | 70.05 | 3
2015-06-27 18:30 | 2015-06-27 | 6 | 18 | 263 | 69.3 | 2
2015-06-27 18:45 | 2015-06-27 | 6 | 18 | 247 | 68.55 | 2
2015-06-27 19:00 | 2015-06-27 | 6 | 19 | 257 | 67.8 | 2
2015-06-27 19:15 | 2015-06-27 | 6 | 19 | 238 | 67.05 | 2
2015-06-27 19:30 | 2015-06-27 | 6 | 19 | 245 | 66.3 | 2
2015-06-27 19:45 | 2015-06-27 | 6 | 19 | 247 | 65.55 | 2
2015-06-27 20:00 | 2015-06-27 | 6 | 20 | 236 | 64.8667 | 1
2015-06-27 20:15 | 2015-06-27 | 6 | 20 | 240 | 64.3667 | 1
2015-06-27 20:30 | 2015-06-27 | 6 | 20 | 237 | 63.8667 | 1
2015-06-27 20:45 | 2015-06-27 | 6 | 20 | 228 | 63.3667 | 1
2015-06-27 21:00 | 2015-06-27 | 6 | 21 | 229 | 63 | 1
2015-06-27 21:15 | 2015-06-27 | 6 | 21 | 212 | 63 | 1
2015-06-27 21:30 | 2015-06-27 | 6 | 21 | 209 | 63 | 1
2015-06-27 21:45 | 2015-06-27 | 6 | 21 | 203 | 63 | 1
2015-06-27 22:00 | 2015-06-27 | 6 | 22 | 202 | 63 | 1
2015-06-27 22:15 | 2015-06-27 | 6 | 22 | 199 | 63 | 1
2015-06-27 22:30 | 2015-06-27 | 6 | 22 | 197 | 63 | 1
2015-06-27 22:45 | 2015-06-27 | 6 | 22 | 203 | 63 | 1
2015-06-27 23:00 | 2015-06-27 | 6 | 23 | 201 | 63 | 1
2015-06-27 23:15 | 2015-06-27 | 6 | 23 | 197 | 63 | 1
2015-06-27 23:30 | 2015-06-27 | 6 | 23 | 197 | 63 | 1
2015-06-27 23:45 | 2015-06-27 | 6 | 23 | 195 | 63 | 1
2015-06-28 | 2015-06-28 | 7 | 0 | 192 | 63 | 1
2015-06-28 00:15 | 2015-06-28 | 7 | 0 | 196 | 63 | 1
2015-06-28 00:30 | 2015-06-28 | 7 | 0 | 191 | 63 | 1
2015-06-28 00:45 | 2015-06-28 | 7 | 0 | 196 | 63 | 1
2015-06-28 01:00 | 2015-06-28 | 7 | 1 | 195 | 63 | 1
2015-06-28 01:15 | 2015-06-28 | 7 | 1 | 189 | 63 | 1
2015-06-28 01:30 | 2015-06-28 | 7 | 1 | 203 | 63 | 1
2015-06-28 01:45 | 2015-06-28 | 7 | 1 | 188 | 63 | 1
2015-06-28 02:00 | 2015-06-28 | 7 | 2 | 190 | 62.9333 | 1
2015-06-28 02:15 | 2015-06-28 | 7 | 2 | 188 | 62.6833 | 1
2015-06-28 02:30 | 2015-06-28 | 7 | 2 | 193 | 62.4333 | 1
2015-06-28 02:45 | 2015-06-28 | 7 | 2 | 193 | 62.1833 | 1
2015-06-28 03:00 | 2015-06-28 | 7 | 3 | 190 | 61.9333 | 1
2015-06-28 03:15 | 2015-06-28 | 7 | 3 | 190 | 61.6833 | 1
2015-06-28 03:30 | 2015-06-28 | 7 | 3 | 187 | 61.4333 | 1
2015-06-28 03:45 | 2015-06-28 | 7 | 3 | 192 | 61.1833 | 1
2015-06-28 04:00 | 2015-06-28 | 7 | 4 | 189 | 61.2667 | 1
2015-06-28 04:15 | 2015-06-28 | 7 | 4 | 190 | 62.2667 | 1
2015-06-28 04:30 | 2015-06-28 | 7 | 4 | 187 | 62.8667 | 1
2015-06-28 04:45 | 2015-06-28 | 7 | 4 | 187 | 62.3667 | 1
2015-06-28 05:00 | 2015-06-28 | 7 | 5 | 182 | 62.2667 | 1
2015-06-28 05:15 | 2015-06-28 | 7 | 5 | 184 | 62.8222 | 1
2015-06-28 05:30 | 2015-06-28 | 7 | 5 | 191 | 62.1556 | 1
2015-06-28 05:45 | 2015-06-28 | 7 | 5 | 183 | 61.4889 | 1
2015-06-28 06:00 | 2015-06-28 | 7 | 6 | 189 | 61.0667 | 1
2015-06-28 06:15 | 2015-06-28 | 7 | 6 | 183 | 61.3167 | 1
2015-06-28 06:30 | 2015-06-28 | 7 | 6 | 201 | 61.5667 | 1
2015-06-28 06:45 | 2015-06-28 | 7 | 6 | 200 | 61.8167 | 1
2015-06-28 07:00 | 2015-06-28 | 7 | 7 | 200 | 62.1333 | 1
2015-06-28 07:15 | 2015-06-28 | 7 | 7 | 203 | 62.6333 | 1
2015-06-28 07:30 | 2015-06-28 | 7 | 7 | 199 | 63.1333 | 1
2015-06-28 07:45 | 2015-06-28 | 7 | 7 | 203 | 63.6333 | 1
2015-06-28 08:00 | 2015-06-28 | 7 | 8 | 199 | 64.0667 | 1
2015-06-28 08:15 | 2015-06-28 | 7 | 8 | 202 | 64.3167 | 1
2015-06-28 08:30 | 2015-06-28 | 7 | 8 | 197 | 64.5667 | 1
2015-06-28 08:45 | 2015-06-28 | 7 | 8 | 208 | 64.8167 | 1
2015-06-28 09:00 | 2015-06-28 | 7 | 9 | 197 | 65.1143 | 2
2015-06-28 09:15 | 2015-06-28 | 7 | 9 | 208 | 65.5429 | 2
2015-06-28 09:30 | 2015-06-28 | 7 | 9 | 209 | 65.9714 | 2
2015-06-28 09:45 | 2015-06-28 | 7 | 9 | 206 | 67.12 | 2
2015-06-28 10:00 | 2015-06-28 | 7 | 10 | 201 | 68.0667 | 2
2015-06-28 10:15 | 2015-06-28 | 7 | 10 | 215 | 68.3167 | 2
2015-06-28 10:30 | 2015-06-28 | 7 | 10 | 218 | 68.5667 | 2
2015-06-28 10:45 | 2015-06-28 | 7 | 10 | 213 | 68.8167 | 2
2015-06-28 11:00 | 2015-06-28 | 7 | 11 | 214 | 69.0667 | 2
2015-06-28 11:15 | 2015-06-28 | 7 | 11 | 221 | 69.3167 | 2
2015-06-28 11:30 | 2015-06-28 | 7 | 11 | 221 | 69.5667 | 2
2015-06-28 11:45 | 2015-06-28 | 7 | 11 | 233 | 69.8167 | 2
2015-06-28 12:00 | 2015-06-28 | 7 | 12 | 231 | 70.0667 | 3
2015-06-28 12:15 | 2015-06-28 | 7 | 12 | 219 | 70.3167 | 3
2015-06-28 12:30 | 2015-06-28 | 7 | 12 | 237 | 70.5667 | 3
2015-06-28 12:45 | 2015-06-28 | 7 | 12 | 225 | 70.8167 | 3
2015-06-28 13:00 | 2015-06-28 | 7 | 13 | 223 | 71 | 3
2015-06-28 13:15 | 2015-06-28 | 7 | 13 | 222 | 71 | 3
2015-06-28 13:30 | 2015-06-28 | 7 | 13 | 227 | 71 | 3
2015-06-28 13:45 | 2015-06-28 | 7 | 13 | 224 | 71 | 3
2015-06-28 14:00 | 2015-06-28 | 7 | 14 | 233 | 70.9333 | 3
2015-06-28 14:15 | 2015-06-28 | 7 | 14 | 226 | 70.6833 | 3
2015-06-28 14:30 | 2015-06-28 | 7 | 14 | 235 | 70.4333 | 3
2015-06-28 14:45 | 2015-06-28 | 7 | 14 | 221 | 70.1833 | 3
2015-06-28 15:00 | 2015-06-28 | 7 | 15 | 238 | 69.8667 | 2
2015-06-28 15:15 | 2015-06-28 | 7 | 15 | 222 | 69.3667 | 2
2015-06-28 15:30 | 2015-06-28 | 7 | 15 | 231 | 68.8667 | 2
2015-06-28 15:45 | 2015-06-28 | 7 | 15 | 233 | 68.3667 | 2
2015-06-28 16:00 | 2015-06-28 | 7 | 16 | 225 | 68 | 2
2015-06-28 16:15 | 2015-06-28 | 7 | 16 | 240 | 68 | 2
2015-06-28 16:30 | 2015-06-28 | 7 | 16 | 233 | 68 | 2
2015-06-28 16:45 | 2015-06-28 | 7 | 16 | 236 | 68 | 2
2015-06-28 17:00 | 2015-06-28 | 7 | 17 | 237 | 67.8 | 2
2015-06-28 17:15 | 2015-06-28 | 7 | 17 | 254 | 67.05 | 2
2015-06-28 17:30 | 2015-06-28 | 7 | 17 | 243 | 66.3 | 2
2015-06-28 17:45 | 2015-06-28 | 7 | 17 | 243 | 65.55 | 2
2015-06-28 18:00 | 2015-06-28 | 7 | 18 | 243 | 64.7838 | 1
2015-06-28 18:15 | 2015-06-28 | 7 | 18 | 243 | 63.973 | 1
2015-06-28 18:30 | 2015-06-28 | 7 | 18 | 241 | 63.1622 | 1
2015-06-28 18:45 | 2015-06-28 | 7 | 18 | 249 | 63 | 1
2015-06-28 19:00 | 2015-06-28 | 7 | 19 | 238 | 62.9333 | 1
2015-06-28 19:15 | 2015-06-28 | 7 | 19 | 240 | 62.6833 | 1
2015-06-28 19:30 | 2015-06-28 | 7 | 19 | 234 | 62.4333 | 1
2015-06-28 19:45 | 2015-06-28 | 7 | 19 | 233 | 62.1833 | 1
2015-06-28 20:00 | 2015-06-28 | 7 | 20 | 223 | 61.8667 | 1
2015-06-28 20:15 | 2015-06-28 | 7 | 20 | 215 | 61.3667 | 1
2015-06-28 20:30 | 2015-06-28 | 7 | 20 | 221 | 60.8667 | 1
2015-06-28 20:45 | 2015-06-28 | 7 | 20 | 212 | 60.3667 | 1
2015-06-28 21:00 | 2015-06-28 | 7 | 21 | 210 | 60.1212 | 1
2015-06-28 21:15 | 2015-06-28 | 7 | 21 | 204 | 60.5758 | 1
2015-06-28 21:30 | 2015-06-28 | 7 | 21 | 194 | 60.963 | 1
2015-06-28 21:45 | 2015-06-28 | 7 | 21 | 193 | 60.4074 | 1
2015-06-28 22:00 | 2015-06-28 | 7 | 22 | 196 | 59.9333 | 1
2015-06-28 22:15 | 2015-06-28 | 7 | 22 | 193 | 59.6833 | 1
2015-06-28 22:30 | 2015-06-28 | 7 | 22 | 193 | 59.4333 | 1
2015-06-28 22:45 | 2015-06-28 | 7 | 22 | 192 | 59.1833 | 1
2015-06-28 23:00 | 2015-06-28 | 7 | 23 | 191 | 59 | 1
2015-06-28 23:15 | 2015-06-28 | 7 | 23 | 188 | 59 | 1
2015-06-28 23:30 | 2015-06-28 | 7 | 23 | 185 | 59 | 1
2015-06-28 23:45 | 2015-06-28 | 7 | 23 | 191 | 59 | 1
2015-06-29 | 2015-06-29 | 1 | 0 | 181 | 59 | 1
2015-06-29 00:15 | 2015-06-29 | 1 | 0 | 184 | 59 | 1
2015-06-29 00:30 | 2015-06-29 | 1 | 0 | 192 | 59 | 1
2015-06-29 00:45 | 2015-06-29 | 1 | 0 | 175 | 59 | 1
2015-06-29 01:00 | 2015-06-29 | 1 | 1 | 174 | 58.7419 | 1
2015-06-29 01:15 | 2015-06-29 | 1 | 1 | 181 | 57.7742 | 1
2015-06-29 01:30 | 2015-06-29 | 1 | 1 | 185 | 57.1034 | 1
2015-06-29 01:45 | 2015-06-29 | 1 | 1 | 170 | 57.6207 | 1
2015-06-29 02:00 | 2015-06-29 | 1 | 2 | 178 | 58 | 1
2015-06-29 02:15 | 2015-06-29 | 1 | 2 | 176 | 58 | 1
2015-06-29 02:30 | 2015-06-29 | 1 | 2 | 179 | 58 | 1
2015-06-29 02:45 | 2015-06-29 | 1 | 2 | 170 | 58 | 1
2015-06-29 03:00 | 2015-06-29 | 1 | 3 | 174 | 57.9 | 1
2015-06-29 03:15 | 2015-06-29 | 1 | 3 | 177 | 57.525 | 1
2015-06-29 03:30 | 2015-06-29 | 1 | 3 | 178 | 57.15 | 1
2015-06-29 03:45 | 2015-06-29 | 1 | 3 | 175 | 57 | 1
2015-06-29 04:00 | 2015-06-29 | 1 | 4 | 168 | 57 | 1
2015-06-29 04:15 | 2015-06-29 | 1 | 4 | 172 | 57 | 1
2015-06-29 04:30 | 2015-06-29 | 1 | 4 | 174 | 57 | 1
2015-06-29 04:45 | 2015-06-29 | 1 | 4 | 171 | 57 | 1
2015-06-29 05:00 | 2015-06-29 | 1 | 5 | 165 | 57 | 1
2015-06-29 05:15 | 2015-06-29 | 1 | 5 | 171 | 57 | 1
2015-06-29 05:30 | 2015-06-29 | 1 | 5 | 170 | 57 | 1
2015-06-29 05:45 | 2015-06-29 | 1 | 5 | 170 | 57 | 1
2015-06-29 06:00 | 2015-06-29 | 1 | 6 | 164 | 57 | 1
2015-06-29 06:15 | 2015-06-29 | 1 | 6 | 167 | 57 | 1
2015-06-29 06:30 | 2015-06-29 | 1 | 6 | 168 | 57 | 1
2015-06-29 06:45 | 2015-06-29 | 1 | 6 | 161 | 57 | 1
2015-06-29 07:00 | 2015-06-29 | 1 | 7 | 173 | 57 | 1
2015-06-29 07:15 | 2015-06-29 | 1 | 7 | 173 | 57 | 1
2015-06-29 07:30 | 2015-06-29 | 1 | 7 | 156 | 57 | 1
2015-06-29 07:45 | 2015-06-29 | 1 | 7 | 169 | 57 | 1
2015-06-29 08:00 | 2015-06-29 | 1 | 8 | 172 | 57.3902 | 1
2015-06-29 08:15 | 2015-06-29 | 1 | 8 | 177 | 58.8537 | 1
2015-06-29 08:30 | 2015-06-29 | 1 | 8 | 192 | 60.3171 | 1
2015-06-29 08:45 | 2015-06-29 | 1 | 8 | 193 | 61.4211 | 1
2015-06-29 09:00 | 2015-06-29 | 1 | 9 | 187 | 62.4211 | 1
2015-06-29 09:15 | 2015-06-29 | 1 | 9 | 197 | 64 | 1
2015-06-29 09:30 | 2015-06-29 | 1 | 9 | 211 | 64 | 1
2015-06-29 09:45 | 2015-06-29 | 1 | 9 | 205 | 64 | 1
2015-06-29 10:00 | 2015-06-29 | 1 | 10 | 208 | 65 | 1
2015-06-29 10:15 | 2015-06-29 | 1 | 10 | 219 | 65 | 1
2015-06-29 10:30 | 2015-06-29 | 1 | 10 | 218 | 65 | 1
2015-06-29 10:45 | 2015-06-29 | 1 | 10 | 227 | 65 | 1
2015-06-29 11:00 | 2015-06-29 | 1 | 11 | 223 | 65.1333 | 2
2015-06-29 11:15 | 2015-06-29 | 1 | 11 | 223 | 65.6333 | 2
2015-06-29 11:30 | 2015-06-29 | 1 | 11 | 221 | 66.1333 | 2
2015-06-29 11:45 | 2015-06-29 | 1 | 11 | 230 | 66.6333 | 2
2015-06-29 12:00 | 2015-06-29 | 1 | 12 | 233 | 67 | 2
2015-06-29 12:15 | 2015-06-29 | 1 | 12 | 236 | 67 | 2
2015-06-29 12:30 | 2015-06-29 | 1 | 12 | 241 | 67 | 2
2015-06-29 12:45 | 2015-06-29 | 1 | 12 | 250 | 67 | 2
2015-06-29 13:00 | 2015-06-29 | 1 | 13 | 237 | 67.0667 | 2
2015-06-29 13:15 | 2015-06-29 | 1 | 13 | 244 | 67.3167 | 2
2015-06-29 13:30 | 2015-06-29 | 1 | 13 | 242 | 67.5667 | 2
2015-06-29 13:45 | 2015-06-29 | 1 | 13 | 258 | 67.8167 | 2
2015-06-29 14:00 | 2015-06-29 | 1 | 14 | 253 | 68 | 2
2015-06-29 14:15 | 2015-06-29 | 1 | 14 | 254 | 68 | 2
2015-06-29 14:30 | 2015-06-29 | 1 | 14 | 254 | 68 | 2
2015-06-29 14:45 | 2015-06-29 | 1 | 14 | 261 | 68 | 2
2015-06-29 15:00 | 2015-06-29 | 1 | 15 | 250 | 68 | 2
2015-06-29 15:15 | 2015-06-29 | 1 | 15 | 259 | 68 | 2
2015-06-29 15:30 | 2015-06-29 | 1 | 15 | 267 | 68 | 2
2015-06-29 15:45 | 2015-06-29 | 1 | 15 | 279 | 68 | 2
2015-06-29 16:00 | 2015-06-29 | 1 | 16 | 264 | 67.8667 | 2
2015-06-29 16:15 | 2015-06-29 | 1 | 16 | 274 | 67.3667 | 2
2015-06-29 16:30 | 2015-06-29 | 1 | 16 | 270 | 66.8667 | 2
2015-06-29 16:45 | 2015-06-29 | 1 | 16 | 274 | 66.3667 | 2
2015-06-29 17:00 | 2015-06-29 | 1 | 17 | 285 | 65.8667 | 2
2015-06-29 17:15 | 2015-06-29 | 1 | 17 | 274 | 65.3667 | 2
2015-06-29 17:30 | 2015-06-29 | 1 | 17 | 271 | 64.8667 | 1
2015-06-29 17:45 | 2015-06-29 | 1 | 17 | 263 | 64.3667 | 1
2015-06-29 18:00 | 2015-06-29 | 1 | 18 | 274 | 63.7333 | 1
2015-06-29 18:15 | 2015-06-29 | 1 | 18 | 259 | 62.7333 | 1
2015-06-29 18:30 | 2015-06-29 | 1 | 18 | 276 | 61.7333 | 1
2015-06-29 18:45 | 2015-06-29 | 1 | 18 | 255 | 60.7333 | 1
2015-06-29 19:00 | 2015-06-29 | 1 | 19 | 255 | 59.9333 | 1
2015-06-29 19:15 | 2015-06-29 | 1 | 19 | 249 | 59.6833 | 1
2015-06-29 19:30 | 2015-06-29 | 1 | 19 | 255 | 59.4333 | 1
2015-06-29 19:45 | 2015-06-29 | 1 | 19 | 248 | 59.1833 | 1
2015-06-29 20:00 | 2015-06-29 | 1 | 20 | 245 | 59 | 1
2015-06-29 20:15 | 2015-06-29 | 1 | 20 | 248 | 59 | 1
2015-06-29 20:30 | 2015-06-29 | 1 | 20 | 247 | 59 | 1
2015-06-29 20:45 | 2015-06-29 | 1 | 20 | 233 | 59 | 1
2015-06-29 21:00 | 2015-06-29 | 1 | 21 | 233 | 59 | 1
2015-06-29 21:15 | 2015-06-29 | 1 | 21 | 215 | 59 | 1
2015-06-29 21:30 | 2015-06-29 | 1 | 21 | 209 | 59 | 1
2015-06-29 21:45 | 2015-06-29 | 1 | 21 | 209 | 59 | 1
2015-06-29 22:00 | 2015-06-29 | 1 | 22 | 202 | 59 | 1
2015-06-29 22:15 | 2015-06-29 | 1 | 22 | 201 | 59 | 1
2015-06-29 22:30 | 2015-06-29 | 1 | 22 | 201 | 59 | 1
2015-06-29 22:45 | 2015-06-29 | 1 | 22 | 200 | 59 | 1
2015-06-29 23:00 | 2015-06-29 | 1 | 23 | 211 | 58.9333 | 1
2015-06-29 23:15 | 2015-06-29 | 1 | 23 | 191 | 58.6833 | 1
2015-06-29 23:30 | 2015-06-29 | 1 | 23 | 192 | 58.4333 | 1
2015-06-29 23:45 | 2015-06-29 | 1 | 23 | 191 | 58.1833 | 1
2015-06-30 | 2015-06-30 | 2 | 0 | 186 | 58 | 1
2015-06-30 00:15 | 2015-06-30 | 2 | 0 | 195 | 58 | 1
2015-06-30 00:30 | 2015-06-30 | 2 | 0 | 189 | 58 | 1
2015-06-30 00:45 | 2015-06-30 | 2 | 0 | 183 | 58 | 1
2015-06-30 01:00 | 2015-06-30 | 2 | 1 | 186 | 57.9333 | 1
2015-06-30 01:15 | 2015-06-30 | 2 | 1 | 183 | 57.6833 | 1
2015-06-30 01:30 | 2015-06-30 | 2 | 1 | 182 | 57.4333 | 1
2015-06-30 01:45 | 2015-06-30 | 2 | 1 | 192 | 57.1833 | 1
2015-06-30 02:00 | 2015-06-30 | 2 | 2 | 185 | 56.9333 | 1
2015-06-30 02:15 | 2015-06-30 | 2 | 2 | 179 | 56.6833 | 1
2015-06-30 02:30 | 2015-06-30 | 2 | 2 | 178 | 56.4333 | 1
2015-06-30 02:45 | 2015-06-30 | 2 | 2 | 186 | 56.1833 | 1
2015-06-30 03:00 | 2015-06-30 | 2 | 3 | 175 | 55.9333 | 1
2015-06-30 03:15 | 2015-06-30 | 2 | 3 | 173 | 55.6833 | 1
2015-06-30 03:30 | 2015-06-30 | 2 | 3 | 172 | 55.4333 | 1
2015-06-30 03:45 | 2015-06-30 | 2 | 3 | 191 | 55.1833 | 1
2015-06-30 04:00 | 2015-06-30 | 2 | 4 | 181 | 55 | 1
2015-06-30 04:15 | 2015-06-30 | 2 | 4 | 176 | 55 | 1
2015-06-30 04:30 | 2015-06-30 | 2 | 4 | 178 | 55 | 1
2015-06-30 04:45 | 2015-06-30 | 2 | 4 | 178 | 55 | 1
2015-06-30 05:00 | 2015-06-30 | 2 | 5 | 185 | 55.0667 | 1
2015-06-30 05:15 | 2015-06-30 | 2 | 5 | 170 | 55.3167 | 1
2015-06-30 05:30 | 2015-06-30 | 2 | 5 | 179 | 55.5667 | 1
2015-06-30 05:45 | 2015-06-30 | 2 | 5 | 173 | 55.8167 | 1
2015-06-30 06:00 | 2015-06-30 | 2 | 6 | 180 | 56.2 | 1
2015-06-30 06:15 | 2015-06-30 | 2 | 6 | 172 | 56.95 | 1
2015-06-30 06:30 | 2015-06-30 | 2 | 6 | 178 | 57.7 | 1
2015-06-30 06:45 | 2015-06-30 | 2 | 6 | 180 | 58.45 | 1
2015-06-30 07:00 | 2015-06-30 | 2 | 7 | 182 | 59.2667 | 1
2015-06-30 07:15 | 2015-06-30 | 2 | 7 | 189 | 60.2667 | 1
2015-06-30 07:30 | 2015-06-30 | 2 | 7 | 179 | 61.2667 | 1
2015-06-30 07:45 | 2015-06-30 | 2 | 7 | 186 | 62.2667 | 1
2015-06-30 08:00 | 2015-06-30 | 2 | 8 | 192 | 63.2 | 1
2015-06-30 08:15 | 2015-06-30 | 2 | 8 | 207 | 63.95 | 1
2015-06-30 08:30 | 2015-06-30 | 2 | 8 | 199 | 64.7 | 1
2015-06-30 08:45 | 2015-06-30 | 2 | 8 | 202 | 65.45 | 2
2015-06-30 09:00 | 2015-06-30 | 2 | 9 | 211 | 66.0667 | 2
2015-06-30 09:15 | 2015-06-30 | 2 | 9 | 213 | 66.3167 | 2
2015-06-30 09:30 | 2015-06-30 | 2 | 9 | 223 | 66.5667 | 2
2015-06-30 09:45 | 2015-06-30 | 2 | 9 | 224 | 66.8167 | 2
2015-06-30 10:00 | 2015-06-30 | 2 | 10 | 233 | 67.3333 | 2
2015-06-30 10:15 | 2015-06-30 | 2 | 10 | 240 | 68.5833 | 2
2015-06-30 10:30 | 2015-06-30 | 2 | 10 | 249 | 69.8333 | 2
2015-06-30 10:45 | 2015-06-30 | 2 | 10 | 257 | 71.0833 | 3
2015-06-30 11:00 | 2015-06-30 | 2 | 11 | 246 | 72.2 | 3
2015-06-30 11:15 | 2015-06-30 | 2 | 11 | 272 | 72.95 | 3
2015-06-30 11:30 | 2015-06-30 | 2 | 11 | 259 | 73.7 | 3
2015-06-30 11:45 | 2015-06-30 | 2 | 11 | 276 | 74.45 | 3
2015-06-30 12:00 | 2015-06-30 | 2 | 12 | 274 | 75.1333 | 4
2015-06-30 12:15 | 2015-06-30 | 2 | 12 | 274 | 75.6333 | 4
2015-06-30 12:30 | 2015-06-30 | 2 | 12 | 268 | 76.1333 | 4
2015-06-30 12:45 | 2015-06-30 | 2 | 12 | 282 | 76.6333 | 4
2015-06-30 13:00 | 2015-06-30 | 2 | 13 | 279 | 76.9333 | 4
2015-06-30 13:15 | 2015-06-30 | 2 | 13 | 276 | 76.6833 | 4
2015-06-30 13:30 | 2015-06-30 | 2 | 13 | 279 | 76.4333 | 4
2015-06-30 13:45 | 2015-06-30 | 2 | 13 | 286 | 76.1833 | 4
2015-06-30 14:00 | 2015-06-30 | 2 | 14 | 284 | 76.0667 | 4
2015-06-30 14:15 | 2015-06-30 | 2 | 14 | 280 | 76.3167 | 4
2015-06-30 14:30 | 2015-06-30 | 2 | 14 | 285 | 76.5667 | 4
2015-06-30 14:45 | 2015-06-30 | 2 | 14 | 288 | 76.8167 | 4
2015-06-30 15:00 | 2015-06-30 | 2 | 15 | 293 | 76.6667 | 4
2015-06-30 15:15 | 2015-06-30 | 2 | 15 | 293 | 75.4167 | 4
2015-06-30 15:30 | 2015-06-30 | 2 | 15 | 290 | 74.1667 | 3
2015-06-30 15:45 | 2015-06-30 | 2 | 15 | 299 | 72.9167 | 3
2015-06-30 16:00 | 2015-06-30 | 2 | 16 | 312 | 71.8 | 3
2015-06-30 16:15 | 2015-06-30 | 2 | 16 | 310 | 71.05 | 3
2015-06-30 16:30 | 2015-06-30 | 2 | 16 | 315 | 70.3 | 3
2015-06-30 16:45 | 2015-06-30 | 2 | 16 | 308 | 69.55 | 2
2015-06-30 17:00 | 2015-06-30 | 2 | 17 | 314 | 69 | 2
2015-06-30 17:15 | 2015-06-30 | 2 | 17 | 310 | 69 | 2
2015-06-30 17:30 | 2015-06-30 | 2 | 17 | 311 | 69 | 2
2015-06-30 17:45 | 2015-06-30 | 2 | 17 | 305 | 69 | 2
2015-06-30 18:00 | 2015-06-30 | 2 | 18 | 298 | 68.8 | 2
2015-06-30 18:15 | 2015-06-30 | 2 | 18 | 282 | 68.05 | 2
2015-06-30 18:30 | 2015-06-30 | 2 | 18 | 290 | 67.3 | 2
2015-06-30 18:45 | 2015-06-30 | 2 | 18 | 291 | 66.55 | 2
2015-06-30 19:00 | 2015-06-30 | 2 | 19 | 285 | 65.7333 | 2
2015-06-30 19:15 | 2015-06-30 | 2 | 19 | 277 | 64.7333 | 1
2015-06-30 19:30 | 2015-06-30 | 2 | 19 | 268 | 63.7333 | 1
2015-06-30 19:45 | 2015-06-30 | 2 | 19 | 270 | 62.7333 | 1
2015-06-30 20:00 | 2015-06-30 | 2 | 20 | 276 | 61.8667 | 1
2015-06-30 20:15 | 2015-06-30 | 2 | 20 | 265 | 61.3667 | 1
2015-06-30 20:30 | 2015-06-30 | 2 | 20 | 250 | 60.8667 | 1
2015-06-30 20:45 | 2015-06-30 | 2 | 20 | 250 | 60.3667 | 1
2015-06-30 21:00 | 2015-06-30 | 2 | 21 | 246 | 59.8667 | 1
2015-06-30 21:15 | 2015-06-30 | 2 | 21 | 232 | 59.3667 | 1
2015-06-30 21:30 | 2015-06-30 | 2 | 21 | 230 | 58.8667 | 1
2015-06-30 21:45 | 2015-06-30 | 2 | 21 | 243 | 58.3667 | 1
2015-06-30 22:00 | 2015-06-30 | 2 | 22 | 222 | 58.0667 | 1
2015-06-30 22:15 | 2015-06-30 | 2 | 22 | 216 | 58.3167 | 1
2015-06-30 22:30 | 2015-06-30 | 2 | 22 | 221 | 58.5667 | 1
2015-06-30 22:45 | 2015-06-30 | 2 | 22 | 221 | 58.8167 | 1
2015-06-30 23:00 | 2015-06-30 | 2 | 23 | 232 | 58.9333 | 1
2015-06-30 23:15 | 2015-06-30 | 2 | 23 | 221 | 58.6833 | 1
2015-06-30 23:30 | 2015-06-30 | 2 | 23 | 213 | 58.4333 | 1
2015-06-30 23:45 | 2015-06-30 | 2 | 23 | 212 | 58.1833 | 1
2015-07-01 | 2015-07-01 | 3 | 0 | 204 | 57.9333 | 1
2015-07-01 00:15 | 2015-07-01 | 3 | 0 | 216 | 57.6833 | 1
2015-07-01 00:30 | 2015-07-01 | 3 | 0 | 210 | 57.4333 | 1
2015-07-01 00:45 | 2015-07-01 | 3 | 0 | 205 | 57.1833 | 1
2015-07-01 01:00 | 2015-07-01 | 3 | 1 | 209 | 56.9333 | 1
2015-07-01 01:15 | 2015-07-01 | 3 | 1 | 206 | 56.6833 | 1
2015-07-01 01:30 | 2015-07-01 | 3 | 1 | 194 | 56.4333 | 1
2015-07-01 01:45 | 2015-07-01 | 3 | 1 | 198 | 56.1833 | 1
2015-07-01 02:00 | 2015-07-01 | 3 | 2 | 190 | 56 | 1
2015-07-01 02:15 | 2015-07-01 | 3 | 2 | 201 | 56 | 1
2015-07-01 02:30 | 2015-07-01 | 3 | 2 | 202 | 56 | 1
2015-07-01 02:45 | 2015-07-01 | 3 | 2 | 207 | 56 | 1
2015-07-01 03:00 | 2015-07-01 | 3 | 3 | 190 | 56.0667 | 1
2015-07-01 03:15 | 2015-07-01 | 3 | 3 | 196 | 56.3167 | 1
2015-07-01 03:30 | 2015-07-01 | 3 | 3 | 193 | 56.5667 | 1
2015-07-01 03:45 | 2015-07-01 | 3 | 3 | 192 | 56.8167 | 1
2015-07-01 04:00 | 2015-07-01 | 3 | 4 | 200 | 56.9333 | 1
2015-07-01 04:15 | 2015-07-01 | 3 | 4 | 193 | 56.6833 | 1
2015-07-01 04:30 | 2015-07-01 | 3 | 4 | 193 | 56.4333 | 1
2015-07-01 04:45 | 2015-07-01 | 3 | 4 | 184 | 56.1833 | 1
2015-07-01 05:00 | 2015-07-01 | 3 | 5 | 195 | 56.1333 | 1
2015-07-01 05:15 | 2015-07-01 | 3 | 5 | 190 | 56.6333 | 1
2015-07-01 05:30 | 2015-07-01 | 3 | 5 | 186 | 57.1333 | 1
2015-07-01 05:45 | 2015-07-01 | 3 | 5 | 194 | 57.6333 | 1
2015-07-01 06:00 | 2015-07-01 | 3 | 6 | 187 | 58.2 | 1
2015-07-01 06:15 | 2015-07-01 | 3 | 6 | 184 | 58.95 | 1
2015-07-01 06:30 | 2015-07-01 | 3 | 6 | 186 | 59.7 | 1
2015-07-01 06:45 | 2015-07-01 | 3 | 6 | 181 | 60.45 | 1
2015-07-01 07:00 | 2015-07-01 | 3 | 7 | 198 | 61.2667 | 1
2015-07-01 07:15 | 2015-07-01 | 3 | 7 | 190 | 62.2667 | 1
2015-07-01 07:30 | 2015-07-01 | 3 | 7 | 190 | 63.2667 | 1
2015-07-01 07:45 | 2015-07-01 | 3 | 7 | 193 | 64.2667 | 1
2015-07-01 08:00 | 2015-07-01 | 3 | 8 | 199 | 65.2 | 2
2015-07-01 08:15 | 2015-07-01 | 3 | 8 | 205 | 65.95 | 2
2015-07-01 08:30 | 2015-07-01 | 3 | 8 | 208 | 66.7 | 2
2015-07-01 08:45 | 2015-07-01 | 3 | 8 | 220 | 67.45 | 2
2015-07-01 09:00 | 2015-07-01 | 3 | 9 | 225 | 68.1333 | 2
2015-07-01 09:15 | 2015-07-01 | 3 | 9 | 228 | 68.6333 | 2
2015-07-01 09:30 | 2015-07-01 | 3 | 9 | 237 | 69.1333 | 2
2015-07-01 09:45 | 2015-07-01 | 3 | 9 | 235 | 69.6333 | 2
2015-07-01 10:00 | 2015-07-01 | 3 | 10 | 238 | 70.2 | 3
2015-07-01 10:15 | 2015-07-01 | 3 | 10 | 265 | 70.95 | 3
2015-07-01 10:30 | 2015-07-01 | 3 | 10 | 245 | 71.7 | 3
2015-07-01 10:45 | 2015-07-01 | 3 | 10 | 263 | 72.45 | 3
2015-07-01 11:00 | 2015-07-01 | 3 | 11 | 264 | 72.8 | 3
2015-07-01 11:15 | 2015-07-01 | 3 | 11 | 282 | 72.05 | 3
2015-07-01 11:30 | 2015-07-01 | 3 | 11 | 278 | 71.3 | 3
2015-07-01 11:45 | 2015-07-01 | 3 | 11 | 285 | 70.55 | 3
2015-07-01 12:00 | 2015-07-01 | 3 | 12 | 286 | 69.9333 | 2
2015-07-01 12:15 | 2015-07-01 | 3 | 12 | 295 | 69.6833 | 2
2015-07-01 12:30 | 2015-07-01 | 3 | 12 | 300 | 69.4333 | 2
2015-07-01 12:45 | 2015-07-01 | 3 | 12 | 295 | 69.1833 | 2
2015-07-01 13:00 | 2015-07-01 | 3 | 13 | 298 | 69.1538 | 2
2015-07-01 13:15 | 2015-07-01 | 3 | 13 | 295 | 69.7308 | 2
2015-07-01 13:30 | 2015-07-01 | 3 | 13 | 297 | 70.4706 | 3
2015-07-01 13:45 | 2015-07-01 | 3 | 13 | 296 | 71.3529 | 3
2015-07-01 14:00 | 2015-07-01 | 3 | 14 | 294 | 71.8667 | 3
2015-07-01 14:15 | 2015-07-01 | 3 | 14 | 292 | 71.3667 | 3
2015-07-01 14:30 | 2015-07-01 | 3 | 14 | 292 | 70.8667 | 3
2015-07-01 14:45 | 2015-07-01 | 3 | 14 | 294 | 70.3667 | 3
2015-07-01 15:00 | 2015-07-01 | 3 | 15 | 293 | 70 | 2
2015-07-01 15:15 | 2015-07-01 | 3 | 15 | 303 | 70 | 2
2015-07-01 15:30 | 2015-07-01 | 3 | 15 | 300 | 70 | 2
2015-07-01 15:45 | 2015-07-01 | 3 | 15 | 294 | 70 | 2
2015-07-01 16:00 | 2015-07-01 | 3 | 16 | 299 | 69.6 | 2
2015-07-01 16:15 | 2015-07-01 | 3 | 16 | 300 | 68.1 | 2
2015-07-01 16:30 | 2015-07-01 | 3 | 16 | 309 | 66.6 | 2
2015-07-01 16:45 | 2015-07-01 | 3 | 16 | 313 | 65.1 | 2
2015-07-01 17:00 | 2015-07-01 | 3 | 17 | 304 | 63.8667 | 1
2015-07-01 17:15 | 2015-07-01 | 3 | 17 | 301 | 63.3667 | 1
2015-07-01 17:30 | 2015-07-01 | 3 | 17 | 286 | 62.8667 | 1
2015-07-01 17:45 | 2015-07-01 | 3 | 17 | 290 | 62.3667 | 1
2015-07-01 18:00 | 2015-07-01 | 3 | 18 | 276 | 62 | 1
2015-07-01 18:15 | 2015-07-01 | 3 | 18 | 280 | 62 | 1
2015-07-01 18:30 | 2015-07-01 | 3 | 18 | 265 | 62 | 1
2015-07-01 18:45 | 2015-07-01 | 3 | 18 | 259 | 62 | 1
2015-07-01 19:00 | 2015-07-01 | 3 | 19 | 254 | 62.0667 | 1
2015-07-01 19:15 | 2015-07-01 | 3 | 19 | 262 | 62.3167 | 1
2015-07-01 19:30 | 2015-07-01 | 3 | 19 | 248 | 62.5667 | 1
2015-07-01 19:45 | 2015-07-01 | 3 | 19 | 249 | 62.8167 | 1
2015-07-01 20:00 | 2015-07-01 | 3 | 20 | 246 | 62.8667 | 1
2015-07-01 20:15 | 2015-07-01 | 3 | 20 | 247 | 62.3667 | 1
2015-07-01 20:30 | 2015-07-01 | 3 | 20 | 249 | 61.8667 | 1
2015-07-01 20:45 | 2015-07-01 | 3 | 20 | 231 | 61.3667 | 1
2015-07-01 21:00 | 2015-07-01 | 3 | 21 | 242 | 61 | 1
2015-07-01 21:15 | 2015-07-01 | 3 | 21 | 238 | 61 | 1
2015-07-01 21:30 | 2015-07-01 | 3 | 21 | 218 | 61 | 1
2015-07-01 21:45 | 2015-07-01 | 3 | 21 | 217 | 61 | 1
2015-07-01 22:00 | 2015-07-01 | 3 | 22 | 215 | 61 | 1
2015-07-01 22:15 | 2015-07-01 | 3 | 22 | 210 | 61 | 1
2015-07-01 22:30 | 2015-07-01 | 3 | 22 | 217 | 61 | 1
2015-07-01 22:45 | 2015-07-01 | 3 | 22 | 220 | 61 | 1
2015-07-01 23:00 | 2015-07-01 | 3 | 23 | 226 | 60.9333 | 1
2015-07-01 23:15 | 2015-07-01 | 3 | 23 | 205 | 60.6833 | 1
2015-07-01 23:30 | 2015-07-01 | 3 | 23 | 206 | 60.4333 | 1
2015-07-01 23:45 | 2015-07-01 | 3 | 23 | 208 | 60.1833 | 1
2015-07-02 | 2015-07-02 | 4 | 0 | 207 | 59.9333 | 1
2015-07-02 00:15 | 2015-07-02 | 4 | 0 | 219 | 59.6833 | 1
2015-07-02 00:30 | 2015-07-02 | 4 | 0 | 219 | 59.4333 | 1
2015-07-02 00:45 | 2015-07-02 | 4 | 0 | 220 | 59.1833 | 1
2015-07-02 01:00 | 2015-07-02 | 4 | 1 | 210 | 59 | 1
2015-07-02 01:15 | 2015-07-02 | 4 | 1 | 210 | 59 | 1
2015-07-02 01:30 | 2015-07-02 | 4 | 1 | 210 | 59 | 1
2015-07-02 01:45 | 2015-07-02 | 4 | 1 | 205 | 59 | 1
2015-07-02 02:00 | 2015-07-02 | 4 | 2 | 215 | 58.9333 | 1
2015-07-02 02:15 | 2015-07-02 | 4 | 2 | 201 | 58.6833 | 1
2015-07-02 02:30 | 2015-07-02 | 4 | 2 | 220 | 58.4333 | 1
2015-07-02 02:45 | 2015-07-02 | 4 | 2 | 207 | 58.1833 | 1
2015-07-02 03:00 | 2015-07-02 | 4 | 3 | 207 | 58 | 1
2015-07-02 03:15 | 2015-07-02 | 4 | 3 | 196 | 58 | 1
2015-07-02 03:30 | 2015-07-02 | 4 | 3 | 208 | 58 | 1
2015-07-02 03:45 | 2015-07-02 | 4 | 3 | 199 | 58 | 1
2015-07-02 04:00 | 2015-07-02 | 4 | 4 | 202 | 58.0667 | 1
2015-07-02 04:15 | 2015-07-02 | 4 | 4 | 202 | 58.3167 | 1
2015-07-02 04:30 | 2015-07-02 | 4 | 4 | 200 | 58.5667 | 1
2015-07-02 04:45 | 2015-07-02 | 4 | 4 | 201 | 58.8167 | 1
2015-07-02 05:00 | 2015-07-02 | 4 | 5 | 191 | 59.1333 | 1
2015-07-02 05:15 | 2015-07-02 | 4 | 5 | 198 | 59.6333 | 1
2015-07-02 05:30 | 2015-07-02 | 4 | 5 | 201 | 60.1333 | 1
2015-07-02 05:45 | 2015-07-02 | 4 | 5 | 190 | 60.6333 | 1
2015-07-02 06:00 | 2015-07-02 | 4 | 6 | 197 | 60.8667 | 1
2015-07-02 06:15 | 2015-07-02 | 4 | 6 | 194 | 60.3667 | 1
2015-07-02 06:30 | 2015-07-02 | 4 | 6 | 191 | 59.8667 | 1
2015-07-02 06:45 | 2015-07-02 | 4 | 6 | 193 | 59.3667 | 1
2015-07-02 07:00 | 2015-07-02 | 4 | 7 | 194 | 59.2667 | 1
2015-07-02 07:15 | 2015-07-02 | 4 | 7 | 189 | 60.2667 | 1
2015-07-02 07:30 | 2015-07-02 | 4 | 7 | 186 | 61.2667 | 1
2015-07-02 07:45 | 2015-07-02 | 4 | 7 | 190 | 62.2667 | 1
2015-07-02 08:00 | 2015-07-02 | 4 | 8 | 199 | 63.2 | 1
2015-07-02 08:15 | 2015-07-02 | 4 | 8 | 195 | 63.95 | 1
2015-07-02 08:30 | 2015-07-02 | 4 | 8 | 197 | 64.7 | 1
2015-07-02 08:45 | 2015-07-02 | 4 | 8 | 206 | 65.45 | 2
2015-07-02 09:00 | 2015-07-02 | 4 | 9 | 221 | 66.1333 | 2
2015-07-02 09:15 | 2015-07-02 | 4 | 9 | 216 | 66.6333 | 2
2015-07-02 09:30 | 2015-07-02 | 4 | 9 | 220 | 67.1333 | 2
2015-07-02 09:45 | 2015-07-02 | 4 | 9 | 230 | 67.6333 | 2
2015-07-02 10:00 | 2015-07-02 | 4 | 10 | 231 | 68.2 | 2
2015-07-02 10:15 | 2015-07-02 | 4 | 10 | 232 | 68.95 | 2
2015-07-02 10:30 | 2015-07-02 | 4 | 10 | 243 | 69.7 | 2
2015-07-02 10:45 | 2015-07-02 | 4 | 10 | 253 | 70.45 | 3
2015-07-02 11:00 | 2015-07-02 | 4 | 11 | 248 | 70.9333 | 3
2015-07-02 11:15 | 2015-07-02 | 4 | 11 | 259 | 70.6833 | 3
2015-07-02 11:30 | 2015-07-02 | 4 | 11 | 251 | 70.4333 | 3
2015-07-02 11:45 | 2015-07-02 | 4 | 11 | 268 | 70.1833 | 3
2015-07-02 12:00 | 2015-07-02 | 4 | 12 | 259 | 70 | 2
2015-07-02 12:15 | 2015-07-02 | 4 | 12 | 272 | 70 | 2
2015-07-02 12:30 | 2015-07-02 | 4 | 12 | 264 | 70 | 2
2015-07-02 12:45 | 2015-07-02 | 4 | 12 | 267 | 70 | 2
2015-07-02 13:00 | 2015-07-02 | 4 | 13 | 258 | 69.1333 | 2
2015-07-02 13:15 | 2015-07-02 | 4 | 13 | 269 | 69.6333 | 2
2015-07-02 13:30 | 2015-07-02 | 4 | 13 | 263 | 70.1333 | 3
2015-07-02 13:45 | 2015-07-02 | 4 | 13 | 272 | 70.6333 | 3
2015-07-02 14:00 | 2015-07-02 | 4 | 14 | 268 | 71 | 3
2015-07-02 14:15 | 2015-07-02 | 4 | 14 | 275 | 71 | 3
2015-07-02 14:30 | 2015-07-02 | 4 | 14 | 271 | 71 | 3
2015-07-02 14:45 | 2015-07-02 | 4 | 14 | 274 | 71 | 3
2015-07-02 15:00 | 2015-07-02 | 4 | 15 | 277 | 70.8667 | 3
2015-07-02 15:15 | 2015-07-02 | 4 | 15 | 263 | 70.3667 | 3
2015-07-02 15:30 | 2015-07-02 | 4 | 15 | 280 | 69.8667 | 2
2015-07-02 15:45 | 2015-07-02 | 4 | 15 | 281 | 69.3667 | 2
2015-07-02 16:00 | 2015-07-02 | 4 | 16 | 273 | 68.8667 | 2
2015-07-02 16:15 | 2015-07-02 | 4 | 16 | 273 | 68.3667 | 2
2015-07-02 16:30 | 2015-07-02 | 4 | 16 | 274 | 67.8667 | 2
2015-07-02 16:45 | 2015-07-02 | 4 | 16 | 271 | 67.3667 | 2
2015-07-02 17:00 | 2015-07-02 | 4 | 17 | 263 | 66.9333 | 2
2015-07-02 17:15 | 2015-07-02 | 4 | 17 | 271 | 66.6833 | 2
2015-07-02 17:30 | 2015-07-02 | 4 | 17 | 262 | 66.4333 | 2
2015-07-02 17:45 | 2015-07-02 | 4 | 17 | 258 | 66.1833 | 2
2015-07-02 18:00 | 2015-07-02 | 4 | 18 | 240 | 65.8667 | 2
2015-07-02 18:15 | 2015-07-02 | 4 | 18 | 257 | 65.3667 | 2
2015-07-02 18:30 | 2015-07-02 | 4 | 18 | 242 | 64.8667 | 1
2015-07-02 18:45 | 2015-07-02 | 4 | 18 | 249 | 64.3667 | 1
2015-07-02 19:00 | 2015-07-02 | 4 | 19 | 241 | 63.9333 | 1
2015-07-02 19:15 | 2015-07-02 | 4 | 19 | 239 | 63.6833 | 1
2015-07-02 19:30 | 2015-07-02 | 4 | 19 | 252 | 63.4333 | 1
2015-07-02 19:45 | 2015-07-02 | 4 | 19 | 244 | 63.1833 | 1
2015-07-02 20:00 | 2015-07-02 | 4 | 20 | 242 | 62.9333 | 1
2015-07-02 20:15 | 2015-07-02 | 4 | 20 | 233 | 62.6833 | 1
2015-07-02 20:30 | 2015-07-02 | 4 | 20 | 235 | 62.4333 | 1
2015-07-02 20:45 | 2015-07-02 | 4 | 20 | 230 | 62.1833 | 1
2015-07-02 21:00 | 2015-07-02 | 4 | 21 | 221 | 62 | 1
2015-07-02 21:15 | 2015-07-02 | 4 | 21 | 210 | 62 | 1
2015-07-02 21:30 | 2015-07-02 | 4 | 21 | 205 | 62 | 1
2015-07-02 21:45 | 2015-07-02 | 4 | 21 | 202 | 62 | 1
2015-07-02 22:00 | 2015-07-02 | 4 | 22 | 193 | 61.8947 | 1
2015-07-02 22:15 | 2015-07-02 | 4 | 22 | 208 | 61.5 | 1
2015-07-02 22:30 | 2015-07-02 | 4 | 22 | 195 | 61.1053 | 1
2015-07-02 22:45 | 2015-07-02 | 4 | 22 | 198 | 60.5 | 1
2015-07-02 23:00 | 2015-07-02 | 4 | 23 | 196 | 60 | 1
2015-07-02 23:15 | 2015-07-02 | 4 | 23 | 194 | 60 | 1
2015-07-02 23:30 | 2015-07-02 | 4 | 23 | 200 | 60 | 1
2015-07-02 23:45 | 2015-07-02 | 4 | 23 | 197 | 60 | 1
2015-07-03 | 2015-07-03 | 0 | 0 | 189 | 59.9333 | 1
2015-07-03 00:15 | 2015-07-03 | 0 | 0 | 192 | 59.6833 | 1
2015-07-03 00:30 | 2015-07-03 | 0 | 0 | 189 | 59.4333 | 1
2015-07-03 00:45 | 2015-07-03 | 0 | 0 | 188 | 59.1833 | 1
2015-07-03 01:00 | 2015-07-03 | 0 | 1 | 188 | 59 | 1
2015-07-03 01:15 | 2015-07-03 | 0 | 1 | 191 | 59 | 1
2015-07-03 01:30 | 2015-07-03 | 0 | 1 | 184 | 59 | 1
2015-07-03 01:45 | 2015-07-03 | 0 | 1 | 183 | 59 | 1
2015-07-03 02:00 | 2015-07-03 | 0 | 2 | 190 | 59 | 1
2015-07-03 02:15 | 2015-07-03 | 0 | 2 | 185 | 59 | 1
2015-07-03 02:30 | 2015-07-03 | 0 | 2 | 186 | 59 | 1
2015-07-03 02:45 | 2015-07-03 | 0 | 2 | 183 | 59 | 1
2015-07-03 03:00 | 2015-07-03 | 0 | 3 | 185 | 59 | 1
2015-07-03 03:15 | 2015-07-03 | 0 | 3 | 186 | 59 | 1
2015-07-03 03:30 | 2015-07-03 | 0 | 3 | 184 | 59 | 1
2015-07-03 03:45 | 2015-07-03 | 0 | 3 | 181 | 59 | 1
2015-07-03 04:00 | 2015-07-03 | 0 | 4 | 185 | 59 | 1
2015-07-03 04:15 | 2015-07-03 | 0 | 4 | 191 | 59 | 1
2015-07-03 04:30 | 2015-07-03 | 0 | 4 | 182 | 59 | 1
2015-07-03 04:45 | 2015-07-03 | 0 | 4 | 182 | 59 | 1
2015-07-03 05:00 | 2015-07-03 | 0 | 5 | 185 | 59.1333 | 1
2015-07-03 05:15 | 2015-07-03 | 0 | 5 | 189 | 59.6333 | 1
2015-07-03 05:30 | 2015-07-03 | 0 | 5 | 182 | 60.1333 | 1
2015-07-03 05:45 | 2015-07-03 | 0 | 5 | 183 | 60.6333 | 1
2015-07-03 06:00 | 2015-07-03 | 0 | 6 | 183 | 61.1333 | 1
2015-07-03 06:15 | 2015-07-03 | 0 | 6 | 182 | 61.6333 | 1
2015-07-03 06:30 | 2015-07-03 | 0 | 6 | 183 | 62.1333 | 1
2015-07-03 06:45 | 2015-07-03 | 0 | 6 | 188 | 62.6333 | 1
2015-07-03 07:00 | 2015-07-03 | 0 | 7 | 182 | 63.1333 | 1
2015-07-03 07:15 | 2015-07-03 | 0 | 7 | 180 | 63.6333 | 1
2015-07-03 07:30 | 2015-07-03 | 0 | 7 | 186 | 64.1333 | 1
2015-07-03 07:45 | 2015-07-03 | 0 | 7 | 180 | 64.6333 | 1
2015-07-03 08:00 | 2015-07-03 | 0 | 8 | 183 | 65.0667 | 2
2015-07-03 08:15 | 2015-07-03 | 0 | 8 | 191 | 65.3167 | 2
2015-07-03 08:30 | 2015-07-03 | 0 | 8 | 183 | 65.5667 | 2
2015-07-03 08:45 | 2015-07-03 | 0 | 8 | 185 | 65.8167 | 2
2015-07-03 09:00 | 2015-07-03 | 0 | 9 | 189 | 66.0667 | 2
2015-07-03 09:15 | 2015-07-03 | 0 | 9 | 190 | 66.3167 | 2
2015-07-03 09:30 | 2015-07-03 | 0 | 9 | 196 | 66.5667 | 2
2015-07-03 09:45 | 2015-07-03 | 0 | 9 | 198 | 66.8167 | 2
2015-07-03 10:00 | 2015-07-03 | 0 | 10 | 200 | 67.2 | 2
2015-07-03 10:15 | 2015-07-03 | 0 | 10 | 204 | 67.95 | 2
2015-07-03 10:30 | 2015-07-03 | 0 | 10 | 214 | 68.7 | 2
2015-07-03 10:45 | 2015-07-03 | 0 | 10 | 217 | 69.45 | 2
2015-07-03 11:00 | 2015-07-03 | 0 | 11 | 208 | 70.1333 | 3
2015-07-03 11:15 | 2015-07-03 | 0 | 11 | 211 | 70.6333 | 3
2015-07-03 11:30 | 2015-07-03 | 0 | 11 | 223 | 71.1333 | 3
2015-07-03 11:45 | 2015-07-03 | 0 | 11 | 219 | 71.6333 | 3
2015-07-03 12:00 | 2015-07-03 | 0 | 12 | 218 | 72 | 3
2015-07-03 12:15 | 2015-07-03 | 0 | 12 | 233 | 72 | 3
2015-07-03 12:30 | 2015-07-03 | 0 | 12 | 221 | 72 | 3
2015-07-03 12:45 | 2015-07-03 | 0 | 12 | 241 | 72 | 3
2015-07-03 13:00 | 2015-07-03 | 0 | 13 | 227 | 72 | 3
2015-07-03 13:15 | 2015-07-03 | 0 | 13 | 233 | 72 | 3
2015-07-03 13:30 | 2015-07-03 | 0 | 13 | 233 | 72 | 3
2015-07-03 13:45 | 2015-07-03 | 0 | 13 | 238 | 71.0476 | 3
2015-07-03 14:00 | 2015-07-03 | 0 | 14 | 232 | 69.9333 | 2
2015-07-03 14:15 | 2015-07-03 | 0 | 14 | 236 | 69.6833 | 2
2015-07-03 14:30 | 2015-07-03 | 0 | 14 | 234 | 69.4333 | 2
2015-07-03 14:45 | 2015-07-03 | 0 | 14 | 246 | 69.1833 | 2
2015-07-03 15:00 | 2015-07-03 | 0 | 15 | 236 | 68.9333 | 2
2015-07-03 15:15 | 2015-07-03 | 0 | 15 | 246 | 68.6833 | 2
2015-07-03 15:30 | 2015-07-03 | 0 | 15 | 248 | 68.4333 | 2
2015-07-03 15:45 | 2015-07-03 | 0 | 15 | 249 | 68.1833 | 2
2015-07-03 16:00 | 2015-07-03 | 0 | 16 | 240 | 67.8667 | 2
2015-07-03 16:15 | 2015-07-03 | 0 | 16 | 252 | 67.3667 | 2
2015-07-03 16:30 | 2015-07-03 | 0 | 16 | 239 | 66.8667 | 2
2015-07-03 16:45 | 2015-07-03 | 0 | 16 | 245 | 66.3667 | 2
2015-07-03 17:00 | 2015-07-03 | 0 | 17 | 254 | 65.8667 | 2
2015-07-03 17:15 | 2015-07-03 | 0 | 17 | 253 | 65.3667 | 2
2015-07-03 17:30 | 2015-07-03 | 0 | 17 | 247 | 64.8667 | 1
2015-07-03 17:45 | 2015-07-03 | 0 | 17 | 243 | 64.3667 | 1
2015-07-03 18:00 | 2015-07-03 | 0 | 18 | 246 | 63.8667 | 1
2015-07-03 18:15 | 2015-07-03 | 0 | 18 | 245 | 63.3667 | 1
2015-07-03 18:30 | 2015-07-03 | 0 | 18 | 249 | 62.8667 | 1
2015-07-03 18:45 | 2015-07-03 | 0 | 18 | 242 | 62.3667 | 1
2015-07-03 19:00 | 2015-07-03 | 0 | 19 | 230 | 61.8667 | 1
2015-07-03 19:15 | 2015-07-03 | 0 | 19 | 243 | 61.3667 | 1
2015-07-03 19:30 | 2015-07-03 | 0 | 19 | 234 | 60.8667 | 1
2015-07-03 19:45 | 2015-07-03 | 0 | 19 | 239 | 60.3667 | 1
2015-07-03 20:00 | 2015-07-03 | 0 | 20 | 233 | 60 | 1
2015-07-03 20:15 | 2015-07-03 | 0 | 20 | 236 | 60 | 1
2015-07-03 20:30 | 2015-07-03 | 0 | 20 | 221 | 60 | 1
2015-07-03 20:45 | 2015-07-03 | 0 | 20 | 213 | 60 | 1
2015-07-03 21:00 | 2015-07-03 | 0 | 21 | 210 | 60 | 1
2015-07-03 21:15 | 2015-07-03 | 0 | 21 | 207 | 60 | 1
2015-07-03 21:30 | 2015-07-03 | 0 | 21 | 215 | 60 | 1
2015-07-03 21:45 | 2015-07-03 | 0 | 21 | 200 | 60 | 1
2015-07-03 22:00 | 2015-07-03 | 0 | 22 | 195 | 59.9333 | 1
2015-07-03 22:15 | 2015-07-03 | 0 | 22 | 201 | 59.6833 | 1
2015-07-03 22:30 | 2015-07-03 | 0 | 22 | 199 | 59.4333 | 1
2015-07-03 22:45 | 2015-07-03 | 0 | 22 | 201 | 59.1833 | 1
2015-07-03 23:00 | 2015-07-03 | 0 | 23 | 203 | 59 | 1
2015-07-03 23:15 | 2015-07-03 | 0 | 23 | 189 | 59 | 1
2015-07-03 23:30 | 2015-07-03 | 0 | 23 | 201 | 59 | 1
2015-07-03 23:45 | 2015-07-03 | 0 | 23 | 190 | 59 | 1
2015-07-04 | 2015-07-04 | 6 | 0 | 191 | 58.9333 | 1
2015-07-04 00:15 | 2015-07-04 | 6 | 0 | 196 | 58.6833 | 1
2015-07-04 00:30 | 2015-07-04 | 6 | 0 | 197 | 58.4333 | 1
2015-07-04 00:45 | 2015-07-04 | 6 | 0 | 188 | 58.1833 | 1
2015-07-04 01:00 | 2015-07-04 | 6 | 1 | 190 | 58 | 1
2015-07-04 01:15 | 2015-07-04 | 6 | 1 | 185 | 58 | 1
2015-07-04 01:30 | 2015-07-04 | 6 | 1 | 183 | 58 | 1
2015-07-04 01:45 | 2015-07-04 | 6 | 1 | 189 | 58 | 1
2015-07-04 02:00 | 2015-07-04 | 6 | 2 | 184 | 58 | 1
2015-07-04 02:15 | 2015-07-04 | 6 | 2 | 184 | 58 | 1
2015-07-04 02:30 | 2015-07-04 | 6 | 2 | 182 | 58 | 1
2015-07-04 02:45 | 2015-07-04 | 6 | 2 | 189 | 58 | 1
2015-07-04 03:00 | 2015-07-04 | 6 | 3 | 187 | 57.7778 | 1
2015-07-04 03:15 | 2015-07-04 | 6 | 3 | 179 | 57.0238 | 1
2015-07-04 03:30 | 2015-07-04 | 6 | 3 | 186 | 57.381 | 1
2015-07-04 03:45 | 2015-07-04 | 6 | 3 | 185 | 57.7381 | 1
2015-07-04 04:00 | 2015-07-04 | 6 | 4 | 183 | 58.0667 | 1
2015-07-04 04:15 | 2015-07-04 | 6 | 4 | 185 | 58.3167 | 1
2015-07-04 04:30 | 2015-07-04 | 6 | 4 | 180 | 58.5667 | 1
2015-07-04 04:45 | 2015-07-04 | 6 | 4 | 187 | 58.8167 | 1
2015-07-04 05:00 | 2015-07-04 | 6 | 5 | 184 | 59 | 1
2015-07-04 05:15 | 2015-07-04 | 6 | 5 | 183 | 59 | 1
2015-07-04 05:30 | 2015-07-04 | 6 | 5 | 183 | 59 | 1
2015-07-04 05:45 | 2015-07-04 | 6 | 5 | 185 | 59 | 1
2015-07-04 06:00 | 2015-07-04 | 6 | 6 | 189 | 59.0667 | 1
2015-07-04 06:15 | 2015-07-04 | 6 | 6 | 181 | 59.3167 | 1
2015-07-04 06:30 | 2015-07-04 | 6 | 6 | 181 | 59.5667 | 1
2015-07-04 06:45 | 2015-07-04 | 6 | 6 | 178 | 59.8167 | 1
2015-07-04 07:00 | 2015-07-04 | 6 | 7 | 181 | 60.3 | 1
2015-07-04 07:15 | 2015-07-04 | 6 | 7 | 183 | 61.425 | 1
2015-07-04 07:30 | 2015-07-04 | 6 | 7 | 182 | 62.55 | 1
2015-07-04 07:45 | 2015-07-04 | 6 | 7 | 180 | 63.45 | 1
2015-07-04 08:00 | 2015-07-04 | 6 | 8 | 176 | 64.2 | 1
2015-07-04 08:15 | 2015-07-04 | 6 | 8 | 183 | 64.95 | 1
2015-07-04 08:30 | 2015-07-04 | 6 | 8 | 181 | 65.7 | 2
2015-07-04 08:45 | 2015-07-04 | 6 | 8 | 179 | 66.45 | 2
2015-07-04 09:00 | 2015-07-04 | 6 | 9 | 185 | 67.0667 | 2
2015-07-04 09:15 | 2015-07-04 | 6 | 9 | 190 | 67.3167 | 2
2015-07-04 09:30 | 2015-07-04 | 6 | 9 | 187 | 67.5667 | 2
2015-07-04 09:45 | 2015-07-04 | 6 | 9 | 190 | 67.8167 | 2
2015-07-04 10:00 | 2015-07-04 | 6 | 10 | 205 | 68.0667 | 2
2015-07-04 10:15 | 2015-07-04 | 6 | 10 | 204 | 68.3167 | 2
2015-07-04 10:30 | 2015-07-04 | 6 | 10 | 208 | 68.5667 | 2
2015-07-04 10:45 | 2015-07-04 | 6 | 10 | 208 | 68.8167 | 2
2015-07-04 11:00 | 2015-07-04 | 6 | 11 | 211 | 69 | 2
2015-07-04 11:15 | 2015-07-04 | 6 | 11 | 218 | 69 | 2
2015-07-04 11:30 | 2015-07-04 | 6 | 11 | 222 | 69 | 2
2015-07-04 11:45 | 2015-07-04 | 6 | 11 | 219 | 69 | 2
2015-07-04 12:00 | 2015-07-04 | 6 | 12 | 222 | 69 | 2
2015-07-04 12:15 | 2015-07-04 | 6 | 12 | 233 | 69 | 2
2015-07-04 12:30 | 2015-07-04 | 6 | 12 | 223 | 69 | 2
2015-07-04 12:45 | 2015-07-04 | 6 | 12 | 224 | 69 | 2
2015-07-04 13:00 | 2015-07-04 | 6 | 13 | 232 | 69.0667 | 2
2015-07-04 13:15 | 2015-07-04 | 6 | 13 | 227 | 69.3167 | 2
2015-07-04 13:30 | 2015-07-04 | 6 | 13 | 227 | 69.5667 | 2
2015-07-04 13:45 | 2015-07-04 | 6 | 13 | 236 | 69.8167 | 2
2015-07-04 14:00 | 2015-07-04 | 6 | 14 | 229 | 69.9333 | 2
2015-07-04 14:15 | 2015-07-04 | 6 | 14 | 236 | 69.6833 | 2
2015-07-04 14:30 | 2015-07-04 | 6 | 14 | 224 | 69.4333 | 2
2015-07-04 14:45 | 2015-07-04 | 6 | 14 | 236 | 69.1833 | 2
2015-07-04 15:00 | 2015-07-04 | 6 | 15 | 229 | 68.9333 | 2
2015-07-04 15:15 | 2015-07-04 | 6 | 15 | 242 | 68.6833 | 2
2015-07-04 15:30 | 2015-07-04 | 6 | 15 | 233 | 68.4333 | 2
2015-07-04 15:45 | 2015-07-04 | 6 | 15 | 245 | 68.1833 | 2
2015-07-04 16:00 | 2015-07-04 | 6 | 16 | 238 | 67.9333 | 2
2015-07-04 16:15 | 2015-07-04 | 6 | 16 | 245 | 67.6833 | 2
2015-07-04 16:30 | 2015-07-04 | 6 | 16 | 234 | 67.4333 | 2
2015-07-04 16:45 | 2015-07-04 | 6 | 16 | 243 | 67.1833 | 2
2015-07-04 17:00 | 2015-07-04 | 6 | 17 | 238 | 66.8667 | 2
2015-07-04 17:15 | 2015-07-04 | 6 | 17 | 245 | 66.3667 | 2
2015-07-04 17:30 | 2015-07-04 | 6 | 17 | 239 | 65.8667 | 2
2015-07-04 17:45 | 2015-07-04 | 6 | 17 | 242 | 65.3667 | 2
2015-07-04 18:00 | 2015-07-04 | 6 | 18 | 228 | 64.8667 | 1
2015-07-04 18:15 | 2015-07-04 | 6 | 18 | 236 | 64.3667 | 1
2015-07-04 18:30 | 2015-07-04 | 6 | 18 | 236 | 63.8667 | 1
2015-07-04 18:45 | 2015-07-04 | 6 | 18 | 241 | 63.3667 | 1
2015-07-04 19:00 | 2015-07-04 | 6 | 19 | 226 | 62.8667 | 1
2015-07-04 19:15 | 2015-07-04 | 6 | 19 | 236 | 62.3667 | 1
2015-07-04 19:30 | 2015-07-04 | 6 | 19 | 232 | 61.8667 | 1
2015-07-04 19:45 | 2015-07-04 | 6 | 19 | 231 | 61.3667 | 1
2015-07-04 20:00 | 2015-07-04 | 6 | 20 | 219 | 61 | 1
2015-07-04 20:15 | 2015-07-04 | 6 | 20 | 223 | 61 | 1
2015-07-04 20:30 | 2015-07-04 | 6 | 20 | 205 | 61 | 1
2015-07-04 20:45 | 2015-07-04 | 6 | 20 | 202 | 61 | 1
2015-07-04 21:00 | 2015-07-04 | 6 | 21 | 204 | 61 | 1
2015-07-04 21:15 | 2015-07-04 | 6 | 21 | 203 | 61 | 1
2015-07-04 21:30 | 2015-07-04 | 6 | 21 | 207 | 61 | 1
2015-07-04 21:45 | 2015-07-04 | 6 | 21 | 195 | 61 | 1
2015-07-04 22:00 | 2015-07-04 | 6 | 22 | 199 | 61 | 1
2015-07-04 22:15 | 2015-07-04 | 6 | 22 | 194 | 61 | 1
2015-07-04 22:30 | 2015-07-04 | 6 | 22 | 202 | 61 | 1
2015-07-04 22:45 | 2015-07-04 | 6 | 22 | 194 | 61 | 1
2015-07-04 23:00 | 2015-07-04 | 6 | 23 | 188 | 61 | 1
2015-07-04 23:15 | 2015-07-04 | 6 | 23 | 203 | 61 | 1
2015-07-04 23:30 | 2015-07-04 | 6 | 23 | 187 | 61 | 1
2015-07-04 23:45 | 2015-07-04 | 6 | 23 | 192 | 61 | 1
2015-07-05 | 2015-07-05 | 7 | 0 | 194 | 61 | 1
2015-07-05 00:15 | 2015-07-05 | 7 | 0 | 185 | 61 | 1
2015-07-05 00:30 | 2015-07-05 | 7 | 0 | 190 | 61 | 1
2015-07-05 00:45 | 2015-07-05 | 7 | 0 | 193 | 61 | 1
2015-07-05 01:00 | 2015-07-05 | 7 | 1 | 186 | 61 | 1
2015-07-05 01:15 | 2015-07-05 | 7 | 1 | 188 | 61 | 1
2015-07-05 01:30 | 2015-07-05 | 7 | 1 | 193 | 60.9286 | 1
2015-07-05 01:45 | 2015-07-05 | 7 | 1 | 185 | 60.3929 | 1
2015-07-05 02:00 | 2015-07-05 | 7 | 2 | 181 | 60.1538 | 1
2015-07-05 02:15 | 2015-07-05 | 7 | 2 | 198 | 60.7308 | 1
2015-07-05 02:30 | 2015-07-05 | 7 | 2 | 192 | 61 | 1
2015-07-05 02:45 | 2015-07-05 | 7 | 2 | 183 | 61 | 1
2015-07-05 03:00 | 2015-07-05 | 7 | 3 | 184 | 61 | 1
2015-07-05 03:15 | 2015-07-05 | 7 | 3 | 182 | 61 | 1
2015-07-05 03:30 | 2015-07-05 | 7 | 3 | 174 | 61 | 1
2015-07-05 03:45 | 2015-07-05 | 7 | 3 | 177 | 61 | 1
2015-07-05 04:00 | 2015-07-05 | 7 | 4 | 176 | 60.9333 | 1
2015-07-05 04:15 | 2015-07-05 | 7 | 4 | 179 | 60.6833 | 1
2015-07-05 04:30 | 2015-07-05 | 7 | 4 | 174 | 60.4333 | 1
2015-07-05 04:45 | 2015-07-05 | 7 | 4 | 170 | 60.1833 | 1
2015-07-05 05:00 | 2015-07-05 | 7 | 5 | 179 | 60 | 1
2015-07-05 05:15 | 2015-07-05 | 7 | 5 | 173 | 60 | 1
2015-07-05 05:30 | 2015-07-05 | 7 | 5 | 177 | 60 | 1
2015-07-05 05:45 | 2015-07-05 | 7 | 5 | 171 | 60 | 1
2015-07-05 06:00 | 2015-07-05 | 7 | 6 | 177 | 60.2 | 1
2015-07-05 06:15 | 2015-07-05 | 7 | 6 | 178 | 60.95 | 1
2015-07-05 06:30 | 2015-07-05 | 7 | 6 | 175 | 61.7 | 1
2015-07-05 06:45 | 2015-07-05 | 7 | 6 | 178 | 62.45 | 1
2015-07-05 07:00 | 2015-07-05 | 7 | 7 | 168 | 63.2 | 1
2015-07-05 07:15 | 2015-07-05 | 7 | 7 | 169 | 63.95 | 1
2015-07-05 07:30 | 2015-07-05 | 7 | 7 | 172 | 64.7 | 1
2015-07-05 07:45 | 2015-07-05 | 7 | 7 | 166 | 65.45 | 2
2015-07-05 08:00 | 2015-07-05 | 7 | 8 | 171 | 66.2 | 2
2015-07-05 08:15 | 2015-07-05 | 7 | 8 | 167 | 66.95 | 2
2015-07-05 08:30 | 2015-07-05 | 7 | 8 | 175 | 67.7 | 2
2015-07-05 08:45 | 2015-07-05 | 7 | 8 | 172 | 68.45 | 2
2015-07-05 09:00 | 2015-07-05 | 7 | 9 | 172 | 69.0667 | 2
2015-07-05 09:15 | 2015-07-05 | 7 | 9 | 172 | 69.3167 | 2
2015-07-05 09:30 | 2015-07-05 | 7 | 9 | 177 | 69.5667 | 2
2015-07-05 09:45 | 2015-07-05 | 7 | 9 | 175 | 69.8167 | 2
2015-07-05 10:00 | 2015-07-05 | 7 | 10 | 180 | 70.2 | 3
2015-07-05 10:15 | 2015-07-05 | 7 | 10 | 188 | 70.95 | 3
2015-07-05 10:30 | 2015-07-05 | 7 | 10 | 197 | 71.7 | 3
2015-07-05 10:45 | 2015-07-05 | 7 | 10 | 193 | 72.45 | 3
2015-07-05 11:00 | 2015-07-05 | 7 | 11 | 191 | 73 | 3
2015-07-05 11:15 | 2015-07-05 | 7 | 11 | 205 | 73 | 3
2015-07-05 11:30 | 2015-07-05 | 7 | 11 | 202 | 73 | 3
2015-07-05 11:45 | 2015-07-05 | 7 | 11 | 209 | 73 | 3
2015-07-05 12:00 | 2015-07-05 | 7 | 12 | 217 | 73.2 | 3
2015-07-05 12:15 | 2015-07-05 | 7 | 12 | 216 | 73.95 | 3
2015-07-05 12:30 | 2015-07-05 | 7 | 12 | 215 | 74.7 | 3
2015-07-05 12:45 | 2015-07-05 | 7 | 12 | 209 | 75.45 | 4
2015-07-05 13:00 | 2015-07-05 | 7 | 13 | 215 | 75.8667 | 4
2015-07-05 13:15 | 2015-07-05 | 7 | 13 | 222 | 75.3667 | 4
2015-07-05 13:30 | 2015-07-05 | 7 | 13 | 226 | 74.8667 | 3
2015-07-05 13:45 | 2015-07-05 | 7 | 13 | 213 | 74.3667 | 3
2015-07-05 14:00 | 2015-07-05 | 7 | 14 | 225 | 73.9333 | 3
2015-07-05 14:15 | 2015-07-05 | 7 | 14 | 222 | 73.6833 | 3
2015-07-05 14:30 | 2015-07-05 | 7 | 14 | 228 | 73.4333 | 3
2015-07-05 14:45 | 2015-07-05 | 7 | 14 | 232 | 73.1833 | 3
2015-07-05 15:00 | 2015-07-05 | 7 | 15 | 228 | 73 | 3
2015-07-05 15:15 | 2015-07-05 | 7 | 15 | 229 | 73 | 3
2015-07-05 15:30 | 2015-07-05 | 7 | 15 | 232 | 73 | 3
2015-07-05 15:45 | 2015-07-05 | 7 | 15 | 235 | 73 | 3
2015-07-05 16:00 | 2015-07-05 | 7 | 16 | 228 | 72.8 | 3
2015-07-05 16:15 | 2015-07-05 | 7 | 16 | 237 | 72.05 | 3
2015-07-05 16:30 | 2015-07-05 | 7 | 16 | 231 | 71.3 | 3
2015-07-05 16:45 | 2015-07-05 | 7 | 16 | 239 | 70.55 | 3
2015-07-05 17:00 | 2015-07-05 | 7 | 17 | 238 | 69.6667 | 2
2015-07-05 17:15 | 2015-07-05 | 7 | 17 | 251 | 68.4167 | 2
2015-07-05 17:30 | 2015-07-05 | 7 | 17 | 236 | 67.1667 | 2
2015-07-05 17:45 | 2015-07-05 | 7 | 17 | 249 | 65.9167 | 2
2015-07-05 18:00 | 2015-07-05 | 7 | 18 | 234 | 64.8667 | 1
2015-07-05 18:15 | 2015-07-05 | 7 | 18 | 237 | 64.3667 | 1
2015-07-05 18:30 | 2015-07-05 | 7 | 18 | 235 | 63.8667 | 1
2015-07-05 18:45 | 2015-07-05 | 7 | 18 | 232 | 63.3667 | 1
2015-07-05 19:00 | 2015-07-05 | 7 | 19 | 232 | 63 | 1
2015-07-05 19:15 | 2015-07-05 | 7 | 19 | 237 | 63 | 1
2015-07-05 19:30 | 2015-07-05 | 7 | 19 | 229 | 63 | 1
2015-07-05 19:45 | 2015-07-05 | 7 | 19 | 224 | 63 | 1
2015-07-05 20:00 | 2015-07-05 | 7 | 20 | 217 | 62.9333 | 1
2015-07-05 20:15 | 2015-07-05 | 7 | 20 | 206 | 62.6833 | 1
2015-07-05 20:30 | 2015-07-05 | 7 | 20 | 210 | 62.4333 | 1
2015-07-05 20:45 | 2015-07-05 | 7 | 20 | 204 | 62.1833 | 1
2015-07-05 21:00 | 2015-07-05 | 7 | 21 | 200 | 62 | 1
2015-07-05 21:15 | 2015-07-05 | 7 | 21 | 189 | 62 | 1
2015-07-05 21:30 | 2015-07-05 | 7 | 21 | 193 | 62 | 1
2015-07-05 21:45 | 2015-07-05 | 7 | 21 | 186 | 62 | 1
2015-07-05 22:00 | 2015-07-05 | 7 | 22 | 192 | 62 | 1
2015-07-05 22:15 | 2015-07-05 | 7 | 22 | 184 | 62 | 1
2015-07-05 22:30 | 2015-07-05 | 7 | 22 | 179 | 62 | 1
2015-07-05 22:45 | 2015-07-05 | 7 | 22 | 189 | 62 | 1
2015-07-05 23:00 | 2015-07-05 | 7 | 23 | 177 | 61.9333 | 1
2015-07-05 23:15 | 2015-07-05 | 7 | 23 | 185 | 61.6833 | 1
2015-07-05 23:30 | 2015-07-05 | 7 | 23 | 180 | 61.4333 | 1
2015-07-05 23:45 | 2015-07-05 | 7 | 23 | 176 | 61.1833 | 1
2015-07-06 | 2015-07-06 | 1 | 0 | 186 | 61.0667 | 1
2015-07-06 00:15 | 2015-07-06 | 1 | 0 | 172 | 61.3167 | 1
2015-07-06 00:30 | 2015-07-06 | 1 | 0 | 178 | 61.5667 | 1
2015-07-06 00:45 | 2015-07-06 | 1 | 0 | 172 | 61.8167 | 1
2015-07-06 01:00 | 2015-07-06 | 1 | 1 | 182 | 61.9333 | 1
2015-07-06 01:15 | 2015-07-06 | 1 | 1 | 172 | 61.6833 | 1
2015-07-06 01:30 | 2015-07-06 | 1 | 1 | 176 | 61.4333 | 1
2015-07-06 01:45 | 2015-07-06 | 1 | 1 | 181 | 61.1833 | 1
2015-07-06 02:00 | 2015-07-06 | 1 | 2 | 168 | 61 | 1
2015-07-06 02:15 | 2015-07-06 | 1 | 2 | 179 | 61 | 1
2015-07-06 02:30 | 2015-07-06 | 1 | 2 | 174 | 61 | 1
2015-07-06 02:45 | 2015-07-06 | 1 | 2 | 180 | 61 | 1
2015-07-06 03:00 | 2015-07-06 | 1 | 3 | 173 | 61 | 1
2015-07-06 03:15 | 2015-07-06 | 1 | 3 | 177 | 61 | 1
2015-07-06 03:30 | 2015-07-06 | 1 | 3 | 175 | 61 | 1
2015-07-06 03:45 | 2015-07-06 | 1 | 3 | 175 | 61 | 1
2015-07-06 04:00 | 2015-07-06 | 1 | 4 | 169 | 61 | 1
2015-07-06 04:15 | 2015-07-06 | 1 | 4 | 172 | 61 | 1
2015-07-06 04:30 | 2015-07-06 | 1 | 4 | 176 | 61 | 1
2015-07-06 04:45 | 2015-07-06 | 1 | 4 | 177 | 61 | 1
2015-07-06 05:00 | 2015-07-06 | 1 | 5 | 175 | 61 | 1
2015-07-06 05:15 | 2015-07-06 | 1 | 5 | 165 | 61 | 1
2015-07-06 05:30 | 2015-07-06 | 1 | 5 | 177 | 61 | 1
2015-07-06 05:45 | 2015-07-06 | 1 | 5 | 167 | 61 | 1
2015-07-06 06:00 | 2015-07-06 | 1 | 6 | 178 | 61 | 1
2015-07-06 06:15 | 2015-07-06 | 1 | 6 | 164 | 61 | 1
2015-07-06 06:30 | 2015-07-06 | 1 | 6 | 177 | 61 | 1
2015-07-06 06:45 | 2015-07-06 | 1 | 6 | 176 | 61 | 1
2015-07-06 07:00 | 2015-07-06 | 1 | 7 | 171 | 61.0667 | 1
2015-07-06 07:15 | 2015-07-06 | 1 | 7 | 172 | 61.3167 | 1
2015-07-06 07:30 | 2015-07-06 | 1 | 7 | 167 | 61.5667 | 1
2015-07-06 07:45 | 2015-07-06 | 1 | 7 | 175 | 61.8167 | 1
2015-07-06 08:00 | 2015-07-06 | 1 | 8 | 181 | 62.1379 | 1
2015-07-06 08:15 | 2015-07-06 | 1 | 8 | 187 | 62.6552 | 1
2015-07-06 08:30 | 2015-07-06 | 1 | 8 | 193 | 63.1724 | 1
2015-07-06 08:45 | 2015-07-06 | 1 | 8 | 195 | 63.6897 | 1
2015-07-06 09:00 | 2015-07-06 | 1 | 9 | 203 | 64.2 | 1
2015-07-06 09:15 | 2015-07-06 | 1 | 9 | 212 | 64.95 | 1
2015-07-06 09:30 | 2015-07-06 | 1 | 9 | 218 | 65.7 | 2
2015-07-06 09:45 | 2015-07-06 | 1 | 9 | 215 | 66.45 | 2
2015-07-06 10:00 | 2015-07-06 | 1 | 10 | 225 | 67.1333 | 2
2015-07-06 10:15 | 2015-07-06 | 1 | 10 | 218 | 67.6333 | 2
2015-07-06 10:30 | 2015-07-06 | 1 | 10 | 221 | 68.1333 | 2
2015-07-06 10:45 | 2015-07-06 | 1 | 10 | 225 | 68.6333 | 2
2015-07-06 11:00 | 2015-07-06 | 1 | 11 | 238 | 69.0667 | 2
2015-07-06 11:15 | 2015-07-06 | 1 | 11 | 244 | 69.3167 | 2
2015-07-06 11:30 | 2015-07-06 | 1 | 11 | 239 | 69.5667 | 2
2015-07-06 11:45 | 2015-07-06 | 1 | 11 | 238 | 69.8167 | 2
2015-07-06 12:00 | 2015-07-06 | 1 | 12 | 241 | 70.0667 | 3
2015-07-06 12:15 | 2015-07-06 | 1 | 12 | 250 | 70.3167 | 3
2015-07-06 12:30 | 2015-07-06 | 1 | 12 | 251 | 70.5667 | 3
2015-07-06 12:45 | 2015-07-06 | 1 | 12 | 246 | 70.8167 | 3
2015-07-06 13:00 | 2015-07-06 | 1 | 13 | 244 | 70.9333 | 3
2015-07-06 13:15 | 2015-07-06 | 1 | 13 | 253 | 70.6833 | 3
2015-07-06 13:30 | 2015-07-06 | 1 | 13 | 252 | 70.4333 | 3
2015-07-06 13:45 | 2015-07-06 | 1 | 13 | 250 | 70.1833 | 3
2015-07-06 14:00 | 2015-07-06 | 1 | 14 | 250 | 70 | 2
2015-07-06 14:15 | 2015-07-06 | 1 | 14 | 256 | 70 | 2
2015-07-06 14:30 | 2015-07-06 | 1 | 14 | 261 | 70 | 2
2015-07-06 14:45 | 2015-07-06 | 1 | 14 | 258 | 70 | 2
2015-07-06 15:00 | 2015-07-06 | 1 | 15 | 253 | 70.0667 | 3
2015-07-06 15:15 | 2015-07-06 | 1 | 15 | 257 | 70.3167 | 3
2015-07-06 15:30 | 2015-07-06 | 1 | 15 | 270 | 70.5667 | 3
2015-07-06 15:45 | 2015-07-06 | 1 | 15 | 264 | 70.8167 | 3
2015-07-06 16:00 | 2015-07-06 | 1 | 16 | 259 | 70.9333 | 3
2015-07-06 16:15 | 2015-07-06 | 1 | 16 | 263 | 70.6833 | 3
2015-07-06 16:30 | 2015-07-06 | 1 | 16 | 258 | 70.4333 | 3
2015-07-06 16:45 | 2015-07-06 | 1 | 16 | 278 | 70.1833 | 3
2015-07-06 17:00 | 2015-07-06 | 1 | 17 | 271 | 69.8667 | 2
2015-07-06 17:15 | 2015-07-06 | 1 | 17 | 276 | 69.3667 | 2
2015-07-06 17:30 | 2015-07-06 | 1 | 17 | 265 | 68.8667 | 2
2015-07-06 17:45 | 2015-07-06 | 1 | 17 | 278 | 68.3667 | 2
2015-07-06 18:00 | 2015-07-06 | 1 | 18 | 260 | 67.8667 | 2
2015-07-06 18:15 | 2015-07-06 | 1 | 18 | 275 | 67.3667 | 2
2015-07-06 18:30 | 2015-07-06 | 1 | 18 | 262 | 66.8667 | 2
2015-07-06 18:45 | 2015-07-06 | 1 | 18 | 269 | 66.3667 | 2
2015-07-06 19:00 | 2015-07-06 | 1 | 19 | 251 | 65.8 | 2
2015-07-06 19:15 | 2015-07-06 | 1 | 19 | 256 | 65.05 | 2
2015-07-06 19:30 | 2015-07-06 | 1 | 19 | 257 | 64.3 | 1
2015-07-06 19:45 | 2015-07-06 | 1 | 19 | 256 | 63.55 | 1
2015-07-06 20:00 | 2015-07-06 | 1 | 20 | 248 | 63 | 1
2015-07-06 20:15 | 2015-07-06 | 1 | 20 | 251 | 63 | 1
2015-07-06 20:30 | 2015-07-06 | 1 | 20 | 241 | 63 | 1
2015-07-06 20:45 | 2015-07-06 | 1 | 20 | 238 | 63 | 1
2015-07-06 21:00 | 2015-07-06 | 1 | 21 | 225 | 63 | 1
2015-07-06 21:15 | 2015-07-06 | 1 | 21 | 213 | 63 | 1
2015-07-06 21:30 | 2015-07-06 | 1 | 21 | 219 | 63 | 1
2015-07-06 21:45 | 2015-07-06 | 1 | 21 | 217 | 63 | 1
2015-07-06 22:00 | 2015-07-06 | 1 | 22 | 204 | 63 | 1
2015-07-06 22:15 | 2015-07-06 | 1 | 22 | 206 | 63 | 1
2015-07-06 22:30 | 2015-07-06 | 1 | 22 | 200 | 63 | 1
2015-07-06 22:45 | 2015-07-06 | 1 | 22 | 200 | 63 | 1
2015-07-06 23:00 | 2015-07-06 | 1 | 23 | 207 | 63 | 1
2015-07-06 23:15 | 2015-07-06 | 1 | 23 | 198 | 63 | 1
2015-07-06 23:30 | 2015-07-06 | 1 | 23 | 208 | 63 | 1
2015-07-06 23:45 | 2015-07-06 | 1 | 23 | 196 | 63 | 1
2015-07-07 | 2015-07-07 | 2 | 0 | 194 | 63 | 1
2015-07-07 00:15 | 2015-07-07 | 2 | 0 | 193 | 63 | 1
2015-07-07 00:30 | 2015-07-07 | 2 | 0 | 191 | 63 | 1
2015-07-07 00:45 | 2015-07-07 | 2 | 0 | 193 | 63 | 1
2015-07-07 01:00 | 2015-07-07 | 2 | 1 | 191 | 62.9333 | 1
2015-07-07 01:15 | 2015-07-07 | 2 | 1 | 185 | 62.6833 | 1
2015-07-07 01:30 | 2015-07-07 | 2 | 1 | 182 | 62.4333 | 1
2015-07-07 01:45 | 2015-07-07 | 2 | 1 | 190 | 62.1833 | 1
2015-07-07 02:00 | 2015-07-07 | 2 | 2 | 177 | 62 | 1
2015-07-07 02:15 | 2015-07-07 | 2 | 2 | 184 | 62 | 1
2015-07-07 02:30 | 2015-07-07 | 2 | 2 | 188 | 62 | 1
2015-07-07 02:45 | 2015-07-07 | 2 | 2 | 185 | 62 | 1
2015-07-07 03:00 | 2015-07-07 | 2 | 3 | 174 | 62.0667 | 1
2015-07-07 03:15 | 2015-07-07 | 2 | 3 | 170 | 62.3167 | 1
2015-07-07 03:30 | 2015-07-07 | 2 | 3 | 176 | 62.5667 | 1
2015-07-07 03:45 | 2015-07-07 | 2 | 3 | 181 | 62.8167 | 1
2015-07-07 04:00 | 2015-07-07 | 2 | 4 | 176 | 63 | 1
2015-07-07 04:15 | 2015-07-07 | 2 | 4 | 182 | 63 | 1
2015-07-07 04:30 | 2015-07-07 | 2 | 4 | 183 | 63 | 1
2015-07-07 04:45 | 2015-07-07 | 2 | 4 | 180 | 63 | 1
2015-07-07 05:00 | 2015-07-07 | 2 | 5 | 176 | 63.069 | 1
2015-07-07 05:15 | 2015-07-07 | 2 | 5 | 176 | 63.3276 | 1
2015-07-07 05:30 | 2015-07-07 | 2 | 5 | 177 | 63.5862 | 1
2015-07-07 05:45 | 2015-07-07 | 2 | 5 | 180 | 63.8448 | 1
2015-07-07 06:00 | 2015-07-07 | 2 | 6 | 180 | 64 | 1
2015-07-07 06:15 | 2015-07-07 | 2 | 6 | 172 | 64 | 1
2015-07-07 06:30 | 2015-07-07 | 2 | 6 | 186 | 64 | 1
2015-07-07 06:45 | 2015-07-07 | 2 | 6 | 181 | 64 | 1
2015-07-07 07:00 | 2015-07-07 | 2 | 7 | 183 | 65.0667 | 2
2015-07-07 07:15 | 2015-07-07 | 2 | 7 | 187 | 65.3167 | 2
2015-07-07 07:30 | 2015-07-07 | 2 | 7 | 178 | 65.5667 | 2
2015-07-07 07:45 | 2015-07-07 | 2 | 7 | 195 | 65.8167 | 2
2015-07-07 08:00 | 2015-07-07 | 2 | 8 | 191 | 66.1333 | 2
2015-07-07 08:15 | 2015-07-07 | 2 | 8 | 195 | 66.6333 | 2
2015-07-07 08:30 | 2015-07-07 | 2 | 8 | 188 | 67.1333 | 2
2015-07-07 08:45 | 2015-07-07 | 2 | 8 | 205 | 67.6333 | 2
2015-07-07 09:00 | 2015-07-07 | 2 | 9 | 204 | 68.0667 | 2
2015-07-07 09:15 | 2015-07-07 | 2 | 9 | 202 | 68.3167 | 2
2015-07-07 09:30 | 2015-07-07 | 2 | 9 | 213 | 68.5667 | 2
2015-07-07 09:45 | 2015-07-07 | 2 | 9 | 215 | 68.8167 | 2
2015-07-07 10:00 | 2015-07-07 | 2 | 10 | 215 | 69.2069 | 2
2015-07-07 10:15 | 2015-07-07 | 2 | 10 | 219 | 69.9828 | 2
2015-07-07 10:30 | 2015-07-07 | 2 | 10 | 224 | 70.7586 | 3
2015-07-07 10:45 | 2015-07-07 | 2 | 10 | 225 | 71.5345 | 3
2015-07-07 11:00 | 2015-07-07 | 2 | 11 | 225 | 72 | 3
2015-07-07 11:15 | 2015-07-07 | 2 | 11 | 229 | 72 | 3
2015-07-07 11:30 | 2015-07-07 | 2 | 11 | 228 | 72 | 3
2015-07-07 11:45 | 2015-07-07 | 2 | 11 | 235 | 72 | 3
2015-07-07 12:00 | 2015-07-07 | 2 | 12 | 232 | 71.9333 | 3
2015-07-07 12:15 | 2015-07-07 | 2 | 12 | 239 | 71.6833 | 3
2015-07-07 12:30 | 2015-07-07 | 2 | 12 | 246 | 71.4333 | 3
2015-07-07 12:45 | 2015-07-07 | 2 | 12 | 242 | 71.1833 | 3
2015-07-07 13:00 | 2015-07-07 | 2 | 13 | 260 | 71.1333 | 3
2015-07-07 13:15 | 2015-07-07 | 2 | 13 | 241 | 71.6333 | 3
2015-07-07 13:30 | 2015-07-07 | 2 | 13 | 258 | 72.1333 | 3
2015-07-07 13:45 | 2015-07-07 | 2 | 13 | 252 | 72.6333 | 3
2015-07-07 14:00 | 2015-07-07 | 2 | 14 | 263 | 72.9333 | 3
2015-07-07 14:15 | 2015-07-07 | 2 | 14 | 261 | 72.6833 | 3
2015-07-07 14:30 | 2015-07-07 | 2 | 14 | 268 | 72.4333 | 3
2015-07-07 14:45 | 2015-07-07 | 2 | 14 | 262 | 72.1833 | 3
2015-07-07 15:00 | 2015-07-07 | 2 | 15 | 274 | 71.8 | 3
2015-07-07 15:15 | 2015-07-07 | 2 | 15 | 263 | 71.05 | 3
2015-07-07 15:30 | 2015-07-07 | 2 | 15 | 273 | 70.3 | 3
2015-07-07 15:45 | 2015-07-07 | 2 | 15 | 267 | 69.55 | 2
2015-07-07 16:00 | 2015-07-07 | 2 | 16 | 279 | 68.907 | 2
2015-07-07 16:15 | 2015-07-07 | 2 | 16 | 266 | 68.5581 | 2
2015-07-07 16:30 | 2015-07-07 | 2 | 16 | 267 | 68.2093 | 2
2015-07-07 16:45 | 2015-07-07 | 2 | 16 | 253 | 67.6471 | 2
2015-07-07 17:00 | 2015-07-07 | 2 | 17 | 276 | 66.8667 | 2
2015-07-07 17:15 | 2015-07-07 | 2 | 17 | 268 | 66.3667 | 2
2015-07-07 17:30 | 2015-07-07 | 2 | 17 | 270 | 65.8667 | 2
2015-07-07 17:45 | 2015-07-07 | 2 | 17 | 260 | 65.3667 | 2
2015-07-07 18:00 | 2015-07-07 | 2 | 18 | 271 | 64.8 | 1
2015-07-07 18:15 | 2015-07-07 | 2 | 18 | 257 | 64.05 | 1
2015-07-07 18:30 | 2015-07-07 | 2 | 18 | 264 | 63.3 | 1
2015-07-07 18:45 | 2015-07-07 | 2 | 18 | 256 | 62.55 | 1
2015-07-07 19:00 | 2015-07-07 | 2 | 19 | 264 | 61.875 | 1
2015-07-07 19:15 | 2015-07-07 | 2 | 19 | 252 | 61.4062 | 1
2015-07-07 19:30 | 2015-07-07 | 2 | 19 | 238 | 61 | 1
2015-07-07 19:45 | 2015-07-07 | 2 | 19 | 238 | 61 | 1
2015-07-07 20:00 | 2015-07-07 | 2 | 20 | 238 | 61 | 1
2015-07-07 20:15 | 2015-07-07 | 2 | 20 | 241 | 61 | 1
2015-07-07 20:30 | 2015-07-07 | 2 | 20 | 230 | 61 | 1
2015-07-07 20:45 | 2015-07-07 | 2 | 20 | 221 | 61 | 1
2015-07-07 21:00 | 2015-07-07 | 2 | 21 | 221 | 61 | 1
2015-07-07 21:15 | 2015-07-07 | 2 | 21 | 212 | 61 | 1
2015-07-07 21:30 | 2015-07-07 | 2 | 21 | 210 | 61 | 1
2015-07-07 21:45 | 2015-07-07 | 2 | 21 | 210 | 61 | 1
2015-07-07 22:00 | 2015-07-07 | 2 | 22 | 193 | 61 | 1
2015-07-07 22:15 | 2015-07-07 | 2 | 22 | 199 | 61 | 1
2015-07-07 22:30 | 2015-07-07 | 2 | 22 | 191 | 61.3158 | 1
2015-07-07 22:45 | 2015-07-07 | 2 | 22 | 189 | 61.7105 | 1
2015-07-07 23:00 | 2015-07-07 | 2 | 23 | 192 | 62 | 1
2015-07-07 23:15 | 2015-07-07 | 2 | 23 | 181 | 62 | 1
2015-07-07 23:30 | 2015-07-07 | 2 | 23 | 178 | 62 | 1
2015-07-07 23:45 | 2015-07-07 | 2 | 23 | 178 | 62 | 1
2015-07-08 | 2015-07-08 | 3 | 0 | 174 | 61.9333 | 1
2015-07-08 00:15 | 2015-07-08 | 3 | 0 | 165 | 61.6833 | 1
2015-07-08 00:30 | 2015-07-08 | 3 | 0 | 188 | 61.4333 | 1
2015-07-08 00:45 | 2015-07-08 | 3 | 0 | 180 | 61.1833 | 1
2015-07-08 01:00 | 2015-07-08 | 3 | 1 | 177 | 61 | 1
2015-07-08 01:15 | 2015-07-08 | 3 | 1 | 175 | 61 | 1
2015-07-08 01:30 | 2015-07-08 | 3 | 1 | 175 | 61 | 1
2015-07-08 01:45 | 2015-07-08 | 3 | 1 | 181 | 61 | 1
2015-07-08 02:00 | 2015-07-08 | 3 | 2 | 176 | 61 | 1
2015-07-08 02:15 | 2015-07-08 | 3 | 2 | 173 | 61 | 1
2015-07-08 02:30 | 2015-07-08 | 3 | 2 | 177 | 61 | 1
2015-07-08 02:45 | 2015-07-08 | 3 | 2 | 170 | 61 | 1
2015-07-08 03:00 | 2015-07-08 | 3 | 3 | 167 | 61 | 1
2015-07-08 03:15 | 2015-07-08 | 3 | 3 | 170 | 61 | 1
2015-07-08 03:30 | 2015-07-08 | 3 | 3 | 176 | 61 | 1
2015-07-08 03:45 | 2015-07-08 | 3 | 3 | 168 | 61 | 1
2015-07-08 04:00 | 2015-07-08 | 3 | 4 | 166 | 61 | 1
2015-07-08 04:15 | 2015-07-08 | 3 | 4 | 161 | 61 | 1
2015-07-08 04:30 | 2015-07-08 | 3 | 4 | 170 | 61 | 1
2015-07-08 04:45 | 2015-07-08 | 3 | 4 | 159 | 61 | 1
2015-07-08 05:00 | 2015-07-08 | 3 | 5 | 180 | 61 | 1
2015-07-08 05:15 | 2015-07-08 | 3 | 5 | 160 | 61 | 1
2015-07-08 05:30 | 2015-07-08 | 3 | 5 | 162 | 61 | 1
2015-07-08 05:45 | 2015-07-08 | 3 | 5 | 160 | 61 | 1
2015-07-08 06:00 | 2015-07-08 | 3 | 6 | 166 | 61 | 1
2015-07-08 06:15 | 2015-07-08 | 3 | 6 | 167 | 61 | 1
2015-07-08 06:30 | 2015-07-08 | 3 | 6 | 166 | 61 | 1
2015-07-08 06:45 | 2015-07-08 | 3 | 6 | 162 | 61 | 1
2015-07-08 07:00 | 2015-07-08 | 3 | 7 | 164 | 61 | 1
2015-07-08 07:15 | 2015-07-08 | 3 | 7 | 172 | 61 | 1
2015-07-08 07:30 | 2015-07-08 | 3 | 7 | 182 | 61 | 1
2015-07-08 07:45 | 2015-07-08 | 3 | 7 | 167 | 61 | 1
2015-07-08 08:00 | 2015-07-08 | 3 | 8 | 168 | 61.1333 | 1
2015-07-08 08:15 | 2015-07-08 | 3 | 8 | 190 | 61.6333 | 1
2015-07-08 08:30 | 2015-07-08 | 3 | 8 | 189 | 62.1333 | 1
2015-07-08 08:45 | 2015-07-08 | 3 | 8 | 204 | 62.6333 | 1
2015-07-08 09:00 | 2015-07-08 | 3 | 9 | 196 | 63 | 1
2015-07-08 09:15 | 2015-07-08 | 3 | 9 | 201 | 63 | 1
2015-07-08 09:30 | 2015-07-08 | 3 | 9 | 215 | 63 | 1
2015-07-08 09:45 | 2015-07-08 | 3 | 9 | 209 | 63 | 1
2015-07-08 10:00 | 2015-07-08 | 3 | 10 | 208 | 63.0667 | 1
2015-07-08 10:15 | 2015-07-08 | 3 | 10 | 206 | 63.3167 | 1
2015-07-08 10:30 | 2015-07-08 | 3 | 10 | 202 | 63.5667 | 1
2015-07-08 10:45 | 2015-07-08 | 3 | 10 | 219 | 63.8167 | 1
2015-07-08 11:00 | 2015-07-08 | 3 | 11 | 221 | 64.1333 | 1
2015-07-08 11:15 | 2015-07-08 | 3 | 11 | 212 | 64.6333 | 1
2015-07-08 11:30 | 2015-07-08 | 3 | 11 | 229 | 65.1333 | 2
2015-07-08 11:45 | 2015-07-08 | 3 | 11 | 218 | 65.6333 | 2
2015-07-08 12:00 | 2015-07-08 | 3 | 12 | 225 | 66.1333 | 2
2015-07-08 12:15 | 2015-07-08 | 3 | 12 | 223 | 66.6333 | 2
2015-07-08 12:30 | 2015-07-08 | 3 | 12 | 229 | 67.1333 | 2
2015-07-08 12:45 | 2015-07-08 | 3 | 12 | 227 | 67.6333 | 2
2015-07-08 13:00 | 2015-07-08 | 3 | 13 | 236 | 68 | 2
2015-07-08 13:15 | 2015-07-08 | 3 | 13 | 231 | 68 | 2
2015-07-08 13:30 | 2015-07-08 | 3 | 13 | 233 | 68 | 2
2015-07-08 13:45 | 2015-07-08 | 3 | 13 | 236 | 68 | 2
2015-07-08 14:00 | 2015-07-08 | 3 | 14 | 238 | 67.8 | 2
2015-07-08 14:15 | 2015-07-08 | 3 | 14 | 240 | 67.05 | 2
2015-07-08 14:30 | 2015-07-08 | 3 | 14 | 253 | 66.3 | 2
2015-07-08 14:45 | 2015-07-08 | 3 | 14 | 242 | 65.55 | 2
2015-07-08 15:00 | 2015-07-08 | 3 | 15 | 245 | 65.1111 | 2
2015-07-08 15:15 | 2015-07-08 | 3 | 15 | 240 | 65.5278 | 2
2015-07-08 15:30 | 2015-07-08 | 3 | 15 | 245 | 65.9444 | 2
2015-07-08 15:45 | 2015-07-08 | 3 | 15 | 248 | 66 | 2
2015-07-08 16:00 | 2015-07-08 | 3 | 16 | 241 | 65.7333 | 2
2015-07-08 16:15 | 2015-07-08 | 3 | 16 | 238 | 64.7333 | 1
2015-07-08 16:30 | 2015-07-08 | 3 | 16 | 247 | 63.7333 | 1
2015-07-08 16:45 | 2015-07-08 | 3 | 16 | 240 | 62.7333 | 1
2015-07-08 17:00 | 2015-07-08 | 3 | 17 | 249 | 61.9333 | 1
2015-07-08 17:15 | 2015-07-08 | 3 | 17 | 260 | 61.6833 | 1
2015-07-08 17:30 | 2015-07-08 | 3 | 17 | 246 | 61.4333 | 1
2015-07-08 17:45 | 2015-07-08 | 3 | 17 | 245 | 61.1833 | 1
2015-07-08 18:00 | 2015-07-08 | 3 | 18 | 242 | 61.1739 | 1
2015-07-08 18:15 | 2015-07-08 | 3 | 18 | 227 | 61.8261 | 1
2015-07-08 18:30 | 2015-07-08 | 3 | 18 | 233 | 62.4783 | 1
2015-07-08 18:45 | 2015-07-08 | 3 | 18 | 228 | 62.5714 | 1
2015-07-08 19:00 | 2015-07-08 | 3 | 19 | 223 | 61.0667 | 1
2015-07-08 19:15 | 2015-07-08 | 3 | 19 | 223 | 61.3167 | 1
2015-07-08 19:30 | 2015-07-08 | 3 | 19 | 227 | 61.5667 | 1
2015-07-08 19:45 | 2015-07-08 | 3 | 19 | 227 | 61.8167 | 1
2015-07-08 20:00 | 2015-07-08 | 3 | 20 | 216 | 61.9333 | 1
2015-07-08 20:15 | 2015-07-08 | 3 | 20 | 206 | 61.6833 | 1
2015-07-08 20:30 | 2015-07-08 | 3 | 20 | 211 | 61.4333 | 1
2015-07-08 20:45 | 2015-07-08 | 3 | 20 | 209 | 61.1833 | 1
2015-07-08 21:00 | 2015-07-08 | 3 | 21 | 209 | 61.0667 | 1
2015-07-08 21:15 | 2015-07-08 | 3 | 21 | 179 | 61.3167 | 1
2015-07-08 21:30 | 2015-07-08 | 3 | 21 | 178 | 61.5667 | 1
2015-07-08 21:45 | 2015-07-08 | 3 | 21 | 189 | 61.8167 | 1
2015-07-08 22:00 | 2015-07-08 | 3 | 22 | 185 | 61.9333 | 1
2015-07-08 22:15 | 2015-07-08 | 3 | 22 | 187 | 61.6833 | 1
2015-07-08 22:30 | 2015-07-08 | 3 | 22 | 198 | 61.4333 | 1
2015-07-08 22:45 | 2015-07-08 | 3 | 22 | 192 | 61.1833 | 1
2015-07-08 23:00 | 2015-07-08 | 3 | 23 | 191 | 60.9333 | 1
2015-07-08 23:15 | 2015-07-08 | 3 | 23 | 191 | 60.6833 | 1
2015-07-08 23:30 | 2015-07-08 | 3 | 23 | 190 | 60.4333 | 1
2015-07-08 23:45 | 2015-07-08 | 3 | 23 | 189 | 60.1833 | 1
2015-07-09 | 2015-07-09 | 4 | 0 | 182 | 60 | 1
2015-07-09 00:15 | 2015-07-09 | 4 | 0 | 177 | 60 | 1
2015-07-09 00:30 | 2015-07-09 | 4 | 0 | 185 | 60 | 1
2015-07-09 00:45 | 2015-07-09 | 4 | 0 | 167 | 60 | 1
2015-07-09 01:00 | 2015-07-09 | 4 | 1 | 171 | 60 | 1
2015-07-09 01:15 | 2015-07-09 | 4 | 1 | 173 | 60 | 1
2015-07-09 01:30 | 2015-07-09 | 4 | 1 | 174 | 60 | 1
2015-07-09 01:45 | 2015-07-09 | 4 | 1 | 181 | 60 | 1
2015-07-09 02:00 | 2015-07-09 | 4 | 2 | 173 | 60.069 | 1
2015-07-09 02:15 | 2015-07-09 | 4 | 2 | 168 | 60.3276 | 1
2015-07-09 02:30 | 2015-07-09 | 4 | 2 | 165 | 60.5862 | 1
2015-07-09 02:45 | 2015-07-09 | 4 | 2 | 171 | 60.8448 | 1
2015-07-09 03:00 | 2015-07-09 | 4 | 3 | 165 | 59 | 1
2015-07-09 03:15 | 2015-07-09 | 4 | 3 | 177 | 59 | 1
2015-07-09 03:30 | 2015-07-09 | 4 | 3 | 172 | 59 | 1
2015-07-09 03:45 | 2015-07-09 | 4 | 3 | 165 | 59 | 1
2015-07-09 04:00 | 2015-07-09 | 4 | 4 | 167 | 59 | 1
2015-07-09 04:15 | 2015-07-09 | 4 | 4 | 174 | 59 | 1
2015-07-09 04:30 | 2015-07-09 | 4 | 4 | 170 | 59 | 1
2015-07-09 04:45 | 2015-07-09 | 4 | 4 | 165 | 59 | 1
2015-07-09 05:00 | 2015-07-09 | 4 | 5 | 174 | 59 | 1
2015-07-09 05:15 | 2015-07-09 | 4 | 5 | 165 | 59 | 1
2015-07-09 05:30 | 2015-07-09 | 4 | 5 | 172 | 59 | 1
2015-07-09 05:45 | 2015-07-09 | 4 | 5 | 168 | 59 | 1
2015-07-09 06:00 | 2015-07-09 | 4 | 6 | 164 | 59.1379 | 1
2015-07-09 06:15 | 2015-07-09 | 4 | 6 | 171 | 59.6552 | 1
2015-07-09 06:30 | 2015-07-09 | 4 | 6 | 162 | 60.1724 | 1
2015-07-09 06:45 | 2015-07-09 | 4 | 6 | 180 | 60.6897 | 1
2015-07-09 07:00 | 2015-07-09 | 4 | 7 | 179 | 60.069 | 1
2015-07-09 07:15 | 2015-07-09 | 4 | 7 | 177 | 60.3276 | 1
2015-07-09 07:30 | 2015-07-09 | 4 | 7 | 171 | 60.5862 | 1
2015-07-09 07:45 | 2015-07-09 | 4 | 7 | 178 | 60.8448 | 1
2015-07-09 08:00 | 2015-07-09 | 4 | 8 | 192 | 61.1333 | 1
2015-07-09 08:15 | 2015-07-09 | 4 | 8 | 186 | 61.6333 | 1
2015-07-09 08:30 | 2015-07-09 | 4 | 8 | 189 | 62.1333 | 1
2015-07-09 08:45 | 2015-07-09 | 4 | 8 | 193 | 62.6333 | 1
2015-07-09 09:00 | 2015-07-09 | 4 | 9 | 203 | 63 | 1
2015-07-09 09:15 | 2015-07-09 | 4 | 9 | 199 | 63 | 1
2015-07-09 09:30 | 2015-07-09 | 4 | 9 | 195 | 63 | 1
2015-07-09 09:45 | 2015-07-09 | 4 | 9 | 203 | 63 | 1
2015-07-09 10:00 | 2015-07-09 | 4 | 10 | 200 | 63.2 | 1
2015-07-09 10:15 | 2015-07-09 | 4 | 10 | 213 | 63.95 | 1
2015-07-09 10:30 | 2015-07-09 | 4 | 10 | 214 | 64.7 | 1
2015-07-09 10:45 | 2015-07-09 | 4 | 10 | 208 | 65.45 | 2
2015-07-09 11:00 | 2015-07-09 | 4 | 11 | 213 | 66 | 2
2015-07-09 11:15 | 2015-07-09 | 4 | 11 | 214 | 66 | 2
2015-07-09 11:30 | 2015-07-09 | 4 | 11 | 207 | 66.2778 | 2
2015-07-09 11:45 | 2015-07-09 | 4 | 11 | 217 | 66.6944 | 2
2015-07-09 12:00 | 2015-07-09 | 4 | 12 | 207 | 66.931 | 2
2015-07-09 12:15 | 2015-07-09 | 4 | 12 | 232 | 66.6724 | 2
2015-07-09 12:30 | 2015-07-09 | 4 | 12 | 219 | 66.4138 | 2
2015-07-09 12:45 | 2015-07-09 | 4 | 12 | 220 | 66.1552 | 2
2015-07-09 13:00 | 2015-07-09 | 4 | 13 | 224 | 66.9333 | 2
2015-07-09 13:15 | 2015-07-09 | 4 | 13 | 226 | 66.6833 | 2
2015-07-09 13:30 | 2015-07-09 | 4 | 13 | 230 | 66.4333 | 2
2015-07-09 13:45 | 2015-07-09 | 4 | 13 | 234 | 66.1833 | 2
2015-07-09 14:00 | 2015-07-09 | 4 | 14 | 229 | 65.8 | 2
2015-07-09 14:15 | 2015-07-09 | 4 | 14 | 235 | 65.05 | 2
2015-07-09 14:30 | 2015-07-09 | 4 | 14 | 238 | 64.3 | 1
2015-07-09 14:45 | 2015-07-09 | 4 | 14 | 232 | 63.55 | 1
2015-07-09 15:00 | 2015-07-09 | 4 | 15 | 241 | 62.9333 | 1
2015-07-09 15:15 | 2015-07-09 | 4 | 15 | 242 | 62.6833 | 1
2015-07-09 15:30 | 2015-07-09 | 4 | 15 | 248 | 62.4333 | 1
2015-07-09 15:45 | 2015-07-09 | 4 | 15 | 227 | 62.1833 | 1
2015-07-09 16:00 | 2015-07-09 | 4 | 16 | 233 | 62.0667 | 1
2015-07-09 16:15 | 2015-07-09 | 4 | 16 | 231 | 62.3167 | 1
2015-07-09 16:30 | 2015-07-09 | 4 | 16 | 238 | 62.5667 | 1
2015-07-09 16:45 | 2015-07-09 | 4 | 16 | 237 | 62.8167 | 1
2015-07-09 17:00 | 2015-07-09 | 4 | 17 | 226 | 63 | 1
2015-07-09 17:15 | 2015-07-09 | 4 | 17 | 223 | 63 | 1
2015-07-09 17:30 | 2015-07-09 | 4 | 17 | 226 | 63 | 1
2015-07-09 17:45 | 2015-07-09 | 4 | 17 | 216 | 63 | 1
2015-07-09 18:00 | 2015-07-09 | 4 | 18 | 226 | 62.9333 | 1
2015-07-09 18:15 | 2015-07-09 | 4 | 18 | 217 | 62.6833 | 1
2015-07-09 18:30 | 2015-07-09 | 4 | 18 | 225 | 62.4333 | 1
2015-07-09 18:45 | 2015-07-09 | 4 | 18 | 217 | 62.1833 | 1
2015-07-09 19:00 | 2015-07-09 | 4 | 19 | 210 | 62 | 1
2015-07-09 19:15 | 2015-07-09 | 4 | 19 | 208 | 62 | 1
2015-07-09 19:30 | 2015-07-09 | 4 | 19 | 206 | 62 | 1
2015-07-09 19:45 | 2015-07-09 | 4 | 19 | 211 | 62 | 1
2015-07-09 20:00 | 2015-07-09 | 4 | 20 | 214 | 61.9333 | 1
2015-07-09 20:15 | 2015-07-09 | 4 | 20 | 204 | 61.6833 | 1
2015-07-09 20:30 | 2015-07-09 | 4 | 20 | 210 | 61.4333 | 1
2015-07-09 20:45 | 2015-07-09 | 4 | 20 | 210 | 61.1833 | 1
2015-07-09 21:00 | 2015-07-09 | 4 | 21 | 201 | 61 | 1
2015-07-09 21:15 | 2015-07-09 | 4 | 21 | 187 | 61 | 1
2015-07-09 21:30 | 2015-07-09 | 4 | 21 | 189 | 61 | 1
2015-07-09 21:45 | 2015-07-09 | 4 | 21 | 200 | 61 | 1
2015-07-09 22:00 | 2015-07-09 | 4 | 22 | 201 | 61 | 1
2015-07-09 22:15 | 2015-07-09 | 4 | 22 | 190 | 61 | 1
2015-07-09 22:30 | 2015-07-09 | 4 | 22 | 196 | 61 | 1
2015-07-09 22:45 | 2015-07-09 | 4 | 22 | 194 | 61 | 1
2015-07-09 23:00 | 2015-07-09 | 4 | 23 | 193 | 61 | 1
2015-07-09 23:15 | 2015-07-09 | 4 | 23 | 183 | 61 | 1
2015-07-09 23:30 | 2015-07-09 | 4 | 23 | 188 | 61 | 1
2015-07-09 23:45 | 2015-07-09 | 4 | 23 | 187 | 61 | 1
2015-07-10 | 2015-07-10 | 5 | 0 | 188 | 61 | 1
2015-07-10 00:15 | 2015-07-10 | 5 | 0 | 197 | 61 | 1
2015-07-10 00:30 | 2015-07-10 | 5 | 0 | 189 | 61 | 1
2015-07-10 00:45 | 2015-07-10 | 5 | 0 | 189 | 61 | 1
2015-07-10 01:00 | 2015-07-10 | 5 | 1 | 184 | 61 | 1
2015-07-10 01:15 | 2015-07-10 | 5 | 1 | 194 | 61 | 1
2015-07-10 01:30 | 2015-07-10 | 5 | 1 | 194 | 61 | 1
2015-07-10 01:45 | 2015-07-10 | 5 | 1 | 177 | 61 | 1
2015-07-10 02:00 | 2015-07-10 | 5 | 2 | 179 | 61 | 1
2015-07-10 02:15 | 2015-07-10 | 5 | 2 | 186 | 61 | 1
2015-07-10 02:30 | 2015-07-10 | 5 | 2 | 174 | 61 | 1
2015-07-10 02:45 | 2015-07-10 | 5 | 2 | 181 | 61 | 1
2015-07-10 03:00 | 2015-07-10 | 5 | 3 | 175 | 61 | 1
2015-07-10 03:15 | 2015-07-10 | 5 | 3 | 178 | 61 | 1
2015-07-10 03:30 | 2015-07-10 | 5 | 3 | 183 | 61 | 1
2015-07-10 03:45 | 2015-07-10 | 5 | 3 | 170 | 61 | 1
2015-07-10 04:00 | 2015-07-10 | 5 | 4 | 167 | 60.9333 | 1
2015-07-10 04:15 | 2015-07-10 | 5 | 4 | 176 | 60.6833 | 1
2015-07-10 04:30 | 2015-07-10 | 5 | 4 | 186 | 60.4333 | 1
2015-07-10 04:45 | 2015-07-10 | 5 | 4 | 170 | 60.1833 | 1
2015-07-10 05:00 | 2015-07-10 | 5 | 5 | 174 | 60.0667 | 1
2015-07-10 05:15 | 2015-07-10 | 5 | 5 | 177 | 60.3167 | 1
2015-07-10 05:30 | 2015-07-10 | 5 | 5 | 180 | 60.5667 | 1
2015-07-10 05:45 | 2015-07-10 | 5 | 5 | 177 | 60.8167 | 1
2015-07-10 06:00 | 2015-07-10 | 5 | 6 | 167 | 61.0667 | 1
2015-07-10 06:15 | 2015-07-10 | 5 | 6 | 173 | 61.3167 | 1
2015-07-10 06:30 | 2015-07-10 | 5 | 6 | 172 | 61.5667 | 1
2015-07-10 06:45 | 2015-07-10 | 5 | 6 | 188 | 61.8167 | 1
2015-07-10 07:00 | 2015-07-10 | 5 | 7 | 183 | 62.0667 | 1
2015-07-10 07:15 | 2015-07-10 | 5 | 7 | 186 | 62.3167 | 1
2015-07-10 07:30 | 2015-07-10 | 5 | 7 | 182 | 62.5667 | 1
2015-07-10 07:45 | 2015-07-10 | 5 | 7 | 180 | 62.8167 | 1
2015-07-10 08:00 | 2015-07-10 | 5 | 8 | 192 | 63.1333 | 1
2015-07-10 08:15 | 2015-07-10 | 5 | 8 | 194 | 63.6333 | 1
2015-07-10 08:30 | 2015-07-10 | 5 | 8 | 192 | 64.1333 | 1
2015-07-10 08:45 | 2015-07-10 | 5 | 8 | 195 | 64.6333 | 1
2015-07-10 09:00 | 2015-07-10 | 5 | 9 | 199 | 65 | 1
2015-07-10 09:15 | 2015-07-10 | 5 | 9 | 204 | 65 | 1
2015-07-10 09:30 | 2015-07-10 | 5 | 9 | 212 | 65 | 1
2015-07-10 09:45 | 2015-07-10 | 5 | 9 | 205 | 65 | 1
2015-07-10 10:00 | 2015-07-10 | 5 | 10 | 206 | 64.4286 | 1
2015-07-10 10:15 | 2015-07-10 | 5 | 10 | 207 | 64.4528 | 1
2015-07-10 10:30 | 2015-07-10 | 5 | 10 | 212 | 65.0189 | 2
2015-07-10 10:45 | 2015-07-10 | 5 | 10 | 224 | 65.5849 | 2
2015-07-10 11:00 | 2015-07-10 | 5 | 11 | 211 | 66.0667 | 2
2015-07-10 11:15 | 2015-07-10 | 5 | 11 | 214 | 66.3167 | 2
2015-07-10 11:30 | 2015-07-10 | 5 | 11 | 218 | 66.5667 | 2
2015-07-10 11:45 | 2015-07-10 | 5 | 11 | 223 | 66.8167 | 2
2015-07-10 12:00 | 2015-07-10 | 5 | 12 | 224 | 67.1333 | 2
2015-07-10 12:15 | 2015-07-10 | 5 | 12 | 217 | 67.6333 | 2
2015-07-10 12:30 | 2015-07-10 | 5 | 12 | 234 | 68.1333 | 2
2015-07-10 12:45 | 2015-07-10 | 5 | 12 | 220 | 68.6333 | 2
2015-07-10 13:00 | 2015-07-10 | 5 | 13 | 217 | 69.0667 | 2
2015-07-10 13:15 | 2015-07-10 | 5 | 13 | 235 | 69.3167 | 2
2015-07-10 13:30 | 2015-07-10 | 5 | 13 | 226 | 69.5667 | 2
2015-07-10 13:45 | 2015-07-10 | 5 | 13 | 237 | 69.8167 | 2
2015-07-10 14:00 | 2015-07-10 | 5 | 14 | 234 | 69.9333 | 2
2015-07-10 14:15 | 2015-07-10 | 5 | 14 | 229 | 69.6833 | 2
2015-07-10 14:30 | 2015-07-10 | 5 | 14 | 227 | 69.4333 | 2
2015-07-10 14:45 | 2015-07-10 | 5 | 14 | 231 | 69.1833 | 2
2015-07-10 15:00 | 2015-07-10 | 5 | 15 | 240 | 69.0667 | 2
2015-07-10 15:15 | 2015-07-10 | 5 | 15 | 243 | 69.3167 | 2
2015-07-10 15:30 | 2015-07-10 | 5 | 15 | 249 | 69.5667 | 2
2015-07-10 15:45 | 2015-07-10 | 5 | 15 | 232 | 69.8167 | 2
2015-07-10 16:00 | 2015-07-10 | 5 | 16 | 238 | 69.9333 | 2
2015-07-10 16:15 | 2015-07-10 | 5 | 16 | 232 | 69.6833 | 2
2015-07-10 16:30 | 2015-07-10 | 5 | 16 | 235 | 69.4333 | 2
2015-07-10 16:45 | 2015-07-10 | 5 | 16 | 238 | 69.1833 | 2
2015-07-10 17:00 | 2015-07-10 | 5 | 17 | 235 | 68.8 | 2
2015-07-10 17:15 | 2015-07-10 | 5 | 17 | 237 | 68.05 | 2
2015-07-10 17:30 | 2015-07-10 | 5 | 17 | 227 | 67.3 | 2
2015-07-10 17:45 | 2015-07-10 | 5 | 17 | 230 | 66.55 | 2
2015-07-10 18:00 | 2015-07-10 | 5 | 18 | 228 | 65.8667 | 2
2015-07-10 18:15 | 2015-07-10 | 5 | 18 | 216 | 65.3667 | 2
2015-07-10 18:30 | 2015-07-10 | 5 | 18 | 229 | 64.8667 | 1
2015-07-10 18:45 | 2015-07-10 | 5 | 18 | 223 | 64.3667 | 1
2015-07-10 19:00 | 2015-07-10 | 5 | 19 | 213 | 63.9333 | 1
2015-07-10 19:15 | 2015-07-10 | 5 | 19 | 213 | 63.6833 | 1
2015-07-10 19:30 | 2015-07-10 | 5 | 19 | 215 | 63.4333 | 1
2015-07-10 19:45 | 2015-07-10 | 5 | 19 | 215 | 63.1833 | 1
2015-07-10 20:00 | 2015-07-10 | 5 | 20 | 209 | 63 | 1
2015-07-10 20:15 | 2015-07-10 | 5 | 20 | 220 | 63 | 1
2015-07-10 20:30 | 2015-07-10 | 5 | 20 | 205 | 63 | 1
2015-07-10 20:45 | 2015-07-10 | 5 | 20 | 203 | 63 | 1
2015-07-10 21:00 | 2015-07-10 | 5 | 21 | 199 | 62.9333 | 1
2015-07-10 21:15 | 2015-07-10 | 5 | 21 | 190 | 62.6833 | 1
2015-07-10 21:30 | 2015-07-10 | 5 | 21 | 197 | 62.4333 | 1
2015-07-10 21:45 | 2015-07-10 | 5 | 21 | 175 | 62.1833 | 1
2015-07-10 22:00 | 2015-07-10 | 5 | 22 | 179 | 62 | 1
2015-07-10 22:15 | 2015-07-10 | 5 | 22 | 181 | 62 | 1
2015-07-10 22:30 | 2015-07-10 | 5 | 22 | 185 | 62 | 1
2015-07-10 22:45 | 2015-07-10 | 5 | 22 | 177 | 62 | 1
2015-07-10 23:00 | 2015-07-10 | 5 | 23 | 172 | 62 | 1
2015-07-10 23:15 | 2015-07-10 | 5 | 23 | 177 | 62 | 1
2015-07-10 23:30 | 2015-07-10 | 5 | 23 | 178 | 62 | 1
2015-07-10 23:45 | 2015-07-10 | 5 | 23 | 171 | 62 | 1
2015-07-11 | 2015-07-11 | 6 | 0 | 179 | 61.9333 | 1
2015-07-11 00:15 | 2015-07-11 | 6 | 0 | 168 | 61.6833 | 1
2015-07-11 00:30 | 2015-07-11 | 6 | 0 | 164 | 61.4333 | 1
2015-07-11 00:45 | 2015-07-11 | 6 | 0 | 168 | 61.1833 | 1
2015-07-11 01:00 | 2015-07-11 | 6 | 1 | 181 | 61 | 1
2015-07-11 01:15 | 2015-07-11 | 6 | 1 | 168 | 61 | 1
2015-07-11 01:30 | 2015-07-11 | 6 | 1 | 168 | 61 | 1
2015-07-11 01:45 | 2015-07-11 | 6 | 1 | 170 | 61 | 1
2015-07-11 02:00 | 2015-07-11 | 6 | 2 | 175 | 61 | 1
2015-07-11 02:15 | 2015-07-11 | 6 | 2 | 171 | 61 | 1
2015-07-11 02:30 | 2015-07-11 | 6 | 2 | 161 | 61 | 1
2015-07-11 02:45 | 2015-07-11 | 6 | 2 | 166 | 61 | 1
2015-07-11 03:00 | 2015-07-11 | 6 | 3 | 158 | 61 | 1
2015-07-11 03:15 | 2015-07-11 | 6 | 3 | 179 | 61 | 1
2015-07-11 03:30 | 2015-07-11 | 6 | 3 | 169 | 61 | 1
2015-07-11 03:45 | 2015-07-11 | 6 | 3 | 159 | 61 | 1
2015-07-11 04:00 | 2015-07-11 | 6 | 4 | 164 | 61 | 1
2015-07-11 04:15 | 2015-07-11 | 6 | 4 | 174 | 61 | 1
2015-07-11 04:30 | 2015-07-11 | 6 | 4 | 184 | 61 | 1
2015-07-11 04:45 | 2015-07-11 | 6 | 4 | 164 | 61 | 1
2015-07-11 05:00 | 2015-07-11 | 6 | 5 | 170 | 61 | 1
2015-07-11 05:15 | 2015-07-11 | 6 | 5 | 169 | 61.1087 | 1
2015-07-11 05:30 | 2015-07-11 | 6 | 5 | 173 | 61.4348 | 1
2015-07-11 05:45 | 2015-07-11 | 6 | 5 | 185 | 61.7609 | 1
2015-07-11 06:00 | 2015-07-11 | 6 | 6 | 162 | 62.0667 | 1
2015-07-11 06:15 | 2015-07-11 | 6 | 6 | 159 | 62.3167 | 1
2015-07-11 06:30 | 2015-07-11 | 6 | 6 | 158 | 62.5667 | 1
2015-07-11 06:45 | 2015-07-11 | 6 | 6 | 169 | 62.8167 | 1
2015-07-11 07:00 | 2015-07-11 | 6 | 7 | 170 | 63.2 | 1
2015-07-11 07:15 | 2015-07-11 | 6 | 7 | 161 | 63.95 | 1
2015-07-11 07:30 | 2015-07-11 | 6 | 7 | 174 | 64.7 | 1
2015-07-11 07:45 | 2015-07-11 | 6 | 7 | 159 | 65.45 | 2
2015-07-11 08:00 | 2015-07-11 | 6 | 8 | 157 | 66.0667 | 2
2015-07-11 08:15 | 2015-07-11 | 6 | 8 | 171 | 66.3167 | 2
2015-07-11 08:30 | 2015-07-11 | 6 | 8 | 185 | 66.5667 | 2
2015-07-11 08:45 | 2015-07-11 | 6 | 8 | 177 | 66.8167 | 2
2015-07-11 09:00 | 2015-07-11 | 6 | 9 | 171 | 67.0667 | 2
2015-07-11 09:15 | 2015-07-11 | 6 | 9 | 170 | 67.3167 | 2
2015-07-11 09:30 | 2015-07-11 | 6 | 9 | 172 | 67.5667 | 2
2015-07-11 09:45 | 2015-07-11 | 6 | 9 | 175 | 67.8167 | 2
2015-07-11 10:00 | 2015-07-11 | 6 | 10 | 195 | 68.0667 | 2
2015-07-11 10:15 | 2015-07-11 | 6 | 10 | 181 | 68.3167 | 2
2015-07-11 10:30 | 2015-07-11 | 6 | 10 | 179 | 68.5667 | 2
2015-07-11 10:45 | 2015-07-11 | 6 | 10 | 184 | 68.8167 | 2
2015-07-11 11:00 | 2015-07-11 | 6 | 11 | 193 | 69.0667 | 2
2015-07-11 11:15 | 2015-07-11 | 6 | 11 | 193 | 69.3167 | 2
2015-07-11 11:30 | 2015-07-11 | 6 | 11 | 185 | 69.5667 | 2
2015-07-11 11:45 | 2015-07-11 | 6 | 11 | 193 | 69.8167 | 2
2015-07-11 12:00 | 2015-07-11 | 6 | 12 | 200 | 70.0667 | 3
2015-07-11 12:15 | 2015-07-11 | 6 | 12 | 191 | 70.3167 | 3
2015-07-11 12:30 | 2015-07-11 | 6 | 12 | 194 | 70.5667 | 3
2015-07-11 12:45 | 2015-07-11 | 6 | 12 | 201 | 70.8167 | 3
2015-07-11 13:00 | 2015-07-11 | 6 | 13 | 209 | 71 | 3
2015-07-11 13:15 | 2015-07-11 | 6 | 13 | 204 | 71 | 3
2015-07-11 13:30 | 2015-07-11 | 6 | 13 | 209 | 71 | 3
2015-07-11 13:45 | 2015-07-11 | 6 | 13 | 199 | 71 | 3
2015-07-11 14:00 | 2015-07-11 | 6 | 14 | 202 | 70.9333 | 3
2015-07-11 14:15 | 2015-07-11 | 6 | 14 | 212 | 70.6833 | 3
2015-07-11 14:30 | 2015-07-11 | 6 | 14 | 219 | 70.4333 | 3
2015-07-11 14:45 | 2015-07-11 | 6 | 14 | 210 | 70.1833 | 3
2015-07-11 15:00 | 2015-07-11 | 6 | 15 | 219 | 69.9333 | 2
2015-07-11 15:15 | 2015-07-11 | 6 | 15 | 214 | 69.6833 | 2
2015-07-11 15:30 | 2015-07-11 | 6 | 15 | 227 | 69.4333 | 2
2015-07-11 15:45 | 2015-07-11 | 6 | 15 | 225 | 69.1833 | 2
2015-07-11 16:00 | 2015-07-11 | 6 | 16 | 232 | 69 | 2
2015-07-11 16:15 | 2015-07-11 | 6 | 16 | 224 | 69 | 2
2015-07-11 16:30 | 2015-07-11 | 6 | 16 | 226 | 69 | 2
2015-07-11 16:45 | 2015-07-11 | 6 | 16 | 234 | 69 | 2
2015-07-11 17:00 | 2015-07-11 | 6 | 17 | 234 | 68.8667 | 2
2015-07-11 17:15 | 2015-07-11 | 6 | 17 | 240 | 68.3667 | 2
2015-07-11 17:30 | 2015-07-11 | 6 | 17 | 234 | 67.8667 | 2
2015-07-11 17:45 | 2015-07-11 | 6 | 17 | 224 | 67.3667 | 2
2015-07-11 18:00 | 2015-07-11 | 6 | 18 | 224 | 66.8667 | 2
2015-07-11 18:15 | 2015-07-11 | 6 | 18 | 226 | 66.3667 | 2
2015-07-11 18:30 | 2015-07-11 | 6 | 18 | 216 | 65.8667 | 2
2015-07-11 18:45 | 2015-07-11 | 6 | 18 | 222 | 65.3667 | 2
2015-07-11 19:00 | 2015-07-11 | 6 | 19 | 225 | 64.9333 | 1
2015-07-11 19:15 | 2015-07-11 | 6 | 19 | 212 | 64.6833 | 1
2015-07-11 19:30 | 2015-07-11 | 6 | 19 | 210 | 64.4333 | 1
2015-07-11 19:45 | 2015-07-11 | 6 | 19 | 209 | 64.1833 | 1
2015-07-11 20:00 | 2015-07-11 | 6 | 20 | 223 | 63.9333 | 1
2015-07-11 20:15 | 2015-07-11 | 6 | 20 | 203 | 63.6833 | 1
2015-07-11 20:30 | 2015-07-11 | 6 | 20 | 199 | 63.4333 | 1
2015-07-11 20:45 | 2015-07-11 | 6 | 20 | 199 | 63.1833 | 1
2015-07-11 21:00 | 2015-07-11 | 6 | 21 | 204 | 63 | 1
2015-07-11 21:15 | 2015-07-11 | 6 | 21 | 193 | 63 | 1
2015-07-11 21:30 | 2015-07-11 | 6 | 21 | 184 | 63 | 1
2015-07-11 21:45 | 2015-07-11 | 6 | 21 | 195 | 63 | 1
2015-07-11 22:00 | 2015-07-11 | 6 | 22 | 180 | 63 | 1
2015-07-11 22:15 | 2015-07-11 | 6 | 22 | 176 | 63 | 1
2015-07-11 22:30 | 2015-07-11 | 6 | 22 | 177 | 63 | 1
2015-07-11 22:45 | 2015-07-11 | 6 | 22 | 183 | 63 | 1
2015-07-11 23:00 | 2015-07-11 | 6 | 23 | 187 | 63 | 1
2015-07-11 23:15 | 2015-07-11 | 6 | 23 | 183 | 63 | 1
2015-07-11 23:30 | 2015-07-11 | 6 | 23 | 177 | 63 | 1
2015-07-11 23:45 | 2015-07-11 | 6 | 23 | 172 | 63 | 1
2015-07-12 | 2015-07-12 | 7 | 0 | 179 | 62.9333 | 1
2015-07-12 00:15 | 2015-07-12 | 7 | 0 | 178 | 62.6833 | 1
2015-07-12 00:30 | 2015-07-12 | 7 | 0 | 162 | 62.4333 | 1
2015-07-12 00:45 | 2015-07-12 | 7 | 0 | 170 | 62.1833 | 1
2015-07-12 01:00 | 2015-07-12 | 7 | 1 | 174 | 62 | 1
2015-07-12 01:15 | 2015-07-12 | 7 | 1 | 160 | 62 | 1
2015-07-12 01:30 | 2015-07-12 | 7 | 1 | 159 | 62 | 1
2015-07-12 01:45 | 2015-07-12 | 7 | 1 | 161 | 62 | 1
2015-07-12 02:00 | 2015-07-12 | 7 | 2 | 175 | 62 | 1
2015-07-12 02:15 | 2015-07-12 | 7 | 2 | 164 | 62 | 1
2015-07-12 02:30 | 2015-07-12 | 7 | 2 | 156 | 62 | 1
2015-07-12 02:45 | 2015-07-12 | 7 | 2 | 162 | 62 | 1
2015-07-12 03:00 | 2015-07-12 | 7 | 3 | 160 | 62 | 1
2015-07-12 03:15 | 2015-07-12 | 7 | 3 | 178 | 62 | 1
2015-07-12 03:30 | 2015-07-12 | 7 | 3 | 173 | 62 | 1
2015-07-12 03:45 | 2015-07-12 | 7 | 3 | 174 | 62 | 1
2015-07-12 04:00 | 2015-07-12 | 7 | 4 | 173 | 62 | 1
2015-07-12 04:15 | 2015-07-12 | 7 | 4 | 180 | 62 | 1
2015-07-12 04:30 | 2015-07-12 | 7 | 4 | 187 | 62 | 1
2015-07-12 04:45 | 2015-07-12 | 7 | 4 | 167 | 62 | 1
2015-07-12 05:00 | 2015-07-12 | 7 | 5 | 177 | 62 | 1
2015-07-12 05:15 | 2015-07-12 | 7 | 5 | 168 | 62 | 1
2015-07-12 05:30 | 2015-07-12 | 7 | 5 | 175 | 62 | 1
2015-07-12 05:45 | 2015-07-12 | 7 | 5 | 173 | 62 | 1
2015-07-12 06:00 | 2015-07-12 | 7 | 6 | 160 | 62.1333 | 1
2015-07-12 06:15 | 2015-07-12 | 7 | 6 | 161 | 62.6333 | 1
2015-07-12 06:30 | 2015-07-12 | 7 | 6 | 159 | 63.1333 | 1
2015-07-12 06:45 | 2015-07-12 | 7 | 6 | 181 | 63.6333 | 1
2015-07-12 07:00 | 2015-07-12 | 7 | 7 | 179 | 64.1333 | 1
2015-07-12 07:15 | 2015-07-12 | 7 | 7 | 171 | 64.6333 | 1
2015-07-12 07:30 | 2015-07-12 | 7 | 7 | 166 | 65.1333 | 2
2015-07-12 07:45 | 2015-07-12 | 7 | 7 | 172 | 65.6333 | 2
2015-07-12 08:00 | 2015-07-12 | 7 | 8 | 185 | 66.2 | 2
2015-07-12 08:15 | 2015-07-12 | 7 | 8 | 185 | 66.95 | 2
2015-07-12 08:30 | 2015-07-12 | 7 | 8 | 176 | 67.7 | 2
2015-07-12 08:45 | 2015-07-12 | 7 | 8 | 177 | 68.45 | 2
2015-07-12 09:00 | 2015-07-12 | 7 | 9 | 187 | 69.1333 | 2
2015-07-12 09:15 | 2015-07-12 | 7 | 9 | 195 | 69.6333 | 2
2015-07-12 09:30 | 2015-07-12 | 7 | 9 | 180 | 70.1333 | 3
2015-07-12 09:45 | 2015-07-12 | 7 | 9 | 182 | 70.6333 | 3
2015-07-12 10:00 | 2015-07-12 | 7 | 10 | 184 | 71.1333 | 3
2015-07-12 10:15 | 2015-07-12 | 7 | 10 | 191 | 71.6333 | 3
2015-07-12 10:30 | 2015-07-12 | 7 | 10 | 199 | 72.1333 | 3
2015-07-12 10:45 | 2015-07-12 | 7 | 10 | 191 | 72.6333 | 3
2015-07-12 11:00 | 2015-07-12 | 7 | 11 | 191 | 73 | 3
2015-07-12 11:15 | 2015-07-12 | 7 | 11 | 199 | 73 | 3
2015-07-12 11:30 | 2015-07-12 | 7 | 11 | 202 | 73 | 3
2015-07-12 11:45 | 2015-07-12 | 7 | 11 | 212 | 73 | 3
2015-07-12 12:00 | 2015-07-12 | 7 | 12 | 207 | 72.9333 | 3
2015-07-12 12:15 | 2015-07-12 | 7 | 12 | 208 | 72.6833 | 3
2015-07-12 12:30 | 2015-07-12 | 7 | 12 | 211 | 72.4333 | 3
2015-07-12 12:45 | 2015-07-12 | 7 | 12 | 208 | 72.1833 | 3
2015-07-12 13:00 | 2015-07-12 | 7 | 13 | 207 | 72.0667 | 3
2015-07-12 13:15 | 2015-07-12 | 7 | 13 | 209 | 72.3167 | 3
2015-07-12 13:30 | 2015-07-12 | 7 | 13 | 212 | 72.5667 | 3
2015-07-12 13:45 | 2015-07-12 | 7 | 13 | 223 | 72.8167 | 3
2015-07-12 14:00 | 2015-07-12 | 7 | 14 | 217 | 72.8667 | 3
2015-07-12 14:15 | 2015-07-12 | 7 | 14 | 209 | 72.3667 | 3
2015-07-12 14:30 | 2015-07-12 | 7 | 14 | 217 | 71.8667 | 3
2015-07-12 14:45 | 2015-07-12 | 7 | 14 | 226 | 71.3667 | 3
2015-07-12 15:00 | 2015-07-12 | 7 | 15 | 217 | 71 | 3
2015-07-12 15:15 | 2015-07-12 | 7 | 15 | 234 | 71 | 3
2015-07-12 15:30 | 2015-07-12 | 7 | 15 | 239 | 71 | 3
2015-07-12 15:45 | 2015-07-12 | 7 | 15 | 220 | 71 | 3
2015-07-12 16:00 | 2015-07-12 | 7 | 16 | 246 | 70.9333 | 3
2015-07-12 16:15 | 2015-07-12 | 7 | 16 | 242 | 70.6833 | 3
2015-07-12 16:30 | 2015-07-12 | 7 | 16 | 231 | 70.4333 | 3
2015-07-12 16:45 | 2015-07-12 | 7 | 16 | 234 | 70.1833 | 3
2015-07-12 17:00 | 2015-07-12 | 7 | 17 | 245 | 69.8667 | 2
2015-07-12 17:15 | 2015-07-12 | 7 | 17 | 226 | 69.3667 | 2
2015-07-12 17:30 | 2015-07-12 | 7 | 17 | 240 | 68.8667 | 2
2015-07-12 17:45 | 2015-07-12 | 7 | 17 | 230 | 68.3667 | 2
2015-07-12 18:00 | 2015-07-12 | 7 | 18 | 238 | 67.8667 | 2
2015-07-12 18:15 | 2015-07-12 | 7 | 18 | 228 | 67.3667 | 2
2015-07-12 18:30 | 2015-07-12 | 7 | 18 | 231 | 66.8667 | 2
2015-07-12 18:45 | 2015-07-12 | 7 | 18 | 215 | 66.3667 | 2
2015-07-12 19:00 | 2015-07-12 | 7 | 19 | 220 | 65.8667 | 2
2015-07-12 19:15 | 2015-07-12 | 7 | 19 | 226 | 65.3667 | 2
2015-07-12 19:30 | 2015-07-12 | 7 | 19 | 220 | 64.8667 | 1
2015-07-12 19:45 | 2015-07-12 | 7 | 19 | 224 | 64.3667 | 1
2015-07-12 20:00 | 2015-07-12 | 7 | 20 | 211 | 63.9333 | 1
2015-07-12 20:15 | 2015-07-12 | 7 | 20 | 209 | 63.6833 | 1
2015-07-12 20:30 | 2015-07-12 | 7 | 20 | 207 | 63.4333 | 1
2015-07-12 20:45 | 2015-07-12 | 7 | 20 | 211 | 63.1833 | 1
2015-07-12 21:00 | 2015-07-12 | 7 | 21 | 205 | 63 | 1
2015-07-12 21:15 | 2015-07-12 | 7 | 21 | 190 | 63 | 1
2015-07-12 21:30 | 2015-07-12 | 7 | 21 | 196 | 63 | 1
2015-07-12 21:45 | 2015-07-12 | 7 | 21 | 187 | 63 | 1
2015-07-12 22:00 | 2015-07-12 | 7 | 22 | 191 | 63 | 1
2015-07-12 22:15 | 2015-07-12 | 7 | 22 | 188 | 63 | 1
2015-07-12 22:30 | 2015-07-12 | 7 | 22 | 184 | 63 | 1
2015-07-12 22:45 | 2015-07-12 | 7 | 22 | 177 | 63 | 1
2015-07-12 23:00 | 2015-07-12 | 7 | 23 | 179 | 63 | 1
2015-07-12 23:15 | 2015-07-12 | 7 | 23 | 174 | 63 | 1
2015-07-12 23:30 | 2015-07-12 | 7 | 23 | 185 | 63 | 1
2015-07-12 23:45 | 2015-07-12 | 7 | 23 | 183 | 63 | 1
2015-07-13 | 2015-07-13 | 1 | 0 | 171 | 63.0667 | 1
2015-07-13 00:15 | 2015-07-13 | 1 | 0 | 179 | 63.3167 | 1
2015-07-13 00:30 | 2015-07-13 | 1 | 0 | 177 | 63.5667 | 1
2015-07-13 00:45 | 2015-07-13 | 1 | 0 | 176 | 63.8167 | 1
2015-07-13 01:00 | 2015-07-13 | 1 | 1 | 171 | 63.8857 | 1
2015-07-13 01:15 | 2015-07-13 | 1 | 1 | 183 | 63.4571 | 1
2015-07-13 01:30 | 2015-07-13 | 1 | 1 | 168 | 63.0286 | 1
2015-07-13 01:45 | 2015-07-13 | 1 | 1 | 167 | 63.56 | 1
2015-07-13 02:00 | 2015-07-13 | 1 | 2 | 166 | 63.9333 | 1
2015-07-13 02:15 | 2015-07-13 | 1 | 2 | 168 | 63.6833 | 1
2015-07-13 02:30 | 2015-07-13 | 1 | 2 | 175 | 63.4333 | 1
2015-07-13 02:45 | 2015-07-13 | 1 | 2 | 164 | 63.1833 | 1
2015-07-13 03:00 | 2015-07-13 | 1 | 3 | 157 | 63 | 1
2015-07-13 03:15 | 2015-07-13 | 1 | 3 | 158 | 63 | 1
2015-07-13 03:30 | 2015-07-13 | 1 | 3 | 169 | 63 | 1
2015-07-13 03:45 | 2015-07-13 | 1 | 3 | 163 | 63 | 1
2015-07-13 04:00 | 2015-07-13 | 1 | 4 | 163 | 63 | 1
2015-07-13 04:15 | 2015-07-13 | 1 | 4 | 157 | 63 | 1
2015-07-13 04:30 | 2015-07-13 | 1 | 4 | 156 | 63 | 1
2015-07-13 04:45 | 2015-07-13 | 1 | 4 | 163 | 63 | 1
2015-07-13 05:00 | 2015-07-13 | 1 | 5 | 170 | 63 | 1
2015-07-13 05:15 | 2015-07-13 | 1 | 5 | 158 | 63 | 1
2015-07-13 05:30 | 2015-07-13 | 1 | 5 | 159 | 63 | 1
2015-07-13 05:45 | 2015-07-13 | 1 | 5 | 162 | 63 | 1
2015-07-13 06:00 | 2015-07-13 | 1 | 6 | 163 | 63 | 1
2015-07-13 06:15 | 2015-07-13 | 1 | 6 | 158 | 63 | 1
2015-07-13 06:30 | 2015-07-13 | 1 | 6 | 154 | 63 | 1
2015-07-13 06:45 | 2015-07-13 | 1 | 6 | 153 | 63 | 1
2015-07-13 07:00 | 2015-07-13 | 1 | 7 | 166 | 63.0667 | 1
2015-07-13 07:15 | 2015-07-13 | 1 | 7 | 191 | 63.3167 | 1
2015-07-13 07:30 | 2015-07-13 | 1 | 7 | 172 | 63.5667 | 1
2015-07-13 07:45 | 2015-07-13 | 1 | 7 | 171 | 63.8167 | 1
2015-07-13 08:00 | 2015-07-13 | 1 | 8 | 188 | 64 | 1
2015-07-13 08:15 | 2015-07-13 | 1 | 8 | 195 | 64 | 1
2015-07-13 08:30 | 2015-07-13 | 1 | 8 | 208 | 64 | 1
2015-07-13 08:45 | 2015-07-13 | 1 | 8 | 197 | 64 | 1
2015-07-13 09:00 | 2015-07-13 | 1 | 9 | 207 | 64.1633 | 1
2015-07-13 09:15 | 2015-07-13 | 1 | 9 | 202 | 64.7755 | 1
2015-07-13 09:30 | 2015-07-13 | 1 | 9 | 215 | 65.3878 | 2
2015-07-13 09:45 | 2015-07-13 | 1 | 9 | 212 | 66 | 2
2015-07-13 10:00 | 2015-07-13 | 1 | 10 | 209 | 67.1111 | 2
2015-07-13 10:15 | 2015-07-13 | 1 | 10 | 219 | 66.5882 | 2
2015-07-13 10:30 | 2015-07-13 | 1 | 10 | 229 | 67.4706 | 2
2015-07-13 10:45 | 2015-07-13 | 1 | 10 | 228 | 68.3529 | 2
2015-07-13 11:00 | 2015-07-13 | 1 | 11 | 219 | 69.1333 | 2
2015-07-13 11:15 | 2015-07-13 | 1 | 11 | 226 | 69.6333 | 2
2015-07-13 11:30 | 2015-07-13 | 1 | 11 | 224 | 70.1333 | 3
2015-07-13 11:45 | 2015-07-13 | 1 | 11 | 235 | 70.6333 | 3
2015-07-13 12:00 | 2015-07-13 | 1 | 12 | 251 | 71 | 3
2015-07-13 12:15 | 2015-07-13 | 1 | 12 | 234 | 71 | 3
2015-07-13 12:30 | 2015-07-13 | 1 | 12 | 235 | 71 | 3
2015-07-13 12:45 | 2015-07-13 | 1 | 12 | 240 | 71 | 3
2015-07-13 13:00 | 2015-07-13 | 1 | 13 | 249 | 70.9333 | 3
2015-07-13 13:15 | 2015-07-13 | 1 | 13 | 251 | 70.6833 | 3
2015-07-13 13:30 | 2015-07-13 | 1 | 13 | 246 | 70.4333 | 3
2015-07-13 13:45 | 2015-07-13 | 1 | 13 | 249 | 70.1833 | 3
2015-07-13 14:00 | 2015-07-13 | 1 | 14 | 258 | 70 | 2
2015-07-13 14:15 | 2015-07-13 | 1 | 14 | 268 | 70 | 2
2015-07-13 14:30 | 2015-07-13 | 1 | 14 | 259 | 70 | 2
2015-07-13 14:45 | 2015-07-13 | 1 | 14 | 266 | 70 | 2
2015-07-13 15:00 | 2015-07-13 | 1 | 15 | 264 | 70 | 2
2015-07-13 15:15 | 2015-07-13 | 1 | 15 | 261 | 70 | 2
2015-07-13 15:30 | 2015-07-13 | 1 | 15 | 267 | 70 | 2
2015-07-13 15:45 | 2015-07-13 | 1 | 15 | 263 | 70 | 2
2015-07-13 16:00 | 2015-07-13 | 1 | 16 | 277 | 69.8667 | 2
2015-07-13 16:15 | 2015-07-13 | 1 | 16 | 259 | 69.3667 | 2
2015-07-13 16:30 | 2015-07-13 | 1 | 16 | 267 | 68.8667 | 2
2015-07-13 16:45 | 2015-07-13 | 1 | 16 | 257 | 68.3667 | 2
2015-07-13 17:00 | 2015-07-13 | 1 | 17 | 267 | 67.9333 | 2
2015-07-13 17:15 | 2015-07-13 | 1 | 17 | 264 | 67.6833 | 2
2015-07-13 17:30 | 2015-07-13 | 1 | 17 | 282 | 67.4333 | 2
2015-07-13 17:45 | 2015-07-13 | 1 | 17 | 251 | 67.1833 | 2
2015-07-13 18:00 | 2015-07-13 | 1 | 18 | 258 | 66.8 | 2
2015-07-13 18:15 | 2015-07-13 | 1 | 18 | 234 | 66.05 | 2
2015-07-13 18:30 | 2015-07-13 | 1 | 18 | 259 | 65.3 | 2
2015-07-13 18:45 | 2015-07-13 | 1 | 18 | 247 | 64.55 | 1
2015-07-13 19:00 | 2015-07-13 | 1 | 19 | 239 | 64 | 1
2015-07-13 19:15 | 2015-07-13 | 1 | 19 | 232 | 64 | 1
2015-07-13 19:30 | 2015-07-13 | 1 | 19 | 238 | 64 | 1
2015-07-13 19:45 | 2015-07-13 | 1 | 19 | 232 | 64 | 1
2015-07-13 20:00 | 2015-07-13 | 1 | 20 | 242 | 63.9333 | 1
2015-07-13 20:15 | 2015-07-13 | 1 | 20 | 220 | 63.6833 | 1
2015-07-13 20:30 | 2015-07-13 | 1 | 20 | 217 | 63.4333 | 1
2015-07-13 20:45 | 2015-07-13 | 1 | 20 | 217 | 63.1833 | 1
2015-07-13 21:00 | 2015-07-13 | 1 | 21 | 229 | 62.9333 | 1
2015-07-13 21:15 | 2015-07-13 | 1 | 21 | 207 | 62.6833 | 1
2015-07-13 21:30 | 2015-07-13 | 1 | 21 | 203 | 62.4333 | 1
2015-07-13 21:45 | 2015-07-13 | 1 | 21 | 197 | 62.1833 | 1
2015-07-13 22:00 | 2015-07-13 | 1 | 22 | 205 | 62 | 1
2015-07-13 22:15 | 2015-07-13 | 1 | 22 | 207 | 62 | 1
2015-07-13 22:30 | 2015-07-13 | 1 | 22 | 195 | 62 | 1
2015-07-13 22:45 | 2015-07-13 | 1 | 22 | 196 | 62 | 1
2015-07-13 23:00 | 2015-07-13 | 1 | 23 | 200 | 62 | 1
2015-07-13 23:15 | 2015-07-13 | 1 | 23 | 202 | 62 | 1
2015-07-13 23:30 | 2015-07-13 | 1 | 23 | 181 | 62 | 1
2015-07-13 23:45 | 2015-07-13 | 1 | 23 | 183 | 62 | 1
2015-07-14 | 2015-07-14 | 2 | 0 | 183 | 61.931 | 1
2015-07-14 00:15 | 2015-07-14 | 2 | 0 | 189 | 61.6724 | 1
2015-07-14 00:30 | 2015-07-14 | 2 | 0 | 178 | 61.4138 | 1
2015-07-14 00:45 | 2015-07-14 | 2 | 0 | 179 | 61.1552 | 1
2015-07-14 01:00 | 2015-07-14 | 2 | 1 | 170 | 60.9333 | 1
2015-07-14 01:15 | 2015-07-14 | 2 | 1 | 185 | 60.6833 | 1
2015-07-14 01:30 | 2015-07-14 | 2 | 1 | 188 | 60.4333 | 1
2015-07-14 01:45 | 2015-07-14 | 2 | 1 | 167 | 60.1833 | 1
2015-07-14 02:00 | 2015-07-14 | 2 | 2 | 172 | 59.9333 | 1
2015-07-14 02:15 | 2015-07-14 | 2 | 2 | 170 | 59.6833 | 1
2015-07-14 02:30 | 2015-07-14 | 2 | 2 | 190 | 59.4333 | 1
2015-07-14 02:45 | 2015-07-14 | 2 | 2 | 168 | 59.1833 | 1
2015-07-14 03:00 | 2015-07-14 | 2 | 3 | 169 | 59 | 1
2015-07-14 03:15 | 2015-07-14 | 2 | 3 | 170 | 59 | 1
2015-07-14 03:30 | 2015-07-14 | 2 | 3 | 178 | 59 | 1
2015-07-14 03:45 | 2015-07-14 | 2 | 3 | 180 | 59 | 1
2015-07-14 04:00 | 2015-07-14 | 2 | 4 | 164 | 59 | 1
2015-07-14 04:15 | 2015-07-14 | 2 | 4 | 169 | 59 | 1
2015-07-14 04:30 | 2015-07-14 | 2 | 4 | 163 | 59 | 1
2015-07-14 04:45 | 2015-07-14 | 2 | 4 | 180 | 59 | 1
2015-07-14 05:00 | 2015-07-14 | 2 | 5 | 168 | 59 | 1
2015-07-14 05:15 | 2015-07-14 | 2 | 5 | 169 | 59 | 1
2015-07-14 05:30 | 2015-07-14 | 2 | 5 | 165 | 59 | 1
2015-07-14 05:45 | 2015-07-14 | 2 | 5 | 165 | 59 | 1
2015-07-14 06:00 | 2015-07-14 | 2 | 6 | 179 | 59.0667 | 1
2015-07-14 06:15 | 2015-07-14 | 2 | 6 | 162 | 59.3167 | 1
2015-07-14 06:30 | 2015-07-14 | 2 | 6 | 161 | 59.5667 | 1
2015-07-14 06:45 | 2015-07-14 | 2 | 6 | 160 | 59.8167 | 1
2015-07-14 07:00 | 2015-07-14 | 2 | 7 | 171 | 60 | 1
2015-07-14 07:15 | 2015-07-14 | 2 | 7 | 171 | 60 | 1
2015-07-14 07:30 | 2015-07-14 | 2 | 7 | 160 | 60 | 1
2015-07-14 07:45 | 2015-07-14 | 2 | 7 | 163 | 60 | 1
2015-07-14 08:00 | 2015-07-14 | 2 | 8 | 172 | 60.0667 | 1
2015-07-14 08:15 | 2015-07-14 | 2 | 8 | 192 | 60.3167 | 1
2015-07-14 08:30 | 2015-07-14 | 2 | 8 | 201 | 60.5667 | 1
2015-07-14 08:45 | 2015-07-14 | 2 | 8 | 191 | 60.8167 | 1
2015-07-14 09:00 | 2015-07-14 | 2 | 9 | 198 | 61.0667 | 1
2015-07-14 09:15 | 2015-07-14 | 2 | 9 | 194 | 61.3167 | 1
2015-07-14 09:30 | 2015-07-14 | 2 | 9 | 215 | 61.5667 | 1
2015-07-14 09:45 | 2015-07-14 | 2 | 9 | 198 | 61.8167 | 1
2015-07-14 10:00 | 2015-07-14 | 2 | 10 | 205 | 62.1667 | 1
2015-07-14 10:15 | 2015-07-14 | 2 | 10 | 203 | 62.7917 | 1
2015-07-14 10:30 | 2015-07-14 | 2 | 10 | 217 | 63 | 1
2015-07-14 10:45 | 2015-07-14 | 2 | 10 | 229 | 63 | 1
2015-07-14 11:00 | 2015-07-14 | 2 | 11 | 209 | 63.1333 | 1
2015-07-14 11:15 | 2015-07-14 | 2 | 11 | 219 | 63.6333 | 1
2015-07-14 11:30 | 2015-07-14 | 2 | 11 | 224 | 64.1333 | 1
2015-07-14 11:45 | 2015-07-14 | 2 | 11 | 219 | 64.6333 | 1
2015-07-14 12:00 | 2015-07-14 | 2 | 12 | 239 | 65.1081 | 2
2015-07-14 12:15 | 2015-07-14 | 2 | 12 | 219 | 65.5135 | 2
2015-07-14 12:30 | 2015-07-14 | 2 | 12 | 217 | 65.9189 | 2
2015-07-14 12:45 | 2015-07-14 | 2 | 12 | 210 | 67.0435 | 2
2015-07-14 13:00 | 2015-07-14 | 2 | 13 | 229 | 67.9333 | 2
2015-07-14 13:15 | 2015-07-14 | 2 | 13 | 225 | 67.6833 | 2
2015-07-14 13:30 | 2015-07-14 | 2 | 13 | 220 | 67.4333 | 2
2015-07-14 13:45 | 2015-07-14 | 2 | 13 | 216 | 67.1833 | 2
2015-07-14 14:00 | 2015-07-14 | 2 | 14 | 236 | 66.8667 | 2
2015-07-14 14:15 | 2015-07-14 | 2 | 14 | 215 | 66.3667 | 2
2015-07-14 14:30 | 2015-07-14 | 2 | 14 | 233 | 65.8667 | 2
2015-07-14 14:45 | 2015-07-14 | 2 | 14 | 221 | 65.3667 | 2
2015-07-14 15:00 | 2015-07-14 | 2 | 15 | 249 | 64.9333 | 1
2015-07-14 15:15 | 2015-07-14 | 2 | 15 | 230 | 64.6833 | 1
2015-07-14 15:30 | 2015-07-14 | 2 | 15 | 238 | 64.4333 | 1
2015-07-14 15:45 | 2015-07-14 | 2 | 15 | 224 | 64.1833 | 1
2015-07-14 16:00 | 2015-07-14 | 2 | 16 | 241 | 63.8667 | 1
2015-07-14 16:15 | 2015-07-14 | 2 | 16 | 236 | 63.3667 | 1
2015-07-14 16:30 | 2015-07-14 | 2 | 16 | 250 | 62.8667 | 1
2015-07-14 16:45 | 2015-07-14 | 2 | 16 | 241 | 62.3667 | 1
2015-07-14 17:00 | 2015-07-14 | 2 | 17 | 243 | 62 | 1
2015-07-14 17:15 | 2015-07-14 | 2 | 17 | 240 | 62 | 1
2015-07-14 17:30 | 2015-07-14 | 2 | 17 | 232 | 62 | 1
2015-07-14 17:45 | 2015-07-14 | 2 | 17 | 261 | 62 | 1
2015-07-14 18:00 | 2015-07-14 | 2 | 18 | 231 | 61.9333 | 1
2015-07-14 18:15 | 2015-07-14 | 2 | 18 | 234 | 61.6833 | 1
2015-07-14 18:30 | 2015-07-14 | 2 | 18 | 239 | 61.4333 | 1
2015-07-14 18:45 | 2015-07-14 | 2 | 18 | 240 | 61.1833 | 1
2015-07-14 19:00 | 2015-07-14 | 2 | 19 | 221 | 61 | 1
2015-07-14 19:15 | 2015-07-14 | 2 | 19 | 223 | 61 | 1
2015-07-14 19:30 | 2015-07-14 | 2 | 19 | 221 | 61 | 1
2015-07-14 19:45 | 2015-07-14 | 2 | 19 | 223 | 61 | 1
2015-07-14 20:00 | 2015-07-14 | 2 | 20 | 210 | 61 | 1
2015-07-14 20:15 | 2015-07-14 | 2 | 20 | 209 | 61 | 1
2015-07-14 20:30 | 2015-07-14 | 2 | 20 | 208 | 61 | 1
2015-07-14 20:45 | 2015-07-14 | 2 | 20 | 221 | 61 | 1
2015-07-14 21:00 | 2015-07-14 | 2 | 21 | 205 | 61 | 1
2015-07-14 21:15 | 2015-07-14 | 2 | 21 | 187 | 61 | 1
2015-07-14 21:30 | 2015-07-14 | 2 | 21 | 196 | 61 | 1
2015-07-14 21:45 | 2015-07-14 | 2 | 21 | 192 | 61 | 1
2015-07-14 22:00 | 2015-07-14 | 2 | 22 | 205 | 61 | 1
2015-07-14 22:15 | 2015-07-14 | 2 | 22 | 178 | 61 | 1
2015-07-14 22:30 | 2015-07-14 | 2 | 22 | 185 | 61 | 1
2015-07-14 22:45 | 2015-07-14 | 2 | 22 | 184 | 61 | 1
2015-07-14 23:00 | 2015-07-14 | 2 | 23 | 184 | 61 | 1
2015-07-14 23:15 | 2015-07-14 | 2 | 23 | 187 | 61 | 1
2015-07-14 23:30 | 2015-07-14 | 2 | 23 | 174 | 61 | 1
2015-07-14 23:45 | 2015-07-14 | 2 | 23 | 168 | 61 | 1
2015-07-15 | 2015-07-15 | 3 | 0 | 171 | 61.0667 | 1
2015-07-15 00:15 | 2015-07-15 | 3 | 0 | 196 | 61.3167 | 1
2015-07-15 00:30 | 2015-07-15 | 3 | 0 | 167 | 61.5667 | 1
2015-07-15 00:45 | 2015-07-15 | 3 | 0 | 174 | 61.8167 | 1
2015-07-15 01:00 | 2015-07-15 | 3 | 1 | 170 | 61.9333 | 1
2015-07-15 01:15 | 2015-07-15 | 3 | 1 | 185 | 61.6833 | 1
2015-07-15 01:30 | 2015-07-15 | 3 | 1 | 174 | 61.4333 | 1
2015-07-15 01:45 | 2015-07-15 | 3 | 1 | 164 | 61.1833 | 1
2015-07-15 02:00 | 2015-07-15 | 3 | 2 | 167 | 61 | 1
2015-07-15 02:15 | 2015-07-15 | 3 | 2 | 174 | 61 | 1
2015-07-15 02:30 | 2015-07-15 | 3 | 2 | 171 | 61 | 1
2015-07-15 02:45 | 2015-07-15 | 3 | 2 | 166 | 61 | 1
2015-07-15 03:00 | 2015-07-15 | 3 | 3 | 171 | 61 | 1
2015-07-15 03:15 | 2015-07-15 | 3 | 3 | 161 | 61 | 1
2015-07-15 03:30 | 2015-07-15 | 3 | 3 | 179 | 61 | 1
2015-07-15 03:45 | 2015-07-15 | 3 | 3 | 163 | 61 | 1
2015-07-15 04:00 | 2015-07-15 | 3 | 4 | 158 | 59.9333 | 1
2015-07-15 04:15 | 2015-07-15 | 3 | 4 | 159 | 59.6833 | 1
2015-07-15 04:30 | 2015-07-15 | 3 | 4 | 161 | 59.4333 | 1
2015-07-15 04:45 | 2015-07-15 | 3 | 4 | 175 | 59.1833 | 1
2015-07-15 05:00 | 2015-07-15 | 3 | 5 | 150 | 59 | 1
2015-07-15 05:15 | 2015-07-15 | 3 | 5 | 150 | 59 | 1
2015-07-15 05:30 | 2015-07-15 | 3 | 5 | 146 | 59 | 1
2015-07-15 05:45 | 2015-07-15 | 3 | 5 | 159 | 59 | 1
2015-07-15 06:00 | 2015-07-15 | 3 | 6 | 156 | 59.2 | 1
2015-07-15 06:15 | 2015-07-15 | 3 | 6 | 155 | 59.95 | 1
2015-07-15 06:30 | 2015-07-15 | 3 | 6 | 149 | 60.7 | 1
2015-07-15 06:45 | 2015-07-15 | 3 | 6 | 159 | 61.45 | 1
2015-07-15 07:00 | 2015-07-15 | 3 | 7 | 172 | 62.2 | 1
2015-07-15 07:15 | 2015-07-15 | 3 | 7 | 160 | 62.95 | 1
2015-07-15 07:30 | 2015-07-15 | 3 | 7 | 163 | 63.7 | 1
2015-07-15 07:45 | 2015-07-15 | 3 | 7 | 165 | 64.45 | 1
2015-07-15 08:00 | 2015-07-15 | 3 | 8 | 173 | 65.1333 | 2
2015-07-15 08:15 | 2015-07-15 | 3 | 8 | 197 | 65.6333 | 2
2015-07-15 08:30 | 2015-07-15 | 3 | 8 | 194 | 66.1333 | 2
2015-07-15 08:45 | 2015-07-15 | 3 | 8 | 196 | 66.6333 | 2
2015-07-15 09:00 | 2015-07-15 | 3 | 9 | 192 | 67.0667 | 2
2015-07-15 09:15 | 2015-07-15 | 3 | 9 | 207 | 67.3167 | 2
2015-07-15 09:30 | 2015-07-15 | 3 | 9 | 210 | 67.5667 | 2
2015-07-15 09:45 | 2015-07-15 | 3 | 9 | 204 | 67.8167 | 2
2015-07-15 10:00 | 2015-07-15 | 3 | 10 | 203 | 68.0667 | 2
2015-07-15 10:15 | 2015-07-15 | 3 | 10 | 207 | 68.3167 | 2
2015-07-15 10:30 | 2015-07-15 | 3 | 10 | 228 | 68.5667 | 2
2015-07-15 10:45 | 2015-07-15 | 3 | 10 | 222 | 68.8167 | 2
2015-07-15 11:00 | 2015-07-15 | 3 | 11 | 216 | 69.2 | 2
2015-07-15 11:15 | 2015-07-15 | 3 | 11 | 221 | 69.95 | 2
2015-07-15 11:30 | 2015-07-15 | 3 | 11 | 221 | 70.7 | 3
2015-07-15 11:45 | 2015-07-15 | 3 | 11 | 236 | 71.45 | 3
2015-07-15 12:00 | 2015-07-15 | 3 | 12 | 230 | 72.069 | 3
2015-07-15 12:15 | 2015-07-15 | 3 | 12 | 240 | 72.3276 | 3
2015-07-15 12:30 | 2015-07-15 | 3 | 12 | 231 | 72.5862 | 3
2015-07-15 12:45 | 2015-07-15 | 3 | 12 | 241 | 72.8448 | 3
2015-07-15 13:00 | 2015-07-15 | 3 | 13 | 251 | 73.1333 | 3
2015-07-15 13:15 | 2015-07-15 | 3 | 13 | 245 | 73.6333 | 3
2015-07-15 13:30 | 2015-07-15 | 3 | 13 | 250 | 74.1333 | 3
2015-07-15 13:45 | 2015-07-15 | 3 | 13 | 253 | 74.6333 | 3
2015-07-15 14:00 | 2015-07-15 | 3 | 14 | 256 | 75 | 3
2015-07-15 14:15 | 2015-07-15 | 3 | 14 | 268 | 75 | 3
2015-07-15 14:30 | 2015-07-15 | 3 | 14 | 249 | 75 | 3
2015-07-15 14:45 | 2015-07-15 | 3 | 14 | 254 | 75.9 | 4
2015-07-15 15:00 | 2015-07-15 | 3 | 15 | 262 | 76.8667 | 4
2015-07-15 15:15 | 2015-07-15 | 3 | 15 | 268 | 76.3667 | 4
2015-07-15 15:30 | 2015-07-15 | 3 | 15 | 266 | 75.8667 | 4
2015-07-15 15:45 | 2015-07-15 | 3 | 15 | 267 | 75.3667 | 4
2015-07-15 16:00 | 2015-07-15 | 3 | 16 | 262 | 74.8667 | 3
2015-07-15 16:15 | 2015-07-15 | 3 | 16 | 269 | 74.3667 | 3
2015-07-15 16:30 | 2015-07-15 | 3 | 16 | 275 | 73.8667 | 3
2015-07-15 16:45 | 2015-07-15 | 3 | 16 | 270 | 73.3667 | 3
2015-07-15 17:00 | 2015-07-15 | 3 | 17 | 276 | 72.6667 | 3
2015-07-15 17:15 | 2015-07-15 | 3 | 17 | 272 | 71.4167 | 3
2015-07-15 17:30 | 2015-07-15 | 3 | 17 | 262 | 70.1667 | 3
2015-07-15 17:45 | 2015-07-15 | 3 | 17 | 257 | 68.9167 | 2
2015-07-15 18:00 | 2015-07-15 | 3 | 18 | 260 | 67.8667 | 2
2015-07-15 18:15 | 2015-07-15 | 3 | 18 | 269 | 67.3667 | 2
2015-07-15 18:30 | 2015-07-15 | 3 | 18 | 265 | 66.8667 | 2
2015-07-15 18:45 | 2015-07-15 | 3 | 18 | 259 | 66.3667 | 2
2015-07-15 19:00 | 2015-07-15 | 3 | 19 | 255 | 65.8667 | 2
2015-07-15 19:15 | 2015-07-15 | 3 | 19 | 248 | 65.3667 | 2
2015-07-15 19:30 | 2015-07-15 | 3 | 19 | 249 | 64.8667 | 1
2015-07-15 19:45 | 2015-07-15 | 3 | 19 | 238 | 64.3667 | 1
2015-07-15 20:00 | 2015-07-15 | 3 | 20 | 234 | 63.9333 | 1
2015-07-15 20:15 | 2015-07-15 | 3 | 20 | 251 | 63.6833 | 1
2015-07-15 20:30 | 2015-07-15 | 3 | 20 | 240 | 63.4333 | 1
2015-07-15 20:45 | 2015-07-15 | 3 | 20 | 220 | 63.1833 | 1
2015-07-15 21:00 | 2015-07-15 | 3 | 21 | 231 | 62.9333 | 1
2015-07-15 21:15 | 2015-07-15 | 3 | 21 | 220 | 62.6833 | 1
2015-07-15 21:30 | 2015-07-15 | 3 | 21 | 225 | 62.4333 | 1
2015-07-15 21:45 | 2015-07-15 | 3 | 21 | 219 | 62.1833 | 1
2015-07-15 22:00 | 2015-07-15 | 3 | 22 | 231 | 61.9333 | 1
2015-07-15 22:15 | 2015-07-15 | 3 | 22 | 216 | 61.6833 | 1
2015-07-15 22:30 | 2015-07-15 | 3 | 22 | 214 | 61.4333 | 1
2015-07-15 22:45 | 2015-07-15 | 3 | 22 | 213 | 61.1833 | 1
2015-07-15 23:00 | 2015-07-15 | 3 | 23 | 216 | 61 | 1
2015-07-15 23:15 | 2015-07-15 | 3 | 23 | 223 | 61 | 1
2015-07-15 23:30 | 2015-07-15 | 3 | 23 | 199 | 61 | 1
2015-07-15 23:45 | 2015-07-15 | 3 | 23 | 198 | 61 | 1
2015-07-16 | 2015-07-16 | 4 | 0 | 190 | 61 | 1
2015-07-16 00:15 | 2015-07-16 | 4 | 0 | 194 | 61 | 1
2015-07-16 00:30 | 2015-07-16 | 4 | 0 | 191 | 61 | 1
2015-07-16 00:45 | 2015-07-16 | 4 | 0 | 200 | 60.44 | 1
2015-07-16 01:00 | 2015-07-16 | 4 | 1 | 189 | 60.3636 | 1
2015-07-16 01:15 | 2015-07-16 | 4 | 1 | 178 | 61 | 1
2015-07-16 01:30 | 2015-07-16 | 4 | 1 | 174 | 61 | 1
2015-07-16 01:45 | 2015-07-16 | 4 | 1 | 187 | 61 | 1
2015-07-16 02:00 | 2015-07-16 | 4 | 2 | 186 | 61 | 1
2015-07-16 02:15 | 2015-07-16 | 4 | 2 | 170 | 61 | 1
2015-07-16 02:30 | 2015-07-16 | 4 | 2 | 175 | 61 | 1
2015-07-16 02:45 | 2015-07-16 | 4 | 2 | 173 | 60.55 | 1
2015-07-16 03:00 | 2015-07-16 | 4 | 3 | 179 | 60.16 | 1
2015-07-16 03:15 | 2015-07-16 | 4 | 3 | 172 | 60.76 | 1
2015-07-16 03:30 | 2015-07-16 | 4 | 3 | 168 | 60.7429 | 1
2015-07-16 03:45 | 2015-07-16 | 4 | 3 | 173 | 60.3143 | 1
2015-07-16 04:00 | 2015-07-16 | 4 | 4 | 181 | 60 | 1
2015-07-16 04:15 | 2015-07-16 | 4 | 4 | 172 | 60 | 1
2015-07-16 04:30 | 2015-07-16 | 4 | 4 | 167 | 60 | 1
2015-07-16 04:45 | 2015-07-16 | 4 | 4 | 170 | 60 | 1
2015-07-16 05:00 | 2015-07-16 | 4 | 5 | 165 | 60 | 1
2015-07-16 05:15 | 2015-07-16 | 4 | 5 | 180 | 60 | 1
2015-07-16 05:30 | 2015-07-16 | 4 | 5 | 165 | 60 | 1
2015-07-16 05:45 | 2015-07-16 | 4 | 5 | 165 | 60 | 1
2015-07-16 06:00 | 2015-07-16 | 4 | 6 | 165 | 60.1333 | 1
2015-07-16 06:15 | 2015-07-16 | 4 | 6 | 180 | 60.6333 | 1
2015-07-16 06:30 | 2015-07-16 | 4 | 6 | 173 | 61.1333 | 1
2015-07-16 06:45 | 2015-07-16 | 4 | 6 | 169 | 61.6333 | 1
2015-07-16 07:00 | 2015-07-16 | 4 | 7 | 172 | 62.1333 | 1
2015-07-16 07:15 | 2015-07-16 | 4 | 7 | 174 | 62.6333 | 1
2015-07-16 07:30 | 2015-07-16 | 4 | 7 | 191 | 63.1333 | 1
2015-07-16 07:45 | 2015-07-16 | 4 | 7 | 170 | 63.6333 | 1
2015-07-16 08:00 | 2015-07-16 | 4 | 8 | 178 | 64.1481 | 1
2015-07-16 08:15 | 2015-07-16 | 4 | 8 | 188 | 64.7037 | 1
2015-07-16 08:30 | 2015-07-16 | 4 | 8 | 197 | 65.2593 | 2
2015-07-16 08:45 | 2015-07-16 | 4 | 8 | 198 | 65.8148 | 2
2015-07-16 09:00 | 2015-07-16 | 4 | 9 | 196 | 66.1333 | 2
2015-07-16 09:15 | 2015-07-16 | 4 | 9 | 212 | 66.6333 | 2
2015-07-16 09:30 | 2015-07-16 | 4 | 9 | 205 | 67.1333 | 2
2015-07-16 09:45 | 2015-07-16 | 4 | 9 | 222 | 67.6333 | 2
2015-07-16 10:00 | 2015-07-16 | 4 | 10 | 214 | 68.1333 | 2
2015-07-16 10:15 | 2015-07-16 | 4 | 10 | 216 | 68.6333 | 2
2015-07-16 10:30 | 2015-07-16 | 4 | 10 | 222 | 69.1333 | 2
2015-07-16 10:45 | 2015-07-16 | 4 | 10 | 227 | 69.6333 | 2
2015-07-16 11:00 | 2015-07-16 | 4 | 11 | 245 | 70.0667 | 3
2015-07-16 11:15 | 2015-07-16 | 4 | 11 | 231 | 70.3167 | 3
2015-07-16 11:30 | 2015-07-16 | 4 | 11 | 245 | 70.5667 | 3
2015-07-16 11:45 | 2015-07-16 | 4 | 11 | 245 | 70.8167 | 3
2015-07-16 12:00 | 2015-07-16 | 4 | 12 | 237 | 71.0667 | 3
2015-07-16 12:15 | 2015-07-16 | 4 | 12 | 247 | 71.3167 | 3
2015-07-16 12:30 | 2015-07-16 | 4 | 12 | 245 | 71.5667 | 3
2015-07-16 12:45 | 2015-07-16 | 4 | 12 | 254 | 71.8167 | 3
2015-07-16 13:00 | 2015-07-16 | 4 | 13 | 253 | 72.2 | 3
2015-07-16 13:15 | 2015-07-16 | 4 | 13 | 267 | 72.95 | 3
2015-07-16 13:30 | 2015-07-16 | 4 | 13 | 250 | 73.7 | 3
2015-07-16 13:45 | 2015-07-16 | 4 | 13 | 266 | 74.45 | 3
2015-07-16 14:00 | 2015-07-16 | 4 | 14 | 252 | 75.0667 | 4
2015-07-16 14:15 | 2015-07-16 | 4 | 14 | 282 | 75.3167 | 4
2015-07-16 14:30 | 2015-07-16 | 4 | 14 | 276 | 75.5667 | 4
2015-07-16 14:45 | 2015-07-16 | 4 | 14 | 262 | 75.8167 | 4
2015-07-16 15:00 | 2015-07-16 | 4 | 15 | 273 | 75.8 | 4
2015-07-16 15:15 | 2015-07-16 | 4 | 15 | 277 | 75.05 | 4
2015-07-16 15:30 | 2015-07-16 | 4 | 15 | 278 | 74.3 | 3
2015-07-16 15:45 | 2015-07-16 | 4 | 15 | 280 | 73.55 | 3
2015-07-16 16:00 | 2015-07-16 | 4 | 16 | 272 | 72.9333 | 3
2015-07-16 16:15 | 2015-07-16 | 4 | 16 | 275 | 72.6833 | 3
2015-07-16 16:30 | 2015-07-16 | 4 | 16 | 269 | 72.4333 | 3
2015-07-16 16:45 | 2015-07-16 | 4 | 16 | 258 | 72.1833 | 3
2015-07-16 17:00 | 2015-07-16 | 4 | 17 | 279 | 71.6667 | 3
2015-07-16 17:15 | 2015-07-16 | 4 | 17 | 275 | 70.4167 | 3
2015-07-16 17:30 | 2015-07-16 | 4 | 17 | 261 | 69.1667 | 2
2015-07-16 17:45 | 2015-07-16 | 4 | 17 | 273 | 67.9167 | 2
2015-07-16 18:00 | 2015-07-16 | 4 | 18 | 263 | 66.8 | 2
2015-07-16 18:15 | 2015-07-16 | 4 | 18 | 264 | 66.05 | 2
2015-07-16 18:30 | 2015-07-16 | 4 | 18 | 260 | 65.3 | 2
2015-07-16 18:45 | 2015-07-16 | 4 | 18 | 263 | 64.55 | 1
2015-07-16 19:00 | 2015-07-16 | 4 | 19 | 246 | 63.8 | 1
2015-07-16 19:15 | 2015-07-16 | 4 | 19 | 255 | 63.05 | 1
2015-07-16 19:30 | 2015-07-16 | 4 | 19 | 238 | 62.3 | 1
2015-07-16 19:45 | 2015-07-16 | 4 | 19 | 249 | 61.55 | 1
2015-07-16 20:00 | 2015-07-16 | 4 | 20 | 253 | 61 | 1
2015-07-16 20:15 | 2015-07-16 | 4 | 20 | 237 | 61 | 1
2015-07-16 20:30 | 2015-07-16 | 4 | 20 | 234 | 61 | 1
2015-07-16 20:45 | 2015-07-16 | 4 | 20 | 225 | 61 | 1
2015-07-16 21:00 | 2015-07-16 | 4 | 21 | 219 | 61 | 1
2015-07-16 21:15 | 2015-07-16 | 4 | 21 | 216 | 61 | 1
2015-07-16 21:30 | 2015-07-16 | 4 | 21 | 218 | 61 | 1
2015-07-16 21:45 | 2015-07-16 | 4 | 21 | 210 | 61 | 1
2015-07-16 22:00 | 2015-07-16 | 4 | 22 | 220 | 60.9333 | 1
2015-07-16 22:15 | 2015-07-16 | 4 | 22 | 208 | 60.6833 | 1
2015-07-16 22:30 | 2015-07-16 | 4 | 22 | 208 | 60.4333 | 1
2015-07-16 22:45 | 2015-07-16 | 4 | 22 | 222 | 60.1833 | 1
2015-07-16 23:00 | 2015-07-16 | 4 | 23 | 203 | 60 | 1
2015-07-16 23:15 | 2015-07-16 | 4 | 23 | 200 | 60 | 1
2015-07-16 23:30 | 2015-07-16 | 4 | 23 | 195 | 60 | 1
2015-07-16 23:45 | 2015-07-16 | 4 | 23 | 197 | 60 | 1
2015-07-17 | 2015-07-17 | 5 | 0 | 206 | 60.0833 | 1
2015-07-17 00:15 | 2015-07-17 | 5 | 0 | 185 | 60.3958 | 1
2015-07-17 00:30 | 2015-07-17 | 5 | 0 | 186 | 60.7083 | 1
2015-07-17 00:45 | 2015-07-17 | 5 | 0 | 189 | 60.9167 | 1
2015-07-17 01:00 | 2015-07-17 | 5 | 1 | 192 | 59.907 | 1
2015-07-17 01:15 | 2015-07-17 | 5 | 1 | 194 | 59.5581 | 1
2015-07-17 01:30 | 2015-07-17 | 5 | 1 | 187 | 59.2093 | 1
2015-07-17 01:45 | 2015-07-17 | 5 | 1 | 179 | 59 | 1
2015-07-17 02:00 | 2015-07-17 | 5 | 2 | 182 | 59.1379 | 1
2015-07-17 02:15 | 2015-07-17 | 5 | 2 | 190 | 59.6552 | 1
2015-07-17 02:30 | 2015-07-17 | 5 | 2 | 187 | 60.1724 | 1
2015-07-17 02:45 | 2015-07-17 | 5 | 2 | 180 | 60.6897 | 1
2015-07-17 03:00 | 2015-07-17 | 5 | 3 | 178 | 60 | 1
2015-07-17 03:15 | 2015-07-17 | 5 | 3 | 184 | 60 | 1
2015-07-17 03:30 | 2015-07-17 | 5 | 3 | 191 | 60 | 1
2015-07-17 03:45 | 2015-07-17 | 5 | 3 | 187 | 60 | 1
2015-07-17 04:00 | 2015-07-17 | 5 | 4 | 168 | 60 | 1
2015-07-17 04:15 | 2015-07-17 | 5 | 4 | 176 | 60 | 1
2015-07-17 04:30 | 2015-07-17 | 5 | 4 | 178 | 60 | 1
2015-07-17 04:45 | 2015-07-17 | 5 | 4 | 189 | 60 | 1
2015-07-17 05:00 | 2015-07-17 | 5 | 5 | 172 | 60.0667 | 1
2015-07-17 05:15 | 2015-07-17 | 5 | 5 | 176 | 60.3167 | 1
2015-07-17 05:30 | 2015-07-17 | 5 | 5 | 178 | 60.5667 | 1
2015-07-17 05:45 | 2015-07-17 | 5 | 5 | 186 | 60.8167 | 1
2015-07-17 06:00 | 2015-07-17 | 5 | 6 | 174 | 61.0667 | 1
2015-07-17 06:15 | 2015-07-17 | 5 | 6 | 169 | 61.3167 | 1
2015-07-17 06:30 | 2015-07-17 | 5 | 6 | 179 | 61.5667 | 1
2015-07-17 06:45 | 2015-07-17 | 5 | 6 | 181 | 61.8167 | 1
2015-07-17 07:00 | 2015-07-17 | 5 | 7 | 190 | 62.0667 | 1
2015-07-17 07:15 | 2015-07-17 | 5 | 7 | 172 | 62.3167 | 1
2015-07-17 07:30 | 2015-07-17 | 5 | 7 | 174 | 62.5667 | 1
2015-07-17 07:45 | 2015-07-17 | 5 | 7 | 172 | 62.8167 | 1
2015-07-17 08:00 | 2015-07-17 | 5 | 8 | 181 | 63.16 | 1
2015-07-17 08:15 | 2015-07-17 | 5 | 8 | 194 | 63.76 | 1
2015-07-17 08:30 | 2015-07-17 | 5 | 8 | 186 | 64.5143 | 1
2015-07-17 08:45 | 2015-07-17 | 5 | 8 | 196 | 65.3714 | 2
2015-07-17 09:00 | 2015-07-17 | 5 | 9 | 198 | 66.1333 | 2
2015-07-17 09:15 | 2015-07-17 | 5 | 9 | 212 | 66.6333 | 2
2015-07-17 09:30 | 2015-07-17 | 5 | 9 | 200 | 67.1333 | 2
2015-07-17 09:45 | 2015-07-17 | 5 | 9 | 202 | 67.6333 | 2
2015-07-17 10:00 | 2015-07-17 | 5 | 10 | 210 | 68.1333 | 2
2015-07-17 10:15 | 2015-07-17 | 5 | 10 | 222 | 68.6333 | 2
2015-07-17 10:30 | 2015-07-17 | 5 | 10 | 232 | 69.1333 | 2
2015-07-17 10:45 | 2015-07-17 | 5 | 10 | 217 | 69.6333 | 2
2015-07-17 11:00 | 2015-07-17 | 5 | 11 | 221 | 70.2 | 3
2015-07-17 11:15 | 2015-07-17 | 5 | 11 | 220 | 70.95 | 3
2015-07-17 11:30 | 2015-07-17 | 5 | 11 | 231 | 71.7 | 3
2015-07-17 11:45 | 2015-07-17 | 5 | 11 | 241 | 72.45 | 3
2015-07-17 12:00 | 2015-07-17 | 5 | 12 | 236 | 72.8667 | 3
2015-07-17 12:15 | 2015-07-17 | 5 | 12 | 232 | 72.3667 | 3
2015-07-17 12:30 | 2015-07-17 | 5 | 12 | 244 | 71.8667 | 3
2015-07-17 12:45 | 2015-07-17 | 5 | 12 | 253 | 71.3667 | 3
2015-07-17 13:00 | 2015-07-17 | 5 | 13 | 238 | 71.0667 | 3
2015-07-17 13:15 | 2015-07-17 | 5 | 13 | 246 | 71.3167 | 3
2015-07-17 13:30 | 2015-07-17 | 5 | 13 | 258 | 71.5667 | 3
2015-07-17 13:45 | 2015-07-17 | 5 | 13 | 268 | 71.8167 | 3
2015-07-17 14:00 | 2015-07-17 | 5 | 14 | 266 | 72 | 3
2015-07-17 14:15 | 2015-07-17 | 5 | 14 | 258 | 72 | 3
2015-07-17 14:30 | 2015-07-17 | 5 | 14 | 266 | 72 | 3
2015-07-17 14:45 | 2015-07-17 | 5 | 14 | 272 | 72 | 3
2015-07-17 15:00 | 2015-07-17 | 5 | 15 | 268 | 71.8667 | 3
2015-07-17 15:15 | 2015-07-17 | 5 | 15 | 275 | 71.3667 | 3
2015-07-17 15:30 | 2015-07-17 | 5 | 15 | 267 | 70.8667 | 3
2015-07-17 15:45 | 2015-07-17 | 5 | 15 | 261 | 70.3667 | 3
2015-07-17 16:00 | 2015-07-17 | 5 | 16 | 251 | 69.8667 | 2
2015-07-17 16:15 | 2015-07-17 | 5 | 16 | 265 | 69.3667 | 2
2015-07-17 16:30 | 2015-07-17 | 5 | 16 | 267 | 68.8667 | 2
2015-07-17 16:45 | 2015-07-17 | 5 | 16 | 254 | 68.3667 | 2
2015-07-17 17:00 | 2015-07-17 | 5 | 17 | 261 | 67.8 | 2
2015-07-17 17:15 | 2015-07-17 | 5 | 17 | 264 | 67.05 | 2
2015-07-17 17:30 | 2015-07-17 | 5 | 17 | 269 | 66.3 | 2
2015-07-17 17:45 | 2015-07-17 | 5 | 17 | 264 | 65.55 | 2
2015-07-17 18:00 | 2015-07-17 | 5 | 18 | 262 | 64.8667 | 1
2015-07-17 18:15 | 2015-07-17 | 5 | 18 | 257 | 64.3667 | 1
2015-07-17 18:30 | 2015-07-17 | 5 | 18 | 266 | 63.8667 | 1
2015-07-17 18:45 | 2015-07-17 | 5 | 18 | 254 | 63.3667 | 1
2015-07-17 19:00 | 2015-07-17 | 5 | 19 | 249 | 62.8667 | 1
2015-07-17 19:15 | 2015-07-17 | 5 | 19 | 246 | 62.3667 | 1
2015-07-17 19:30 | 2015-07-17 | 5 | 19 | 236 | 61.8667 | 1
2015-07-17 19:45 | 2015-07-17 | 5 | 19 | 247 | 61.3667 | 1
2015-07-17 20:00 | 2015-07-17 | 5 | 20 | 249 | 61 | 1
2015-07-17 20:15 | 2015-07-17 | 5 | 20 | 223 | 61 | 1
2015-07-17 20:30 | 2015-07-17 | 5 | 20 | 234 | 61 | 1
2015-07-17 20:45 | 2015-07-17 | 5 | 20 | 215 | 61 | 1
2015-07-17 21:00 | 2015-07-17 | 5 | 21 | 226 | 61 | 1
2015-07-17 21:15 | 2015-07-17 | 5 | 21 | 201 | 61 | 1
2015-07-17 21:30 | 2015-07-17 | 5 | 21 | 193 | 61 | 1
2015-07-17 21:45 | 2015-07-17 | 5 | 21 | 196 | 61 | 1
2015-07-17 22:00 | 2015-07-17 | 5 | 22 | 191 | 60.9333 | 1
2015-07-17 22:15 | 2015-07-17 | 5 | 22 | 182 | 60.6833 | 1
2015-07-17 22:30 | 2015-07-17 | 5 | 22 | 187 | 60.4333 | 1
2015-07-17 22:45 | 2015-07-17 | 5 | 22 | 192 | 60.1833 | 1
2015-07-17 23:00 | 2015-07-17 | 5 | 23 | 193 | 60 | 1
2015-07-17 23:15 | 2015-07-17 | 5 | 23 | 182 | 60 | 1
2015-07-17 23:30 | 2015-07-17 | 5 | 23 | 178 | 60 | 1
2015-07-17 23:45 | 2015-07-17 | 5 | 23 | 182 | 60 | 1
2015-07-18 | 2015-07-18 | 6 | 0 | 190 | 60 | 1
2015-07-18 00:15 | 2015-07-18 | 6 | 0 | 175 | 60 | 1
2015-07-18 00:30 | 2015-07-18 | 6 | 0 | 178 | 60 | 1
2015-07-18 00:45 | 2015-07-18 | 6 | 0 | 172 | 60 | 1
2015-07-18 01:00 | 2015-07-18 | 6 | 1 | 178 | 60 | 1
2015-07-18 01:15 | 2015-07-18 | 6 | 1 | 181 | 60 | 1
2015-07-18 01:30 | 2015-07-18 | 6 | 1 | 170 | 60 | 1
2015-07-18 01:45 | 2015-07-18 | 6 | 1 | 172 | 60 | 1
2015-07-18 02:00 | 2015-07-18 | 6 | 2 | 164 | 59.9333 | 1
2015-07-18 02:15 | 2015-07-18 | 6 | 2 | 182 | 59.6833 | 1
2015-07-18 02:30 | 2015-07-18 | 6 | 2 | 173 | 59.4333 | 1
2015-07-18 02:45 | 2015-07-18 | 6 | 2 | 167 | 59.1833 | 1
2015-07-18 03:00 | 2015-07-18 | 6 | 3 | 164 | 59 | 1
2015-07-18 03:15 | 2015-07-18 | 6 | 3 | 170 | 59 | 1
2015-07-18 03:30 | 2015-07-18 | 6 | 3 | 185 | 59 | 1
2015-07-18 03:45 | 2015-07-18 | 6 | 3 | 162 | 59 | 1
2015-07-18 04:00 | 2015-07-18 | 6 | 4 | 172 | 59.0667 | 1
2015-07-18 04:15 | 2015-07-18 | 6 | 4 | 165 | 59.3167 | 1
2015-07-18 04:30 | 2015-07-18 | 6 | 4 | 179 | 59.5667 | 1
2015-07-18 04:45 | 2015-07-18 | 6 | 4 | 176 | 59.8167 | 1
2015-07-18 05:00 | 2015-07-18 | 6 | 5 | 162 | 60.069 | 1
2015-07-18 05:15 | 2015-07-18 | 6 | 5 | 164 | 60.3276 | 1
2015-07-18 05:30 | 2015-07-18 | 6 | 5 | 175 | 60.5862 | 1
2015-07-18 05:45 | 2015-07-18 | 6 | 5 | 178 | 60.8448 | 1
2015-07-18 06:00 | 2015-07-18 | 6 | 6 | 158 | 61.0667 | 1
2015-07-18 06:15 | 2015-07-18 | 6 | 6 | 161 | 61.3167 | 1
2015-07-18 06:30 | 2015-07-18 | 6 | 6 | 164 | 61.5667 | 1
2015-07-18 06:45 | 2015-07-18 | 6 | 6 | 177 | 61.8167 | 1
2015-07-18 07:00 | 2015-07-18 | 6 | 7 | 163 | 62.1333 | 1
2015-07-18 07:15 | 2015-07-18 | 6 | 7 | 166 | 62.6333 | 1
2015-07-18 07:30 | 2015-07-18 | 6 | 7 | 158 | 63.1333 | 1
2015-07-18 07:45 | 2015-07-18 | 6 | 7 | 169 | 63.6333 | 1
2015-07-18 08:00 | 2015-07-18 | 6 | 8 | 175 | 64.1333 | 1
2015-07-18 08:15 | 2015-07-18 | 6 | 8 | 167 | 64.6333 | 1
2015-07-18 08:30 | 2015-07-18 | 6 | 8 | 167 | 65.1333 | 2
2015-07-18 08:45 | 2015-07-18 | 6 | 8 | 164 | 65.6333 | 2
2015-07-18 09:00 | 2015-07-18 | 6 | 9 | 174 | 66 | 2
2015-07-18 09:15 | 2015-07-18 | 6 | 9 | 191 | 66 | 2
2015-07-18 09:30 | 2015-07-18 | 6 | 9 | 177 | 66.8919 | 2
2015-07-18 09:45 | 2015-07-18 | 6 | 9 | 182 | 68.1081 | 2
2015-07-18 10:00 | 2015-07-18 | 6 | 10 | 179 | 69.1333 | 2
2015-07-18 10:15 | 2015-07-18 | 6 | 10 | 187 | 69.6333 | 2
2015-07-18 10:30 | 2015-07-18 | 6 | 10 | 187 | 70.1333 | 3
2015-07-18 10:45 | 2015-07-18 | 6 | 10 | 185 | 70.6333 | 3
2015-07-18 11:00 | 2015-07-18 | 6 | 11 | 182 | 71.1333 | 3
2015-07-18 11:15 | 2015-07-18 | 6 | 11 | 186 | 71.6333 | 3
2015-07-18 11:30 | 2015-07-18 | 6 | 11 | 203 | 72.1333 | 3
2015-07-18 11:45 | 2015-07-18 | 6 | 11 | 193 | 72.6333 | 3
2015-07-18 12:00 | 2015-07-18 | 6 | 12 | 193 | 73.1333 | 3
2015-07-18 12:15 | 2015-07-18 | 6 | 12 | 187 | 73.6333 | 3
2015-07-18 12:30 | 2015-07-18 | 6 | 12 | 198 | 74.1333 | 3
2015-07-18 12:45 | 2015-07-18 | 6 | 12 | 203 | 74.6333 | 3
2015-07-18 13:00 | 2015-07-18 | 6 | 13 | 192 | 75 | 3
2015-07-18 13:15 | 2015-07-18 | 6 | 13 | 197 | 75 | 3
2015-07-18 13:30 | 2015-07-18 | 6 | 13 | 197 | 75 | 3
2015-07-18 13:45 | 2015-07-18 | 6 | 13 | 214 | 75 | 3
2015-07-18 14:00 | 2015-07-18 | 6 | 14 | 210 | 75 | 3
2015-07-18 14:15 | 2015-07-18 | 6 | 14 | 205 | 75 | 3
2015-07-18 14:30 | 2015-07-18 | 6 | 14 | 203 | 75 | 3
2015-07-18 14:45 | 2015-07-18 | 6 | 14 | 209 | 75 | 3
2015-07-18 15:00 | 2015-07-18 | 6 | 15 | 226 | 74.9333 | 3
2015-07-18 15:15 | 2015-07-18 | 6 | 15 | 227 | 74.6833 | 3
2015-07-18 15:30 | 2015-07-18 | 6 | 15 | 227 | 74.4333 | 3
2015-07-18 15:45 | 2015-07-18 | 6 | 15 | 220 | 74.1833 | 3
2015-07-18 16:00 | 2015-07-18 | 6 | 16 | 226 | 73.9333 | 3
2015-07-18 16:15 | 2015-07-18 | 6 | 16 | 224 | 73.6833 | 3
2015-07-18 16:30 | 2015-07-18 | 6 | 16 | 236 | 73.4333 | 3
2015-07-18 16:45 | 2015-07-18 | 6 | 16 | 215 | 73.1833 | 3
2015-07-18 17:00 | 2015-07-18 | 6 | 17 | 232 | 72.8 | 3
2015-07-18 17:15 | 2015-07-18 | 6 | 17 | 223 | 72.05 | 3
2015-07-18 17:30 | 2015-07-18 | 6 | 17 | 235 | 71.3 | 3
2015-07-18 17:45 | 2015-07-18 | 6 | 17 | 231 | 70.55 | 3
2015-07-18 18:00 | 2015-07-18 | 6 | 18 | 229 | 69.8667 | 2
2015-07-18 18:15 | 2015-07-18 | 6 | 18 | 214 | 69.3667 | 2
2015-07-18 18:30 | 2015-07-18 | 6 | 18 | 219 | 68.8667 | 2
2015-07-18 18:45 | 2015-07-18 | 6 | 18 | 230 | 68.3667 | 2
2015-07-18 19:00 | 2015-07-18 | 6 | 19 | 228 | 67.9333 | 2
2015-07-18 19:15 | 2015-07-18 | 6 | 19 | 221 | 67.6833 | 2
2015-07-18 19:30 | 2015-07-18 | 6 | 19 | 217 | 67.4333 | 2
2015-07-18 19:45 | 2015-07-18 | 6 | 19 | 208 | 67.1833 | 2
2015-07-18 20:00 | 2015-07-18 | 6 | 20 | 220 | 66.9333 | 2
2015-07-18 20:15 | 2015-07-18 | 6 | 20 | 218 | 66.6833 | 2
2015-07-18 20:30 | 2015-07-18 | 6 | 20 | 204 | 66.4333 | 2
2015-07-18 20:45 | 2015-07-18 | 6 | 20 | 210 | 66.1833 | 2
2015-07-18 21:00 | 2015-07-18 | 6 | 21 | 200 | 66 | 2
2015-07-18 21:15 | 2015-07-18 | 6 | 21 | 198 | 66 | 2
2015-07-18 21:30 | 2015-07-18 | 6 | 21 | 189 | 66 | 2
2015-07-18 21:45 | 2015-07-18 | 6 | 21 | 197 | 66 | 2
2015-07-18 22:00 | 2015-07-18 | 6 | 22 | 192 | 66 | 2
2015-07-18 22:15 | 2015-07-18 | 6 | 22 | 183 | 66 | 2
2015-07-18 22:30 | 2015-07-18 | 6 | 22 | 185 | 66 | 2
2015-07-18 22:45 | 2015-07-18 | 6 | 22 | 179 | 66 | 2
2015-07-18 23:00 | 2015-07-18 | 6 | 23 | 201 | 66 | 2
2015-07-18 23:15 | 2015-07-18 | 6 | 23 | 182 | 66 | 2
2015-07-18 23:30 | 2015-07-18 | 6 | 23 | 179 | 66 | 2
2015-07-18 23:45 | 2015-07-18 | 6 | 23 | 182 | 66 | 2
2015-07-19 | 2015-07-19 | 7 | 0 | 192 | 66 | 2
2015-07-19 00:15 | 2015-07-19 | 7 | 0 | 181 | 66 | 2
2015-07-19 00:30 | 2015-07-19 | 7 | 0 | 175 | 66 | 2
2015-07-19 00:45 | 2015-07-19 | 7 | 0 | 176 | 66 | 2
2015-07-19 01:00 | 2015-07-19 | 7 | 1 | 175 | 65.9333 | 2
2015-07-19 01:15 | 2015-07-19 | 7 | 1 | 186 | 65.6833 | 2
2015-07-19 01:30 | 2015-07-19 | 7 | 1 | 171 | 65.4333 | 2
2015-07-19 01:45 | 2015-07-19 | 7 | 1 | 167 | 65.1833 | 2
2015-07-19 02:00 | 2015-07-19 | 7 | 2 | 174 | 64.9333 | 1
2015-07-19 02:15 | 2015-07-19 | 7 | 2 | 182 | 64.6833 | 1
2015-07-19 02:30 | 2015-07-19 | 7 | 2 | 176 | 64.4333 | 1
2015-07-19 02:45 | 2015-07-19 | 7 | 2 | 172 | 64.1833 | 1
2015-07-19 03:00 | 2015-07-19 | 7 | 3 | 176 | 64 | 1
2015-07-19 03:15 | 2015-07-19 | 7 | 3 | 171 | 64 | 1
2015-07-19 03:30 | 2015-07-19 | 7 | 3 | 180 | 64 | 1
2015-07-19 03:45 | 2015-07-19 | 7 | 3 | 180 | 64 | 1
2015-07-19 04:00 | 2015-07-19 | 7 | 4 | 170 | 63.9333 | 1
2015-07-19 04:15 | 2015-07-19 | 7 | 4 | 162 | 63.6833 | 1
2015-07-19 04:30 | 2015-07-19 | 7 | 4 | 165 | 63.4333 | 1
2015-07-19 04:45 | 2015-07-19 | 7 | 4 | 185 | 63.1833 | 1
2015-07-19 05:00 | 2015-07-19 | 7 | 5 | 174 | 63.1333 | 1
2015-07-19 05:15 | 2015-07-19 | 7 | 5 | 165 | 63.6333 | 1
2015-07-19 05:30 | 2015-07-19 | 7 | 5 | 169 | 64.1333 | 1
2015-07-19 05:45 | 2015-07-19 | 7 | 5 | 173 | 64.6333 | 1
2015-07-19 06:00 | 2015-07-19 | 7 | 6 | 184 | 65.0667 | 2
2015-07-19 06:15 | 2015-07-19 | 7 | 6 | 171 | 65.3167 | 2
2015-07-19 06:30 | 2015-07-19 | 7 | 6 | 171 | 65.5667 | 2
2015-07-19 06:45 | 2015-07-19 | 7 | 6 | 176 | 65.8167 | 2
2015-07-19 07:00 | 2015-07-19 | 7 | 7 | 189 | 66.1333 | 2
2015-07-19 07:15 | 2015-07-19 | 7 | 7 | 181 | 66.6333 | 2
2015-07-19 07:30 | 2015-07-19 | 7 | 7 | 171 | 67.1333 | 2
2015-07-19 07:45 | 2015-07-19 | 7 | 7 | 180 | 67.6333 | 2
2015-07-19 08:00 | 2015-07-19 | 7 | 8 | 174 | 68.1333 | 2
2015-07-19 08:15 | 2015-07-19 | 7 | 8 | 193 | 68.6333 | 2
2015-07-19 08:30 | 2015-07-19 | 7 | 8 | 187 | 69.1333 | 2
2015-07-19 08:45 | 2015-07-19 | 7 | 8 | 182 | 69.6333 | 2
2015-07-19 09:00 | 2015-07-19 | 7 | 9 | 182 | 70.0667 | 3
2015-07-19 09:15 | 2015-07-19 | 7 | 9 | 184 | 70.3167 | 3
2015-07-19 09:30 | 2015-07-19 | 7 | 9 | 193 | 70.5667 | 3
2015-07-19 09:45 | 2015-07-19 | 7 | 9 | 194 | 70.8167 | 3
2015-07-19 10:00 | 2015-07-19 | 7 | 10 | 182 | 71.3333 | 3
2015-07-19 10:15 | 2015-07-19 | 7 | 10 | 191 | 72.5833 | 3
2015-07-19 10:30 | 2015-07-19 | 7 | 10 | 197 | 73.8333 | 3
2015-07-19 10:45 | 2015-07-19 | 7 | 10 | 195 | 75.0833 | 4
2015-07-19 11:00 | 2015-07-19 | 7 | 11 | 206 | 75.7333 | 4
2015-07-19 11:15 | 2015-07-19 | 7 | 11 | 189 | 75.0889 | 4
2015-07-19 11:30 | 2015-07-19 | 7 | 11 | 190 | 75.4222 | 4
2015-07-19 11:45 | 2015-07-19 | 7 | 11 | 189 | 75.7556 | 4
2015-07-19 12:00 | 2015-07-19 | 7 | 12 | 201 | 76.2 | 4
2015-07-19 12:15 | 2015-07-19 | 7 | 12 | 212 | 76.95 | 4
2015-07-19 12:30 | 2015-07-19 | 7 | 12 | 194 | 77.7 | 4
2015-07-19 12:45 | 2015-07-19 | 7 | 12 | 198 | 78.45 | 4
2015-07-19 13:00 | 2015-07-19 | 7 | 13 | 199 | 79.5333 | 4
2015-07-19 13:15 | 2015-07-19 | 7 | 13 | 212 | 81.5333 | 5
2015-07-19 13:30 | 2015-07-19 | 7 | 13 | 217 | 83.5333 | 5
2015-07-19 13:45 | 2015-07-19 | 7 | 13 | 219 | 85.5333 | 6
2015-07-19 14:00 | 2015-07-19 | 7 | 14 | 215 | 87.25 | 6
2015-07-19 14:15 | 2015-07-19 | 7 | 14 | 229 | 87.5909 | 6
2015-07-19 14:30 | 2015-07-19 | 7 | 14 | 245 | 85.5455 | 6
2015-07-19 14:45 | 2015-07-19 | 7 | 14 | 229 | 83.5 | 5
2015-07-19 15:00 | 2015-07-19 | 7 | 15 | 235 | 81.8 | 5
2015-07-19 15:15 | 2015-07-19 | 7 | 15 | 239 | 81.05 | 5
2015-07-19 15:30 | 2015-07-19 | 7 | 15 | 243 | 80.3 | 5
2015-07-19 15:45 | 2015-07-19 | 7 | 15 | 258 | 79.55 | 4
2015-07-19 16:00 | 2015-07-19 | 7 | 16 | 246 | 78.8667 | 4
2015-07-19 16:15 | 2015-07-19 | 7 | 16 | 232 | 78.3667 | 4
2015-07-19 16:30 | 2015-07-19 | 7 | 16 | 242 | 77.8667 | 4
2015-07-19 16:45 | 2015-07-19 | 7 | 16 | 255 | 77.3667 | 4
2015-07-19 17:00 | 2015-07-19 | 7 | 17 | 255 | 76.7333 | 4
2015-07-19 17:15 | 2015-07-19 | 7 | 17 | 238 | 75.7333 | 4
2015-07-19 17:30 | 2015-07-19 | 7 | 17 | 237 | 74.7333 | 3
2015-07-19 17:45 | 2015-07-19 | 7 | 17 | 240 | 73.7333 | 3
2015-07-19 18:00 | 2015-07-19 | 7 | 18 | 240 | 72.8667 | 3
2015-07-19 18:15 | 2015-07-19 | 7 | 18 | 245 | 72.3667 | 3
2015-07-19 18:30 | 2015-07-19 | 7 | 18 | 223 | 71.8667 | 3
2015-07-19 18:45 | 2015-07-19 | 7 | 18 | 228 | 71.3667 | 3
2015-07-19 19:00 | 2015-07-19 | 7 | 19 | 221 | 71 | 3
2015-07-19 19:15 | 2015-07-19 | 7 | 19 | 243 | 71 | 3
2015-07-19 19:30 | 2015-07-19 | 7 | 19 | 216 | 71 | 3
2015-07-19 19:45 | 2015-07-19 | 7 | 19 | 216 | 71 | 3
2015-07-19 20:00 | 2015-07-19 | 7 | 20 | 233 | 71.1333 | 3
2015-07-19 20:15 | 2015-07-19 | 7 | 20 | 211 | 71.6333 | 3
2015-07-19 20:30 | 2015-07-19 | 7 | 20 | 205 | 72.1333 | 3
2015-07-19 20:45 | 2015-07-19 | 7 | 20 | 211 | 72.6333 | 3
2015-07-19 21:00 | 2015-07-19 | 7 | 21 | 206 | 73 | 3
2015-07-19 21:15 | 2015-07-19 | 7 | 21 | 211 | 73 | 3
2015-07-19 21:30 | 2015-07-19 | 7 | 21 | 189 | 73 | 3
2015-07-19 21:45 | 2015-07-19 | 7 | 21 | 190 | 73 | 3
2015-07-19 22:00 | 2015-07-19 | 7 | 22 | 186 | 72.8667 | 3
2015-07-19 22:15 | 2015-07-19 | 7 | 22 | 190 | 72.3667 | 3
2015-07-19 22:30 | 2015-07-19 | 7 | 22 | 192 | 71.8667 | 3
2015-07-19 22:45 | 2015-07-19 | 7 | 22 | 182 | 71.3667 | 3
2015-07-19 23:00 | 2015-07-19 | 7 | 23 | 175 | 70.9333 | 3
2015-07-19 23:15 | 2015-07-19 | 7 | 23 | 186 | 70.6833 | 3
2015-07-19 23:30 | 2015-07-19 | 7 | 23 | 192 | 70.4333 | 3
2015-07-19 23:45 | 2015-07-19 | 7 | 23 | 179 | 70.1833 | 3
2015-07-20 | 2015-07-20 | 1 | 0 | 178 | 69.8667 | 2
2015-07-20 00:15 | 2015-07-20 | 1 | 0 | 175 | 69.3667 | 2
2015-07-20 00:30 | 2015-07-20 | 1 | 0 | 197 | 68.8667 | 2
2015-07-20 00:45 | 2015-07-20 | 1 | 0 | 205 | 68.3667 | 2
2015-07-20 01:00 | 2015-07-20 | 1 | 1 | 188 | 68.0667 | 2
2015-07-20 01:15 | 2015-07-20 | 1 | 1 | 184 | 68.3167 | 2
2015-07-20 01:30 | 2015-07-20 | 1 | 1 | 177 | 68.5667 | 2
2015-07-20 01:45 | 2015-07-20 | 1 | 1 | 196 | 68.8167 | 2
2015-07-20 02:00 | 2015-07-20 | 1 | 2 | 194 | 69.0667 | 2
2015-07-20 02:15 | 2015-07-20 | 1 | 2 | 175 | 69.3167 | 2
2015-07-20 02:30 | 2015-07-20 | 1 | 2 | 184 | 69.5667 | 2
2015-07-20 02:45 | 2015-07-20 | 1 | 2 | 182 | 69.8167 | 2
2015-07-20 03:00 | 2015-07-20 | 1 | 3 | 193 | 69.9333 | 2
2015-07-20 03:15 | 2015-07-20 | 1 | 3 | 186 | 69.6833 | 2
2015-07-20 03:30 | 2015-07-20 | 1 | 3 | 179 | 69.4333 | 2
2015-07-20 03:45 | 2015-07-20 | 1 | 3 | 177 | 69.1833 | 2
2015-07-20 04:00 | 2015-07-20 | 1 | 4 | 191 | 69 | 2
2015-07-20 04:15 | 2015-07-20 | 1 | 4 | 188 | 69 | 2
2015-07-20 04:30 | 2015-07-20 | 1 | 4 | 179 | 69 | 2
2015-07-20 04:45 | 2015-07-20 | 1 | 4 | 176 | 69 | 2
2015-07-20 05:00 | 2015-07-20 | 1 | 5 | 177 | 68.9333 | 2
2015-07-20 05:15 | 2015-07-20 | 1 | 5 | 199 | 68.6833 | 2
2015-07-20 05:30 | 2015-07-20 | 1 | 5 | 182 | 68.4333 | 2
2015-07-20 05:45 | 2015-07-20 | 1 | 5 | 175 | 68.1833 | 2
2015-07-20 06:00 | 2015-07-20 | 1 | 6 | 176 | 68.2 | 2
2015-07-20 06:15 | 2015-07-20 | 1 | 6 | 183 | 68.95 | 2
2015-07-20 06:30 | 2015-07-20 | 1 | 6 | 194 | 69.7 | 2
2015-07-20 06:45 | 2015-07-20 | 1 | 6 | 189 | 70.45 | 3
2015-07-20 07:00 | 2015-07-20 | 1 | 7 | 180 | 71.1333 | 3
2015-07-20 07:15 | 2015-07-20 | 1 | 7 | 185 | 71.6333 | 3
2015-07-20 07:30 | 2015-07-20 | 1 | 7 | 190 | 72.1333 | 3
2015-07-20 07:45 | 2015-07-20 | 1 | 7 | 204 | 72.6333 | 3
2015-07-20 08:00 | 2015-07-20 | 1 | 8 | 195 | 73.1333 | 3
2015-07-20 08:15 | 2015-07-20 | 1 | 8 | 194 | 73.6333 | 3
2015-07-20 08:30 | 2015-07-20 | 1 | 8 | 208 | 74.1333 | 3
2015-07-20 08:45 | 2015-07-20 | 1 | 8 | 219 | 74.6333 | 3
2015-07-20 09:00 | 2015-07-20 | 1 | 9 | 225 | 75.0667 | 4
2015-07-20 09:15 | 2015-07-20 | 1 | 9 | 207 | 75.3167 | 4
2015-07-20 09:30 | 2015-07-20 | 1 | 9 | 212 | 75.5667 | 4
2015-07-20 09:45 | 2015-07-20 | 1 | 9 | 213 | 75.8167 | 4
2015-07-20 10:00 | 2015-07-20 | 1 | 10 | 231 | 75.9333 | 4
2015-07-20 10:15 | 2015-07-20 | 1 | 10 | 232 | 75.6833 | 4
2015-07-20 10:30 | 2015-07-20 | 1 | 10 | 224 | 75.4333 | 4
2015-07-20 10:45 | 2015-07-20 | 1 | 10 | 234 | 75.1833 | 4
2015-07-20 11:00 | 2015-07-20 | 1 | 11 | 248 | 74.8667 | 3
2015-07-20 11:15 | 2015-07-20 | 1 | 11 | 250 | 74.3667 | 3
2015-07-20 11:30 | 2015-07-20 | 1 | 11 | 242 | 73.8667 | 3
2015-07-20 11:45 | 2015-07-20 | 1 | 11 | 250 | 73.3667 | 3
2015-07-20 12:00 | 2015-07-20 | 1 | 12 | 258 | 72.9333 | 3
2015-07-20 12:15 | 2015-07-20 | 1 | 12 | 253 | 72.6833 | 3
2015-07-20 12:30 | 2015-07-20 | 1 | 12 | 273 | 72.4333 | 3
2015-07-20 12:45 | 2015-07-20 | 1 | 12 | 247 | 72.1833 | 3
2015-07-20 13:00 | 2015-07-20 | 1 | 13 | 257 | 72.0667 | 3
2015-07-20 13:15 | 2015-07-20 | 1 | 13 | 245 | 72.3167 | 3
2015-07-20 13:30 | 2015-07-20 | 1 | 13 | 267 | 72.5667 | 3
2015-07-20 13:45 | 2015-07-20 | 1 | 13 | 267 | 72.8167 | 3
2015-07-20 14:00 | 2015-07-20 | 1 | 14 | 249 | 73 | 3
2015-07-20 14:15 | 2015-07-20 | 1 | 14 | 263 | 73 | 3
2015-07-20 14:30 | 2015-07-20 | 1 | 14 | 263 | 73 | 3
2015-07-20 14:45 | 2015-07-20 | 1 | 14 | 264 | 73 | 3
2015-07-20 15:00 | 2015-07-20 | 1 | 15 | 265 | 72.8 | 3
2015-07-20 15:15 | 2015-07-20 | 1 | 15 | 273 | 72.05 | 3
2015-07-20 15:30 | 2015-07-20 | 1 | 15 | 258 | 71.3 | 3
2015-07-20 15:45 | 2015-07-20 | 1 | 15 | 266 | 70.55 | 3
2015-07-20 16:00 | 2015-07-20 | 1 | 16 | 261 | 69.7333 | 2
2015-07-20 16:15 | 2015-07-20 | 1 | 16 | 265 | 68.7333 | 2
2015-07-20 16:30 | 2015-07-20 | 1 | 16 | 280 | 67.7333 | 2
2015-07-20 16:45 | 2015-07-20 | 1 | 16 | 271 | 66.7333 | 2
2015-07-20 17:00 | 2015-07-20 | 1 | 17 | 267 | 66 | 2
2015-07-20 17:15 | 2015-07-20 | 1 | 17 | 280 | 66 | 2
2015-07-20 17:30 | 2015-07-20 | 1 | 17 | 265 | 66 | 2
2015-07-20 17:45 | 2015-07-20 | 1 | 17 | 263 | 66 | 2
2015-07-20 18:00 | 2015-07-20 | 1 | 18 | 257 | 65.8 | 2
2015-07-20 18:15 | 2015-07-20 | 1 | 18 | 256 | 65.05 | 2
2015-07-20 18:30 | 2015-07-20 | 1 | 18 | 261 | 64.3 | 1
2015-07-20 18:45 | 2015-07-20 | 1 | 18 | 266 | 63.55 | 1
2015-07-20 19:00 | 2015-07-20 | 1 | 19 | 240 | 62.9333 | 1
2015-07-20 19:15 | 2015-07-20 | 1 | 19 | 255 | 62.6833 | 1
2015-07-20 19:30 | 2015-07-20 | 1 | 19 | 234 | 62.4333 | 1
2015-07-20 19:45 | 2015-07-20 | 1 | 19 | 236 | 62.1833 | 1
2015-07-20 20:00 | 2015-07-20 | 1 | 20 | 237 | 62 | 1
2015-07-20 20:15 | 2015-07-20 | 1 | 20 | 241 | 62 | 1
2015-07-20 20:30 | 2015-07-20 | 1 | 20 | 228 | 62 | 1
2015-07-20 20:45 | 2015-07-20 | 1 | 20 | 226 | 62 | 1
2015-07-20 21:00 | 2015-07-20 | 1 | 21 | 215 | 62 | 1
2015-07-20 21:15 | 2015-07-20 | 1 | 21 | 212 | 62 | 1
2015-07-20 21:30 | 2015-07-20 | 1 | 21 | 206 | 62 | 1
2015-07-20 21:45 | 2015-07-20 | 1 | 21 | 198 | 62 | 1
2015-07-20 22:00 | 2015-07-20 | 1 | 22 | 201 | 61.8667 | 1
2015-07-20 22:15 | 2015-07-20 | 1 | 22 | 222 | 61.3667 | 1
2015-07-20 22:30 | 2015-07-20 | 1 | 22 | 203 | 60.8667 | 1
2015-07-20 22:45 | 2015-07-20 | 1 | 22 | 199 | 60.3667 | 1
2015-07-20 23:00 | 2015-07-20 | 1 | 23 | 200 | 60.069 | 1
2015-07-20 23:15 | 2015-07-20 | 1 | 23 | 189 | 60.3276 | 1
2015-07-20 23:30 | 2015-07-20 | 1 | 23 | 205 | 60.5862 | 1
2015-07-20 23:45 | 2015-07-20 | 1 | 23 | 187 | 60.8448 | 1
2015-07-21 | 2015-07-21 | 2 | 0 | 187 | 60 | 1
2015-07-21 00:15 | 2015-07-21 | 2 | 0 | 177 | 60 | 1
2015-07-21 00:30 | 2015-07-21 | 2 | 0 | 181 | 60 | 1
2015-07-21 00:45 | 2015-07-21 | 2 | 0 | 191 | 60 | 1
2015-07-21 01:00 | 2015-07-21 | 2 | 1 | 173 | 60.2222 | 1
2015-07-21 01:15 | 2015-07-21 | 2 | 1 | 180 | 60.9762 | 1
2015-07-21 01:30 | 2015-07-21 | 2 | 1 | 178 | 60.619 | 1
2015-07-21 01:45 | 2015-07-21 | 2 | 1 | 175 | 60.2619 | 1
2015-07-21 02:00 | 2015-07-21 | 2 | 2 | 190 | 60 | 1
2015-07-21 02:15 | 2015-07-21 | 2 | 2 | 170 | 60 | 1
2015-07-21 02:30 | 2015-07-21 | 2 | 2 | 166 | 60 | 1
2015-07-21 02:45 | 2015-07-21 | 2 | 2 | 169 | 60 | 1
2015-07-21 03:00 | 2015-07-21 | 2 | 3 | 179 | 60 | 1
2015-07-21 03:15 | 2015-07-21 | 2 | 3 | 176 | 60 | 1
2015-07-21 03:30 | 2015-07-21 | 2 | 3 | 164 | 60 | 1
2015-07-21 03:45 | 2015-07-21 | 2 | 3 | 173 | 60 | 1
2015-07-21 04:00 | 2015-07-21 | 2 | 4 | 165 | 60 | 1
2015-07-21 04:15 | 2015-07-21 | 2 | 4 | 181 | 60 | 1
2015-07-21 04:30 | 2015-07-21 | 2 | 4 | 174 | 60 | 1
2015-07-21 04:45 | 2015-07-21 | 2 | 4 | 163 | 60 | 1
2015-07-21 05:00 | 2015-07-21 | 2 | 5 | 166 | 60.1081 | 1
2015-07-21 05:15 | 2015-07-21 | 2 | 5 | 165 | 60.5135 | 1
2015-07-21 05:30 | 2015-07-21 | 2 | 5 | 184 | 60.9189 | 1
2015-07-21 05:45 | 2015-07-21 | 2 | 5 | 164 | 60.4783 | 1
2015-07-21 06:00 | 2015-07-21 | 2 | 6 | 166 | 60.0667 | 1
2015-07-21 06:15 | 2015-07-21 | 2 | 6 | 161 | 60.3167 | 1
2015-07-21 06:30 | 2015-07-21 | 2 | 6 | 178 | 60.5667 | 1
2015-07-21 06:45 | 2015-07-21 | 2 | 6 | 180 | 60.8167 | 1
2015-07-21 07:00 | 2015-07-21 | 2 | 7 | 167 | 61.1905 | 1
2015-07-21 07:15 | 2015-07-21 | 2 | 7 | 169 | 61.9048 | 1
2015-07-21 07:30 | 2015-07-21 | 2 | 7 | 169 | 62.619 | 1
2015-07-21 07:45 | 2015-07-21 | 2 | 7 | 185 | 63.3889 | 1
2015-07-21 08:00 | 2015-07-21 | 2 | 8 | 172 | 64.0667 | 1
2015-07-21 08:15 | 2015-07-21 | 2 | 8 | 175 | 64.3167 | 1
2015-07-21 08:30 | 2015-07-21 | 2 | 8 | 187 | 64.5667 | 1
2015-07-21 08:45 | 2015-07-21 | 2 | 8 | 200 | 64.8167 | 1
2015-07-21 09:00 | 2015-07-21 | 2 | 9 | 202 | 65.0667 | 2
2015-07-21 09:15 | 2015-07-21 | 2 | 9 | 192 | 65.3167 | 2
2015-07-21 09:30 | 2015-07-21 | 2 | 9 | 192 | 65.5667 | 2
2015-07-21 09:45 | 2015-07-21 | 2 | 9 | 192 | 65.8167 | 2
2015-07-21 10:00 | 2015-07-21 | 2 | 10 | 209 | 66.1333 | 2
2015-07-21 10:15 | 2015-07-21 | 2 | 10 | 204 | 66.6333 | 2
2015-07-21 10:30 | 2015-07-21 | 2 | 10 | 203 | 67.1333 | 2
2015-07-21 10:45 | 2015-07-21 | 2 | 10 | 206 | 67.6333 | 2
2015-07-21 11:00 | 2015-07-21 | 2 | 11 | 208 | 68.0667 | 2
2015-07-21 11:15 | 2015-07-21 | 2 | 11 | 213 | 68.3167 | 2
2015-07-21 11:30 | 2015-07-21 | 2 | 11 | 233 | 68.5667 | 2
2015-07-21 11:45 | 2015-07-21 | 2 | 11 | 214 | 68.8167 | 2
2015-07-21 12:00 | 2015-07-21 | 2 | 12 | 231 | 69.0667 | 2
2015-07-21 12:15 | 2015-07-21 | 2 | 12 | 208 | 69.3167 | 2
2015-07-21 12:30 | 2015-07-21 | 2 | 12 | 236 | 69.5667 | 2
2015-07-21 12:45 | 2015-07-21 | 2 | 12 | 226 | 69.8167 | 2
2015-07-21 13:00 | 2015-07-21 | 2 | 13 | 230 | 69.9333 | 2
2015-07-21 13:15 | 2015-07-21 | 2 | 13 | 219 | 69.6833 | 2
2015-07-21 13:30 | 2015-07-21 | 2 | 13 | 227 | 69.4333 | 2
2015-07-21 13:45 | 2015-07-21 | 2 | 13 | 223 | 69.1833 | 2
2015-07-21 14:00 | 2015-07-21 | 2 | 14 | 243 | 68.8667 | 2
2015-07-21 14:15 | 2015-07-21 | 2 | 14 | 234 | 68.3667 | 2
2015-07-21 14:30 | 2015-07-21 | 2 | 14 | 223 | 67.8667 | 2
2015-07-21 14:45 | 2015-07-21 | 2 | 14 | 235 | 67.3667 | 2
2015-07-21 15:00 | 2015-07-21 | 2 | 15 | 240 | 66.7333 | 2
2015-07-21 15:15 | 2015-07-21 | 2 | 15 | 243 | 65.7333 | 2
2015-07-21 15:30 | 2015-07-21 | 2 | 15 | 238 | 64.7333 | 1
2015-07-21 15:45 | 2015-07-21 | 2 | 15 | 247 | 64.2667 | 1
2015-07-21 16:00 | 2015-07-21 | 2 | 16 | 230 | 64.9333 | 1
2015-07-21 16:15 | 2015-07-21 | 2 | 16 | 234 | 64.6833 | 1
2015-07-21 16:30 | 2015-07-21 | 2 | 16 | 229 | 64.4333 | 1
2015-07-21 16:45 | 2015-07-21 | 2 | 16 | 251 | 64.1833 | 1
2015-07-21 17:00 | 2015-07-21 | 2 | 17 | 230 | 63.9333 | 1
2015-07-21 17:15 | 2015-07-21 | 2 | 17 | 238 | 63.6833 | 1
2015-07-21 17:30 | 2015-07-21 | 2 | 17 | 228 | 63.4333 | 1
2015-07-21 17:45 | 2015-07-21 | 2 | 17 | 234 | 63.1833 | 1
2015-07-21 18:00 | 2015-07-21 | 2 | 18 | 242 | 62.9333 | 1
2015-07-21 18:15 | 2015-07-21 | 2 | 18 | 232 | 62.6833 | 1
2015-07-21 18:30 | 2015-07-21 | 2 | 18 | 237 | 62.4333 | 1
2015-07-21 18:45 | 2015-07-21 | 2 | 18 | 235 | 62.1833 | 1
2015-07-21 19:00 | 2015-07-21 | 2 | 19 | 232 | 62.1379 | 1
2015-07-21 19:15 | 2015-07-21 | 2 | 19 | 232 | 62.6552 | 1
2015-07-21 19:30 | 2015-07-21 | 2 | 19 | 231 | 62.6774 | 1
2015-07-21 19:45 | 2015-07-21 | 2 | 19 | 212 | 61.7097 | 1
2015-07-21 20:00 | 2015-07-21 | 2 | 20 | 212 | 61 | 1
2015-07-21 20:15 | 2015-07-21 | 2 | 20 | 206 | 61 | 1
2015-07-21 20:30 | 2015-07-21 | 2 | 20 | 214 | 61 | 1
2015-07-21 20:45 | 2015-07-21 | 2 | 20 | 209 | 61 | 1
2015-07-21 21:00 | 2015-07-21 | 2 | 21 | 201 | 61.0667 | 1
2015-07-21 21:15 | 2015-07-21 | 2 | 21 | 192 | 61.3167 | 1
2015-07-21 21:30 | 2015-07-21 | 2 | 21 | 202 | 61.5667 | 1
2015-07-21 21:45 | 2015-07-21 | 2 | 21 | 190 | 61.8167 | 1
2015-07-21 22:00 | 2015-07-21 | 2 | 22 | 187 | 61.931 | 1
2015-07-21 22:15 | 2015-07-21 | 2 | 22 | 184 | 61.6724 | 1
2015-07-21 22:30 | 2015-07-21 | 2 | 22 | 188 | 61.4138 | 1
2015-07-21 22:45 | 2015-07-21 | 2 | 22 | 202 | 61.1552 | 1
2015-07-21 23:00 | 2015-07-21 | 2 | 23 | 194 | 61.0667 | 1
2015-07-21 23:15 | 2015-07-21 | 2 | 23 | 185 | 61.3167 | 1
2015-07-21 23:30 | 2015-07-21 | 2 | 23 | 174 | 61.5667 | 1
2015-07-21 23:45 | 2015-07-21 | 2 | 23 | 184 | 61.8167 | 1
2015-07-22 | 2015-07-22 | 3 | 0 | 199 | 61.9333 | 1
2015-07-22 00:15 | 2015-07-22 | 3 | 0 | 176 | 61.6833 | 1
2015-07-22 00:30 | 2015-07-22 | 3 | 0 | 181 | 61.4333 | 1
2015-07-22 00:45 | 2015-07-22 | 3 | 0 | 185 | 61.1833 | 1
2015-07-22 01:00 | 2015-07-22 | 3 | 1 | 172 | 61 | 1
2015-07-22 01:15 | 2015-07-22 | 3 | 1 | 173 | 61 | 1
2015-07-22 01:30 | 2015-07-22 | 3 | 1 | 176 | 61 | 1
2015-07-22 01:45 | 2015-07-22 | 3 | 1 | 189 | 61 | 1
2015-07-22 02:00 | 2015-07-22 | 3 | 2 | 172 | 61 | 1
2015-07-22 02:15 | 2015-07-22 | 3 | 2 | 172 | 61 | 1
2015-07-22 02:30 | 2015-07-22 | 3 | 2 | 169 | 61 | 1
2015-07-22 02:45 | 2015-07-22 | 3 | 2 | 172 | 61 | 1
2015-07-22 03:00 | 2015-07-22 | 3 | 3 | 179 | 60.9333 | 1
2015-07-22 03:15 | 2015-07-22 | 3 | 3 | 169 | 60.6833 | 1
2015-07-22 03:30 | 2015-07-22 | 3 | 3 | 169 | 60.4333 | 1
2015-07-22 03:45 | 2015-07-22 | 3 | 3 | 161 | 60.1833 | 1
2015-07-22 04:00 | 2015-07-22 | 3 | 4 | 176 | 60 | 1
2015-07-22 04:15 | 2015-07-22 | 3 | 4 | 175 | 60 | 1
2015-07-22 04:30 | 2015-07-22 | 3 | 4 | 167 | 60 | 1
2015-07-22 04:45 | 2015-07-22 | 3 | 4 | 163 | 60 | 1
2015-07-22 05:00 | 2015-07-22 | 3 | 5 | 161 | 60.0667 | 1
2015-07-22 05:15 | 2015-07-22 | 3 | 5 | 177 | 60.3167 | 1
2015-07-22 05:30 | 2015-07-22 | 3 | 5 | 176 | 60.5667 | 1
2015-07-22 05:45 | 2015-07-22 | 3 | 5 | 157 | 60.8167 | 1
2015-07-22 06:00 | 2015-07-22 | 3 | 6 | 165 | 61.0667 | 1
2015-07-22 06:15 | 2015-07-22 | 3 | 6 | 166 | 61.3167 | 1
2015-07-22 06:30 | 2015-07-22 | 3 | 6 | 177 | 61.5667 | 1
2015-07-22 06:45 | 2015-07-22 | 3 | 6 | 165 | 61.8167 | 1
2015-07-22 07:00 | 2015-07-22 | 3 | 7 | 168 | 62.1333 | 1
2015-07-22 07:15 | 2015-07-22 | 3 | 7 | 169 | 62.6333 | 1
2015-07-22 07:30 | 2015-07-22 | 3 | 7 | 175 | 63.1333 | 1
2015-07-22 07:45 | 2015-07-22 | 3 | 7 | 182 | 63.6333 | 1
2015-07-22 08:00 | 2015-07-22 | 3 | 8 | 172 | 64.0667 | 1
2015-07-22 08:15 | 2015-07-22 | 3 | 8 | 179 | 64.3167 | 1
2015-07-22 08:30 | 2015-07-22 | 3 | 8 | 182 | 64.5667 | 1
2015-07-22 08:45 | 2015-07-22 | 3 | 8 | 196 | 64.8167 | 1
2015-07-22 09:00 | 2015-07-22 | 3 | 9 | 195 | 64.8621 | 1
2015-07-22 09:15 | 2015-07-22 | 3 | 9 | 198 | 64.3448 | 1
2015-07-22 09:30 | 2015-07-22 | 3 | 9 | 194 | 64.1613 | 1
2015-07-22 09:45 | 2015-07-22 | 3 | 9 | 196 | 64.6452 | 1
2015-07-22 10:00 | 2015-07-22 | 3 | 10 | 219 | 64.9333 | 1
2015-07-22 10:15 | 2015-07-22 | 3 | 10 | 197 | 64.6833 | 1
2015-07-22 10:30 | 2015-07-22 | 3 | 10 | 206 | 64.4333 | 1
2015-07-22 10:45 | 2015-07-22 | 3 | 10 | 199 | 64.1833 | 1
2015-07-22 11:00 | 2015-07-22 | 3 | 11 | 227 | 64 | 1
2015-07-22 11:15 | 2015-07-22 | 3 | 11 | 218 | 64 | 1
2015-07-22 11:30 | 2015-07-22 | 3 | 11 | 212 | 64.1613 | 1
2015-07-22 11:45 | 2015-07-22 | 3 | 11 | 222 | 64.6452 | 1
2015-07-22 12:00 | 2015-07-22 | 3 | 12 | 217 | 65.1333 | 2
2015-07-22 12:15 | 2015-07-22 | 3 | 12 | 228 | 65.6333 | 2
2015-07-22 12:30 | 2015-07-22 | 3 | 12 | 236 | 66.1333 | 2
2015-07-22 12:45 | 2015-07-22 | 3 | 12 | 216 | 66.6333 | 2
2015-07-22 13:00 | 2015-07-22 | 3 | 13 | 217 | 66.8667 | 2
2015-07-22 13:15 | 2015-07-22 | 3 | 13 | 226 | 66.3667 | 2
2015-07-22 13:30 | 2015-07-22 | 3 | 13 | 233 | 65.8667 | 2
2015-07-22 13:45 | 2015-07-22 | 3 | 13 | 236 | 65.3667 | 2
2015-07-22 14:00 | 2015-07-22 | 3 | 14 | 221 | 65.0667 | 2
2015-07-22 14:15 | 2015-07-22 | 3 | 14 | 228 | 65.3167 | 2
2015-07-22 14:30 | 2015-07-22 | 3 | 14 | 224 | 65.5667 | 2
2015-07-22 14:45 | 2015-07-22 | 3 | 14 | 238 | 65.8167 | 2
2015-07-22 15:00 | 2015-07-22 | 3 | 15 | 223 | 65.9333 | 2
2015-07-22 15:15 | 2015-07-22 | 3 | 15 | 225 | 65.6833 | 2
2015-07-22 15:30 | 2015-07-22 | 3 | 15 | 232 | 65.4333 | 2
2015-07-22 15:45 | 2015-07-22 | 3 | 15 | 227 | 65.1833 | 2
2015-07-22 16:00 | 2015-07-22 | 3 | 16 | 237 | 64.8667 | 1
2015-07-22 16:15 | 2015-07-22 | 3 | 16 | 225 | 64.3667 | 1
2015-07-22 16:30 | 2015-07-22 | 3 | 16 | 223 | 63.8667 | 1
2015-07-22 16:45 | 2015-07-22 | 3 | 16 | 232 | 63.3667 | 1
2015-07-22 17:00 | 2015-07-22 | 3 | 17 | 222 | 63 | 1
2015-07-22 17:15 | 2015-07-22 | 3 | 17 | 248 | 63 | 1
2015-07-22 17:30 | 2015-07-22 | 3 | 17 | 239 | 63 | 1
2015-07-22 17:45 | 2015-07-22 | 3 | 17 | 225 | 63 | 1
2015-07-22 18:00 | 2015-07-22 | 3 | 18 | 237 | 62.9333 | 1
2015-07-22 18:15 | 2015-07-22 | 3 | 18 | 218 | 62.6833 | 1
2015-07-22 18:30 | 2015-07-22 | 3 | 18 | 234 | 62.4333 | 1
2015-07-22 18:45 | 2015-07-22 | 3 | 18 | 237 | 62.1833 | 1
2015-07-22 19:00 | 2015-07-22 | 3 | 19 | 214 | 62 | 1
2015-07-22 19:15 | 2015-07-22 | 3 | 19 | 215 | 62 | 1
2015-07-22 19:30 | 2015-07-22 | 3 | 19 | 207 | 62 | 1
2015-07-22 19:45 | 2015-07-22 | 3 | 19 | 223 | 62 | 1
2015-07-22 20:00 | 2015-07-22 | 3 | 20 | 211 | 61.9333 | 1
2015-07-22 20:15 | 2015-07-22 | 3 | 20 | 206 | 61.6833 | 1
2015-07-22 20:30 | 2015-07-22 | 3 | 20 | 205 | 61.4333 | 1
2015-07-22 20:45 | 2015-07-22 | 3 | 20 | 209 | 61.1833 | 1
2015-07-22 21:00 | 2015-07-22 | 3 | 21 | 205 | 61.0667 | 1
2015-07-22 21:15 | 2015-07-22 | 3 | 21 | 189 | 61.3167 | 1
2015-07-22 21:30 | 2015-07-22 | 3 | 21 | 199 | 61.5667 | 1
2015-07-22 21:45 | 2015-07-22 | 3 | 21 | 184 | 61.8167 | 1
2015-07-22 22:00 | 2015-07-22 | 3 | 22 | 181 | 61.9333 | 1
2015-07-22 22:15 | 2015-07-22 | 3 | 22 | 184 | 61.6833 | 1
2015-07-22 22:30 | 2015-07-22 | 3 | 22 | 201 | 61.4333 | 1
2015-07-22 22:45 | 2015-07-22 | 3 | 22 | 176 | 61.1833 | 1
2015-07-22 23:00 | 2015-07-22 | 3 | 23 | 185 | 61 | 1
2015-07-22 23:15 | 2015-07-22 | 3 | 23 | 176 | 61 | 1
2015-07-22 23:30 | 2015-07-22 | 3 | 23 | 188 | 61 | 1
2015-07-22 23:45 | 2015-07-22 | 3 | 23 | 182 | 61 | 1
2015-07-23 | 2015-07-23 | 4 | 0 | 160 | 61 | 1
2015-07-23 00:15 | 2015-07-23 | 4 | 0 | 167 | 61 | 1
2015-07-23 00:30 | 2015-07-23 | 4 | 0 | 172 | 61 | 1
2015-07-23 00:45 | 2015-07-23 | 4 | 0 | 177 | 61 | 1
2015-07-23 01:00 | 2015-07-23 | 4 | 1 | 161 | 61 | 1
2015-07-23 01:15 | 2015-07-23 | 4 | 1 | 167 | 61 | 1
2015-07-23 01:30 | 2015-07-23 | 4 | 1 | 164 | 61 | 1
2015-07-23 01:45 | 2015-07-23 | 4 | 1 | 168 | 61 | 1
2015-07-23 02:00 | 2015-07-23 | 4 | 2 | 163 | 60.9333 | 1
2015-07-23 02:15 | 2015-07-23 | 4 | 2 | 159 | 60.6833 | 1
2015-07-23 02:30 | 2015-07-23 | 4 | 2 | 155 | 60.4333 | 1
2015-07-23 02:45 | 2015-07-23 | 4 | 2 | 157 | 60.1833 | 1
2015-07-23 03:00 | 2015-07-23 | 4 | 3 | 159 | 60 | 1
2015-07-23 03:15 | 2015-07-23 | 4 | 3 | 171 | 60 | 1
2015-07-23 03:30 | 2015-07-23 | 4 | 3 | 148 | 60 | 1
2015-07-23 03:45 | 2015-07-23 | 4 | 3 | 148 | 60 | 1
2015-07-23 04:00 | 2015-07-23 | 4 | 4 | 145 | 60 | 1
2015-07-23 04:15 | 2015-07-23 | 4 | 4 | 148 | 60 | 1
2015-07-23 04:30 | 2015-07-23 | 4 | 4 | 161 | 60 | 1
2015-07-23 04:45 | 2015-07-23 | 4 | 4 | 149 | 60 | 1
2015-07-23 05:00 | 2015-07-23 | 4 | 5 | 149 | 60 | 1
2015-07-23 05:15 | 2015-07-23 | 4 | 5 | 142 | 60 | 1
2015-07-23 05:30 | 2015-07-23 | 4 | 5 | 149 | 60 | 1
2015-07-23 05:45 | 2015-07-23 | 4 | 5 | 162 | 60 | 1
2015-07-23 06:00 | 2015-07-23 | 4 | 6 | 152 | 60 | 1
2015-07-23 06:15 | 2015-07-23 | 4 | 6 | 130 | 60 | 1
2015-07-23 06:30 | 2015-07-23 | 4 | 6 | 97 | 60 | 1
2015-07-23 06:45 | 2015-07-23 | 4 | 6 | 95 | 60 | 1
2015-07-23 07:00 | 2015-07-23 | 4 | 7 | 135 | 60.0667 | 1
2015-07-23 07:15 | 2015-07-23 | 4 | 7 | 152 | 60.3167 | 1
2015-07-23 07:30 | 2015-07-23 | 4 | 7 | 147 | 60.5667 | 1
2015-07-23 07:45 | 2015-07-23 | 4 | 7 | 165 | 60.8167 | 1
2015-07-23 08:00 | 2015-07-23 | 4 | 8 | 156 | 61.0667 | 1
2015-07-23 08:15 | 2015-07-23 | 4 | 8 | 167 | 61.3167 | 1
2015-07-23 08:30 | 2015-07-23 | 4 | 8 | 166 | 61.5667 | 1
2015-07-23 08:45 | 2015-07-23 | 4 | 8 | 168 | 61.8167 | 1
2015-07-23 09:00 | 2015-07-23 | 4 | 9 | 180 | 62 | 1
2015-07-23 09:15 | 2015-07-23 | 4 | 9 | 177 | 62 | 1
2015-07-23 09:30 | 2015-07-23 | 4 | 9 | 178 | 62 | 1
2015-07-23 09:45 | 2015-07-23 | 4 | 9 | 180 | 62 | 1
2015-07-23 10:00 | 2015-07-23 | 4 | 10 | 178 | 62.1333 | 1
2015-07-23 10:15 | 2015-07-23 | 4 | 10 | 182 | 62.6333 | 1
2015-07-23 10:30 | 2015-07-23 | 4 | 10 | 185 | 63.1333 | 1
2015-07-23 10:45 | 2015-07-23 | 4 | 10 | 182 | 63.6333 | 1
2015-07-23 11:00 | 2015-07-23 | 4 | 11 | 181 | 63.9333 | 1
2015-07-23 11:15 | 2015-07-23 | 4 | 11 | 208 | 63.6833 | 1
2015-07-23 11:30 | 2015-07-23 | 4 | 11 | 189 | 63.4333 | 1
2015-07-23 11:45 | 2015-07-23 | 4 | 11 | 188 | 63.1833 | 1
2015-07-23 12:00 | 2015-07-23 | 4 | 12 | 197 | 63.2667 | 1
2015-07-23 12:15 | 2015-07-23 | 4 | 12 | 195 | 64.2667 | 1
2015-07-23 12:30 | 2015-07-23 | 4 | 12 | 206 | 65.2667 | 2
2015-07-23 12:45 | 2015-07-23 | 4 | 12 | 212 | 66.2667 | 2
2015-07-23 13:00 | 2015-07-23 | 4 | 13 | 195 | 66.9333 | 2
2015-07-23 13:15 | 2015-07-23 | 4 | 13 | 210 | 66.6833 | 2
2015-07-23 13:30 | 2015-07-23 | 4 | 13 | 196 | 66.4333 | 2
2015-07-23 13:45 | 2015-07-23 | 4 | 13 | 199 | 66.1833 | 2
2015-07-23 14:00 | 2015-07-23 | 4 | 14 | 197 | 66 | 2
2015-07-23 14:15 | 2015-07-23 | 4 | 14 | 212 | 66 | 2
2015-07-23 14:30 | 2015-07-23 | 4 | 14 | 206 | 66 | 2
2015-07-23 14:45 | 2015-07-23 | 4 | 14 | 202 | 66 | 2
2015-07-23 15:00 | 2015-07-23 | 4 | 15 | 205 | 66 | 2
2015-07-23 15:15 | 2015-07-23 | 4 | 15 | 202 | 66 | 2
2015-07-23 15:30 | 2015-07-23 | 4 | 15 | 206 | 66 | 2
2015-07-23 15:45 | 2015-07-23 | 4 | 15 | 203 | 66 | 2
2015-07-23 16:00 | 2015-07-23 | 4 | 16 | 217 | 66 | 2
2015-07-23 16:15 | 2015-07-23 | 4 | 16 | 215 | 66 | 2
2015-07-23 16:30 | 2015-07-23 | 4 | 16 | 224 | 66 | 2
2015-07-23 16:45 | 2015-07-23 | 4 | 16 | 217 | 66 | 2
2015-07-23 17:00 | 2015-07-23 | 4 | 17 | 211 | 65.8667 | 2
2015-07-23 17:15 | 2015-07-23 | 4 | 17 | 226 | 65.3667 | 2
2015-07-23 17:30 | 2015-07-23 | 4 | 17 | 212 | 64.8667 | 1
2015-07-23 17:45 | 2015-07-23 | 4 | 17 | 224 | 64.3667 | 1
2015-07-23 18:00 | 2015-07-23 | 4 | 18 | 211 | 63.8667 | 1
2015-07-23 18:15 | 2015-07-23 | 4 | 18 | 213 | 63.3667 | 1
2015-07-23 18:30 | 2015-07-23 | 4 | 18 | 220 | 62.8667 | 1
2015-07-23 18:45 | 2015-07-23 | 4 | 18 | 229 | 62.3667 | 1
2015-07-23 19:00 | 2015-07-23 | 4 | 19 | 212 | 61.9333 | 1
2015-07-23 19:15 | 2015-07-23 | 4 | 19 | 212 | 61.6833 | 1
2015-07-23 19:30 | 2015-07-23 | 4 | 19 | 211 | 61.4333 | 1
2015-07-23 19:45 | 2015-07-23 | 4 | 19 | 212 | 61.1833 | 1
2015-07-23 20:00 | 2015-07-23 | 4 | 20 | 201 | 61 | 1
2015-07-23 20:15 | 2015-07-23 | 4 | 20 | 212 | 61 | 1
2015-07-23 20:30 | 2015-07-23 | 4 | 20 | 196 | 61 | 1
2015-07-23 20:45 | 2015-07-23 | 4 | 20 | 191 | 61 | 1
2015-07-23 21:00 | 2015-07-23 | 4 | 21 | 199 | 61 | 1
2015-07-23 21:15 | 2015-07-23 | 4 | 21 | 179 | 61 | 1
2015-07-23 21:30 | 2015-07-23 | 4 | 21 | 189 | 61 | 1
2015-07-23 21:45 | 2015-07-23 | 4 | 21 | 183 | 61 | 1
2015-07-23 22:00 | 2015-07-23 | 4 | 22 | 167 | 60.9333 | 1
2015-07-23 22:15 | 2015-07-23 | 4 | 22 | 176 | 60.6833 | 1
2015-07-23 22:30 | 2015-07-23 | 4 | 22 | 169 | 60.4333 | 1
2015-07-23 22:45 | 2015-07-23 | 4 | 22 | 190 | 60.1833 | 1
2015-07-23 23:00 | 2015-07-23 | 4 | 23 | 170 | 60.0667 | 1
2015-07-23 23:15 | 2015-07-23 | 4 | 23 | 170 | 60.3167 | 1
2015-07-23 23:30 | 2015-07-23 | 4 | 23 | 161 | 60.5667 | 1
2015-07-23 23:45 | 2015-07-23 | 4 | 23 | 169 | 60.8167 | 1
2015-07-24 | 2015-07-24 | 5 | 0 | 175 | 61 | 1
2015-07-24 00:15 | 2015-07-24 | 5 | 0 | 163 | 61 | 1
2015-07-24 00:30 | 2015-07-24 | 5 | 0 | 165 | 61 | 1
2015-07-24 00:45 | 2015-07-24 | 5 | 0 | 151 | 61 | 1
2015-07-24 01:00 | 2015-07-24 | 5 | 1 | 169 | 61 | 1
2015-07-24 01:15 | 2015-07-24 | 5 | 1 | 169 | 61 | 1
2015-07-24 01:30 | 2015-07-24 | 5 | 1 | 157 | 61 | 1
2015-07-24 01:45 | 2015-07-24 | 5 | 1 | 166 | 61 | 1
2015-07-24 02:00 | 2015-07-24 | 5 | 2 | 152 | 60.9333 | 1
2015-07-24 02:15 | 2015-07-24 | 5 | 2 | 170 | 60.6833 | 1
2015-07-24 02:30 | 2015-07-24 | 5 | 2 | 153 | 60.4333 | 1
2015-07-24 02:45 | 2015-07-24 | 5 | 2 | 155 | 60.1833 | 1
2015-07-24 03:00 | 2015-07-24 | 5 | 3 | 143 | 59.8919 | 1
2015-07-24 03:15 | 2015-07-24 | 5 | 3 | 145 | 59.4865 | 1
2015-07-24 03:30 | 2015-07-24 | 5 | 3 | 154 | 59.0811 | 1
2015-07-24 03:45 | 2015-07-24 | 5 | 3 | 158 | 59 | 1
2015-07-24 04:00 | 2015-07-24 | 5 | 4 | 148 | 58.9333 | 1
2015-07-24 04:15 | 2015-07-24 | 5 | 4 | 151 | 58.6833 | 1
2015-07-24 04:30 | 2015-07-24 | 5 | 4 | 152 | 58.4333 | 1
2015-07-24 04:45 | 2015-07-24 | 5 | 4 | 159 | 58.1833 | 1
2015-07-24 05:00 | 2015-07-24 | 5 | 5 | 148 | 58.1333 | 1
2015-07-24 05:15 | 2015-07-24 | 5 | 5 | 146 | 58.6333 | 1
2015-07-24 05:30 | 2015-07-24 | 5 | 5 | 143 | 59.1333 | 1
2015-07-24 05:45 | 2015-07-24 | 5 | 5 | 144 | 59.6333 | 1
2015-07-24 06:00 | 2015-07-24 | 5 | 6 | 151 | 60.1333 | 1
2015-07-24 06:15 | 2015-07-24 | 5 | 6 | 151 | 60.6333 | 1
2015-07-24 06:30 | 2015-07-24 | 5 | 6 | 150 | 61.1333 | 1
2015-07-24 06:45 | 2015-07-24 | 5 | 6 | 145 | 61.6333 | 1
2015-07-24 07:00 | 2015-07-24 | 5 | 7 | 164 | 62.0667 | 1
2015-07-24 07:15 | 2015-07-24 | 5 | 7 | 154 | 62.3167 | 1
2015-07-24 07:30 | 2015-07-24 | 5 | 7 | 153 | 62.5667 | 1
2015-07-24 07:45 | 2015-07-24 | 5 | 7 | 151 | 62.8167 | 1
2015-07-24 08:00 | 2015-07-24 | 5 | 8 | 154 | 63.2 | 1
2015-07-24 08:15 | 2015-07-24 | 5 | 8 | 165 | 63.95 | 1
2015-07-24 08:30 | 2015-07-24 | 5 | 8 | 171 | 64.7 | 1
2015-07-24 08:45 | 2015-07-24 | 5 | 8 | 188 | 65.45 | 2
2015-07-24 09:00 | 2015-07-24 | 5 | 9 | 174 | 66.1333 | 2
2015-07-24 09:15 | 2015-07-24 | 5 | 9 | 180 | 66.6333 | 2
2015-07-24 09:30 | 2015-07-24 | 5 | 9 | 181 | 67.1333 | 2
2015-07-24 09:45 | 2015-07-24 | 5 | 9 | 195 | 67.6333 | 2
2015-07-24 10:00 | 2015-07-24 | 5 | 10 | 188 | 68.1333 | 2
2015-07-24 10:15 | 2015-07-24 | 5 | 10 | 181 | 68.6333 | 2
2015-07-24 10:30 | 2015-07-24 | 5 | 10 | 190 | 69.1333 | 2
2015-07-24 10:45 | 2015-07-24 | 5 | 10 | 206 | 69.6333 | 2
2015-07-24 11:00 | 2015-07-24 | 5 | 11 | 190 | 70.0667 | 3
2015-07-24 11:15 | 2015-07-24 | 5 | 11 | 197 | 70.3167 | 3
2015-07-24 11:30 | 2015-07-24 | 5 | 11 | 203 | 70.5667 | 3
2015-07-24 11:45 | 2015-07-24 | 5 | 11 | 193 | 70.8167 | 3
2015-07-24 12:00 | 2015-07-24 | 5 | 12 | 206 | 71.0667 | 3
2015-07-24 12:15 | 2015-07-24 | 5 | 12 | 201 | 71.3167 | 3
2015-07-24 12:30 | 2015-07-24 | 5 | 12 | 201 | 71.5667 | 3
2015-07-24 12:45 | 2015-07-24 | 5 | 12 | 201 | 71.8167 | 3
2015-07-24 13:00 | 2015-07-24 | 5 | 13 | 204 | 72 | 3
2015-07-24 13:15 | 2015-07-24 | 5 | 13 | 216 | 72 | 3
2015-07-24 13:30 | 2015-07-24 | 5 | 13 | 207 | 72 | 3
2015-07-24 13:45 | 2015-07-24 | 5 | 13 | 208 | 72 | 3
2015-07-24 14:00 | 2015-07-24 | 5 | 14 | 212 | 71.9333 | 3
2015-07-24 14:15 | 2015-07-24 | 5 | 14 | 209 | 71.6833 | 3
2015-07-24 14:30 | 2015-07-24 | 5 | 14 | 210 | 71.4333 | 3
2015-07-24 14:45 | 2015-07-24 | 5 | 14 | 221 | 71.1833 | 3
2015-07-24 15:00 | 2015-07-24 | 5 | 15 | 210 | 70.8667 | 3
2015-07-24 15:15 | 2015-07-24 | 5 | 15 | 210 | 70.3667 | 3
2015-07-24 15:30 | 2015-07-24 | 5 | 15 | 220 | 69.8667 | 2
2015-07-24 15:45 | 2015-07-24 | 5 | 15 | 210 | 69.3667 | 2
2015-07-24 16:00 | 2015-07-24 | 5 | 16 | 224 | 68.9333 | 2
2015-07-24 16:15 | 2015-07-24 | 5 | 16 | 225 | 68.6833 | 2
2015-07-24 16:30 | 2015-07-24 | 5 | 16 | 214 | 68.4333 | 2
2015-07-24 16:45 | 2015-07-24 | 5 | 16 | 220 | 68.1833 | 2
2015-07-24 17:00 | 2015-07-24 | 5 | 17 | 220 | 67.9333 | 2
2015-07-24 17:15 | 2015-07-24 | 5 | 17 | 216 | 67.6833 | 2
2015-07-24 17:30 | 2015-07-24 | 5 | 17 | 216 | 67.4333 | 2
2015-07-24 17:45 | 2015-07-24 | 5 | 17 | 227 | 67.1833 | 2
2015-07-24 18:00 | 2015-07-24 | 5 | 18 | 222 | 66.8 | 2
2015-07-24 18:15 | 2015-07-24 | 5 | 18 | 215 | 66.05 | 2
2015-07-24 18:30 | 2015-07-24 | 5 | 18 | 212 | 65.3 | 2
2015-07-24 18:45 | 2015-07-24 | 5 | 18 | 223 | 64.55 | 1
2015-07-24 19:00 | 2015-07-24 | 5 | 19 | 205 | 63.9333 | 1
2015-07-24 19:15 | 2015-07-24 | 5 | 19 | 210 | 63.6833 | 1
2015-07-24 19:30 | 2015-07-24 | 5 | 19 | 210 | 63.4333 | 1
2015-07-24 19:45 | 2015-07-24 | 5 | 19 | 222 | 63.1833 | 1
2015-07-24 20:00 | 2015-07-24 | 5 | 20 | 202 | 62.9333 | 1
2015-07-24 20:15 | 2015-07-24 | 5 | 20 | 199 | 62.6833 | 1
2015-07-24 20:30 | 2015-07-24 | 5 | 20 | 200 | 62.4333 | 1
2015-07-24 20:45 | 2015-07-24 | 5 | 20 | 187 | 62.1833 | 1
2015-07-24 21:00 | 2015-07-24 | 5 | 21 | 205 | 61.9333 | 1
2015-07-24 21:15 | 2015-07-24 | 5 | 21 | 184 | 61.6833 | 1
2015-07-24 21:30 | 2015-07-24 | 5 | 21 | 176 | 61.4333 | 1
2015-07-24 21:45 | 2015-07-24 | 5 | 21 | 170 | 61.1833 | 1
2015-07-24 22:00 | 2015-07-24 | 5 | 22 | 172 | 60.8667 | 1
2015-07-24 22:15 | 2015-07-24 | 5 | 22 | 182 | 60.3667 | 1
2015-07-24 22:30 | 2015-07-24 | 5 | 22 | 166 | 59.8667 | 1
2015-07-24 22:45 | 2015-07-24 | 5 | 22 | 170 | 59.3667 | 1
2015-07-24 23:00 | 2015-07-24 | 5 | 23 | 165 | 59 | 1
2015-07-24 23:15 | 2015-07-24 | 5 | 23 | 171 | 59 | 1
2015-07-24 23:30 | 2015-07-24 | 5 | 23 | 172 | 59 | 1
2015-07-24 23:45 | 2015-07-24 | 5 | 23 | 157 | 59 | 1
2015-07-25 | 2015-07-25 | 6 | 0 | 161 | 59 | 1
2015-07-25 00:15 | 2015-07-25 | 6 | 0 | 161 | 59 | 1
2015-07-25 00:30 | 2015-07-25 | 6 | 0 | 155 | 59 | 1
2015-07-25 00:45 | 2015-07-25 | 6 | 0 | 168 | 59 | 1
2015-07-25 01:00 | 2015-07-25 | 6 | 1 | 151 | 59 | 1
2015-07-25 01:15 | 2015-07-25 | 6 | 1 | 157 | 59 | 1
2015-07-25 01:30 | 2015-07-25 | 6 | 1 | 155 | 59 | 1
2015-07-25 01:45 | 2015-07-25 | 6 | 1 | 169 | 59 | 1
2015-07-25 02:00 | 2015-07-25 | 6 | 2 | 154 | 59 | 1
2015-07-25 02:15 | 2015-07-25 | 6 | 2 | 153 | 59 | 1
2015-07-25 02:30 | 2015-07-25 | 6 | 2 | 153 | 59 | 1
2015-07-25 02:45 | 2015-07-25 | 6 | 2 | 146 | 59 | 1
2015-07-25 03:00 | 2015-07-25 | 6 | 3 | 160 | 59 | 1
2015-07-25 03:15 | 2015-07-25 | 6 | 3 | 157 | 59 | 1
2015-07-25 03:30 | 2015-07-25 | 6 | 3 | 149 | 59 | 1
2015-07-25 03:45 | 2015-07-25 | 6 | 3 | 149 | 59 | 1
2015-07-25 04:00 | 2015-07-25 | 6 | 4 | 150 | 59 | 1
2015-07-25 04:15 | 2015-07-25 | 6 | 4 | 150 | 59 | 1
2015-07-25 04:30 | 2015-07-25 | 6 | 4 | 161 | 59 | 1
2015-07-25 04:45 | 2015-07-25 | 6 | 4 | 151 | 59 | 1
2015-07-25 05:00 | 2015-07-25 | 6 | 5 | 146 | 59 | 1
2015-07-25 05:15 | 2015-07-25 | 6 | 5 | 142 | 59 | 1
2015-07-25 05:30 | 2015-07-25 | 6 | 5 | 143 | 59 | 1
2015-07-25 05:45 | 2015-07-25 | 6 | 5 | 145 | 59 | 1
2015-07-25 06:00 | 2015-07-25 | 6 | 6 | 154 | 59.0667 | 1
2015-07-25 06:15 | 2015-07-25 | 6 | 6 | 144 | 59.3167 | 1
2015-07-25 06:30 | 2015-07-25 | 6 | 6 | 146 | 59.5667 | 1
2015-07-25 06:45 | 2015-07-25 | 6 | 6 | 145 | 59.8167 | 1
2015-07-25 07:00 | 2015-07-25 | 6 | 7 | 160 | 60 | 1
2015-07-25 07:15 | 2015-07-25 | 6 | 7 | 152 | 60 | 1
2015-07-25 07:30 | 2015-07-25 | 6 | 7 | 147 | 60 | 1
2015-07-25 07:45 | 2015-07-25 | 6 | 7 | 144 | 60 | 1
2015-07-25 08:00 | 2015-07-25 | 6 | 8 | 150 | 60.1333 | 1
2015-07-25 08:15 | 2015-07-25 | 6 | 8 | 168 | 60.6333 | 1
2015-07-25 08:30 | 2015-07-25 | 6 | 8 | 168 | 61.1333 | 1
2015-07-25 08:45 | 2015-07-25 | 6 | 8 | 158 | 61.6333 | 1
2015-07-25 09:00 | 2015-07-25 | 6 | 9 | 162 | 62.0667 | 1
2015-07-25 09:15 | 2015-07-25 | 6 | 9 | 161 | 62.3167 | 1
2015-07-25 09:30 | 2015-07-25 | 6 | 9 | 167 | 62.5667 | 1
2015-07-25 09:45 | 2015-07-25 | 6 | 9 | 170 | 62.8167 | 1
2015-07-25 10:00 | 2015-07-25 | 6 | 10 | 162 | 63.1333 | 1
2015-07-25 10:15 | 2015-07-25 | 6 | 10 | 163 | 63.6333 | 1
2015-07-25 10:30 | 2015-07-25 | 6 | 10 | 161 | 64.1333 | 1
2015-07-25 10:45 | 2015-07-25 | 6 | 10 | 170 | 64.6333 | 1
2015-07-25 11:00 | 2015-07-25 | 6 | 11 | 183 | 65 | 1
2015-07-25 11:15 | 2015-07-25 | 6 | 11 | 165 | 65 | 1
2015-07-25 11:30 | 2015-07-25 | 6 | 11 | 174 | 65 | 1
2015-07-25 11:45 | 2015-07-25 | 6 | 11 | 173 | 65 | 1
2015-07-25 12:00 | 2015-07-25 | 6 | 12 | 185 | 65.0667 | 2
2015-07-25 12:15 | 2015-07-25 | 6 | 12 | 182 | 65.3167 | 2
2015-07-25 12:30 | 2015-07-25 | 6 | 12 | 180 | 65.5667 | 2
2015-07-25 12:45 | 2015-07-25 | 6 | 12 | 175 | 65.8167 | 2
2015-07-25 13:00 | 2015-07-25 | 6 | 13 | 184 | 66.1333 | 2
2015-07-25 13:15 | 2015-07-25 | 6 | 13 | 194 | 66.6333 | 2
2015-07-25 13:30 | 2015-07-25 | 6 | 13 | 187 | 67.1333 | 2
2015-07-25 13:45 | 2015-07-25 | 6 | 13 | 185 | 67.6333 | 2
2015-07-25 14:00 | 2015-07-25 | 6 | 14 | 183 | 67.9333 | 2
2015-07-25 14:15 | 2015-07-25 | 6 | 14 | 186 | 67.6833 | 2
2015-07-25 14:30 | 2015-07-25 | 6 | 14 | 187 | 67.4333 | 2
2015-07-25 14:45 | 2015-07-25 | 6 | 14 | 191 | 67.1833 | 2
2015-07-25 15:00 | 2015-07-25 | 6 | 15 | 185 | 66.9333 | 2
2015-07-25 15:15 | 2015-07-25 | 6 | 15 | 188 | 66.6833 | 2
2015-07-25 15:30 | 2015-07-25 | 6 | 15 | 192 | 66.4333 | 2
2015-07-25 15:45 | 2015-07-25 | 6 | 15 | 214 | 66.1833 | 2
2015-07-25 16:00 | 2015-07-25 | 6 | 16 | 202 | 65.8 | 2
2015-07-25 16:15 | 2015-07-25 | 6 | 16 | 200 | 65.05 | 2
2015-07-25 16:30 | 2015-07-25 | 6 | 16 | 203 | 64.3 | 1
2015-07-25 16:45 | 2015-07-25 | 6 | 16 | 198 | 63.55 | 1
2015-07-25 17:00 | 2015-07-25 | 6 | 17 | 200 | 62.8667 | 1
2015-07-25 17:15 | 2015-07-25 | 6 | 17 | 219 | 62.3667 | 1
2015-07-25 17:30 | 2015-07-25 | 6 | 17 | 202 | 61.8667 | 1
2015-07-25 17:45 | 2015-07-25 | 6 | 17 | 198 | 61.3667 | 1
2015-07-25 18:00 | 2015-07-25 | 6 | 18 | 210 | 61 | 1
2015-07-25 18:15 | 2015-07-25 | 6 | 18 | 207 | 61 | 1
2015-07-25 18:30 | 2015-07-25 | 6 | 18 | 210 | 61 | 1
2015-07-25 18:45 | 2015-07-25 | 6 | 18 | 200 | 61 | 1
2015-07-25 19:00 | 2015-07-25 | 6 | 19 | 201 | 60.9333 | 1
2015-07-25 19:15 | 2015-07-25 | 6 | 19 | 195 | 60.6833 | 1
2015-07-25 19:30 | 2015-07-25 | 6 | 19 | 192 | 60.4333 | 1
2015-07-25 19:45 | 2015-07-25 | 6 | 19 | 193 | 60.1833 | 1
2015-07-25 20:00 | 2015-07-25 | 6 | 20 | 202 | 60.0667 | 1
2015-07-25 20:15 | 2015-07-25 | 6 | 20 | 189 | 60.3167 | 1
2015-07-25 20:30 | 2015-07-25 | 6 | 20 | 185 | 60.5667 | 1
2015-07-25 20:45 | 2015-07-25 | 6 | 20 | 175 | 60.8167 | 1
2015-07-25 21:00 | 2015-07-25 | 6 | 21 | 192 | 61 | 1
2015-07-25 21:15 | 2015-07-25 | 6 | 21 | 182 | 61 | 1
2015-07-25 21:30 | 2015-07-25 | 6 | 21 | 171 | 61 | 1
2015-07-25 21:45 | 2015-07-25 | 6 | 21 | 183 | 61 | 1
2015-07-25 22:00 | 2015-07-25 | 6 | 22 | 170 | 61 | 1
2015-07-25 22:15 | 2015-07-25 | 6 | 22 | 161 | 61 | 1
2015-07-25 22:30 | 2015-07-25 | 6 | 22 | 176 | 61 | 1
2015-07-25 22:45 | 2015-07-25 | 6 | 22 | 181 | 61 | 1
2015-07-25 23:00 | 2015-07-25 | 6 | 23 | 160 | 61 | 1
2015-07-25 23:15 | 2015-07-25 | 6 | 23 | 173 | 61 | 1
2015-07-25 23:30 | 2015-07-25 | 6 | 23 | 161 | 61 | 1
2015-07-25 23:45 | 2015-07-25 | 6 | 23 | 169 | 61 | 1
2015-07-26 | 2015-07-26 | 7 | 0 | 182 | 61 | 1
2015-07-26 00:15 | 2015-07-26 | 7 | 0 | 169 | 61 | 1
2015-07-26 00:30 | 2015-07-26 | 7 | 0 | 164 | 61 | 1
2015-07-26 00:45 | 2015-07-26 | 7 | 0 | 162 | 61 | 1
2015-07-26 01:00 | 2015-07-26 | 7 | 1 | 178 | 60.9333 | 1
2015-07-26 01:15 | 2015-07-26 | 7 | 1 | 164 | 60.6833 | 1
2015-07-26 01:30 | 2015-07-26 | 7 | 1 | 158 | 60.4333 | 1
2015-07-26 01:45 | 2015-07-26 | 7 | 1 | 164 | 60.1833 | 1
2015-07-26 02:00 | 2015-07-26 | 7 | 2 | 172 | 60 | 1
2015-07-26 02:15 | 2015-07-26 | 7 | 2 | 167 | 60 | 1
2015-07-26 02:30 | 2015-07-26 | 7 | 2 | 160 | 60 | 1
2015-07-26 02:45 | 2015-07-26 | 7 | 2 | 158 | 60 | 1
2015-07-26 03:00 | 2015-07-26 | 7 | 3 | 170 | 60.069 | 1
2015-07-26 03:15 | 2015-07-26 | 7 | 3 | 163 | 60.3276 | 1
2015-07-26 03:30 | 2015-07-26 | 7 | 3 | 159 | 60.5862 | 1
2015-07-26 03:45 | 2015-07-26 | 7 | 3 | 158 | 60.8448 | 1
2015-07-26 04:00 | 2015-07-26 | 7 | 4 | 152 | 59.8182 | 1
2015-07-26 04:15 | 2015-07-26 | 7 | 4 | 175 | 59.1364 | 1
2015-07-26 04:30 | 2015-07-26 | 7 | 4 | 166 | 59.3158 | 1
2015-07-26 04:45 | 2015-07-26 | 7 | 4 | 157 | 59.7105 | 1
2015-07-26 05:00 | 2015-07-26 | 7 | 5 | 158 | 59.3333 | 1
2015-07-26 05:15 | 2015-07-26 | 7 | 5 | 170 | 59.2407 | 1
2015-07-26 05:30 | 2015-07-26 | 7 | 5 | 161 | 59.5185 | 1
2015-07-26 05:45 | 2015-07-26 | 7 | 5 | 156 | 59.7963 | 1
2015-07-26 06:00 | 2015-07-26 | 7 | 6 | 154 | 60.1333 | 1
2015-07-26 06:15 | 2015-07-26 | 7 | 6 | 151 | 60.6333 | 1
2015-07-26 06:30 | 2015-07-26 | 7 | 6 | 172 | 61.1333 | 1
2015-07-26 06:45 | 2015-07-26 | 7 | 6 | 158 | 61.6333 | 1
2015-07-26 07:00 | 2015-07-26 | 7 | 7 | 164 | 62.1333 | 1
2015-07-26 07:15 | 2015-07-26 | 7 | 7 | 165 | 62.6333 | 1
2015-07-26 07:30 | 2015-07-26 | 7 | 7 | 176 | 63.1333 | 1
2015-07-26 07:45 | 2015-07-26 | 7 | 7 | 174 | 63.6333 | 1
2015-07-26 08:00 | 2015-07-26 | 7 | 8 | 168 | 64.1333 | 1
2015-07-26 08:15 | 2015-07-26 | 7 | 8 | 173 | 64.6333 | 1
2015-07-26 08:30 | 2015-07-26 | 7 | 8 | 170 | 65.1333 | 2
2015-07-26 08:45 | 2015-07-26 | 7 | 8 | 187 | 65.6333 | 2
2015-07-26 09:00 | 2015-07-26 | 7 | 9 | 179 | 66.1333 | 2
2015-07-26 09:15 | 2015-07-26 | 7 | 9 | 171 | 66.6333 | 2
2015-07-26 09:30 | 2015-07-26 | 7 | 9 | 169 | 67.1333 | 2
2015-07-26 09:45 | 2015-07-26 | 7 | 9 | 178 | 67.6333 | 2
2015-07-26 10:00 | 2015-07-26 | 7 | 10 | 190 | 68.1333 | 2
2015-07-26 10:15 | 2015-07-26 | 7 | 10 | 176 | 68.6333 | 2
2015-07-26 10:30 | 2015-07-26 | 7 | 10 | 186 | 69.1333 | 2
2015-07-26 10:45 | 2015-07-26 | 7 | 10 | 181 | 69.6333 | 2
2015-07-26 11:00 | 2015-07-26 | 7 | 11 | 196 | 70.2667 | 3
2015-07-26 11:15 | 2015-07-26 | 7 | 11 | 197 | 71.2667 | 3
2015-07-26 11:30 | 2015-07-26 | 7 | 11 | 190 | 72.2667 | 3
2015-07-26 11:45 | 2015-07-26 | 7 | 11 | 192 | 73.2667 | 3
2015-07-26 12:00 | 2015-07-26 | 7 | 12 | 189 | 73.4286 | 3
2015-07-26 12:15 | 2015-07-26 | 7 | 12 | 207 | 71.8679 | 3
2015-07-26 12:30 | 2015-07-26 | 7 | 12 | 202 | 70.4528 | 3
2015-07-26 12:45 | 2015-07-26 | 7 | 12 | 198 | 69.0377 | 2
2015-07-26 13:00 | 2015-07-26 | 7 | 13 | 199 | 68.0667 | 2
2015-07-26 13:15 | 2015-07-26 | 7 | 13 | 204 | 68.3167 | 2
2015-07-26 13:30 | 2015-07-26 | 7 | 13 | 199 | 68.5667 | 2
2015-07-26 13:45 | 2015-07-26 | 7 | 13 | 217 | 68.8167 | 2
2015-07-26 14:00 | 2015-07-26 | 7 | 14 | 192 | 69.0667 | 2
2015-07-26 14:15 | 2015-07-26 | 7 | 14 | 211 | 69.3167 | 2
2015-07-26 14:30 | 2015-07-26 | 7 | 14 | 196 | 69.5667 | 2
2015-07-26 14:45 | 2015-07-26 | 7 | 14 | 227 | 69.8167 | 2
2015-07-26 15:00 | 2015-07-26 | 7 | 15 | 201 | 69.8667 | 2
2015-07-26 15:15 | 2015-07-26 | 7 | 15 | 207 | 69.3667 | 2
2015-07-26 15:30 | 2015-07-26 | 7 | 15 | 209 | 68.8667 | 2
2015-07-26 15:45 | 2015-07-26 | 7 | 15 | 208 | 68.3667 | 2
2015-07-26 16:00 | 2015-07-26 | 7 | 16 | 204 | 67.9333 | 2
2015-07-26 16:15 | 2015-07-26 | 7 | 16 | 223 | 67.6833 | 2
2015-07-26 16:30 | 2015-07-26 | 7 | 16 | 205 | 67.4333 | 2
2015-07-26 16:45 | 2015-07-26 | 7 | 16 | 208 | 67.1833 | 2
2015-07-26 17:00 | 2015-07-26 | 7 | 17 | 206 | 66.9333 | 2
2015-07-26 17:15 | 2015-07-26 | 7 | 17 | 214 | 66.6833 | 2
2015-07-26 17:30 | 2015-07-26 | 7 | 17 | 227 | 66.4333 | 2
2015-07-26 17:45 | 2015-07-26 | 7 | 17 | 213 | 66.1833 | 2
2015-07-26 18:00 | 2015-07-26 | 7 | 18 | 213 | 65.8667 | 2
2015-07-26 18:15 | 2015-07-26 | 7 | 18 | 213 | 65.3667 | 2
2015-07-26 18:30 | 2015-07-26 | 7 | 18 | 211 | 64.8667 | 1
2015-07-26 18:45 | 2015-07-26 | 7 | 18 | 202 | 64.3667 | 1
2015-07-26 19:00 | 2015-07-26 | 7 | 19 | 212 | 63.9333 | 1
2015-07-26 19:15 | 2015-07-26 | 7 | 19 | 219 | 63.6833 | 1
2015-07-26 19:30 | 2015-07-26 | 7 | 19 | 198 | 63.4333 | 1
2015-07-26 19:45 | 2015-07-26 | 7 | 19 | 199 | 63.1833 | 1
2015-07-26 20:00 | 2015-07-26 | 7 | 20 | 198 | 62.9333 | 1
2015-07-26 20:15 | 2015-07-26 | 7 | 20 | 194 | 62.6833 | 1
2015-07-26 20:30 | 2015-07-26 | 7 | 20 | 206 | 62.4333 | 1
2015-07-26 20:45 | 2015-07-26 | 7 | 20 | 192 | 62.1833 | 1
2015-07-26 21:00 | 2015-07-26 | 7 | 21 | 190 | 61.8667 | 1
2015-07-26 21:15 | 2015-07-26 | 7 | 21 | 180 | 61.3667 | 1
2015-07-26 21:30 | 2015-07-26 | 7 | 21 | 185 | 60.8667 | 1
2015-07-26 21:45 | 2015-07-26 | 7 | 21 | 182 | 60.3667 | 1
2015-07-26 22:00 | 2015-07-26 | 7 | 22 | 174 | 60 | 1
2015-07-26 22:15 | 2015-07-26 | 7 | 22 | 170 | 60 | 1
2015-07-26 22:30 | 2015-07-26 | 7 | 22 | 175 | 60 | 1
2015-07-26 22:45 | 2015-07-26 | 7 | 22 | 185 | 60 | 1
2015-07-26 23:00 | 2015-07-26 | 7 | 23 | 165 | 59.9333 | 1
2015-07-26 23:15 | 2015-07-26 | 7 | 23 | 174 | 59.6833 | 1
2015-07-26 23:30 | 2015-07-26 | 7 | 23 | 167 | 59.4333 | 1
2015-07-26 23:45 | 2015-07-26 | 7 | 23 | 179 | 59.1833 | 1
2015-07-27 | 2015-07-27 | 1 | 0 | 162 | 59 | 1
2015-07-27 00:15 | 2015-07-27 | 1 | 0 | 159 | 59 | 1
2015-07-27 00:30 | 2015-07-27 | 1 | 0 | 159 | 59 | 1
2015-07-27 00:45 | 2015-07-27 | 1 | 0 | 171 | 59 | 1
2015-07-27 01:00 | 2015-07-27 | 1 | 1 | 158 | 58.9333 | 1
2015-07-27 01:15 | 2015-07-27 | 1 | 1 | 154 | 58.6833 | 1
2015-07-27 01:30 | 2015-07-27 | 1 | 1 | 162 | 58.4333 | 1
2015-07-27 01:45 | 2015-07-27 | 1 | 1 | 153 | 58.1833 | 1
2015-07-27 02:00 | 2015-07-27 | 1 | 2 | 179 | 58 | 1
2015-07-27 02:15 | 2015-07-27 | 1 | 2 | 149 | 58 | 1
2015-07-27 02:30 | 2015-07-27 | 1 | 2 | 157 | 58 | 1
2015-07-27 02:45 | 2015-07-27 | 1 | 2 | 151 | 58 | 1
2015-07-27 03:00 | 2015-07-27 | 1 | 3 | 171 | 57.9333 | 1
2015-07-27 03:15 | 2015-07-27 | 1 | 3 | 150 | 57.6833 | 1
2015-07-27 03:30 | 2015-07-27 | 1 | 3 | 155 | 57.4333 | 1
2015-07-27 03:45 | 2015-07-27 | 1 | 3 | 147 | 57.1833 | 1
2015-07-27 04:00 | 2015-07-27 | 1 | 4 | 147 | 57 | 1
2015-07-27 04:15 | 2015-07-27 | 1 | 4 | 159 | 57 | 1
2015-07-27 04:30 | 2015-07-27 | 1 | 4 | 152 | 57 | 1
2015-07-27 04:45 | 2015-07-27 | 1 | 4 | 154 | 57 | 1
2015-07-27 05:00 | 2015-07-27 | 1 | 5 | 150 | 57.0667 | 1
2015-07-27 05:15 | 2015-07-27 | 1 | 5 | 145 | 57.3167 | 1
2015-07-27 05:30 | 2015-07-27 | 1 | 5 | 155 | 57.5667 | 1
2015-07-27 05:45 | 2015-07-27 | 1 | 5 | 153 | 57.8167 | 1
2015-07-27 06:00 | 2015-07-27 | 1 | 6 | 147 | 58.2667 | 1
2015-07-27 06:15 | 2015-07-27 | 1 | 6 | 143 | 59.2667 | 1
2015-07-27 06:30 | 2015-07-27 | 1 | 6 | 145 | 60.2667 | 1
2015-07-27 06:45 | 2015-07-27 | 1 | 6 | 153 | 61.2667 | 1
2015-07-27 07:00 | 2015-07-27 | 1 | 7 | 165 | 62.2667 | 1
2015-07-27 07:15 | 2015-07-27 | 1 | 7 | 159 | 63.2667 | 1
2015-07-27 07:30 | 2015-07-27 | 1 | 7 | 158 | 64.2667 | 1
2015-07-27 07:45 | 2015-07-27 | 1 | 7 | 157 | 65.2667 | 2
2015-07-27 08:00 | 2015-07-27 | 1 | 8 | 162 | 66.1333 | 2
2015-07-27 08:15 | 2015-07-27 | 1 | 8 | 176 | 66.6333 | 2
2015-07-27 08:30 | 2015-07-27 | 1 | 8 | 177 | 67.1333 | 2
2015-07-27 08:45 | 2015-07-27 | 1 | 8 | 166 | 67.6333 | 2
2015-07-27 09:00 | 2015-07-27 | 1 | 9 | 176 | 68.2 | 2
2015-07-27 09:15 | 2015-07-27 | 1 | 9 | 179 | 68.95 | 2
2015-07-27 09:30 | 2015-07-27 | 1 | 9 | 188 | 69.7 | 2
2015-07-27 09:45 | 2015-07-27 | 1 | 9 | 196 | 70.45 | 3
2015-07-27 10:00 | 2015-07-27 | 1 | 10 | 197 | 71.5333 | 3
2015-07-27 10:15 | 2015-07-27 | 1 | 10 | 195 | 73.5333 | 3
2015-07-27 10:30 | 2015-07-27 | 1 | 10 | 197 | 75.5333 | 4
2015-07-27 10:45 | 2015-07-27 | 1 | 10 | 215 | 77.5333 | 4
2015-07-27 11:00 | 2015-07-27 | 1 | 11 | 201 | 79.0667 | 4
2015-07-27 11:15 | 2015-07-27 | 1 | 11 | 209 | 79.3167 | 4
2015-07-27 11:30 | 2015-07-27 | 1 | 11 | 203 | 79.5667 | 4
2015-07-27 11:45 | 2015-07-27 | 1 | 11 | 209 | 79.8167 | 4
2015-07-27 12:00 | 2015-07-27 | 1 | 12 | 219 | 79.9333 | 4
2015-07-27 12:15 | 2015-07-27 | 1 | 12 | 208 | 79.6833 | 4
2015-07-27 12:30 | 2015-07-27 | 1 | 12 | 213 | 79.4333 | 4
2015-07-27 12:45 | 2015-07-27 | 1 | 12 | 221 | 79.1833 | 4
2015-07-27 13:00 | 2015-07-27 | 1 | 13 | 216 | 78.8 | 4
2015-07-27 13:15 | 2015-07-27 | 1 | 13 | 236 | 78.05 | 4
2015-07-27 13:30 | 2015-07-27 | 1 | 13 | 214 | 77.3 | 4
2015-07-27 13:45 | 2015-07-27 | 1 | 13 | 225 | 76.55 | 4
2015-07-27 14:00 | 2015-07-27 | 1 | 14 | 226 | 75.9333 | 4
2015-07-27 14:15 | 2015-07-27 | 1 | 14 | 231 | 75.6833 | 4
2015-07-27 14:30 | 2015-07-27 | 1 | 14 | 237 | 75.4333 | 4
2015-07-27 14:45 | 2015-07-27 | 1 | 14 | 234 | 75.1833 | 4
2015-07-27 15:00 | 2015-07-27 | 1 | 15 | 238 | 74.8667 | 3
2015-07-27 15:15 | 2015-07-27 | 1 | 15 | 240 | 74.3667 | 3
2015-07-27 15:30 | 2015-07-27 | 1 | 15 | 248 | 73.8667 | 3
2015-07-27 15:45 | 2015-07-27 | 1 | 15 | 242 | 73.3667 | 3
2015-07-27 16:00 | 2015-07-27 | 1 | 16 | 251 | 72.9333 | 3
2015-07-27 16:15 | 2015-07-27 | 1 | 16 | 237 | 72.6833 | 3
2015-07-27 16:30 | 2015-07-27 | 1 | 16 | 255 | 72.4333 | 3
2015-07-27 16:45 | 2015-07-27 | 1 | 16 | 264 | 72.1833 | 3
2015-07-27 17:00 | 2015-07-27 | 1 | 17 | 246 | 71.7333 | 3
2015-07-27 17:15 | 2015-07-27 | 1 | 17 | 248 | 70.7333 | 3
2015-07-27 17:30 | 2015-07-27 | 1 | 17 | 246 | 69.7333 | 2
2015-07-27 17:45 | 2015-07-27 | 1 | 17 | 251 | 68.7333 | 2
2015-07-27 18:00 | 2015-07-27 | 1 | 18 | 260 | 67.7333 | 2
2015-07-27 18:15 | 2015-07-27 | 1 | 18 | 229 | 66.7333 | 2
2015-07-27 18:30 | 2015-07-27 | 1 | 18 | 240 | 65.7333 | 2
2015-07-27 18:45 | 2015-07-27 | 1 | 18 | 233 | 64.7333 | 1
2015-07-27 19:00 | 2015-07-27 | 1 | 19 | 244 | 63.8 | 1
2015-07-27 19:15 | 2015-07-27 | 1 | 19 | 238 | 63.05 | 1
2015-07-27 19:30 | 2015-07-27 | 1 | 19 | 226 | 62.3 | 1
2015-07-27 19:45 | 2015-07-27 | 1 | 19 | 216 | 61.55 | 1
2015-07-27 20:00 | 2015-07-27 | 1 | 20 | 222 | 61 | 1
2015-07-27 20:15 | 2015-07-27 | 1 | 20 | 208 | 61 | 1
2015-07-27 20:30 | 2015-07-27 | 1 | 20 | 216 | 61 | 1
2015-07-27 20:45 | 2015-07-27 | 1 | 20 | 215 | 61 | 1
2015-07-27 21:00 | 2015-07-27 | 1 | 21 | 203 | 61 | 1
2015-07-27 21:15 | 2015-07-27 | 1 | 21 | 191 | 61 | 1
2015-07-27 21:30 | 2015-07-27 | 1 | 21 | 190 | 61 | 1
2015-07-27 21:45 | 2015-07-27 | 1 | 21 | 199 | 61 | 1
2015-07-27 22:00 | 2015-07-27 | 1 | 22 | 189 | 60.9333 | 1
2015-07-27 22:15 | 2015-07-27 | 1 | 22 | 188 | 60.6833 | 1
2015-07-27 22:30 | 2015-07-27 | 1 | 22 | 193 | 60.4333 | 1
2015-07-27 22:45 | 2015-07-27 | 1 | 22 | 193 | 60.1833 | 1
2015-07-27 23:00 | 2015-07-27 | 1 | 23 | 203 | 60 | 1
2015-07-27 23:15 | 2015-07-27 | 1 | 23 | 182 | 60 | 1
2015-07-27 23:30 | 2015-07-27 | 1 | 23 | 181 | 60 | 1
2015-07-27 23:45 | 2015-07-27 | 1 | 23 | 181 | 60 | 1
2015-07-28 | 2015-07-28 | 2 | 0 | 194 | 60 | 1
2015-07-28 00:15 | 2015-07-28 | 2 | 0 | 173 | 60 | 1
2015-07-28 00:30 | 2015-07-28 | 2 | 0 | 176 | 60 | 1
2015-07-28 00:45 | 2015-07-28 | 2 | 0 | 169 | 60 | 1
2015-07-28 01:00 | 2015-07-28 | 2 | 1 | 174 | 59.9333 | 1
2015-07-28 01:15 | 2015-07-28 | 2 | 1 | 172 | 59.6833 | 1
2015-07-28 01:30 | 2015-07-28 | 2 | 1 | 161 | 59.4333 | 1
2015-07-28 01:45 | 2015-07-28 | 2 | 1 | 159 | 59.1833 | 1
2015-07-28 02:00 | 2015-07-28 | 2 | 2 | 165 | 58.9333 | 1
2015-07-28 02:15 | 2015-07-28 | 2 | 2 | 171 | 58.6833 | 1
2015-07-28 02:30 | 2015-07-28 | 2 | 2 | 161 | 58.4333 | 1
2015-07-28 02:45 | 2015-07-28 | 2 | 2 | 152 | 58.1833 | 1
2015-07-28 03:00 | 2015-07-28 | 2 | 3 | 158 | 58 | 1
2015-07-28 03:15 | 2015-07-28 | 2 | 3 | 170 | 58 | 1
2015-07-28 03:30 | 2015-07-28 | 2 | 3 | 157 | 58 | 1
2015-07-28 03:45 | 2015-07-28 | 2 | 3 | 152 | 58 | 1
2015-07-28 04:00 | 2015-07-28 | 2 | 4 | 157 | 58 | 1
2015-07-28 04:15 | 2015-07-28 | 2 | 4 | 149 | 58 | 1
2015-07-28 04:30 | 2015-07-28 | 2 | 4 | 169 | 58 | 1
2015-07-28 04:45 | 2015-07-28 | 2 | 4 | 154 | 58 | 1
2015-07-28 05:00 | 2015-07-28 | 2 | 5 | 159 | 58.1333 | 1
2015-07-28 05:15 | 2015-07-28 | 2 | 5 | 151 | 58.6333 | 1
2015-07-28 05:30 | 2015-07-28 | 2 | 5 | 170 | 59.1333 | 1
2015-07-28 05:45 | 2015-07-28 | 2 | 5 | 154 | 59.6333 | 1
2015-07-28 06:00 | 2015-07-28 | 2 | 6 | 163 | 60.3333 | 1
2015-07-28 06:15 | 2015-07-28 | 2 | 6 | 151 | 61.5833 | 1
2015-07-28 06:30 | 2015-07-28 | 2 | 6 | 151 | 62.8333 | 1
2015-07-28 06:45 | 2015-07-28 | 2 | 6 | 158 | 64.0833 | 1
2015-07-28 07:00 | 2015-07-28 | 2 | 7 | 170 | 65.1333 | 2
2015-07-28 07:15 | 2015-07-28 | 2 | 7 | 167 | 65.6333 | 2
2015-07-28 07:30 | 2015-07-28 | 2 | 7 | 162 | 66.1333 | 2
2015-07-28 07:45 | 2015-07-28 | 2 | 7 | 167 | 66.6333 | 2
2015-07-28 08:00 | 2015-07-28 | 2 | 8 | 166 | 67.1333 | 2
2015-07-28 08:15 | 2015-07-28 | 2 | 8 | 176 | 67.6333 | 2
2015-07-28 08:30 | 2015-07-28 | 2 | 8 | 180 | 68.1333 | 2
2015-07-28 08:45 | 2015-07-28 | 2 | 8 | 188 | 68.6333 | 2
2015-07-28 09:00 | 2015-07-28 | 2 | 9 | 172 | 69.2 | 2
2015-07-28 09:15 | 2015-07-28 | 2 | 9 | 186 | 69.95 | 2
2015-07-28 09:30 | 2015-07-28 | 2 | 9 | 187 | 70.7 | 3
2015-07-28 09:45 | 2015-07-28 | 2 | 9 | 201 | 71.45 | 3
2015-07-28 10:00 | 2015-07-28 | 2 | 10 | 194 | 72.1333 | 3
2015-07-28 10:15 | 2015-07-28 | 2 | 10 | 195 | 72.6333 | 3
2015-07-28 10:30 | 2015-07-28 | 2 | 10 | 200 | 73.1333 | 3
2015-07-28 10:45 | 2015-07-28 | 2 | 10 | 221 | 73.6333 | 3
2015-07-28 11:00 | 2015-07-28 | 2 | 11 | 206 | 74.8 | 3
2015-07-28 11:15 | 2015-07-28 | 2 | 11 | 210 | 77.8 | 4
2015-07-28 11:30 | 2015-07-28 | 2 | 11 | 225 | 80.8 | 5
2015-07-28 11:45 | 2015-07-28 | 2 | 11 | 224 | 83.8 | 5
2015-07-28 12:00 | 2015-07-28 | 2 | 12 | 238 | 86.0667 | 6
2015-07-28 12:15 | 2015-07-28 | 2 | 12 | 230 | 86.3167 | 6
2015-07-28 12:30 | 2015-07-28 | 2 | 12 | 236 | 86.5667 | 6
2015-07-28 12:45 | 2015-07-28 | 2 | 12 | 245 | 86.8167 | 6
2015-07-28 13:00 | 2015-07-28 | 2 | 13 | 250 | 86.7333 | 6
2015-07-28 13:15 | 2015-07-28 | 2 | 13 | 259 | 85.7333 | 6
2015-07-28 13:30 | 2015-07-28 | 2 | 13 | 247 | 84.7333 | 5
2015-07-28 13:45 | 2015-07-28 | 2 | 13 | 249 | 83.7333 | 5
2015-07-28 14:00 | 2015-07-28 | 2 | 14 | 247 | 83.1333 | 5
2015-07-28 14:15 | 2015-07-28 | 2 | 14 | 267 | 83.6333 | 5
2015-07-28 14:30 | 2015-07-28 | 2 | 14 | 253 | 84.1333 | 5
2015-07-28 14:45 | 2015-07-28 | 2 | 14 | 256 | 84.6333 | 5
2015-07-28 15:00 | 2015-07-28 | 2 | 15 | 257 | 84.8 | 5
2015-07-28 15:15 | 2015-07-28 | 2 | 15 | 261 | 84.05 | 5
2015-07-28 15:30 | 2015-07-28 | 2 | 15 | 258 | 83.3 | 5
2015-07-28 15:45 | 2015-07-28 | 2 | 15 | 278 | 82.55 | 5
2015-07-28 16:00 | 2015-07-28 | 2 | 16 | 267 | 81.9333 | 5
2015-07-28 16:15 | 2015-07-28 | 2 | 16 | 274 | 81.6833 | 5
2015-07-28 16:30 | 2015-07-28 | 2 | 16 | 270 | 81.4333 | 5
2015-07-28 16:45 | 2015-07-28 | 2 | 16 | 268 | 81.1833 | 5
2015-07-28 17:00 | 2015-07-28 | 2 | 17 | 285 | 80.8667 | 5
2015-07-28 17:15 | 2015-07-28 | 2 | 17 | 278 | 80.3667 | 5
2015-07-28 17:30 | 2015-07-28 | 2 | 17 | 268 | 79.8667 | 4
2015-07-28 17:45 | 2015-07-28 | 2 | 17 | 273 | 79.3667 | 4
2015-07-28 18:00 | 2015-07-28 | 2 | 18 | 285 | 78.5333 | 4
2015-07-28 18:15 | 2015-07-28 | 2 | 18 | 266 | 76.7833 | 4
2015-07-28 18:30 | 2015-07-28 | 2 | 18 | 263 | 75.0333 | 4
2015-07-28 18:45 | 2015-07-28 | 2 | 18 | 263 | 73.2833 | 3
2015-07-28 19:00 | 2015-07-28 | 2 | 19 | 256 | 71.8 | 3
2015-07-28 19:15 | 2015-07-28 | 2 | 19 | 258 | 71.05 | 3
2015-07-28 19:30 | 2015-07-28 | 2 | 19 | 254 | 70.3 | 3
2015-07-28 19:45 | 2015-07-28 | 2 | 19 | 247 | 69.55 | 2
2015-07-28 20:00 | 2015-07-28 | 2 | 20 | 247 | 69.1333 | 2
2015-07-28 20:15 | 2015-07-28 | 2 | 20 | 234 | 69.6333 | 2
2015-07-28 20:30 | 2015-07-28 | 2 | 20 | 239 | 70.1333 | 3
2015-07-28 20:45 | 2015-07-28 | 2 | 20 | 234 | 70.6333 | 3
2015-07-28 21:00 | 2015-07-28 | 2 | 21 | 227 | 70.8667 | 3
2015-07-28 21:15 | 2015-07-28 | 2 | 21 | 218 | 70.3667 | 3
2015-07-28 21:30 | 2015-07-28 | 2 | 21 | 202 | 69.8667 | 2
2015-07-28 21:45 | 2015-07-28 | 2 | 21 | 209 | 69.3667 | 2
2015-07-28 22:00 | 2015-07-28 | 2 | 22 | 210 | 68.8 | 2
2015-07-28 22:15 | 2015-07-28 | 2 | 22 | 197 | 68.05 | 2
2015-07-28 22:30 | 2015-07-28 | 2 | 22 | 202 | 67.3 | 2
2015-07-28 22:45 | 2015-07-28 | 2 | 22 | 206 | 66.55 | 2
2015-07-28 23:00 | 2015-07-28 | 2 | 23 | 208 | 65.8667 | 2
2015-07-28 23:15 | 2015-07-28 | 2 | 23 | 191 | 65.3667 | 2
2015-07-28 23:30 | 2015-07-28 | 2 | 23 | 188 | 64.8667 | 1
2015-07-28 23:45 | 2015-07-28 | 2 | 23 | 190 | 64.3667 | 1
2015-07-29 | 2015-07-29 | 3 | 0 | 200 | 63.9333 | 1
2015-07-29 00:15 | 2015-07-29 | 3 | 0 | 181 | 63.6833 | 1
2015-07-29 00:30 | 2015-07-29 | 3 | 0 | 185 | 63.4333 | 1
2015-07-29 00:45 | 2015-07-29 | 3 | 0 | 175 | 63.1833 | 1
2015-07-29 01:00 | 2015-07-29 | 3 | 1 | 192 | 62.9333 | 1
2015-07-29 01:15 | 2015-07-29 | 3 | 1 | 184 | 62.6833 | 1
2015-07-29 01:30 | 2015-07-29 | 3 | 1 | 174 | 62.4333 | 1
2015-07-29 01:45 | 2015-07-29 | 3 | 1 | 170 | 62.1833 | 1
2015-07-29 02:00 | 2015-07-29 | 3 | 2 | 175 | 61.8667 | 1
2015-07-29 02:15 | 2015-07-29 | 3 | 2 | 181 | 61.3667 | 1
2015-07-29 02:30 | 2015-07-29 | 3 | 2 | 169 | 60.8667 | 1
2015-07-29 02:45 | 2015-07-29 | 3 | 2 | 166 | 60.3667 | 1
2015-07-29 03:00 | 2015-07-29 | 3 | 3 | 175 | 60 | 1
2015-07-29 03:15 | 2015-07-29 | 3 | 3 | 173 | 60 | 1
2015-07-29 03:30 | 2015-07-29 | 3 | 3 | 165 | 60 | 1
2015-07-29 03:45 | 2015-07-29 | 3 | 3 | 160 | 60 | 1
2015-07-29 04:00 | 2015-07-29 | 3 | 4 | 163 | 59.8667 | 1
2015-07-29 04:15 | 2015-07-29 | 3 | 4 | 175 | 59.3667 | 1
2015-07-29 04:30 | 2015-07-29 | 3 | 4 | 156 | 58.8667 | 1
2015-07-29 04:45 | 2015-07-29 | 3 | 4 | 164 | 58.3667 | 1
2015-07-29 05:00 | 2015-07-29 | 3 | 5 | 163 | 58 | 1
2015-07-29 05:15 | 2015-07-29 | 3 | 5 | 168 | 58 | 1
2015-07-29 05:30 | 2015-07-29 | 3 | 5 | 161 | 58 | 1
2015-07-29 05:45 | 2015-07-29 | 3 | 5 | 155 | 58 | 1
2015-07-29 06:00 | 2015-07-29 | 3 | 6 | 163 | 58.2 | 1
2015-07-29 06:15 | 2015-07-29 | 3 | 6 | 158 | 58.95 | 1
2015-07-29 06:30 | 2015-07-29 | 3 | 6 | 168 | 59.7 | 1
2015-07-29 06:45 | 2015-07-29 | 3 | 6 | 178 | 60.45 | 1
2015-07-29 07:00 | 2015-07-29 | 3 | 7 | 176 | 61.3333 | 1
2015-07-29 07:15 | 2015-07-29 | 3 | 7 | 181 | 62.5833 | 1
2015-07-29 07:30 | 2015-07-29 | 3 | 7 | 171 | 63.8333 | 1
2015-07-29 07:45 | 2015-07-29 | 3 | 7 | 170 | 65.0833 | 2
2015-07-29 08:00 | 2015-07-29 | 3 | 8 | 195 | 66.1333 | 2
2015-07-29 08:15 | 2015-07-29 | 3 | 8 | 177 | 66.6333 | 2
2015-07-29 08:30 | 2015-07-29 | 3 | 8 | 180 | 67.1333 | 2
2015-07-29 08:45 | 2015-07-29 | 3 | 8 | 196 | 67.6333 | 2
2015-07-29 09:00 | 2015-07-29 | 3 | 9 | 203 | 68.2 | 2
2015-07-29 09:15 | 2015-07-29 | 3 | 9 | 180 | 68.95 | 2
2015-07-29 09:30 | 2015-07-29 | 3 | 9 | 194 | 69.7 | 2
2015-07-29 09:45 | 2015-07-29 | 3 | 9 | 194 | 70.45 | 3
2015-07-29 10:00 | 2015-07-29 | 3 | 10 | 203 | 71.3333 | 3
2015-07-29 10:15 | 2015-07-29 | 3 | 10 | 222 | 72.5833 | 3
2015-07-29 10:30 | 2015-07-29 | 3 | 10 | 208 | 73.8333 | 3
2015-07-29 10:45 | 2015-07-29 | 3 | 10 | 212 | 75.0833 | 4
2015-07-29 11:00 | 2015-07-29 | 3 | 11 | 216 | 76.0667 | 4
2015-07-29 11:15 | 2015-07-29 | 3 | 11 | 236 | 76.3167 | 4
2015-07-29 11:30 | 2015-07-29 | 3 | 11 | 226 | 76.5667 | 4
2015-07-29 11:45 | 2015-07-29 | 3 | 11 | 236 | 76.8167 | 4
2015-07-29 12:00 | 2015-07-29 | 3 | 12 | 229 | 77 | 4
2015-07-29 12:15 | 2015-07-29 | 3 | 12 | 245 | 77 | 4
2015-07-29 12:30 | 2015-07-29 | 3 | 12 | 243 | 77 | 4
2015-07-29 12:45 | 2015-07-29 | 3 | 12 | 239 | 77 | 4
2015-07-29 13:00 | 2015-07-29 | 3 | 13 | 230 | 77.0667 | 4
2015-07-29 13:15 | 2015-07-29 | 3 | 13 | 238 | 77.3167 | 4
2015-07-29 13:30 | 2015-07-29 | 3 | 13 | 230 | 77.5667 | 4
2015-07-29 13:45 | 2015-07-29 | 3 | 13 | 268 | 77.8167 | 4
2015-07-29 14:00 | 2015-07-29 | 3 | 14 | 234 | 77.9333 | 4
2015-07-29 14:15 | 2015-07-29 | 3 | 14 | 248 | 77.6833 | 4
2015-07-29 14:30 | 2015-07-29 | 3 | 14 | 242 | 77.4333 | 4
2015-07-29 14:45 | 2015-07-29 | 3 | 14 | 252 | 77.1833 | 4
2015-07-29 15:00 | 2015-07-29 | 3 | 15 | 272 | 76.8 | 4
2015-07-29 15:15 | 2015-07-29 | 3 | 15 | 259 | 76.05 | 4
2015-07-29 15:30 | 2015-07-29 | 3 | 15 | 249 | 75.3 | 4
2015-07-29 15:45 | 2015-07-29 | 3 | 15 | 255 | 74.55 | 3
2015-07-29 16:00 | 2015-07-29 | 3 | 16 | 258 | 73.7333 | 3
2015-07-29 16:15 | 2015-07-29 | 3 | 16 | 271 | 72.7333 | 3
2015-07-29 16:30 | 2015-07-29 | 3 | 16 | 248 | 71.7333 | 3
2015-07-29 16:45 | 2015-07-29 | 3 | 16 | 253 | 70.7333 | 3
2015-07-29 17:00 | 2015-07-29 | 3 | 17 | 260 | 69.8 | 2
2015-07-29 17:15 | 2015-07-29 | 3 | 17 | 251 | 69.05 | 2
2015-07-29 17:30 | 2015-07-29 | 3 | 17 | 252 | 68.3 | 2
2015-07-29 17:45 | 2015-07-29 | 3 | 17 | 250 | 67.55 | 2
2015-07-29 18:00 | 2015-07-29 | 3 | 18 | 245 | 66.8 | 2
2015-07-29 18:15 | 2015-07-29 | 3 | 18 | 253 | 66.05 | 2
2015-07-29 18:30 | 2015-07-29 | 3 | 18 | 251 | 65.3 | 2
2015-07-29 18:45 | 2015-07-29 | 3 | 18 | 243 | 64.55 | 1
2015-07-29 19:00 | 2015-07-29 | 3 | 19 | 236 | 63.8667 | 1
2015-07-29 19:15 | 2015-07-29 | 3 | 19 | 238 | 63.3667 | 1
2015-07-29 19:30 | 2015-07-29 | 3 | 19 | 233 | 62.8667 | 1
2015-07-29 19:45 | 2015-07-29 | 3 | 19 | 229 | 62.3667 | 1
2015-07-29 20:00 | 2015-07-29 | 3 | 20 | 231 | 62 | 1
2015-07-29 20:15 | 2015-07-29 | 3 | 20 | 224 | 62 | 1
2015-07-29 20:30 | 2015-07-29 | 3 | 20 | 215 | 62 | 1
2015-07-29 20:45 | 2015-07-29 | 3 | 20 | 222 | 62 | 1
2015-07-29 21:00 | 2015-07-29 | 3 | 21 | 218 | 62 | 1
2015-07-29 21:15 | 2015-07-29 | 3 | 21 | 218 | 62 | 1
2015-07-29 21:30 | 2015-07-29 | 3 | 21 | 204 | 62 | 1
2015-07-29 21:45 | 2015-07-29 | 3 | 21 | 200 | 62 | 1
2015-07-29 22:00 | 2015-07-29 | 3 | 22 | 199 | 61.9333 | 1
2015-07-29 22:15 | 2015-07-29 | 3 | 22 | 210 | 61.6833 | 1
2015-07-29 22:30 | 2015-07-29 | 3 | 22 | 198 | 61.4333 | 1
2015-07-29 22:45 | 2015-07-29 | 3 | 22 | 194 | 61.1833 | 1
2015-07-29 23:00 | 2015-07-29 | 3 | 23 | 185 | 61 | 1
2015-07-29 23:15 | 2015-07-29 | 3 | 23 | 188 | 61 | 1
2015-07-29 23:30 | 2015-07-29 | 3 | 23 | 193 | 61 | 1
2015-07-29 23:45 | 2015-07-29 | 3 | 23 | 179 | 61 | 1
2015-07-30 | 2015-07-30 | 4 | 0 | 183 | 61 | 1
2015-07-30 00:15 | 2015-07-30 | 4 | 0 | 176 | 61 | 1
2015-07-30 00:30 | 2015-07-30 | 4 | 0 | 196 | 61 | 1
2015-07-30 00:45 | 2015-07-30 | 4 | 0 | 186 | 61 | 1
2015-07-30 01:00 | 2015-07-30 | 4 | 1 | 183 | 60.9333 | 1
2015-07-30 01:15 | 2015-07-30 | 4 | 1 | 187 | 60.6833 | 1
2015-07-30 01:30 | 2015-07-30 | 4 | 1 | 175 | 60.4333 | 1
2015-07-30 01:45 | 2015-07-30 | 4 | 1 | 191 | 60.1833 | 1
2015-07-30 02:00 | 2015-07-30 | 4 | 2 | 179 | 60.0755 | 1
2015-07-30 02:15 | 2015-07-30 | 4 | 2 | 169 | 60.3585 | 1
2015-07-30 02:30 | 2015-07-30 | 4 | 2 | 176 | 60.6415 | 1
2015-07-30 02:45 | 2015-07-30 | 4 | 2 | 177 | 60.9245 | 1
2015-07-30 03:00 | 2015-07-30 | 4 | 3 | 186 | 60.087 | 1
2015-07-30 03:15 | 2015-07-30 | 4 | 3 | 170 | 60.413 | 1
2015-07-30 03:30 | 2015-07-30 | 4 | 3 | 177 | 60.7391 | 1
2015-07-30 03:45 | 2015-07-30 | 4 | 3 | 175 | 61 | 1
2015-07-30 04:00 | 2015-07-30 | 4 | 4 | 172 | 60 | 1
2015-07-30 04:15 | 2015-07-30 | 4 | 4 | 184 | 60 | 1
2015-07-30 04:30 | 2015-07-30 | 4 | 4 | 173 | 60 | 1
2015-07-30 04:45 | 2015-07-30 | 4 | 4 | 171 | 60 | 1
2015-07-30 05:00 | 2015-07-30 | 4 | 5 | 171 | 60.069 | 1
2015-07-30 05:15 | 2015-07-30 | 4 | 5 | 191 | 60.3276 | 1
2015-07-30 05:30 | 2015-07-30 | 4 | 5 | 172 | 60.5862 | 1
2015-07-30 05:45 | 2015-07-30 | 4 | 5 | 169 | 60.8448 | 1
2015-07-30 06:00 | 2015-07-30 | 4 | 6 | 172 | 61.0667 | 1
2015-07-30 06:15 | 2015-07-30 | 4 | 6 | 174 | 61.3167 | 1
2015-07-30 06:30 | 2015-07-30 | 4 | 6 | 186 | 61.5667 | 1
2015-07-30 06:45 | 2015-07-30 | 4 | 6 | 174 | 61.8167 | 1
2015-07-30 07:00 | 2015-07-30 | 4 | 7 | 178 | 62.1333 | 1
2015-07-30 07:15 | 2015-07-30 | 4 | 7 | 182 | 62.6333 | 1
2015-07-30 07:30 | 2015-07-30 | 4 | 7 | 181 | 63.1333 | 1
2015-07-30 07:45 | 2015-07-30 | 4 | 7 | 180 | 63.6333 | 1
2015-07-30 08:00 | 2015-07-30 | 4 | 8 | 179 | 64.3077 | 1
2015-07-30 08:15 | 2015-07-30 | 4 | 8 | 182 | 65.4615 | 2
2015-07-30 08:30 | 2015-07-30 | 4 | 8 | 183 | 66.2353 | 2
2015-07-30 08:45 | 2015-07-30 | 4 | 8 | 194 | 66.6765 | 2
2015-07-30 09:00 | 2015-07-30 | 4 | 9 | 191 | 67.1333 | 2
2015-07-30 09:15 | 2015-07-30 | 4 | 9 | 184 | 67.6333 | 2
2015-07-30 09:30 | 2015-07-30 | 4 | 9 | 196 | 68.1333 | 2
2015-07-30 09:45 | 2015-07-30 | 4 | 9 | 201 | 68.6333 | 2
2015-07-30 10:00 | 2015-07-30 | 4 | 10 | 220 | 69.0667 | 2
2015-07-30 10:15 | 2015-07-30 | 4 | 10 | 200 | 69.3167 | 2
2015-07-30 10:30 | 2015-07-30 | 4 | 10 | 214 | 69.5667 | 2
2015-07-30 10:45 | 2015-07-30 | 4 | 10 | 207 | 69.8167 | 2
2015-07-30 11:00 | 2015-07-30 | 4 | 11 | 206 | 70 | 2
2015-07-30 11:15 | 2015-07-30 | 4 | 11 | 226 | 70 | 2
2015-07-30 11:30 | 2015-07-30 | 4 | 11 | 222 | 70 | 2
2015-07-30 11:45 | 2015-07-30 | 4 | 11 | 223 | 70 | 2
2015-07-30 12:00 | 2015-07-30 | 4 | 12 | 215 | 70.0667 | 3
2015-07-30 12:15 | 2015-07-30 | 4 | 12 | 221 | 70.3167 | 3
2015-07-30 12:30 | 2015-07-30 | 4 | 12 | 242 | 70.5667 | 3
2015-07-30 12:45 | 2015-07-30 | 4 | 12 | 215 | 70.8167 | 3
2015-07-30 13:00 | 2015-07-30 | 4 | 13 | 235 | 71.0667 | 3
2015-07-30 13:15 | 2015-07-30 | 4 | 13 | 232 | 71.3167 | 3
2015-07-30 13:30 | 2015-07-30 | 4 | 13 | 227 | 71.5667 | 3
2015-07-30 13:45 | 2015-07-30 | 4 | 13 | 229 | 71.8167 | 3
2015-07-30 14:00 | 2015-07-30 | 4 | 14 | 238 | 71.9333 | 3
2015-07-30 14:15 | 2015-07-30 | 4 | 14 | 239 | 71.6833 | 3
2015-07-30 14:30 | 2015-07-30 | 4 | 14 | 264 | 71.4333 | 3
2015-07-30 14:45 | 2015-07-30 | 4 | 14 | 233 | 71.1833 | 3
2015-07-30 15:00 | 2015-07-30 | 4 | 15 | 246 | 70.9333 | 3
2015-07-30 15:15 | 2015-07-30 | 4 | 15 | 244 | 70.6833 | 3
2015-07-30 15:30 | 2015-07-30 | 4 | 15 | 256 | 70.4333 | 3
2015-07-30 15:45 | 2015-07-30 | 4 | 15 | 250 | 70.1833 | 3
2015-07-30 16:00 | 2015-07-30 | 4 | 16 | 252 | 69.8667 | 2
2015-07-30 16:15 | 2015-07-30 | 4 | 16 | 263 | 69.3667 | 2
2015-07-30 16:30 | 2015-07-30 | 4 | 16 | 254 | 68.8667 | 2
2015-07-30 16:45 | 2015-07-30 | 4 | 16 | 238 | 68.3667 | 2
2015-07-30 17:00 | 2015-07-30 | 4 | 17 | 251 | 67.8667 | 2
2015-07-30 17:15 | 2015-07-30 | 4 | 17 | 257 | 67.3667 | 2
2015-07-30 17:30 | 2015-07-30 | 4 | 17 | 243 | 66.8667 | 2
2015-07-30 17:45 | 2015-07-30 | 4 | 17 | 272 | 66.3667 | 2
2015-07-30 18:00 | 2015-07-30 | 4 | 18 | 251 | 65.8667 | 2
2015-07-30 18:15 | 2015-07-30 | 4 | 18 | 254 | 65.3667 | 2
2015-07-30 18:30 | 2015-07-30 | 4 | 18 | 249 | 64.8667 | 1
2015-07-30 18:45 | 2015-07-30 | 4 | 18 | 254 | 64.3667 | 1
2015-07-30 19:00 | 2015-07-30 | 4 | 19 | 241 | 63.8667 | 1
2015-07-30 19:15 | 2015-07-30 | 4 | 19 | 235 | 63.3667 | 1
2015-07-30 19:30 | 2015-07-30 | 4 | 19 | 223 | 62.8667 | 1
2015-07-30 19:45 | 2015-07-30 | 4 | 19 | 226 | 62.3667 | 1
2015-07-30 20:00 | 2015-07-30 | 4 | 20 | 219 | 62 | 1
2015-07-30 20:15 | 2015-07-30 | 4 | 20 | 231 | 62 | 1
2015-07-30 20:30 | 2015-07-30 | 4 | 20 | 216 | 62 | 1
2015-07-30 20:45 | 2015-07-30 | 4 | 20 | 209 | 62 | 1
2015-07-30 21:00 | 2015-07-30 | 4 | 21 | 219 | 61.9333 | 1
2015-07-30 21:15 | 2015-07-30 | 4 | 21 | 211 | 61.6833 | 1
2015-07-30 21:30 | 2015-07-30 | 4 | 21 | 202 | 61.4333 | 1
2015-07-30 21:45 | 2015-07-30 | 4 | 21 | 194 | 61.1833 | 1
2015-07-30 22:00 | 2015-07-30 | 4 | 22 | 193 | 61 | 1
2015-07-30 22:15 | 2015-07-30 | 4 | 22 | 192 | 61 | 1
2015-07-30 22:30 | 2015-07-30 | 4 | 22 | 193 | 61 | 1
2015-07-30 22:45 | 2015-07-30 | 4 | 22 | 203 | 61 | 1
2015-07-30 23:00 | 2015-07-30 | 4 | 23 | 186 | 60.9333 | 1
2015-07-30 23:15 | 2015-07-30 | 4 | 23 | 192 | 60.6833 | 1
2015-07-30 23:30 | 2015-07-30 | 4 | 23 | 192 | 60.4333 | 1
2015-07-30 23:45 | 2015-07-30 | 4 | 23 | 199 | 60.1833 | 1
2015-07-31 | 2015-07-31 | 5 | 0 | 187 | 60 | 1
2015-07-31 00:15 | 2015-07-31 | 5 | 0 | 185 | 60 | 1
2015-07-31 00:30 | 2015-07-31 | 5 | 0 | 187 | 60 | 1
2015-07-31 00:45 | 2015-07-31 | 5 | 0 | 191 | 60 | 1
2015-07-31 01:00 | 2015-07-31 | 5 | 1 | 198 | 60 | 1
2015-07-31 01:15 | 2015-07-31 | 5 | 1 | 185 | 60 | 1
2015-07-31 01:30 | 2015-07-31 | 5 | 1 | 184 | 60 | 1
2015-07-31 01:45 | 2015-07-31 | 5 | 1 | 180 | 60 | 1
2015-07-31 02:00 | 2015-07-31 | 5 | 2 | 199 | 60 | 1
2015-07-31 02:15 | 2015-07-31 | 5 | 2 | 183 | 60 | 1
2015-07-31 02:30 | 2015-07-31 | 5 | 2 | 185 | 60 | 1
2015-07-31 02:45 | 2015-07-31 | 5 | 2 | 187 | 60 | 1
2015-07-31 03:00 | 2015-07-31 | 5 | 3 | 174 | 60.2667 | 1
2015-07-31 03:15 | 2015-07-31 | 5 | 3 | 176 | 60.9111 | 1
2015-07-31 03:30 | 2015-07-31 | 5 | 3 | 182 | 60.5778 | 1
2015-07-31 03:45 | 2015-07-31 | 5 | 3 | 190 | 60.2444 | 1
2015-07-31 04:00 | 2015-07-31 | 5 | 4 | 174 | 60.125 | 1
2015-07-31 04:15 | 2015-07-31 | 5 | 4 | 173 | 60.5938 | 1
2015-07-31 04:30 | 2015-07-31 | 5 | 4 | 166 | 60.9286 | 1
2015-07-31 04:45 | 2015-07-31 | 5 | 4 | 187 | 60.3929 | 1
2015-07-31 05:00 | 2015-07-31 | 5 | 5 | 180 | 60.0667 | 1
2015-07-31 05:15 | 2015-07-31 | 5 | 5 | 162 | 60.3167 | 1
2015-07-31 05:30 | 2015-07-31 | 5 | 5 | 167 | 60.5667 | 1
2015-07-31 05:45 | 2015-07-31 | 5 | 5 | 168 | 60.8167 | 1
2015-07-31 06:00 | 2015-07-31 | 5 | 6 | 183 | 61.0667 | 1
2015-07-31 06:15 | 2015-07-31 | 5 | 6 | 170 | 61.3167 | 1
2015-07-31 06:30 | 2015-07-31 | 5 | 6 | 183 | 61.5667 | 1
2015-07-31 06:45 | 2015-07-31 | 5 | 6 | 178 | 61.8167 | 1
2015-07-31 07:00 | 2015-07-31 | 5 | 7 | 178 | 62.2 | 1
2015-07-31 07:15 | 2015-07-31 | 5 | 7 | 195 | 62.95 | 1
2015-07-31 07:30 | 2015-07-31 | 5 | 7 | 180 | 63.7 | 1
2015-07-31 07:45 | 2015-07-31 | 5 | 7 | 181 | 64.45 | 1
2015-07-31 08:00 | 2015-07-31 | 5 | 8 | 184 | 65.1333 | 2
2015-07-31 08:15 | 2015-07-31 | 5 | 8 | 198 | 65.6333 | 2
2015-07-31 08:30 | 2015-07-31 | 5 | 8 | 183 | 66.1333 | 2
2015-07-31 08:45 | 2015-07-31 | 5 | 8 | 178 | 66.6333 | 2
2015-07-31 09:00 | 2015-07-31 | 5 | 9 | 173 | 66.8667 | 2
2015-07-31 09:15 | 2015-07-31 | 5 | 9 | 186 | 66.3667 | 2
2015-07-31 09:30 | 2015-07-31 | 5 | 9 | 202 | 65.8667 | 2
2015-07-31 09:45 | 2015-07-31 | 5 | 9 | 197 | 65.3667 | 2
2015-07-31 10:00 | 2015-07-31 | 5 | 10 | 215 | 65 | 1
2015-07-31 10:15 | 2015-07-31 | 5 | 10 | 204 | 65 | 1
2015-07-31 10:30 | 2015-07-31 | 5 | 10 | 194 | 65 | 1
2015-07-31 10:45 | 2015-07-31 | 5 | 10 | 197 | 65 | 1
2015-07-31 11:00 | 2015-07-31 | 5 | 11 | 216 | 65.2667 | 2
2015-07-31 11:15 | 2015-07-31 | 5 | 11 | 211 | 66.2667 | 2
2015-07-31 11:30 | 2015-07-31 | 5 | 11 | 205 | 67.2667 | 2
2015-07-31 11:45 | 2015-07-31 | 5 | 11 | 207 | 68.2667 | 2
2015-07-31 12:00 | 2015-07-31 | 5 | 12 | 207 | 69.1333 | 2
2015-07-31 12:15 | 2015-07-31 | 5 | 12 | 223 | 69.6333 | 2
2015-07-31 12:30 | 2015-07-31 | 5 | 12 | 229 | 70.1333 | 3
2015-07-31 12:45 | 2015-07-31 | 5 | 12 | 215 | 70.6333 | 3
2015-07-31 13:00 | 2015-07-31 | 5 | 13 | 206 | 71.0667 | 3
2015-07-31 13:15 | 2015-07-31 | 5 | 13 | 213 | 71.3167 | 3
2015-07-31 13:30 | 2015-07-31 | 5 | 13 | 227 | 71.5667 | 3
2015-07-31 13:45 | 2015-07-31 | 5 | 13 | 232 | 71.8167 | 3
2015-07-31 14:00 | 2015-07-31 | 5 | 14 | 223 | 71.9333 | 3
2015-07-31 14:15 | 2015-07-31 | 5 | 14 | 229 | 71.6833 | 3
2015-07-31 14:30 | 2015-07-31 | 5 | 14 | 228 | 71.4333 | 3
2015-07-31 14:45 | 2015-07-31 | 5 | 14 | 222 | 71.1833 | 3
2015-07-31 15:00 | 2015-07-31 | 5 | 15 | 229 | 70.9333 | 3
2015-07-31 15:15 | 2015-07-31 | 5 | 15 | 231 | 70.6833 | 3
2015-07-31 15:30 | 2015-07-31 | 5 | 15 | 251 | 70.4333 | 3
2015-07-31 15:45 | 2015-07-31 | 5 | 15 | 216 | 70.1833 | 3
2015-07-31 16:00 | 2015-07-31 | 5 | 16 | 231 | 69.8667 | 2
2015-07-31 16:15 | 2015-07-31 | 5 | 16 | 224 | 69.3667 | 2
2015-07-31 16:30 | 2015-07-31 | 5 | 16 | 240 | 68.8667 | 2
2015-07-31 16:45 | 2015-07-31 | 5 | 16 | 232 | 68.3667 | 2
2015-07-31 17:00 | 2015-07-31 | 5 | 17 | 226 | 67.8 | 2
2015-07-31 17:15 | 2015-07-31 | 5 | 17 | 239 | 67.05 | 2
2015-07-31 17:30 | 2015-07-31 | 5 | 17 | 231 | 66.3 | 2
2015-07-31 17:45 | 2015-07-31 | 5 | 17 | 243 | 65.55 | 2
2015-07-31 18:00 | 2015-07-31 | 5 | 18 | 222 | 64.8974 | 1
2015-07-31 18:15 | 2015-07-31 | 5 | 18 | 229 | 64.5128 | 1
2015-07-31 18:30 | 2015-07-31 | 5 | 18 | 219 | 64.1282 | 1
2015-07-31 18:45 | 2015-07-31 | 5 | 18 | 219 | 64.4762 | 1
2015-07-31 19:00 | 2015-07-31 | 5 | 19 | 236 | 64.7333 | 1
2015-07-31 19:15 | 2015-07-31 | 5 | 19 | 228 | 64 | 1
2015-07-31 19:30 | 2015-07-31 | 5 | 19 | 216 | 64 | 1
2015-07-31 19:45 | 2015-07-31 | 5 | 19 | 218 | 64 | 1
2015-07-31 20:00 | 2015-07-31 | 5 | 20 | 229 | 64 | 1
2015-07-31 20:15 | 2015-07-31 | 5 | 20 | 211 | 64 | 1
2015-07-31 20:30 | 2015-07-31 | 5 | 20 | 206 | 64 | 1
2015-07-31 20:45 | 2015-07-31 | 5 | 20 | 207 | 64 | 1
2015-07-31 21:00 | 2015-07-31 | 5 | 21 | 204 | 64 | 1
2015-07-31 21:15 | 2015-07-31 | 5 | 21 | 194 | 64 | 1
2015-07-31 21:30 | 2015-07-31 | 5 | 21 | 198 | 64 | 1
2015-07-31 21:45 | 2015-07-31 | 5 | 21 | 178 | 64 | 1
2015-07-31 22:00 | 2015-07-31 | 5 | 22 | 188 | 63.913 | 1
2015-07-31 22:15 | 2015-07-31 | 5 | 22 | 180 | 63.587 | 1
2015-07-31 22:30 | 2015-07-31 | 5 | 22 | 190 | 63.2609 | 1
2015-07-31 22:45 | 2015-07-31 | 5 | 22 | 196 | 63 | 1
2015-07-31 23:00 | 2015-07-31 | 5 | 23 | 182 | 63 | 1
2015-07-31 23:15 | 2015-07-31 | 5 | 23 | 200 | 63 | 1
2015-07-31 23:30 | 2015-07-31 | 5 | 23 | 180 | 63 | 1
2015-07-31 23:45 | 2015-07-31 | 5 | 23 | 176 | 63 | 1
2015-08-01 | 2015-08-01 | 6 | 0 | 173 | 63 | 1
2015-08-01 00:15 | 2015-08-01 | 6 | 0 | 179 | 63 | 1
2015-08-01 00:30 | 2015-08-01 | 6 | 0 | 170 | 63 | 1
2015-08-01 00:45 | 2015-08-01 | 6 | 0 | 162 | 63 | 1
2015-08-01 01:00 | 2015-08-01 | 6 | 1 | 164 | 63 | 1
2015-08-01 01:15 | 2015-08-01 | 6 | 1 | 152 | 63 | 1
2015-08-01 01:30 | 2015-08-01 | 6 | 1 | 174 | 63 | 1
2015-08-01 01:45 | 2015-08-01 | 6 | 1 | 168 | 63 | 1
2015-08-01 02:00 | 2015-08-01 | 6 | 2 | 156 | 62.9333 | 1
2015-08-01 02:15 | 2015-08-01 | 6 | 2 | 156 | 62.6833 | 1
2015-08-01 02:30 | 2015-08-01 | 6 | 2 | 172 | 62.4333 | 1
2015-08-01 02:45 | 2015-08-01 | 6 | 2 | 167 | 62.1833 | 1
2015-08-01 03:00 | 2015-08-01 | 6 | 3 | 159 | 62.0816 | 1
2015-08-01 03:15 | 2015-08-01 | 6 | 3 | 158 | 62.3878 | 1
2015-08-01 03:30 | 2015-08-01 | 6 | 3 | 157 | 62.6939 | 1
2015-08-01 03:45 | 2015-08-01 | 6 | 3 | 173 | 63 | 1
2015-08-01 04:00 | 2015-08-01 | 6 | 4 | 158 | 62.125 | 1
2015-08-01 04:15 | 2015-08-01 | 6 | 4 | 157 | 62.5938 | 1
2015-08-01 04:30 | 2015-08-01 | 6 | 4 | 156 | 62.9286 | 1
2015-08-01 04:45 | 2015-08-01 | 6 | 4 | 166 | 62.3929 | 1
2015-08-01 05:00 | 2015-08-01 | 6 | 5 | 165 | 62.0667 | 1
2015-08-01 05:15 | 2015-08-01 | 6 | 5 | 158 | 62.3167 | 1
2015-08-01 05:30 | 2015-08-01 | 6 | 5 | 154 | 62.5667 | 1
2015-08-01 05:45 | 2015-08-01 | 6 | 5 | 148 | 62.8167 | 1
2015-08-01 06:00 | 2015-08-01 | 6 | 6 | 167 | 63.1333 | 1
2015-08-01 06:15 | 2015-08-01 | 6 | 6 | 157 | 63.6333 | 1
2015-08-01 06:30 | 2015-08-01 | 6 | 6 | 151 | 64.1333 | 1
2015-08-01 06:45 | 2015-08-01 | 6 | 6 | 148 | 64.6333 | 1
2015-08-01 07:00 | 2015-08-01 | 6 | 7 | 167 | 65.1333 | 2
2015-08-01 07:15 | 2015-08-01 | 6 | 7 | 164 | 65.6333 | 2
2015-08-01 07:30 | 2015-08-01 | 6 | 7 | 154 | 66.1333 | 2
2015-08-01 07:45 | 2015-08-01 | 6 | 7 | 157 | 66.6333 | 2
2015-08-01 08:00 | 2015-08-01 | 6 | 8 | 154 | 67.1333 | 2
2015-08-01 08:15 | 2015-08-01 | 6 | 8 | 169 | 67.6333 | 2
2015-08-01 08:30 | 2015-08-01 | 6 | 8 | 158 | 68.1333 | 2
2015-08-01 08:45 | 2015-08-01 | 6 | 8 | 154 | 68.6333 | 2
2015-08-01 09:00 | 2015-08-01 | 6 | 9 | 155 | 69.0667 | 2
2015-08-01 09:15 | 2015-08-01 | 6 | 9 | 162 | 69.3167 | 2
2015-08-01 09:30 | 2015-08-01 | 6 | 9 | 167 | 69.5667 | 2
2015-08-01 09:45 | 2015-08-01 | 6 | 9 | 157 | 69.8167 | 2
2015-08-01 10:00 | 2015-08-01 | 6 | 10 | 160 | 70.1333 | 3
2015-08-01 10:15 | 2015-08-01 | 6 | 10 | 161 | 70.6333 | 3
2015-08-01 10:30 | 2015-08-01 | 6 | 10 | 169 | 71.1333 | 3
2015-08-01 10:45 | 2015-08-01 | 6 | 10 | 179 | 71.6333 | 3
2015-08-01 11:00 | 2015-08-01 | 6 | 11 | 163 | 72.0667 | 3
2015-08-01 11:15 | 2015-08-01 | 6 | 11 | 173 | 72.3167 | 3
2015-08-01 11:30 | 2015-08-01 | 6 | 11 | 172 | 72.5667 | 3
2015-08-01 11:45 | 2015-08-01 | 6 | 11 | 196 | 72.8167 | 3
2015-08-01 12:00 | 2015-08-01 | 6 | 12 | 178 | 73 | 3
2015-08-01 12:15 | 2015-08-01 | 6 | 12 | 180 | 73 | 3
2015-08-01 12:30 | 2015-08-01 | 6 | 12 | 176 | 73 | 3
2015-08-01 12:45 | 2015-08-01 | 6 | 12 | 179 | 73 | 3
2015-08-01 13:00 | 2015-08-01 | 6 | 13 | 195 | 73.1333 | 3
2015-08-01 13:15 | 2015-08-01 | 6 | 13 | 177 | 73.6333 | 3
2015-08-01 13:30 | 2015-08-01 | 6 | 13 | 182 | 74.1333 | 3
2015-08-01 13:45 | 2015-08-01 | 6 | 13 | 177 | 74.6333 | 3
2015-08-01 14:00 | 2015-08-01 | 6 | 14 | 191 | 74.8667 | 3
2015-08-01 14:15 | 2015-08-01 | 6 | 14 | 191 | 74.3667 | 3
2015-08-01 14:30 | 2015-08-01 | 6 | 14 | 188 | 73.8667 | 3
2015-08-01 14:45 | 2015-08-01 | 6 | 14 | 188 | 73.3667 | 3
2015-08-01 15:00 | 2015-08-01 | 6 | 15 | 186 | 73 | 3
2015-08-01 15:15 | 2015-08-01 | 6 | 15 | 185 | 73 | 3
2015-08-01 15:30 | 2015-08-01 | 6 | 15 | 207 | 73 | 3
2015-08-01 15:45 | 2015-08-01 | 6 | 15 | 193 | 73 | 3
2015-08-01 16:00 | 2015-08-01 | 6 | 16 | 198 | 72.8667 | 3
2015-08-01 16:15 | 2015-08-01 | 6 | 16 | 188 | 72.3667 | 3
2015-08-01 16:30 | 2015-08-01 | 6 | 16 | 189 | 71.8667 | 3
2015-08-01 16:45 | 2015-08-01 | 6 | 16 | 210 | 71.3667 | 3
2015-08-01 17:00 | 2015-08-01 | 6 | 17 | 196 | 70.9333 | 3
2015-08-01 17:15 | 2015-08-01 | 6 | 17 | 209 | 70.6833 | 3
2015-08-01 17:30 | 2015-08-01 | 6 | 17 | 202 | 70.4333 | 3
2015-08-01 17:45 | 2015-08-01 | 6 | 17 | 203 | 70.1833 | 3
2015-08-01 18:00 | 2015-08-01 | 6 | 18 | 194 | 69.8 | 2
2015-08-01 18:15 | 2015-08-01 | 6 | 18 | 194 | 69.05 | 2
2015-08-01 18:30 | 2015-08-01 | 6 | 18 | 214 | 68.3 | 2
2015-08-01 18:45 | 2015-08-01 | 6 | 18 | 201 | 67.55 | 2
2015-08-01 19:00 | 2015-08-01 | 6 | 19 | 193 | 66.9333 | 2
2015-08-01 19:15 | 2015-08-01 | 6 | 19 | 195 | 66.6833 | 2
2015-08-01 19:30 | 2015-08-01 | 6 | 19 | 190 | 66.4333 | 2
2015-08-01 19:45 | 2015-08-01 | 6 | 19 | 203 | 66.1833 | 2
2015-08-01 20:00 | 2015-08-01 | 6 | 20 | 179 | 66 | 2
2015-08-01 20:15 | 2015-08-01 | 6 | 20 | 185 | 66 | 2
2015-08-01 20:30 | 2015-08-01 | 6 | 20 | 178 | 66 | 2
2015-08-01 20:45 | 2015-08-01 | 6 | 20 | 194 | 66 | 2
2015-08-01 21:00 | 2015-08-01 | 6 | 21 | 181 | 65.8667 | 2
2015-08-01 21:15 | 2015-08-01 | 6 | 21 | 183 | 65.3667 | 2
2015-08-01 21:30 | 2015-08-01 | 6 | 21 | 173 | 64.8667 | 1
2015-08-01 21:45 | 2015-08-01 | 6 | 21 | 175 | 64.3667 | 1
2015-08-01 22:00 | 2015-08-01 | 6 | 22 | 182 | 64 | 1
2015-08-01 22:15 | 2015-08-01 | 6 | 22 | 179 | 64 | 1
2015-08-01 22:30 | 2015-08-01 | 6 | 22 | 168 | 64 | 1
2015-08-01 22:45 | 2015-08-01 | 6 | 22 | 165 | 64 | 1
2015-08-01 23:00 | 2015-08-01 | 6 | 23 | 177 | 63.9333 | 1
2015-08-01 23:15 | 2015-08-01 | 6 | 23 | 181 | 63.6833 | 1
2015-08-01 23:30 | 2015-08-01 | 6 | 23 | 163 | 63.4333 | 1
2015-08-01 23:45 | 2015-08-01 | 6 | 23 | 177 | 63.1833 | 1
2015-08-02 | 2015-08-02 | 7 | 0 | 169 | 63 | 1
2015-08-02 00:15 | 2015-08-02 | 7 | 0 | 170 | 63 | 1
2015-08-02 00:30 | 2015-08-02 | 7 | 0 | 170 | 63 | 1
2015-08-02 00:45 | 2015-08-02 | 7 | 0 | 166 | 63 | 1
2015-08-02 01:00 | 2015-08-02 | 7 | 1 | 163 | 63 | 1
2015-08-02 01:15 | 2015-08-02 | 7 | 1 | 167 | 63 | 1
2015-08-02 01:30 | 2015-08-02 | 7 | 1 | 175 | 63 | 1
2015-08-02 01:45 | 2015-08-02 | 7 | 1 | 166 | 63 | 1
2015-08-02 02:00 | 2015-08-02 | 7 | 2 | 160 | 63 | 1
2015-08-02 02:15 | 2015-08-02 | 7 | 2 | 162 | 63 | 1
2015-08-02 02:30 | 2015-08-02 | 7 | 2 | 177 | 63 | 1
2015-08-02 02:45 | 2015-08-02 | 7 | 2 | 164 | 63 | 1
2015-08-02 03:00 | 2015-08-02 | 7 | 3 | 158 | 62.9333 | 1
2015-08-02 03:15 | 2015-08-02 | 7 | 3 | 159 | 62.6833 | 1
2015-08-02 03:30 | 2015-08-02 | 7 | 3 | 163 | 62.4333 | 1
2015-08-02 03:45 | 2015-08-02 | 7 | 3 | 171 | 62.1833 | 1
2015-08-02 04:00 | 2015-08-02 | 7 | 4 | 157 | 62 | 1
2015-08-02 04:15 | 2015-08-02 | 7 | 4 | 162 | 62 | 1
2015-08-02 04:30 | 2015-08-02 | 7 | 4 | 159 | 62 | 1
2015-08-02 04:45 | 2015-08-02 | 7 | 4 | 154 | 62 | 1
2015-08-02 05:00 | 2015-08-02 | 7 | 5 | 173 | 62 | 1
2015-08-02 05:15 | 2015-08-02 | 7 | 5 | 158 | 62 | 1
2015-08-02 05:30 | 2015-08-02 | 7 | 5 | 156 | 62 | 1
2015-08-02 05:45 | 2015-08-02 | 7 | 5 | 153 | 62 | 1
2015-08-02 06:00 | 2015-08-02 | 7 | 6 | 168 | 62 | 1
2015-08-02 06:15 | 2015-08-02 | 7 | 6 | 172 | 62 | 1
2015-08-02 06:30 | 2015-08-02 | 7 | 6 | 165 | 62 | 1
2015-08-02 06:45 | 2015-08-02 | 7 | 6 | 164 | 62 | 1
2015-08-02 07:00 | 2015-08-02 | 7 | 7 | 163 | 62.0667 | 1
2015-08-02 07:15 | 2015-08-02 | 7 | 7 | 182 | 62.3167 | 1
2015-08-02 07:30 | 2015-08-02 | 7 | 7 | 163 | 62.5667 | 1
2015-08-02 07:45 | 2015-08-02 | 7 | 7 | 162 | 62.8167 | 1
2015-08-02 08:00 | 2015-08-02 | 7 | 8 | 160 | 63 | 1
2015-08-02 08:15 | 2015-08-02 | 7 | 8 | 160 | 63 | 1
2015-08-02 08:30 | 2015-08-02 | 7 | 8 | 169 | 63 | 1
2015-08-02 08:45 | 2015-08-02 | 7 | 8 | 157 | 63 | 1
2015-08-02 09:00 | 2015-08-02 | 7 | 9 | 159 | 63.1333 | 1
2015-08-02 09:15 | 2015-08-02 | 7 | 9 | 156 | 63.6333 | 1
2015-08-02 09:30 | 2015-08-02 | 7 | 9 | 161 | 64.1333 | 1
2015-08-02 09:45 | 2015-08-02 | 7 | 9 | 173 | 64.6333 | 1
2015-08-02 10:00 | 2015-08-02 | 7 | 10 | 157 | 65.2 | 2
2015-08-02 10:15 | 2015-08-02 | 7 | 10 | 155 | 65.95 | 2
2015-08-02 10:30 | 2015-08-02 | 7 | 10 | 156 | 66.7 | 2
2015-08-02 10:45 | 2015-08-02 | 7 | 10 | 177 | 67.45 | 2
2015-08-02 11:00 | 2015-08-02 | 7 | 11 | 169 | 68 | 2
2015-08-02 11:15 | 2015-08-02 | 7 | 11 | 173 | 68 | 2
2015-08-02 11:30 | 2015-08-02 | 7 | 11 | 164 | 68 | 2
2015-08-02 11:45 | 2015-08-02 | 7 | 11 | 187 | 68 | 2
2015-08-02 12:00 | 2015-08-02 | 7 | 12 | 182 | 68.1333 | 2
2015-08-02 12:15 | 2015-08-02 | 7 | 12 | 175 | 68.6333 | 2
2015-08-02 12:30 | 2015-08-02 | 7 | 12 | 178 | 69.1333 | 2
2015-08-02 12:45 | 2015-08-02 | 7 | 12 | 181 | 69.6333 | 2
2015-08-02 13:00 | 2015-08-02 | 7 | 13 | 188 | 70.0667 | 3
2015-08-02 13:15 | 2015-08-02 | 7 | 13 | 178 | 70.3167 | 3
2015-08-02 13:30 | 2015-08-02 | 7 | 13 | 178 | 70.5667 | 3
2015-08-02 13:45 | 2015-08-02 | 7 | 13 | 174 | 70.8167 | 3
2015-08-02 14:00 | 2015-08-02 | 7 | 14 | 186 | 70.9333 | 3
2015-08-02 14:15 | 2015-08-02 | 7 | 14 | 198 | 70.6833 | 3
2015-08-02 14:30 | 2015-08-02 | 7 | 14 | 178 | 70.4333 | 3
2015-08-02 14:45 | 2015-08-02 | 7 | 14 | 189 | 70.1833 | 3
2015-08-02 15:00 | 2015-08-02 | 7 | 15 | 186 | 70 | 2
2015-08-02 15:15 | 2015-08-02 | 7 | 15 | 206 | 70 | 2
2015-08-02 15:30 | 2015-08-02 | 7 | 15 | 191 | 70 | 2
2015-08-02 15:45 | 2015-08-02 | 7 | 15 | 188 | 70 | 2
2015-08-02 16:00 | 2015-08-02 | 7 | 16 | 191 | 69.9333 | 2
2015-08-02 16:15 | 2015-08-02 | 7 | 16 | 185 | 69.6833 | 2
2015-08-02 16:30 | 2015-08-02 | 7 | 16 | 196 | 69.4333 | 2
2015-08-02 16:45 | 2015-08-02 | 7 | 16 | 203 | 69.1833 | 2
2015-08-02 17:00 | 2015-08-02 | 7 | 17 | 198 | 68.8667 | 2
2015-08-02 17:15 | 2015-08-02 | 7 | 17 | 191 | 68.3667 | 2
2015-08-02 17:30 | 2015-08-02 | 7 | 17 | 194 | 67.8667 | 2
2015-08-02 17:45 | 2015-08-02 | 7 | 17 | 200 | 67.3667 | 2
2015-08-02 18:00 | 2015-08-02 | 7 | 18 | 210 | 66.9333 | 2
2015-08-02 18:15 | 2015-08-02 | 7 | 18 | 196 | 66.6833 | 2
2015-08-02 18:30 | 2015-08-02 | 7 | 18 | 208 | 66.4333 | 2
2015-08-02 18:45 | 2015-08-02 | 7 | 18 | 200 | 66.1833 | 2
2015-08-02 19:00 | 2015-08-02 | 7 | 19 | 192 | 65.9333 | 2
2015-08-02 19:15 | 2015-08-02 | 7 | 19 | 198 | 65.6833 | 2
2015-08-02 19:30 | 2015-08-02 | 7 | 19 | 188 | 65.4333 | 2
2015-08-02 19:45 | 2015-08-02 | 7 | 19 | 208 | 65.1833 | 2
2015-08-02 20:00 | 2015-08-02 | 7 | 20 | 180 | 64.9333 | 1
2015-08-02 20:15 | 2015-08-02 | 7 | 20 | 185 | 64.6833 | 1
2015-08-02 20:30 | 2015-08-02 | 7 | 20 | 182 | 64.4333 | 1
2015-08-02 20:45 | 2015-08-02 | 7 | 20 | 175 | 64.1833 | 1
2015-08-02 21:00 | 2015-08-02 | 7 | 21 | 189 | 63.9333 | 1
2015-08-02 21:15 | 2015-08-02 | 7 | 21 | 179 | 63.6833 | 1
2015-08-02 21:30 | 2015-08-02 | 7 | 21 | 167 | 63.4333 | 1
2015-08-02 21:45 | 2015-08-02 | 7 | 21 | 173 | 63.1833 | 1
2015-08-02 22:00 | 2015-08-02 | 7 | 22 | 177 | 63 | 1
2015-08-02 22:15 | 2015-08-02 | 7 | 22 | 175 | 63 | 1
2015-08-02 22:30 | 2015-08-02 | 7 | 22 | 168 | 63 | 1
2015-08-02 22:45 | 2015-08-02 | 7 | 22 | 163 | 63 | 1
2015-08-02 23:00 | 2015-08-02 | 7 | 23 | 161 | 63 | 1
2015-08-02 23:15 | 2015-08-02 | 7 | 23 | 182 | 63 | 1
2015-08-02 23:30 | 2015-08-02 | 7 | 23 | 162 | 63 | 1
2015-08-02 23:45 | 2015-08-02 | 7 | 23 | 161 | 63 | 1
2015-08-03 | 2015-08-03 | 1 | 0 | 160 | 63 | 1
2015-08-03 00:15 | 2015-08-03 | 1 | 0 | 173 | 63 | 1
2015-08-03 00:30 | 2015-08-03 | 1 | 0 | 155 | 63 | 1
2015-08-03 00:45 | 2015-08-03 | 1 | 0 | 159 | 63 | 1
2015-08-03 01:00 | 2015-08-03 | 1 | 1 | 158 | 64 | 1
2015-08-03 01:15 | 2015-08-03 | 1 | 1 | 159 | 64 | 1
2015-08-03 01:30 | 2015-08-03 | 1 | 1 | 170 | 64 | 1
2015-08-03 01:45 | 2015-08-03 | 1 | 1 | 153 | 64 | 1
2015-08-03 02:00 | 2015-08-03 | 1 | 2 | 147 | 64 | 1
2015-08-03 02:15 | 2015-08-03 | 1 | 2 | 152 | 64 | 1
2015-08-03 02:30 | 2015-08-03 | 1 | 2 | 160 | 64 | 1
2015-08-03 02:45 | 2015-08-03 | 1 | 2 | 164 | 64 | 1
2015-08-03 03:00 | 2015-08-03 | 1 | 3 | 150 | 63.9333 | 1
2015-08-03 03:15 | 2015-08-03 | 1 | 3 | 153 | 63.6833 | 1
2015-08-03 03:30 | 2015-08-03 | 1 | 3 | 151 | 63.4333 | 1
2015-08-03 03:45 | 2015-08-03 | 1 | 3 | 162 | 63.1833 | 1
2015-08-03 04:00 | 2015-08-03 | 1 | 4 | 154 | 63.0667 | 1
2015-08-03 04:15 | 2015-08-03 | 1 | 4 | 149 | 63.3167 | 1
2015-08-03 04:30 | 2015-08-03 | 1 | 4 | 143 | 63.5667 | 1
2015-08-03 04:45 | 2015-08-03 | 1 | 4 | 153 | 63.8167 | 1
2015-08-03 05:00 | 2015-08-03 | 1 | 5 | 170 | 64 | 1
2015-08-03 05:15 | 2015-08-03 | 1 | 5 | 146 | 64 | 1
2015-08-03 05:30 | 2015-08-03 | 1 | 5 | 152 | 64 | 1
2015-08-03 05:45 | 2015-08-03 | 1 | 5 | 152 | 64 | 1
2015-08-03 06:00 | 2015-08-03 | 1 | 6 | 152 | 64 | 1
2015-08-03 06:15 | 2015-08-03 | 1 | 6 | 170 | 64 | 1
2015-08-03 06:30 | 2015-08-03 | 1 | 6 | 150 | 64 | 1
2015-08-03 06:45 | 2015-08-03 | 1 | 6 | 152 | 64 | 1
2015-08-03 07:00 | 2015-08-03 | 1 | 7 | 148 | 64.0667 | 1
2015-08-03 07:15 | 2015-08-03 | 1 | 7 | 161 | 64.3167 | 1
2015-08-03 07:30 | 2015-08-03 | 1 | 7 | 160 | 64.5667 | 1
2015-08-03 07:45 | 2015-08-03 | 1 | 7 | 154 | 64.8167 | 1
2015-08-03 08:00 | 2015-08-03 | 1 | 8 | 158 | 65.1176 | 2
2015-08-03 08:15 | 2015-08-03 | 1 | 8 | 159 | 65.5588 | 2
2015-08-03 08:30 | 2015-08-03 | 1 | 8 | 180 | 66 | 2
2015-08-03 08:45 | 2015-08-03 | 1 | 8 | 181 | 67.1538 | 2
2015-08-03 09:00 | 2015-08-03 | 1 | 9 | 173 | 68.0667 | 2
2015-08-03 09:15 | 2015-08-03 | 1 | 9 | 170 | 68.3167 | 2
2015-08-03 09:30 | 2015-08-03 | 1 | 9 | 181 | 68.5667 | 2
2015-08-03 09:45 | 2015-08-03 | 1 | 9 | 192 | 68.8167 | 2
2015-08-03 10:00 | 2015-08-03 | 1 | 10 | 189 | 69 | 2
2015-08-03 10:15 | 2015-08-03 | 1 | 10 | 188 | 69 | 2
2015-08-03 10:30 | 2015-08-03 | 1 | 10 | 197 | 69 | 2
2015-08-03 10:45 | 2015-08-03 | 1 | 10 | 191 | 69 | 2
2015-08-03 11:00 | 2015-08-03 | 1 | 11 | 213 | 69.1333 | 2
2015-08-03 11:15 | 2015-08-03 | 1 | 11 | 196 | 69.6333 | 2
2015-08-03 11:30 | 2015-08-03 | 1 | 11 | 202 | 70.1333 | 3
2015-08-03 11:45 | 2015-08-03 | 1 | 11 | 204 | 70.6333 | 3
2015-08-03 12:00 | 2015-08-03 | 1 | 12 | 195 | 71.0667 | 3
2015-08-03 12:15 | 2015-08-03 | 1 | 12 | 218 | 71.3167 | 3
2015-08-03 12:30 | 2015-08-03 | 1 | 12 | 204 | 71.5667 | 3
2015-08-03 12:45 | 2015-08-03 | 1 | 12 | 196 | 71.8167 | 3
2015-08-03 13:00 | 2015-08-03 | 1 | 13 | 203 | 72.0667 | 3
2015-08-03 13:15 | 2015-08-03 | 1 | 13 | 206 | 72.3167 | 3
2015-08-03 13:30 | 2015-08-03 | 1 | 13 | 221 | 72.5667 | 3
2015-08-03 13:45 | 2015-08-03 | 1 | 13 | 202 | 72.8167 | 3
2015-08-03 14:00 | 2015-08-03 | 1 | 14 | 210 | 72.9333 | 3
2015-08-03 14:15 | 2015-08-03 | 1 | 14 | 212 | 72.6833 | 3
2015-08-03 14:30 | 2015-08-03 | 1 | 14 | 218 | 72.4333 | 3
2015-08-03 14:45 | 2015-08-03 | 1 | 14 | 226 | 72.1833 | 3
2015-08-03 15:00 | 2015-08-03 | 1 | 15 | 211 | 72 | 3
2015-08-03 15:15 | 2015-08-03 | 1 | 15 | 218 | 72 | 3
2015-08-03 15:30 | 2015-08-03 | 1 | 15 | 219 | 72 | 3
2015-08-03 15:45 | 2015-08-03 | 1 | 15 | 221 | 72 | 3
2015-08-03 16:00 | 2015-08-03 | 1 | 16 | 231 | 71.8667 | 3
2015-08-03 16:15 | 2015-08-03 | 1 | 16 | 239 | 71.3667 | 3
2015-08-03 16:30 | 2015-08-03 | 1 | 16 | 222 | 70.8667 | 3
2015-08-03 16:45 | 2015-08-03 | 1 | 16 | 218 | 70.3667 | 3
2015-08-03 17:00 | 2015-08-03 | 1 | 17 | 240 | 69.9333 | 2
2015-08-03 17:15 | 2015-08-03 | 1 | 17 | 240 | 69.6833 | 2
2015-08-03 17:30 | 2015-08-03 | 1 | 17 | 221 | 69.4333 | 2
2015-08-03 17:45 | 2015-08-03 | 1 | 17 | 228 | 69.1833 | 2
2015-08-03 18:00 | 2015-08-03 | 1 | 18 | 225 | 68.8667 | 2
2015-08-03 18:15 | 2015-08-03 | 1 | 18 | 228 | 68.3667 | 2
2015-08-03 18:30 | 2015-08-03 | 1 | 18 | 248 | 67.8667 | 2
2015-08-03 18:45 | 2015-08-03 | 1 | 18 | 216 | 67.3667 | 2
2015-08-03 19:00 | 2015-08-03 | 1 | 19 | 220 | 66.9333 | 2
2015-08-03 19:15 | 2015-08-03 | 1 | 19 | 218 | 66.6833 | 2
2015-08-03 19:30 | 2015-08-03 | 1 | 19 | 215 | 66.4333 | 2
2015-08-03 19:45 | 2015-08-03 | 1 | 19 | 229 | 66.1833 | 2
2015-08-03 20:00 | 2015-08-03 | 1 | 20 | 209 | 65.9333 | 2
2015-08-03 20:15 | 2015-08-03 | 1 | 20 | 217 | 65.6833 | 2
2015-08-03 20:30 | 2015-08-03 | 1 | 20 | 210 | 65.4333 | 2
2015-08-03 20:45 | 2015-08-03 | 1 | 20 | 201 | 65.1833 | 2
2015-08-03 21:00 | 2015-08-03 | 1 | 21 | 201 | 65 | 1
2015-08-03 21:15 | 2015-08-03 | 1 | 21 | 199 | 65 | 1
2015-08-03 21:30 | 2015-08-03 | 1 | 21 | 195 | 65 | 1
2015-08-03 21:45 | 2015-08-03 | 1 | 21 | 189 | 65 | 1
2015-08-03 22:00 | 2015-08-03 | 1 | 22 | 183 | 65 | 1
2015-08-03 22:15 | 2015-08-03 | 1 | 22 | 185 | 65 | 1
2015-08-03 22:30 | 2015-08-03 | 1 | 22 | 199 | 65 | 1
2015-08-03 22:45 | 2015-08-03 | 1 | 22 | 173 | 65 | 1
2015-08-03 23:00 | 2015-08-03 | 1 | 23 | 176 | 64.9333 | 1
2015-08-03 23:15 | 2015-08-03 | 1 | 23 | 171 | 64.6833 | 1
2015-08-03 23:30 | 2015-08-03 | 1 | 23 | 168 | 64.4333 | 1
2015-08-03 23:45 | 2015-08-03 | 1 | 23 | 171 | 64.1833 | 1
2015-08-04 | 2015-08-04 | 2 | 0 | 177 | 64 | 1
2015-08-04 00:15 | 2015-08-04 | 2 | 0 | 166 | 64 | 1
2015-08-04 00:30 | 2015-08-04 | 2 | 0 | 168 | 64 | 1
2015-08-04 00:45 | 2015-08-04 | 2 | 0 | 160 | 64 | 1
2015-08-04 01:00 | 2015-08-04 | 2 | 1 | 171 | 63.9333 | 1
2015-08-04 01:15 | 2015-08-04 | 2 | 1 | 166 | 63.6833 | 1
2015-08-04 01:30 | 2015-08-04 | 2 | 1 | 164 | 63.4333 | 1
2015-08-04 01:45 | 2015-08-04 | 2 | 1 | 158 | 63.1833 | 1
2015-08-04 02:00 | 2015-08-04 | 2 | 2 | 176 | 63 | 1
2015-08-04 02:15 | 2015-08-04 | 2 | 2 | 160 | 63 | 1
2015-08-04 02:30 | 2015-08-04 | 2 | 2 | 159 | 63 | 1
2015-08-04 02:45 | 2015-08-04 | 2 | 2 | 155 | 63 | 1
2015-08-04 03:00 | 2015-08-04 | 2 | 3 | 153 | 62.9333 | 1
2015-08-04 03:15 | 2015-08-04 | 2 | 3 | 162 | 62.6833 | 1
2015-08-04 03:30 | 2015-08-04 | 2 | 3 | 167 | 62.4333 | 1
2015-08-04 03:45 | 2015-08-04 | 2 | 3 | 154 | 62.1833 | 1
2015-08-04 04:00 | 2015-08-04 | 2 | 4 | 157 | 61.9333 | 1
2015-08-04 04:15 | 2015-08-04 | 2 | 4 | 154 | 61.6833 | 1
2015-08-04 04:30 | 2015-08-04 | 2 | 4 | 166 | 61.4333 | 1
2015-08-04 04:45 | 2015-08-04 | 2 | 4 | 158 | 61.1833 | 1
2015-08-04 05:00 | 2015-08-04 | 2 | 5 | 157 | 61.0667 | 1
2015-08-04 05:15 | 2015-08-04 | 2 | 5 | 154 | 61.3167 | 1
2015-08-04 05:30 | 2015-08-04 | 2 | 5 | 151 | 61.5667 | 1
2015-08-04 05:45 | 2015-08-04 | 2 | 5 | 170 | 61.8167 | 1
2015-08-04 06:00 | 2015-08-04 | 2 | 6 | 159 | 62.0667 | 1
2015-08-04 06:15 | 2015-08-04 | 2 | 6 | 153 | 62.3167 | 1
2015-08-04 06:30 | 2015-08-04 | 2 | 6 | 160 | 62.5667 | 1
2015-08-04 06:45 | 2015-08-04 | 2 | 6 | 155 | 62.8167 | 1
2015-08-04 07:00 | 2015-08-04 | 2 | 7 | 160 | 63.2 | 1
2015-08-04 07:15 | 2015-08-04 | 2 | 7 | 179 | 63.95 | 1
2015-08-04 07:30 | 2015-08-04 | 2 | 7 | 160 | 64.7 | 1
2015-08-04 07:45 | 2015-08-04 | 2 | 7 | 161 | 65.45 | 2
2015-08-04 08:00 | 2015-08-04 | 2 | 8 | 166 | 66 | 2
2015-08-04 08:15 | 2015-08-04 | 2 | 8 | 173 | 66 | 2
2015-08-04 08:30 | 2015-08-04 | 2 | 8 | 177 | 66 | 2
2015-08-04 08:45 | 2015-08-04 | 2 | 8 | 183 | 66 | 2
2015-08-04 09:00 | 2015-08-04 | 2 | 9 | 180 | 66.1333 | 2
2015-08-04 09:15 | 2015-08-04 | 2 | 9 | 182 | 66.6333 | 2
2015-08-04 09:30 | 2015-08-04 | 2 | 9 | 176 | 67.1333 | 2
2015-08-04 09:45 | 2015-08-04 | 2 | 9 | 191 | 67.6333 | 2
2015-08-04 10:00 | 2015-08-04 | 2 | 10 | 194 | 68 | 2
2015-08-04 10:15 | 2015-08-04 | 2 | 10 | 181 | 68 | 2
2015-08-04 10:30 | 2015-08-04 | 2 | 10 | 188 | 68 | 2
2015-08-04 10:45 | 2015-08-04 | 2 | 10 | 189 | 68 | 2
2015-08-04 11:00 | 2015-08-04 | 2 | 11 | 201 | 68.0667 | 2
2015-08-04 11:15 | 2015-08-04 | 2 | 11 | 192 | 68.3167 | 2
2015-08-04 11:30 | 2015-08-04 | 2 | 11 | 187 | 68.5667 | 2
2015-08-04 11:45 | 2015-08-04 | 2 | 11 | 195 | 68.8167 | 2
2015-08-04 12:00 | 2015-08-04 | 2 | 12 | 192 | 69.0667 | 2
2015-08-04 12:15 | 2015-08-04 | 2 | 12 | 216 | 69.3167 | 2
2015-08-04 12:30 | 2015-08-04 | 2 | 12 | 202 | 69.5667 | 2
2015-08-04 12:45 | 2015-08-04 | 2 | 12 | 198 | 69.8167 | 2
2015-08-04 13:00 | 2015-08-04 | 2 | 13 | 208 | 70.0667 | 3
2015-08-04 13:15 | 2015-08-04 | 2 | 13 | 201 | 70.3167 | 3
2015-08-04 13:30 | 2015-08-04 | 2 | 13 | 224 | 70.5667 | 3
2015-08-04 13:45 | 2015-08-04 | 2 | 13 | 216 | 70.8167 | 3
2015-08-04 14:00 | 2015-08-04 | 2 | 14 | 212 | 71 | 3
2015-08-04 14:15 | 2015-08-04 | 2 | 14 | 213 | 71 | 3
2015-08-04 14:30 | 2015-08-04 | 2 | 14 | 207 | 71 | 3
2015-08-04 14:45 | 2015-08-04 | 2 | 14 | 217 | 71 | 3
2015-08-04 15:00 | 2015-08-04 | 2 | 15 | 208 | 71.0667 | 3
2015-08-04 15:15 | 2015-08-04 | 2 | 15 | 203 | 71.3167 | 3
2015-08-04 15:30 | 2015-08-04 | 2 | 15 | 203 | 71.5667 | 3
2015-08-04 15:45 | 2015-08-04 | 2 | 15 | 214 | 71.8167 | 3
2015-08-04 16:00 | 2015-08-04 | 2 | 16 | 220 | 72 | 3
2015-08-04 16:15 | 2015-08-04 | 2 | 16 | 209 | 72 | 3
2015-08-04 16:30 | 2015-08-04 | 2 | 16 | 215 | 72 | 3
2015-08-04 16:45 | 2015-08-04 | 2 | 16 | 206 | 72 | 3
2015-08-04 17:00 | 2015-08-04 | 2 | 17 | 221 | 71.8667 | 3
2015-08-04 17:15 | 2015-08-04 | 2 | 17 | 236 | 71.3667 | 3
2015-08-04 17:30 | 2015-08-04 | 2 | 17 | 210 | 70.8667 | 3
2015-08-04 17:45 | 2015-08-04 | 2 | 17 | 229 | 70.3667 | 3
2015-08-04 18:00 | 2015-08-04 | 2 | 18 | 216 | 69.8667 | 2
2015-08-04 18:15 | 2015-08-04 | 2 | 18 | 214 | 69.3667 | 2
2015-08-04 18:30 | 2015-08-04 | 2 | 18 | 223 | 68.8667 | 2
2015-08-04 18:45 | 2015-08-04 | 2 | 18 | 221 | 68.3667 | 2
2015-08-04 19:00 | 2015-08-04 | 2 | 19 | 213 | 67.8667 | 2
2015-08-04 19:15 | 2015-08-04 | 2 | 19 | 209 | 67.3667 | 2
2015-08-04 19:30 | 2015-08-04 | 2 | 19 | 205 | 66.8667 | 2
2015-08-04 19:45 | 2015-08-04 | 2 | 19 | 213 | 66.3667 | 2
2015-08-04 20:00 | 2015-08-04 | 2 | 20 | 216 | 65.9333 | 2
2015-08-04 20:15 | 2015-08-04 | 2 | 20 | 201 | 65.6833 | 2
2015-08-04 20:30 | 2015-08-04 | 2 | 20 | 210 | 65.4333 | 2
2015-08-04 20:45 | 2015-08-04 | 2 | 20 | 197 | 65.1833 | 2
2015-08-04 21:00 | 2015-08-04 | 2 | 21 | 196 | 64.9333 | 1
2015-08-04 21:15 | 2015-08-04 | 2 | 21 | 185 | 64.6833 | 1
2015-08-04 21:30 | 2015-08-04 | 2 | 21 | 200 | 64.4333 | 1
2015-08-04 21:45 | 2015-08-04 | 2 | 21 | 189 | 64.1833 | 1
2015-08-04 22:00 | 2015-08-04 | 2 | 22 | 180 | 64 | 1
2015-08-04 22:15 | 2015-08-04 | 2 | 22 | 181 | 64 | 1
2015-08-04 22:30 | 2015-08-04 | 2 | 22 | 184 | 64 | 1
2015-08-04 22:45 | 2015-08-04 | 2 | 22 | 194 | 64 | 1
2015-08-04 23:00 | 2015-08-04 | 2 | 23 | 176 | 63.9333 | 1
2015-08-04 23:15 | 2015-08-04 | 2 | 23 | 181 | 63.6833 | 1
2015-08-04 23:30 | 2015-08-04 | 2 | 23 | 172 | 63.4333 | 1
2015-08-04 23:45 | 2015-08-04 | 2 | 23 | 185 | 63.1833 | 1
2015-08-05 | 2015-08-05 | 3 | 0 | 170 | 62.9333 | 1
2015-08-05 00:15 | 2015-08-05 | 3 | 0 | 168 | 62.6833 | 1
2015-08-05 00:30 | 2015-08-05 | 3 | 0 | 167 | 62.4333 | 1
2015-08-05 00:45 | 2015-08-05 | 3 | 0 | 169 | 62.1833 | 1
2015-08-05 01:00 | 2015-08-05 | 3 | 1 | 182 | 61.9333 | 1
2015-08-05 01:15 | 2015-08-05 | 3 | 1 | 162 | 61.6833 | 1
2015-08-05 01:30 | 2015-08-05 | 3 | 1 | 164 | 61.4333 | 1
2015-08-05 01:45 | 2015-08-05 | 3 | 1 | 156 | 61.1833 | 1
2015-08-05 02:00 | 2015-08-05 | 3 | 2 | 168 | 61 | 1
2015-08-05 02:15 | 2015-08-05 | 3 | 2 | 174 | 61 | 1
2015-08-05 02:30 | 2015-08-05 | 3 | 2 | 157 | 61 | 1
2015-08-05 02:45 | 2015-08-05 | 3 | 2 | 157 | 61 | 1
2015-08-05 03:00 | 2015-08-05 | 3 | 3 | 162 | 60.9333 | 1
2015-08-05 03:15 | 2015-08-05 | 3 | 3 | 158 | 60.6833 | 1
2015-08-05 03:30 | 2015-08-05 | 3 | 3 | 168 | 60.4333 | 1
2015-08-05 03:45 | 2015-08-05 | 3 | 3 | 160 | 60.1833 | 1
2015-08-05 04:00 | 2015-08-05 | 3 | 4 | 154 | 60.069 | 1
2015-08-05 04:15 | 2015-08-05 | 3 | 4 | 150 | 60.3276 | 1
2015-08-05 04:30 | 2015-08-05 | 3 | 4 | 162 | 60.5862 | 1
2015-08-05 04:45 | 2015-08-05 | 3 | 4 | 169 | 60.8448 | 1
2015-08-05 05:00 | 2015-08-05 | 3 | 5 | 155 | 60.0667 | 1
2015-08-05 05:15 | 2015-08-05 | 3 | 5 | 158 | 60.3167 | 1
2015-08-05 05:30 | 2015-08-05 | 3 | 5 | 156 | 60.5667 | 1
2015-08-05 05:45 | 2015-08-05 | 3 | 5 | 165 | 60.8167 | 1
2015-08-05 06:00 | 2015-08-05 | 3 | 6 | 162 | 61.1333 | 1
2015-08-05 06:15 | 2015-08-05 | 3 | 6 | 156 | 61.6333 | 1
2015-08-05 06:30 | 2015-08-05 | 3 | 6 | 156 | 62.1333 | 1
2015-08-05 06:45 | 2015-08-05 | 3 | 6 | 150 | 62.6333 | 1
2015-08-05 07:00 | 2015-08-05 | 3 | 7 | 163 | 63.069 | 1
2015-08-05 07:15 | 2015-08-05 | 3 | 7 | 174 | 63.3276 | 1
2015-08-05 07:30 | 2015-08-05 | 3 | 7 | 160 | 63.5862 | 1
2015-08-05 07:45 | 2015-08-05 | 3 | 7 | 160 | 63.8448 | 1
2015-08-05 08:00 | 2015-08-05 | 3 | 8 | 177 | 65 | 1
2015-08-05 08:15 | 2015-08-05 | 3 | 8 | 168 | 65 | 1
2015-08-05 08:30 | 2015-08-05 | 3 | 8 | 194 | 65 | 1
2015-08-05 08:45 | 2015-08-05 | 3 | 8 | 179 | 65 | 1
2015-08-05 09:00 | 2015-08-05 | 3 | 9 | 188 | 65.1333 | 2
2015-08-05 09:15 | 2015-08-05 | 3 | 9 | 186 | 65.6333 | 2
2015-08-05 09:30 | 2015-08-05 | 3 | 9 | 195 | 66.1333 | 2
2015-08-05 09:45 | 2015-08-05 | 3 | 9 | 212 | 66.6333 | 2
2015-08-05 10:00 | 2015-08-05 | 3 | 10 | 202 | 67.125 | 2
2015-08-05 10:15 | 2015-08-05 | 3 | 10 | 198 | 67.5938 | 2
2015-08-05 10:30 | 2015-08-05 | 3 | 10 | 198 | 68.0714 | 2
2015-08-05 10:45 | 2015-08-05 | 3 | 10 | 212 | 68.6071 | 2
2015-08-05 11:00 | 2015-08-05 | 3 | 11 | 209 | 69.2 | 2
2015-08-05 11:15 | 2015-08-05 | 3 | 11 | 210 | 69.95 | 2
2015-08-05 11:30 | 2015-08-05 | 3 | 11 | 203 | 70.7 | 3
2015-08-05 11:45 | 2015-08-05 | 3 | 11 | 212 | 71.45 | 3
2015-08-05 12:00 | 2015-08-05 | 3 | 12 | 217 | 72.0667 | 3
2015-08-05 12:15 | 2015-08-05 | 3 | 12 | 206 | 72.3167 | 3
2015-08-05 12:30 | 2015-08-05 | 3 | 12 | 212 | 72.5667 | 3
2015-08-05 12:45 | 2015-08-05 | 3 | 12 | 212 | 72.8167 | 3
2015-08-05 13:00 | 2015-08-05 | 3 | 13 | 214 | 72.9333 | 3
2015-08-05 13:15 | 2015-08-05 | 3 | 13 | 230 | 72.6833 | 3
2015-08-05 13:30 | 2015-08-05 | 3 | 13 | 216 | 72.4333 | 3
2015-08-05 13:45 | 2015-08-05 | 3 | 13 | 218 | 72.1833 | 3
2015-08-05 14:00 | 2015-08-05 | 3 | 14 | 226 | 71.9333 | 3
2015-08-05 14:15 | 2015-08-05 | 3 | 14 | 231 | 71.6833 | 3
2015-08-05 14:30 | 2015-08-05 | 3 | 14 | 239 | 71.4333 | 3
2015-08-05 14:45 | 2015-08-05 | 3 | 14 | 222 | 71.1833 | 3
2015-08-05 15:00 | 2015-08-05 | 3 | 15 | 229 | 70.8667 | 3
2015-08-05 15:15 | 2015-08-05 | 3 | 15 | 233 | 70.3667 | 3
2015-08-05 15:30 | 2015-08-05 | 3 | 15 | 229 | 69.8667 | 2
2015-08-05 15:45 | 2015-08-05 | 3 | 15 | 238 | 69.3667 | 2
2015-08-05 16:00 | 2015-08-05 | 3 | 16 | 240 | 68.8667 | 2
2015-08-05 16:15 | 2015-08-05 | 3 | 16 | 237 | 68.3667 | 2
2015-08-05 16:30 | 2015-08-05 | 3 | 16 | 235 | 67.8667 | 2
2015-08-05 16:45 | 2015-08-05 | 3 | 16 | 235 | 67.3667 | 2
2015-08-05 17:00 | 2015-08-05 | 3 | 17 | 253 | 66.9333 | 2
2015-08-05 17:15 | 2015-08-05 | 3 | 17 | 242 | 66.6833 | 2
2015-08-05 17:30 | 2015-08-05 | 3 | 17 | 230 | 66.4333 | 2
2015-08-05 17:45 | 2015-08-05 | 3 | 17 | 235 | 66.1833 | 2
2015-08-05 18:00 | 2015-08-05 | 3 | 18 | 231 | 65.8667 | 2
2015-08-05 18:15 | 2015-08-05 | 3 | 18 | 237 | 65.3667 | 2
2015-08-05 18:30 | 2015-08-05 | 3 | 18 | 236 | 64.8667 | 1
2015-08-05 18:45 | 2015-08-05 | 3 | 18 | 226 | 64.3667 | 1
2015-08-05 19:00 | 2015-08-05 | 3 | 19 | 228 | 63.9333 | 1
2015-08-05 19:15 | 2015-08-05 | 3 | 19 | 241 | 63.6833 | 1
2015-08-05 19:30 | 2015-08-05 | 3 | 19 | 224 | 63.4333 | 1
2015-08-05 19:45 | 2015-08-05 | 3 | 19 | 214 | 63.1833 | 1
2015-08-05 20:00 | 2015-08-05 | 3 | 20 | 215 | 62.9333 | 1
2015-08-05 20:15 | 2015-08-05 | 3 | 20 | 207 | 62.6833 | 1
2015-08-05 20:30 | 2015-08-05 | 3 | 20 | 222 | 62.4333 | 1
2015-08-05 20:45 | 2015-08-05 | 3 | 20 | 218 | 62.1833 | 1
2015-08-05 21:00 | 2015-08-05 | 3 | 21 | 203 | 62 | 1
2015-08-05 21:15 | 2015-08-05 | 3 | 21 | 200 | 62 | 1
2015-08-05 21:30 | 2015-08-05 | 3 | 21 | 193 | 62 | 1
2015-08-05 21:45 | 2015-08-05 | 3 | 21 | 213 | 62 | 1
2015-08-05 22:00 | 2015-08-05 | 3 | 22 | 198 | 62 | 1
2015-08-05 22:15 | 2015-08-05 | 3 | 22 | 212 | 62 | 1
2015-08-05 22:30 | 2015-08-05 | 3 | 22 | 200 | 62 | 1
2015-08-05 22:45 | 2015-08-05 | 3 | 22 | 197 | 62 | 1
2015-08-05 23:00 | 2015-08-05 | 3 | 23 | 197 | 61.9333 | 1
2015-08-05 23:15 | 2015-08-05 | 3 | 23 | 205 | 61.6833 | 1
2015-08-05 23:30 | 2015-08-05 | 3 | 23 | 196 | 61.4333 | 1
2015-08-05 23:45 | 2015-08-05 | 3 | 23 | 189 | 61.1833 | 1
2015-08-06 | 2015-08-06 | 4 | 0 | 184 | 61 | 1
2015-08-06 00:15 | 2015-08-06 | 4 | 0 | 185 | 61 | 1
2015-08-06 00:30 | 2015-08-06 | 4 | 0 | 198 | 61 | 1
2015-08-06 00:45 | 2015-08-06 | 4 | 0 | 182 | 61 | 1
2015-08-06 01:00 | 2015-08-06 | 4 | 1 | 176 | 61 | 1
2015-08-06 01:15 | 2015-08-06 | 4 | 1 | 173 | 61 | 1
2015-08-06 01:30 | 2015-08-06 | 4 | 1 | 186 | 61 | 1
2015-08-06 01:45 | 2015-08-06 | 4 | 1 | 181 | 61 | 1
2015-08-06 02:00 | 2015-08-06 | 4 | 2 | 168 | 60.9333 | 1
2015-08-06 02:15 | 2015-08-06 | 4 | 2 | 176 | 60.6833 | 1
2015-08-06 02:30 | 2015-08-06 | 4 | 2 | 167 | 60.4333 | 1
2015-08-06 02:45 | 2015-08-06 | 4 | 2 | 181 | 60.1833 | 1
2015-08-06 03:00 | 2015-08-06 | 4 | 3 | 169 | 59.9333 | 1
2015-08-06 03:15 | 2015-08-06 | 4 | 3 | 172 | 59.6833 | 1
2015-08-06 03:30 | 2015-08-06 | 4 | 3 | 164 | 59.4333 | 1
2015-08-06 03:45 | 2015-08-06 | 4 | 3 | 170 | 59.1833 | 1
2015-08-06 04:00 | 2015-08-06 | 4 | 4 | 189 | 59 | 1
2015-08-06 04:15 | 2015-08-06 | 4 | 4 | 169 | 59 | 1
2015-08-06 04:30 | 2015-08-06 | 4 | 4 | 163 | 59 | 1
2015-08-06 04:45 | 2015-08-06 | 4 | 4 | 167 | 59 | 1
2015-08-06 05:00 | 2015-08-06 | 4 | 5 | 168 | 59 | 1
2015-08-06 05:15 | 2015-08-06 | 4 | 5 | 172 | 59 | 1
2015-08-06 05:30 | 2015-08-06 | 4 | 5 | 167 | 59 | 1
2015-08-06 05:45 | 2015-08-06 | 4 | 5 | 159 | 59 | 1
2015-08-06 06:00 | 2015-08-06 | 4 | 6 | 160 | 60.0667 | 1
2015-08-06 06:15 | 2015-08-06 | 4 | 6 | 158 | 60.3167 | 1
2015-08-06 06:30 | 2015-08-06 | 4 | 6 | 179 | 60.5667 | 1
2015-08-06 06:45 | 2015-08-06 | 4 | 6 | 161 | 60.8167 | 1
2015-08-06 07:00 | 2015-08-06 | 4 | 7 | 160 | 61.0667 | 1
2015-08-06 07:15 | 2015-08-06 | 4 | 7 | 171 | 61.3167 | 1
2015-08-06 07:30 | 2015-08-06 | 4 | 7 | 163 | 61.5667 | 1
2015-08-06 07:45 | 2015-08-06 | 4 | 7 | 182 | 61.8167 | 1
2015-08-06 08:00 | 2015-08-06 | 4 | 8 | 175 | 62.1333 | 1
2015-08-06 08:15 | 2015-08-06 | 4 | 8 | 174 | 62.6333 | 1
2015-08-06 08:30 | 2015-08-06 | 4 | 8 | 179 | 63.1333 | 1
2015-08-06 08:45 | 2015-08-06 | 4 | 8 | 200 | 63.6333 | 1
2015-08-06 09:00 | 2015-08-06 | 4 | 9 | 195 | 64.1333 | 1
2015-08-06 09:15 | 2015-08-06 | 4 | 9 | 189 | 64.6333 | 1
2015-08-06 09:30 | 2015-08-06 | 4 | 9 | 198 | 65.1333 | 2
2015-08-06 09:45 | 2015-08-06 | 4 | 9 | 193 | 65.6333 | 2
2015-08-06 10:00 | 2015-08-06 | 4 | 10 | 210 | 66 | 2
2015-08-06 10:15 | 2015-08-06 | 4 | 10 | 205 | 66 | 2
2015-08-06 10:30 | 2015-08-06 | 4 | 10 | 201 | 66 | 2
2015-08-06 10:45 | 2015-08-06 | 4 | 10 | 200 | 66 | 2
2015-08-06 11:00 | 2015-08-06 | 4 | 11 | 206 | 66.2 | 2
2015-08-06 11:15 | 2015-08-06 | 4 | 11 | 207 | 66.95 | 2
2015-08-06 11:30 | 2015-08-06 | 4 | 11 | 198 | 67.7 | 2
2015-08-06 11:45 | 2015-08-06 | 4 | 11 | 209 | 68.45 | 2
2015-08-06 12:00 | 2015-08-06 | 4 | 12 | 204 | 68.931 | 2
2015-08-06 12:15 | 2015-08-06 | 4 | 12 | 214 | 68.6724 | 2
2015-08-06 12:30 | 2015-08-06 | 4 | 12 | 227 | 68.4138 | 2
2015-08-06 12:45 | 2015-08-06 | 4 | 12 | 214 | 68.1552 | 2
2015-08-06 13:00 | 2015-08-06 | 4 | 13 | 209 | 67.9333 | 2
2015-08-06 13:15 | 2015-08-06 | 4 | 13 | 207 | 67.6833 | 2
2015-08-06 13:30 | 2015-08-06 | 4 | 13 | 212 | 67.4333 | 2
2015-08-06 13:45 | 2015-08-06 | 4 | 13 | 207 | 67.1833 | 2
2015-08-06 14:00 | 2015-08-06 | 4 | 14 | 212 | 67.1333 | 2
2015-08-06 14:15 | 2015-08-06 | 4 | 14 | 211 | 67.6333 | 2
2015-08-06 14:30 | 2015-08-06 | 4 | 14 | 215 | 68.1333 | 2
2015-08-06 14:45 | 2015-08-06 | 4 | 14 | 226 | 68.6333 | 2
2015-08-06 15:00 | 2015-08-06 | 4 | 15 | 209 | 69 | 2
2015-08-06 15:15 | 2015-08-06 | 4 | 15 | 220 | 69 | 2
2015-08-06 15:30 | 2015-08-06 | 4 | 15 | 215 | 69 | 2
2015-08-06 15:45 | 2015-08-06 | 4 | 15 | 232 | 69 | 2
2015-08-06 16:00 | 2015-08-06 | 4 | 16 | 231 | 68.8667 | 2
2015-08-06 16:15 | 2015-08-06 | 4 | 16 | 220 | 68.3667 | 2
2015-08-06 16:30 | 2015-08-06 | 4 | 16 | 225 | 67.8667 | 2
2015-08-06 16:45 | 2015-08-06 | 4 | 16 | 234 | 67.3667 | 2
2015-08-06 17:00 | 2015-08-06 | 4 | 17 | 211 | 66.8 | 2
2015-08-06 17:15 | 2015-08-06 | 4 | 17 | 225 | 66.05 | 2
2015-08-06 17:30 | 2015-08-06 | 4 | 17 | 225 | 65.3 | 2
2015-08-06 17:45 | 2015-08-06 | 4 | 17 | 249 | 64.55 | 1
2015-08-06 18:00 | 2015-08-06 | 4 | 18 | 232 | 63.9333 | 1
2015-08-06 18:15 | 2015-08-06 | 4 | 18 | 231 | 63.6833 | 1
2015-08-06 18:30 | 2015-08-06 | 4 | 18 | 236 | 63.4333 | 1
2015-08-06 18:45 | 2015-08-06 | 4 | 18 | 219 | 63.1833 | 1
2015-08-06 19:00 | 2015-08-06 | 4 | 19 | 245 | 62.9333 | 1
2015-08-06 19:15 | 2015-08-06 | 4 | 19 | 224 | 62.6833 | 1
2015-08-06 19:30 | 2015-08-06 | 4 | 19 | 209 | 62.4333 | 1
2015-08-06 19:45 | 2015-08-06 | 4 | 19 | 208 | 62.1833 | 1
2015-08-06 20:00 | 2015-08-06 | 4 | 20 | 205 | 61.9333 | 1
2015-08-06 20:15 | 2015-08-06 | 4 | 20 | 217 | 61.6833 | 1
2015-08-06 20:30 | 2015-08-06 | 4 | 20 | 204 | 61.4333 | 1
2015-08-06 20:45 | 2015-08-06 | 4 | 20 | 193 | 61.1833 | 1
2015-08-06 21:00 | 2015-08-06 | 4 | 21 | 201 | 61.0667 | 1
2015-08-06 21:15 | 2015-08-06 | 4 | 21 | 196 | 61.3167 | 1
2015-08-06 21:30 | 2015-08-06 | 4 | 21 | 206 | 61.5667 | 1
2015-08-06 21:45 | 2015-08-06 | 4 | 21 | 191 | 61.8167 | 1
2015-08-06 22:00 | 2015-08-06 | 4 | 22 | 178 | 62.087 | 1
2015-08-06 22:15 | 2015-08-06 | 4 | 22 | 184 | 62.413 | 1
2015-08-06 22:30 | 2015-08-06 | 4 | 22 | 207 | 62.7391 | 1
2015-08-06 22:45 | 2015-08-06 | 4 | 22 | 188 | 63 | 1
2015-08-06 23:00 | 2015-08-06 | 4 | 23 | 189 | 63 | 1
2015-08-06 23:15 | 2015-08-06 | 4 | 23 | 197 | 63 | 1
2015-08-06 23:30 | 2015-08-06 | 4 | 23 | 188 | 62.8387 | 1
2015-08-06 23:45 | 2015-08-06 | 4 | 23 | 192 | 62.3548 | 1
2015-08-07 | 2015-08-07 | 5 | 0 | 179 | 61.9333 | 1
2015-08-07 00:15 | 2015-08-07 | 5 | 0 | 171 | 61.6833 | 1
2015-08-07 00:30 | 2015-08-07 | 5 | 0 | 160 | 61.4333 | 1
2015-08-07 00:45 | 2015-08-07 | 5 | 0 | 167 | 61.1833 | 1
2015-08-07 01:00 | 2015-08-07 | 5 | 1 | 175 | 61 | 1
2015-08-07 01:15 | 2015-08-07 | 5 | 1 | 162 | 61 | 1
2015-08-07 01:30 | 2015-08-07 | 5 | 1 | 157 | 61 | 1
2015-08-07 01:45 | 2015-08-07 | 5 | 1 | 155 | 61 | 1
2015-08-07 02:00 | 2015-08-07 | 5 | 2 | 173 | 61 | 1
2015-08-07 02:15 | 2015-08-07 | 5 | 2 | 170 | 61 | 1
2015-08-07 02:30 | 2015-08-07 | 5 | 2 | 157 | 61 | 1
2015-08-07 02:45 | 2015-08-07 | 5 | 2 | 155 | 61 | 1
2015-08-07 03:00 | 2015-08-07 | 5 | 3 | 171 | 60.9333 | 1
2015-08-07 03:15 | 2015-08-07 | 5 | 3 | 169 | 60.6833 | 1
2015-08-07 03:30 | 2015-08-07 | 5 | 3 | 155 | 60.4333 | 1
2015-08-07 03:45 | 2015-08-07 | 5 | 3 | 162 | 60.1833 | 1
2015-08-07 04:00 | 2015-08-07 | 5 | 4 | 170 | 59.8667 | 1
2015-08-07 04:15 | 2015-08-07 | 5 | 4 | 150 | 59.3667 | 1
2015-08-07 04:30 | 2015-08-07 | 5 | 4 | 146 | 58.8667 | 1
2015-08-07 04:45 | 2015-08-07 | 5 | 4 | 151 | 58.3667 | 1
2015-08-07 05:00 | 2015-08-07 | 5 | 5 | 161 | 58.0667 | 1
2015-08-07 05:15 | 2015-08-07 | 5 | 5 | 159 | 58.3167 | 1
2015-08-07 05:30 | 2015-08-07 | 5 | 5 | 143 | 58.5667 | 1
2015-08-07 05:45 | 2015-08-07 | 5 | 5 | 147 | 58.8167 | 1
2015-08-07 06:00 | 2015-08-07 | 5 | 6 | 145 | 59.2 | 1
2015-08-07 06:15 | 2015-08-07 | 5 | 6 | 164 | 59.95 | 1
2015-08-07 06:30 | 2015-08-07 | 5 | 6 | 158 | 60.7 | 1
2015-08-07 06:45 | 2015-08-07 | 5 | 6 | 150 | 61.45 | 1
2015-08-07 07:00 | 2015-08-07 | 5 | 7 | 150 | 62.2 | 1
2015-08-07 07:15 | 2015-08-07 | 5 | 7 | 166 | 62.95 | 1
2015-08-07 07:30 | 2015-08-07 | 5 | 7 | 163 | 63.7 | 1
2015-08-07 07:45 | 2015-08-07 | 5 | 7 | 153 | 64.45 | 1
2015-08-07 08:00 | 2015-08-07 | 5 | 8 | 160 | 65.2 | 2
2015-08-07 08:15 | 2015-08-07 | 5 | 8 | 162 | 65.95 | 2
2015-08-07 08:30 | 2015-08-07 | 5 | 8 | 180 | 66.7 | 2
2015-08-07 08:45 | 2015-08-07 | 5 | 8 | 178 | 67.45 | 2
2015-08-07 09:00 | 2015-08-07 | 5 | 9 | 177 | 68.0667 | 2
2015-08-07 09:15 | 2015-08-07 | 5 | 9 | 180 | 68.3167 | 2
2015-08-07 09:30 | 2015-08-07 | 5 | 9 | 180 | 68.5667 | 2
2015-08-07 09:45 | 2015-08-07 | 5 | 9 | 199 | 68.8167 | 2
2015-08-07 10:00 | 2015-08-07 | 5 | 10 | 182 | 69.2 | 2
2015-08-07 10:15 | 2015-08-07 | 5 | 10 | 181 | 69.95 | 2
2015-08-07 10:30 | 2015-08-07 | 5 | 10 | 193 | 70.7 | 3
2015-08-07 10:45 | 2015-08-07 | 5 | 10 | 200 | 71.45 | 3
2015-08-07 11:00 | 2015-08-07 | 5 | 11 | 206 | 72 | 3
2015-08-07 11:15 | 2015-08-07 | 5 | 11 | 203 | 72 | 3
2015-08-07 11:30 | 2015-08-07 | 5 | 11 | 193 | 72 | 3
2015-08-07 11:45 | 2015-08-07 | 5 | 11 | 200 | 72 | 3
2015-08-07 12:00 | 2015-08-07 | 5 | 12 | 199 | 72.2 | 3
2015-08-07 12:15 | 2015-08-07 | 5 | 12 | 216 | 72.95 | 3
2015-08-07 12:30 | 2015-08-07 | 5 | 12 | 202 | 73.7 | 3
2015-08-07 12:45 | 2015-08-07 | 5 | 12 | 205 | 74.45 | 3
2015-08-07 13:00 | 2015-08-07 | 5 | 13 | 207 | 75 | 3
2015-08-07 13:15 | 2015-08-07 | 5 | 13 | 204 | 75 | 3
2015-08-07 13:30 | 2015-08-07 | 5 | 13 | 224 | 75 | 3
2015-08-07 13:45 | 2015-08-07 | 5 | 13 | 213 | 75 | 3
2015-08-07 14:00 | 2015-08-07 | 5 | 14 | 220 | 75 | 3
2015-08-07 14:15 | 2015-08-07 | 5 | 14 | 216 | 75 | 3
2015-08-07 14:30 | 2015-08-07 | 5 | 14 | 236 | 75 | 3
2015-08-07 14:45 | 2015-08-07 | 5 | 14 | 235 | 75 | 3
2015-08-07 15:00 | 2015-08-07 | 5 | 15 | 230 | 74.9333 | 3
2015-08-07 15:15 | 2015-08-07 | 5 | 15 | 237 | 74.6833 | 3
2015-08-07 15:30 | 2015-08-07 | 5 | 15 | 230 | 74.4333 | 3
2015-08-07 15:45 | 2015-08-07 | 5 | 15 | 245 | 74.1833 | 3
2015-08-07 16:00 | 2015-08-07 | 5 | 16 | 245 | 73.9333 | 3
2015-08-07 16:15 | 2015-08-07 | 5 | 16 | 231 | 73.6833 | 3
2015-08-07 16:30 | 2015-08-07 | 5 | 16 | 232 | 73.4333 | 3
2015-08-07 16:45 | 2015-08-07 | 5 | 16 | 234 | 73.1833 | 3
2015-08-07 17:00 | 2015-08-07 | 5 | 17 | 239 | 72.8667 | 3
2015-08-07 17:15 | 2015-08-07 | 5 | 17 | 247 | 72.3667 | 3
2015-08-07 17:30 | 2015-08-07 | 5 | 17 | 237 | 71.8667 | 3
2015-08-07 17:45 | 2015-08-07 | 5 | 17 | 232 | 71.3667 | 3
2015-08-07 18:00 | 2015-08-07 | 5 | 18 | 236 | 70.8 | 3
2015-08-07 18:15 | 2015-08-07 | 5 | 18 | 229 | 70.05 | 3
2015-08-07 18:30 | 2015-08-07 | 5 | 18 | 234 | 69.3 | 2
2015-08-07 18:45 | 2015-08-07 | 5 | 18 | 222 | 68.55 | 2
2015-08-07 19:00 | 2015-08-07 | 5 | 19 | 224 | 67.8667 | 2
2015-08-07 19:15 | 2015-08-07 | 5 | 19 | 211 | 67.3667 | 2
2015-08-07 19:30 | 2015-08-07 | 5 | 19 | 229 | 66.8667 | 2
2015-08-07 19:45 | 2015-08-07 | 5 | 19 | 222 | 66.3667 | 2
2015-08-07 20:00 | 2015-08-07 | 5 | 20 | 204 | 65.8667 | 2
2015-08-07 20:15 | 2015-08-07 | 5 | 20 | 223 | 65.3667 | 2
2015-08-07 20:30 | 2015-08-07 | 5 | 20 | 208 | 64.8667 | 1
2015-08-07 20:45 | 2015-08-07 | 5 | 20 | 206 | 64.3667 | 1
2015-08-07 21:00 | 2015-08-07 | 5 | 21 | 201 | 63.9333 | 1
2015-08-07 21:15 | 2015-08-07 | 5 | 21 | 200 | 63.6833 | 1
2015-08-07 21:30 | 2015-08-07 | 5 | 21 | 196 | 63.4333 | 1
2015-08-07 21:45 | 2015-08-07 | 5 | 21 | 196 | 63.1833 | 1
2015-08-07 22:00 | 2015-08-07 | 5 | 22 | 191 | 63 | 1
2015-08-07 22:15 | 2015-08-07 | 5 | 22 | 188 | 63 | 1
2015-08-07 22:30 | 2015-08-07 | 5 | 22 | 193 | 63 | 1
2015-08-07 22:45 | 2015-08-07 | 5 | 22 | 198 | 63 | 1
2015-08-07 23:00 | 2015-08-07 | 5 | 23 | 191 | 62.9333 | 1
2015-08-07 23:15 | 2015-08-07 | 5 | 23 | 183 | 62.6833 | 1
2015-08-07 23:30 | 2015-08-07 | 5 | 23 | 181 | 62.4333 | 1
2015-08-07 23:45 | 2015-08-07 | 5 | 23 | 194 | 62.1833 | 1
2015-08-08 | 2015-08-08 | 6 | 0 | 165 | 62 | 1
2015-08-08 00:15 | 2015-08-08 | 6 | 0 | 168 | 62 | 1
2015-08-08 00:30 | 2015-08-08 | 6 | 0 | 165 | 62 | 1
2015-08-08 00:45 | 2015-08-08 | 6 | 0 | 163 | 62 | 1
2015-08-08 01:00 | 2015-08-08 | 6 | 1 | 178 | 61.9333 | 1
2015-08-08 01:15 | 2015-08-08 | 6 | 1 | 163 | 61.6833 | 1
2015-08-08 01:30 | 2015-08-08 | 6 | 1 | 155 | 61.4333 | 1
2015-08-08 01:45 | 2015-08-08 | 6 | 1 | 165 | 61.1833 | 1
2015-08-08 02:00 | 2015-08-08 | 6 | 2 | 171 | 61.1429 | 1
2015-08-08 02:15 | 2015-08-08 | 6 | 2 | 163 | 61.6786 | 1
2015-08-08 02:30 | 2015-08-08 | 6 | 2 | 156 | 62.2143 | 1
2015-08-08 02:45 | 2015-08-08 | 6 | 2 | 154 | 62.75 | 1
2015-08-08 03:00 | 2015-08-08 | 6 | 3 | 169 | 61.9333 | 1
2015-08-08 03:15 | 2015-08-08 | 6 | 3 | 166 | 61.6833 | 1
2015-08-08 03:30 | 2015-08-08 | 6 | 3 | 154 | 61.4333 | 1
2015-08-08 03:45 | 2015-08-08 | 6 | 3 | 154 | 61.1833 | 1
2015-08-08 04:00 | 2015-08-08 | 6 | 4 | 157 | 61 | 1
2015-08-08 04:15 | 2015-08-08 | 6 | 4 | 161 | 61 | 1
2015-08-08 04:30 | 2015-08-08 | 6 | 4 | 166 | 61 | 1
2015-08-08 04:45 | 2015-08-08 | 6 | 4 | 154 | 61 | 1
2015-08-08 05:00 | 2015-08-08 | 6 | 5 | 146 | 61 | 1
2015-08-08 05:15 | 2015-08-08 | 6 | 5 | 162 | 61 | 1
2015-08-08 05:30 | 2015-08-08 | 6 | 5 | 164 | 61 | 1
2015-08-08 05:45 | 2015-08-08 | 6 | 5 | 148 | 61 | 1
2015-08-08 06:00 | 2015-08-08 | 6 | 6 | 141 | 61.0667 | 1
2015-08-08 06:15 | 2015-08-08 | 6 | 6 | 147 | 61.3167 | 1
2015-08-08 06:30 | 2015-08-08 | 6 | 6 | 163 | 61.5667 | 1
2015-08-08 06:45 | 2015-08-08 | 6 | 6 | 150 | 61.8167 | 1
2015-08-08 07:00 | 2015-08-08 | 6 | 7 | 144 | 62.1333 | 1
2015-08-08 07:15 | 2015-08-08 | 6 | 7 | 150 | 62.6333 | 1
2015-08-08 07:30 | 2015-08-08 | 6 | 7 | 151 | 63.1333 | 1
2015-08-08 07:45 | 2015-08-08 | 6 | 7 | 157 | 63.6333 | 1
2015-08-08 08:00 | 2015-08-08 | 6 | 8 | 143 | 64.1333 | 1
2015-08-08 08:15 | 2015-08-08 | 6 | 8 | 145 | 64.6333 | 1
2015-08-08 08:30 | 2015-08-08 | 6 | 8 | 145 | 65.1333 | 2
2015-08-08 08:45 | 2015-08-08 | 6 | 8 | 159 | 65.6333 | 2
2015-08-08 09:00 | 2015-08-08 | 6 | 9 | 160 | 66 | 2
2015-08-08 09:15 | 2015-08-08 | 6 | 9 | 152 | 66.0465 | 2
2015-08-08 09:30 | 2015-08-08 | 6 | 9 | 153 | 66.3953 | 2
2015-08-08 09:45 | 2015-08-08 | 6 | 9 | 149 | 66.7442 | 2
2015-08-08 10:00 | 2015-08-08 | 6 | 10 | 167 | 67.1333 | 2
2015-08-08 10:15 | 2015-08-08 | 6 | 10 | 158 | 67.6333 | 2
2015-08-08 10:30 | 2015-08-08 | 6 | 10 | 151 | 68.1333 | 2
2015-08-08 10:45 | 2015-08-08 | 6 | 10 | 158 | 68.6333 | 2
2015-08-08 11:00 | 2015-08-08 | 6 | 11 | 152 | 69 | 2
2015-08-08 11:15 | 2015-08-08 | 6 | 11 | 163 | 69 | 2
2015-08-08 11:30 | 2015-08-08 | 6 | 11 | 185 | 69 | 2
2015-08-08 11:45 | 2015-08-08 | 6 | 11 | 166 | 69 | 2
2015-08-08 12:00 | 2015-08-08 | 6 | 12 | 164 | 69.1333 | 2
2015-08-08 12:15 | 2015-08-08 | 6 | 12 | 166 | 69.6333 | 2
2015-08-08 12:30 | 2015-08-08 | 6 | 12 | 177 | 70.1333 | 3
2015-08-08 12:45 | 2015-08-08 | 6 | 12 | 183 | 70.6333 | 3
2015-08-08 13:00 | 2015-08-08 | 6 | 13 | 169 | 70.8667 | 3
2015-08-08 13:15 | 2015-08-08 | 6 | 13 | 169 | 70.3667 | 3
2015-08-08 13:30 | 2015-08-08 | 6 | 13 | 180 | 69.8667 | 2
2015-08-08 13:45 | 2015-08-08 | 6 | 13 | 185 | 69.3667 | 2
2015-08-08 14:00 | 2015-08-08 | 6 | 14 | 172 | 68.9333 | 2
2015-08-08 14:15 | 2015-08-08 | 6 | 14 | 170 | 68.6833 | 2
2015-08-08 14:30 | 2015-08-08 | 6 | 14 | 181 | 68.4333 | 2
2015-08-08 14:45 | 2015-08-08 | 6 | 14 | 178 | 68.1833 | 2
2015-08-08 15:00 | 2015-08-08 | 6 | 15 | 196 | 67.9333 | 2
2015-08-08 15:15 | 2015-08-08 | 6 | 15 | 177 | 67.6833 | 2
2015-08-08 15:30 | 2015-08-08 | 6 | 15 | 186 | 67.4333 | 2
2015-08-08 15:45 | 2015-08-08 | 6 | 15 | 177 | 67.1833 | 2
2015-08-08 16:00 | 2015-08-08 | 6 | 16 | 202 | 66.8667 | 2
2015-08-08 16:15 | 2015-08-08 | 6 | 16 | 189 | 66.3667 | 2
2015-08-08 16:30 | 2015-08-08 | 6 | 16 | 181 | 65.8667 | 2
2015-08-08 16:45 | 2015-08-08 | 6 | 16 | 189 | 65.3667 | 2
2015-08-08 17:00 | 2015-08-08 | 6 | 17 | 177 | 65 | 1
2015-08-08 17:15 | 2015-08-08 | 6 | 17 | 198 | 65 | 1
2015-08-08 17:30 | 2015-08-08 | 6 | 17 | 185 | 65 | 1
2015-08-08 17:45 | 2015-08-08 | 6 | 17 | 180 | 65 | 1
2015-08-08 18:00 | 2015-08-08 | 6 | 18 | 178 | 64.8667 | 1
2015-08-08 18:15 | 2015-08-08 | 6 | 18 | 177 | 64.3667 | 1
2015-08-08 18:30 | 2015-08-08 | 6 | 18 | 188 | 63.8667 | 1
2015-08-08 18:45 | 2015-08-08 | 6 | 18 | 190 | 63.3667 | 1
2015-08-08 19:00 | 2015-08-08 | 6 | 19 | 177 | 63 | 1
2015-08-08 19:15 | 2015-08-08 | 6 | 19 | 177 | 63 | 1
2015-08-08 19:30 | 2015-08-08 | 6 | 19 | 173 | 63 | 1
2015-08-08 19:45 | 2015-08-08 | 6 | 19 | 186 | 63 | 1
2015-08-08 20:00 | 2015-08-08 | 6 | 20 | 179 | 63 | 1
2015-08-08 20:15 | 2015-08-08 | 6 | 20 | 169 | 63 | 1
2015-08-08 20:30 | 2015-08-08 | 6 | 20 | 166 | 63 | 1
2015-08-08 20:45 | 2015-08-08 | 6 | 20 | 170 | 63 | 1
2015-08-08 21:00 | 2015-08-08 | 6 | 21 | 180 | 63 | 1
2015-08-08 21:15 | 2015-08-08 | 6 | 21 | 162 | 63 | 1
2015-08-08 21:30 | 2015-08-08 | 6 | 21 | 158 | 63 | 1
2015-08-08 21:45 | 2015-08-08 | 6 | 21 | 154 | 63 | 1
2015-08-08 22:00 | 2015-08-08 | 6 | 22 | 172 | 63 | 1
2015-08-08 22:15 | 2015-08-08 | 6 | 22 | 161 | 63 | 1
2015-08-08 22:30 | 2015-08-08 | 6 | 22 | 154 | 63 | 1
2015-08-08 22:45 | 2015-08-08 | 6 | 22 | 154 | 63 | 1
2015-08-08 23:00 | 2015-08-08 | 6 | 23 | 163 | 62.9333 | 1
2015-08-08 23:15 | 2015-08-08 | 6 | 23 | 159 | 62.6833 | 1
2015-08-08 23:30 | 2015-08-08 | 6 | 23 | 155 | 62.4333 | 1
2015-08-08 23:45 | 2015-08-08 | 6 | 23 | 147 | 62.1833 | 1
2015-08-09 | 2015-08-09 | 7 | 0 | 153 | 62.08 | 1
2015-08-09 00:15 | 2015-08-09 | 7 | 0 | 163 | 62.38 | 1
2015-08-09 00:30 | 2015-08-09 | 7 | 0 | 144 | 62.68 | 1
2015-08-09 00:45 | 2015-08-09 | 7 | 0 | 149 | 62.98 | 1
2015-08-09 01:00 | 2015-08-09 | 7 | 1 | 145 | 61.9245 | 1
2015-08-09 01:15 | 2015-08-09 | 7 | 1 | 160 | 61.6415 | 1
2015-08-09 01:30 | 2015-08-09 | 7 | 1 | 154 | 61.3585 | 1
2015-08-09 01:45 | 2015-08-09 | 7 | 1 | 145 | 61.0755 | 1
2015-08-09 02:00 | 2015-08-09 | 7 | 2 | 142 | 61 | 1
2015-08-09 02:15 | 2015-08-09 | 7 | 2 | 143 | 61 | 1
2015-08-09 02:30 | 2015-08-09 | 7 | 2 | 163 | 60.7027 | 1
2015-08-09 02:45 | 2015-08-09 | 7 | 2 | 134 | 60.2973 | 1
2015-08-09 03:00 | 2015-08-09 | 7 | 3 | 145 | 60.2105 | 1
2015-08-09 03:15 | 2015-08-09 | 7 | 3 | 137 | 61 | 1
2015-08-09 03:30 | 2015-08-09 | 7 | 3 | 139 | 60.6341 | 1
2015-08-09 03:45 | 2015-08-09 | 7 | 3 | 158 | 60.2683 | 1
2015-08-09 04:00 | 2015-08-09 | 7 | 4 | 137 | 60 | 1
2015-08-09 04:15 | 2015-08-09 | 7 | 4 | 143 | 60 | 1
2015-08-09 04:30 | 2015-08-09 | 7 | 4 | 135 | 60 | 1
2015-08-09 04:45 | 2015-08-09 | 7 | 4 | 155 | 60 | 1
2015-08-09 05:00 | 2015-08-09 | 7 | 5 | 142 | 60 | 1
2015-08-09 05:15 | 2015-08-09 | 7 | 5 | 144 | 60 | 1
2015-08-09 05:30 | 2015-08-09 | 7 | 5 | 138 | 60 | 1
2015-08-09 05:45 | 2015-08-09 | 7 | 5 | 133 | 60 | 1
2015-08-09 06:00 | 2015-08-09 | 7 | 6 | 150 | 60 | 1
2015-08-09 06:15 | 2015-08-09 | 7 | 6 | 143 | 60 | 1
2015-08-09 06:30 | 2015-08-09 | 7 | 6 | 149 | 60 | 1
2015-08-09 06:45 | 2015-08-09 | 7 | 6 | 149 | 60 | 1
2015-08-09 07:00 | 2015-08-09 | 7 | 7 | 150 | 60.2353 | 1
2015-08-09 07:15 | 2015-08-09 | 7 | 7 | 174 | 61.1176 | 1
2015-08-09 07:30 | 2015-08-09 | 7 | 7 | 151 | 62 | 1
2015-08-09 07:45 | 2015-08-09 | 7 | 7 | 160 | 62.8824 | 1
2015-08-09 08:00 | 2015-08-09 | 7 | 8 | 157 | 62.1818 | 1
2015-08-09 08:15 | 2015-08-09 | 7 | 8 | 159 | 62.8636 | 1
2015-08-09 08:30 | 2015-08-09 | 7 | 8 | 166 | 63.3158 | 1
2015-08-09 08:45 | 2015-08-09 | 7 | 8 | 158 | 63.7105 | 1
2015-08-09 09:00 | 2015-08-09 | 7 | 9 | 165 | 64.1333 | 1
2015-08-09 09:15 | 2015-08-09 | 7 | 9 | 150 | 64.6333 | 1
2015-08-09 09:30 | 2015-08-09 | 7 | 9 | 163 | 65.1333 | 2
2015-08-09 09:45 | 2015-08-09 | 7 | 9 | 163 | 65.6333 | 2
2015-08-09 10:00 | 2015-08-09 | 7 | 10 | 176 | 66.1333 | 2
2015-08-09 10:15 | 2015-08-09 | 7 | 10 | 168 | 66.6333 | 2
2015-08-09 10:30 | 2015-08-09 | 7 | 10 | 161 | 67.1333 | 2
2015-08-09 10:45 | 2015-08-09 | 7 | 10 | 161 | 67.6333 | 2
2015-08-09 11:00 | 2015-08-09 | 7 | 11 | 175 | 68.0667 | 2
2015-08-09 11:15 | 2015-08-09 | 7 | 11 | 178 | 68.3167 | 2
2015-08-09 11:30 | 2015-08-09 | 7 | 11 | 195 | 68.5667 | 2
2015-08-09 11:45 | 2015-08-09 | 7 | 11 | 182 | 68.8167 | 2
2015-08-09 12:00 | 2015-08-09 | 7 | 12 | 177 | 69 | 2
2015-08-09 12:15 | 2015-08-09 | 7 | 12 | 182 | 69 | 2
2015-08-09 12:30 | 2015-08-09 | 7 | 12 | 189 | 69 | 2
2015-08-09 12:45 | 2015-08-09 | 7 | 12 | 197 | 69 | 2
2015-08-09 13:00 | 2015-08-09 | 7 | 13 | 183 | 69.0667 | 2
2015-08-09 13:15 | 2015-08-09 | 7 | 13 | 186 | 69.3167 | 2
2015-08-09 13:30 | 2015-08-09 | 7 | 13 | 190 | 69.5667 | 2
2015-08-09 13:45 | 2015-08-09 | 7 | 13 | 206 | 69.8167 | 2
2015-08-09 14:00 | 2015-08-09 | 7 | 14 | 183 | 70 | 2
2015-08-09 14:15 | 2015-08-09 | 7 | 14 | 188 | 70 | 2
2015-08-09 14:30 | 2015-08-09 | 7 | 14 | 192 | 70 | 2
2015-08-09 14:45 | 2015-08-09 | 7 | 14 | 195 | 70 | 2
2015-08-09 15:00 | 2015-08-09 | 7 | 15 | 210 | 69.9333 | 2
2015-08-09 15:15 | 2015-08-09 | 7 | 15 | 193 | 69.6833 | 2
2015-08-09 15:30 | 2015-08-09 | 7 | 15 | 203 | 69.4333 | 2
2015-08-09 15:45 | 2015-08-09 | 7 | 15 | 197 | 69.1833 | 2
2015-08-09 16:00 | 2015-08-09 | 7 | 16 | 223 | 68.8 | 2
2015-08-09 16:15 | 2015-08-09 | 7 | 16 | 209 | 68.05 | 2
2015-08-09 16:30 | 2015-08-09 | 7 | 16 | 210 | 67.3 | 2
2015-08-09 16:45 | 2015-08-09 | 7 | 16 | 206 | 66.55 | 2
2015-08-09 17:00 | 2015-08-09 | 7 | 17 | 213 | 65.9333 | 2
2015-08-09 17:15 | 2015-08-09 | 7 | 17 | 206 | 65.6833 | 2
2015-08-09 17:30 | 2015-08-09 | 7 | 17 | 232 | 65.4333 | 2
2015-08-09 17:45 | 2015-08-09 | 7 | 17 | 214 | 65.1833 | 2
2015-08-09 18:00 | 2015-08-09 | 7 | 18 | 209 | 64.8667 | 1
2015-08-09 18:15 | 2015-08-09 | 7 | 18 | 211 | 64.3667 | 1
2015-08-09 18:30 | 2015-08-09 | 7 | 18 | 215 | 63.8667 | 1
2015-08-09 18:45 | 2015-08-09 | 7 | 18 | 217 | 63.3667 | 1
2015-08-09 19:00 | 2015-08-09 | 7 | 19 | 197 | 62.9333 | 1
2015-08-09 19:15 | 2015-08-09 | 7 | 19 | 197 | 62.6833 | 1
2015-08-09 19:30 | 2015-08-09 | 7 | 19 | 194 | 62.4333 | 1
2015-08-09 19:45 | 2015-08-09 | 7 | 19 | 195 | 62.1833 | 1
2015-08-09 20:00 | 2015-08-09 | 7 | 20 | 202 | 62 | 1
2015-08-09 20:15 | 2015-08-09 | 7 | 20 | 189 | 62 | 1
2015-08-09 20:30 | 2015-08-09 | 7 | 20 | 191 | 62 | 1
2015-08-09 20:45 | 2015-08-09 | 7 | 20 | 184 | 62 | 1
2015-08-09 21:00 | 2015-08-09 | 7 | 21 | 201 | 62 | 1
2015-08-09 21:15 | 2015-08-09 | 7 | 21 | 173 | 62 | 1
2015-08-09 21:30 | 2015-08-09 | 7 | 21 | 183 | 62 | 1
2015-08-09 21:45 | 2015-08-09 | 7 | 21 | 188 | 62 | 1
2015-08-09 22:00 | 2015-08-09 | 7 | 22 | 172 | 62 | 1
2015-08-09 22:15 | 2015-08-09 | 7 | 22 | 178 | 62 | 1
2015-08-09 22:30 | 2015-08-09 | 7 | 22 | 175 | 62 | 1
2015-08-09 22:45 | 2015-08-09 | 7 | 22 | 188 | 62 | 1
2015-08-09 23:00 | 2015-08-09 | 7 | 23 | 170 | 62.0667 | 1
2015-08-09 23:15 | 2015-08-09 | 7 | 23 | 166 | 62.3167 | 1
2015-08-09 23:30 | 2015-08-09 | 7 | 23 | 167 | 62.5667 | 1
2015-08-09 23:45 | 2015-08-09 | 7 | 23 | 176 | 62.8167 | 1
2015-08-10 | 2015-08-10 | 1 | 0 | 181 | 62.9333 | 1
2015-08-10 00:15 | 2015-08-10 | 1 | 0 | 163 | 62.6833 | 1
2015-08-10 00:30 | 2015-08-10 | 1 | 0 | 167 | 62.4333 | 1
2015-08-10 00:45 | 2015-08-10 | 1 | 0 | 163 | 62.1833 | 1
2015-08-10 01:00 | 2015-08-10 | 1 | 1 | 174 | 61.9333 | 1
2015-08-10 01:15 | 2015-08-10 | 1 | 1 | 176 | 61.6833 | 1
2015-08-10 01:30 | 2015-08-10 | 1 | 1 | 160 | 61.4333 | 1
2015-08-10 01:45 | 2015-08-10 | 1 | 1 | 161 | 61.1833 | 1
2015-08-10 02:00 | 2015-08-10 | 1 | 2 | 162 | 60.9333 | 1
2015-08-10 02:15 | 2015-08-10 | 1 | 2 | 185 | 60.6833 | 1
2015-08-10 02:30 | 2015-08-10 | 1 | 2 | 158 | 60.4333 | 1
2015-08-10 02:45 | 2015-08-10 | 1 | 2 | 159 | 60.1833 | 1
2015-08-10 03:00 | 2015-08-10 | 1 | 3 | 158 | 60 | 1
2015-08-10 03:15 | 2015-08-10 | 1 | 3 | 156 | 60 | 1
2015-08-10 03:30 | 2015-08-10 | 1 | 3 | 168 | 60 | 1
2015-08-10 03:45 | 2015-08-10 | 1 | 3 | 155 | 60 | 1
2015-08-10 04:00 | 2015-08-10 | 1 | 4 | 152 | 60 | 1
2015-08-10 04:15 | 2015-08-10 | 1 | 4 | 146 | 60 | 1
2015-08-10 04:30 | 2015-08-10 | 1 | 4 | 167 | 60 | 1
2015-08-10 04:45 | 2015-08-10 | 1 | 4 | 161 | 60 | 1
2015-08-10 05:00 | 2015-08-10 | 1 | 5 | 147 | 60 | 1
2015-08-10 05:15 | 2015-08-10 | 1 | 5 | 150 | 60 | 1
2015-08-10 05:30 | 2015-08-10 | 1 | 5 | 152 | 60 | 1
2015-08-10 05:45 | 2015-08-10 | 1 | 5 | 161 | 60 | 1
2015-08-10 06:00 | 2015-08-10 | 1 | 6 | 156 | 60.0667 | 1
2015-08-10 06:15 | 2015-08-10 | 1 | 6 | 148 | 60.3167 | 1
2015-08-10 06:30 | 2015-08-10 | 1 | 6 | 149 | 60.5667 | 1
2015-08-10 06:45 | 2015-08-10 | 1 | 6 | 154 | 60.8167 | 1
2015-08-10 07:00 | 2015-08-10 | 1 | 7 | 165 | 61.2 | 1
2015-08-10 07:15 | 2015-08-10 | 1 | 7 | 159 | 61.95 | 1
2015-08-10 07:30 | 2015-08-10 | 1 | 7 | 157 | 62.7 | 1
2015-08-10 07:45 | 2015-08-10 | 1 | 7 | 158 | 63.45 | 1
2015-08-10 08:00 | 2015-08-10 | 1 | 8 | 167 | 64 | 1
2015-08-10 08:15 | 2015-08-10 | 1 | 8 | 183 | 64 | 1
2015-08-10 08:30 | 2015-08-10 | 1 | 8 | 170 | 64 | 1
2015-08-10 08:45 | 2015-08-10 | 1 | 8 | 173 | 64.5769 | 1
2015-08-10 09:00 | 2015-08-10 | 1 | 9 | 184 | 65.2 | 2
2015-08-10 09:15 | 2015-08-10 | 1 | 9 | 189 | 65.95 | 2
2015-08-10 09:30 | 2015-08-10 | 1 | 9 | 193 | 66.7 | 2
2015-08-10 09:45 | 2015-08-10 | 1 | 9 | 193 | 67.45 | 2
2015-08-10 10:00 | 2015-08-10 | 1 | 10 | 201 | 68.2667 | 2
2015-08-10 10:15 | 2015-08-10 | 1 | 10 | 194 | 69.2667 | 2
2015-08-10 10:30 | 2015-08-10 | 1 | 10 | 200 | 70.2667 | 3
2015-08-10 10:45 | 2015-08-10 | 1 | 10 | 205 | 71.2667 | 3
2015-08-10 11:00 | 2015-08-10 | 1 | 11 | 195 | 72 | 3
2015-08-10 11:15 | 2015-08-10 | 1 | 11 | 207 | 72 | 3
2015-08-10 11:30 | 2015-08-10 | 1 | 11 | 201 | 72 | 3
2015-08-10 11:45 | 2015-08-10 | 1 | 11 | 217 | 72 | 3
2015-08-10 12:00 | 2015-08-10 | 1 | 12 | 216 | 71.8667 | 3
2015-08-10 12:15 | 2015-08-10 | 1 | 12 | 207 | 71.3667 | 3
2015-08-10 12:30 | 2015-08-10 | 1 | 12 | 206 | 70.8667 | 3
2015-08-10 12:45 | 2015-08-10 | 1 | 12 | 207 | 70.3667 | 3
2015-08-10 13:00 | 2015-08-10 | 1 | 13 | 231 | 70 | 2
2015-08-10 13:15 | 2015-08-10 | 1 | 13 | 219 | 70 | 2
2015-08-10 13:30 | 2015-08-10 | 1 | 13 | 231 | 70 | 2
2015-08-10 13:45 | 2015-08-10 | 1 | 13 | 219 | 70 | 2
2015-08-10 14:00 | 2015-08-10 | 1 | 14 | 234 | 69.9333 | 2
2015-08-10 14:15 | 2015-08-10 | 1 | 14 | 241 | 69.6833 | 2
2015-08-10 14:30 | 2015-08-10 | 1 | 14 | 239 | 69.4333 | 2
2015-08-10 14:45 | 2015-08-10 | 1 | 14 | 236 | 69.1833 | 2
2015-08-10 15:00 | 2015-08-10 | 1 | 15 | 225 | 69 | 2
2015-08-10 15:15 | 2015-08-10 | 1 | 15 | 236 | 69 | 2
2015-08-10 15:30 | 2015-08-10 | 1 | 15 | 227 | 69 | 2
2015-08-10 15:45 | 2015-08-10 | 1 | 15 | 245 | 69 | 2
2015-08-10 16:00 | 2015-08-10 | 1 | 16 | 227 | 68.8 | 2
2015-08-10 16:15 | 2015-08-10 | 1 | 16 | 239 | 68.05 | 2
2015-08-10 16:30 | 2015-08-10 | 1 | 16 | 227 | 67.3 | 2
2015-08-10 16:45 | 2015-08-10 | 1 | 16 | 230 | 66.55 | 2
2015-08-10 17:00 | 2015-08-10 | 1 | 17 | 247 | 66 | 2
2015-08-10 17:15 | 2015-08-10 | 1 | 17 | 237 | 66 | 2
2015-08-10 17:30 | 2015-08-10 | 1 | 17 | 230 | 66 | 2
2015-08-10 17:45 | 2015-08-10 | 1 | 17 | 226 | 66 | 2
2015-08-10 18:00 | 2015-08-10 | 1 | 18 | 229 | 66 | 2
2015-08-10 18:15 | 2015-08-10 | 1 | 18 | 242 | 66 | 2
2015-08-10 18:30 | 2015-08-10 | 1 | 18 | 219 | 66 | 2
2015-08-10 18:45 | 2015-08-10 | 1 | 18 | 231 | 66 | 2
2015-08-10 19:00 | 2015-08-10 | 1 | 19 | 218 | 65.8667 | 2
2015-08-10 19:15 | 2015-08-10 | 1 | 19 | 212 | 65.3667 | 2
2015-08-10 19:30 | 2015-08-10 | 1 | 19 | 203 | 64.8667 | 1
2015-08-10 19:45 | 2015-08-10 | 1 | 19 | 222 | 64.3667 | 1
2015-08-10 20:00 | 2015-08-10 | 1 | 20 | 210 | 63.9273 | 1
2015-08-10 20:15 | 2015-08-10 | 1 | 20 | 200 | 63.6545 | 1
2015-08-10 20:30 | 2015-08-10 | 1 | 20 | 204 | 63.3818 | 1
2015-08-10 20:45 | 2015-08-10 | 1 | 20 | 201 | 63.1091 | 1
2015-08-10 21:00 | 2015-08-10 | 1 | 21 | 209 | 62.9333 | 1
2015-08-10 21:15 | 2015-08-10 | 1 | 21 | 190 | 62.6833 | 1
2015-08-10 21:30 | 2015-08-10 | 1 | 21 | 183 | 62.4333 | 1
2015-08-10 21:45 | 2015-08-10 | 1 | 21 | 188 | 62.1833 | 1
2015-08-10 22:00 | 2015-08-10 | 1 | 22 | 200 | 62 | 1
2015-08-10 22:15 | 2015-08-10 | 1 | 22 | 190 | 62 | 1
2015-08-10 22:30 | 2015-08-10 | 1 | 22 | 182 | 62 | 1
2015-08-10 22:45 | 2015-08-10 | 1 | 22 | 184 | 62 | 1
2015-08-10 23:00 | 2015-08-10 | 1 | 23 | 177 | 61.9333 | 1
2015-08-10 23:15 | 2015-08-10 | 1 | 23 | 191 | 61.6833 | 1
2015-08-10 23:30 | 2015-08-10 | 1 | 23 | 176 | 61.4333 | 1
2015-08-10 23:45 | 2015-08-10 | 1 | 23 | 159 | 61.1833 | 1
2015-08-11 | 2015-08-11 | 2 | 0 | 167 | 61 | 1
2015-08-11 00:15 | 2015-08-11 | 2 | 0 | 177 | 61 | 1
2015-08-11 00:30 | 2015-08-11 | 2 | 0 | 163 | 61 | 1
2015-08-11 00:45 | 2015-08-11 | 2 | 0 | 162 | 60.5 | 1
2015-08-11 01:00 | 2015-08-11 | 2 | 1 | 159 | 60 | 1
2015-08-11 01:15 | 2015-08-11 | 2 | 1 | 160 | 60 | 1
2015-08-11 01:30 | 2015-08-11 | 2 | 1 | 176 | 60 | 1
2015-08-11 01:45 | 2015-08-11 | 2 | 1 | 158 | 60 | 1
2015-08-11 02:00 | 2015-08-11 | 2 | 2 | 154 | 60 | 1
2015-08-11 02:15 | 2015-08-11 | 2 | 2 | 158 | 60 | 1
2015-08-11 02:30 | 2015-08-11 | 2 | 2 | 164 | 60 | 1
2015-08-11 02:45 | 2015-08-11 | 2 | 2 | 166 | 60 | 1
2015-08-11 03:00 | 2015-08-11 | 2 | 3 | 155 | 60 | 1
2015-08-11 03:15 | 2015-08-11 | 2 | 3 | 162 | 60 | 1
2015-08-11 03:30 | 2015-08-11 | 2 | 3 | 149 | 60 | 1
2015-08-11 03:45 | 2015-08-11 | 2 | 3 | 171 | 60 | 1
2015-08-11 04:00 | 2015-08-11 | 2 | 4 | 161 | 60.2857 | 1
2015-08-11 04:15 | 2015-08-11 | 2 | 4 | 151 | 60.8913 | 1
2015-08-11 04:30 | 2015-08-11 | 2 | 4 | 156 | 60.5652 | 1
2015-08-11 04:45 | 2015-08-11 | 2 | 4 | 172 | 60.2391 | 1
2015-08-11 05:00 | 2015-08-11 | 2 | 5 | 159 | 60 | 1
2015-08-11 05:15 | 2015-08-11 | 2 | 5 | 158 | 60 | 1
2015-08-11 05:30 | 2015-08-11 | 2 | 5 | 156 | 60 | 1
2015-08-11 05:45 | 2015-08-11 | 2 | 5 | 154 | 60 | 1
2015-08-11 06:00 | 2015-08-11 | 2 | 6 | 174 | 60.1333 | 1
2015-08-11 06:15 | 2015-08-11 | 2 | 6 | 155 | 60.6333 | 1
2015-08-11 06:30 | 2015-08-11 | 2 | 6 | 150 | 61.1333 | 1
2015-08-11 06:45 | 2015-08-11 | 2 | 6 | 160 | 61.6333 | 1
2015-08-11 07:00 | 2015-08-11 | 2 | 7 | 165 | 62.0667 | 1
2015-08-11 07:15 | 2015-08-11 | 2 | 7 | 177 | 62.3167 | 1
2015-08-11 07:30 | 2015-08-11 | 2 | 7 | 162 | 62.5667 | 1
2015-08-11 07:45 | 2015-08-11 | 2 | 7 | 164 | 62.8167 | 1
2015-08-11 08:00 | 2015-08-11 | 2 | 8 | 171 | 63.2 | 1
2015-08-11 08:15 | 2015-08-11 | 2 | 8 | 179 | 63.95 | 1
2015-08-11 08:30 | 2015-08-11 | 2 | 8 | 193 | 64.7 | 1
2015-08-11 08:45 | 2015-08-11 | 2 | 8 | 175 | 65.45 | 2
2015-08-11 09:00 | 2015-08-11 | 2 | 9 | 183 | 66.1333 | 2
2015-08-11 09:15 | 2015-08-11 | 2 | 9 | 178 | 66.6333 | 2
2015-08-11 09:30 | 2015-08-11 | 2 | 9 | 177 | 67.1333 | 2
2015-08-11 09:45 | 2015-08-11 | 2 | 9 | 192 | 67.6333 | 2
2015-08-11 10:00 | 2015-08-11 | 2 | 10 | 197 | 68.0667 | 2
2015-08-11 10:15 | 2015-08-11 | 2 | 10 | 191 | 68.3167 | 2
2015-08-11 10:30 | 2015-08-11 | 2 | 10 | 194 | 68.5667 | 2
2015-08-11 10:45 | 2015-08-11 | 2 | 10 | 199 | 68.8167 | 2
2015-08-11 11:00 | 2015-08-11 | 2 | 11 | 204 | 69.0667 | 2
2015-08-11 11:15 | 2015-08-11 | 2 | 11 | 210 | 69.3167 | 2
2015-08-11 11:30 | 2015-08-11 | 2 | 11 | 200 | 69.5667 | 2
2015-08-11 11:45 | 2015-08-11 | 2 | 11 | 210 | 69.8167 | 2
2015-08-11 12:00 | 2015-08-11 | 2 | 12 | 212 | 70.1333 | 3
2015-08-11 12:15 | 2015-08-11 | 2 | 12 | 207 | 70.6333 | 3
2015-08-11 12:30 | 2015-08-11 | 2 | 12 | 203 | 71.1333 | 3
2015-08-11 12:45 | 2015-08-11 | 2 | 12 | 217 | 71.6333 | 3
2015-08-11 13:00 | 2015-08-11 | 2 | 13 | 222 | 71.8667 | 3
2015-08-11 13:15 | 2015-08-11 | 2 | 13 | 210 | 71.3667 | 3
2015-08-11 13:30 | 2015-08-11 | 2 | 13 | 214 | 70.8667 | 3
2015-08-11 13:45 | 2015-08-11 | 2 | 13 | 216 | 70.3667 | 3
2015-08-11 14:00 | 2015-08-11 | 2 | 14 | 229 | 69.9333 | 2
2015-08-11 14:15 | 2015-08-11 | 2 | 14 | 235 | 69.6833 | 2
2015-08-11 14:30 | 2015-08-11 | 2 | 14 | 226 | 69.4333 | 2
2015-08-11 14:45 | 2015-08-11 | 2 | 14 | 224 | 69.1833 | 2
2015-08-11 15:00 | 2015-08-11 | 2 | 15 | 234 | 69 | 2
2015-08-11 15:15 | 2015-08-11 | 2 | 15 | 228 | 69 | 2
2015-08-11 15:30 | 2015-08-11 | 2 | 15 | 229 | 69 | 2
2015-08-11 15:45 | 2015-08-11 | 2 | 15 | 221 | 69 | 2
2015-08-11 16:00 | 2015-08-11 | 2 | 16 | 227 | 68.9333 | 2
2015-08-11 16:15 | 2015-08-11 | 2 | 16 | 230 | 68.6833 | 2
2015-08-11 16:30 | 2015-08-11 | 2 | 16 | 235 | 68.4333 | 2
2015-08-11 16:45 | 2015-08-11 | 2 | 16 | 225 | 68.1833 | 2
2015-08-11 17:00 | 2015-08-11 | 2 | 17 | 232 | 67.8667 | 2
2015-08-11 17:15 | 2015-08-11 | 2 | 17 | 236 | 67.3667 | 2
2015-08-11 17:30 | 2015-08-11 | 2 | 17 | 226 | 66.8667 | 2
2015-08-11 17:45 | 2015-08-11 | 2 | 17 | 240 | 66.3667 | 2
2015-08-11 18:00 | 2015-08-11 | 2 | 18 | 230 | 65.8 | 2
2015-08-11 18:15 | 2015-08-11 | 2 | 18 | 227 | 65.05 | 2
2015-08-11 18:30 | 2015-08-11 | 2 | 18 | 214 | 64.3 | 1
2015-08-11 18:45 | 2015-08-11 | 2 | 18 | 227 | 63.55 | 1
2015-08-11 19:00 | 2015-08-11 | 2 | 19 | 233 | 62.9333 | 1
2015-08-11 19:15 | 2015-08-11 | 2 | 19 | 209 | 62.6833 | 1
2015-08-11 19:30 | 2015-08-11 | 2 | 19 | 215 | 62.4333 | 1
2015-08-11 19:45 | 2015-08-11 | 2 | 19 | 208 | 62.1833 | 1
2015-08-11 20:00 | 2015-08-11 | 2 | 20 | 210 | 62 | 1
2015-08-11 20:15 | 2015-08-11 | 2 | 20 | 219 | 62 | 1
2015-08-11 20:30 | 2015-08-11 | 2 | 20 | 206 | 62 | 1
2015-08-11 20:45 | 2015-08-11 | 2 | 20 | 190 | 62 | 1
2015-08-11 21:00 | 2015-08-11 | 2 | 21 | 197 | 62 | 1
2015-08-11 21:15 | 2015-08-11 | 2 | 21 | 199 | 62 | 1
2015-08-11 21:30 | 2015-08-11 | 2 | 21 | 197 | 62 | 1
2015-08-11 21:45 | 2015-08-11 | 2 | 21 | 183 | 62 | 1
2015-08-11 22:00 | 2015-08-11 | 2 | 22 | 191 | 62 | 1
2015-08-11 22:15 | 2015-08-11 | 2 | 22 | 185 | 62 | 1
2015-08-11 22:30 | 2015-08-11 | 2 | 22 | 179 | 62 | 1
2015-08-11 22:45 | 2015-08-11 | 2 | 22 | 179 | 62 | 1
2015-08-11 23:00 | 2015-08-11 | 2 | 23 | 194 | 61.9333 | 1
2015-08-11 23:15 | 2015-08-11 | 2 | 23 | 167 | 61.6833 | 1
2015-08-11 23:30 | 2015-08-11 | 2 | 23 | 178 | 61.4333 | 1
2015-08-11 23:45 | 2015-08-11 | 2 | 23 | 168 | 61.1833 | 1
2015-08-12 | 2015-08-12 | 3 | 0 | 170 | 60.9333 | 1
2015-08-12 00:15 | 2015-08-12 | 3 | 0 | 186 | 60.6833 | 1
2015-08-12 00:30 | 2015-08-12 | 3 | 0 | 163 | 60.4333 | 1
2015-08-12 00:45 | 2015-08-12 | 3 | 0 | 166 | 60.1833 | 1
2015-08-12 01:00 | 2015-08-12 | 3 | 1 | 164 | 60 | 1
2015-08-12 01:15 | 2015-08-12 | 3 | 1 | 176 | 60 | 1
2015-08-12 01:30 | 2015-08-12 | 3 | 1 | 168 | 60 | 1
2015-08-12 01:45 | 2015-08-12 | 3 | 1 | 159 | 60 | 1
2015-08-12 02:00 | 2015-08-12 | 3 | 2 | 160 | 59.9333 | 1
2015-08-12 02:15 | 2015-08-12 | 3 | 2 | 150 | 59.6833 | 1
2015-08-12 02:30 | 2015-08-12 | 3 | 2 | 171 | 59.4333 | 1
2015-08-12 02:45 | 2015-08-12 | 3 | 2 | 161 | 59.1833 | 1
2015-08-12 03:00 | 2015-08-12 | 3 | 3 | 157 | 59 | 1
2015-08-12 03:15 | 2015-08-12 | 3 | 3 | 160 | 59 | 1
2015-08-12 03:30 | 2015-08-12 | 3 | 3 | 151 | 59 | 1
2015-08-12 03:45 | 2015-08-12 | 3 | 3 | 177 | 59 | 1
2015-08-12 04:00 | 2015-08-12 | 3 | 4 | 154 | 59 | 1
2015-08-12 04:15 | 2015-08-12 | 3 | 4 | 156 | 59 | 1
2015-08-12 04:30 | 2015-08-12 | 3 | 4 | 160 | 59 | 1
2015-08-12 04:45 | 2015-08-12 | 3 | 4 | 155 | 59 | 1
2015-08-12 05:00 | 2015-08-12 | 3 | 5 | 172 | 59 | 1
2015-08-12 05:15 | 2015-08-12 | 3 | 5 | 148 | 59 | 1
2015-08-12 05:30 | 2015-08-12 | 3 | 5 | 159 | 59 | 1
2015-08-12 05:45 | 2015-08-12 | 3 | 5 | 145 | 59 | 1
2015-08-12 06:00 | 2015-08-12 | 3 | 6 | 155 | 59.2 | 1
2015-08-12 06:15 | 2015-08-12 | 3 | 6 | 166 | 59.95 | 1
2015-08-12 06:30 | 2015-08-12 | 3 | 6 | 158 | 60.7 | 1
2015-08-12 06:45 | 2015-08-12 | 3 | 6 | 151 | 61.45 | 1
2015-08-12 07:00 | 2015-08-12 | 3 | 7 | 158 | 62.2 | 1
2015-08-12 07:15 | 2015-08-12 | 3 | 7 | 150 | 62.95 | 1
2015-08-12 07:30 | 2015-08-12 | 3 | 7 | 163 | 63.7 | 1
2015-08-12 07:45 | 2015-08-12 | 3 | 7 | 167 | 64.45 | 1
2015-08-12 08:00 | 2015-08-12 | 3 | 8 | 162 | 65.1333 | 2
2015-08-12 08:15 | 2015-08-12 | 3 | 8 | 162 | 65.6333 | 2
2015-08-12 08:30 | 2015-08-12 | 3 | 8 | 165 | 66.1333 | 2
2015-08-12 08:45 | 2015-08-12 | 3 | 8 | 179 | 66.6333 | 2
2015-08-12 09:00 | 2015-08-12 | 3 | 9 | 180 | 67.1333 | 2
2015-08-12 09:15 | 2015-08-12 | 3 | 9 | 175 | 67.6333 | 2
2015-08-12 09:30 | 2015-08-12 | 3 | 9 | 184 | 68.1333 | 2
2015-08-12 09:45 | 2015-08-12 | 3 | 9 | 182 | 68.6333 | 2
2015-08-12 10:00 | 2015-08-12 | 3 | 10 | 197 | 69.1333 | 2
2015-08-12 10:15 | 2015-08-12 | 3 | 10 | 206 | 69.6333 | 2
2015-08-12 10:30 | 2015-08-12 | 3 | 10 | 192 | 70.1333 | 3
2015-08-12 10:45 | 2015-08-12 | 3 | 10 | 186 | 70.6333 | 3
2015-08-12 11:00 | 2015-08-12 | 3 | 11 | 197 | 71.4 | 3
2015-08-12 11:15 | 2015-08-12 | 3 | 11 | 204 | 72.9 | 3
2015-08-12 11:30 | 2015-08-12 | 3 | 11 | 214 | 74.4 | 3
2015-08-12 11:45 | 2015-08-12 | 3 | 11 | 203 | 75.9 | 4
2015-08-12 12:00 | 2015-08-12 | 3 | 12 | 201 | 76.8667 | 4
2015-08-12 12:15 | 2015-08-12 | 3 | 12 | 202 | 76.3667 | 4
2015-08-12 12:30 | 2015-08-12 | 3 | 12 | 216 | 75.8667 | 4
2015-08-12 12:45 | 2015-08-12 | 3 | 12 | 213 | 75.3667 | 4
2015-08-12 13:00 | 2015-08-12 | 3 | 13 | 211 | 74.9333 | 3
2015-08-12 13:15 | 2015-08-12 | 3 | 13 | 202 | 74.6833 | 3
2015-08-12 13:30 | 2015-08-12 | 3 | 13 | 210 | 74.4333 | 3
2015-08-12 13:45 | 2015-08-12 | 3 | 13 | 223 | 74.1833 | 3
2015-08-12 14:00 | 2015-08-12 | 3 | 14 | 205 | 74.0667 | 3
2015-08-12 14:15 | 2015-08-12 | 3 | 14 | 214 | 74.3167 | 3
2015-08-12 14:30 | 2015-08-12 | 3 | 14 | 225 | 74.5667 | 3
2015-08-12 14:45 | 2015-08-12 | 3 | 14 | 207 | 74.8167 | 3
2015-08-12 15:00 | 2015-08-12 | 3 | 15 | 227 | 75.0667 | 4
2015-08-12 15:15 | 2015-08-12 | 3 | 15 | 230 | 75.3167 | 4
2015-08-12 15:30 | 2015-08-12 | 3 | 15 | 216 | 75.5667 | 4
2015-08-12 15:45 | 2015-08-12 | 3 | 15 | 225 | 75.8167 | 4
2015-08-12 16:00 | 2015-08-12 | 3 | 16 | 213 | 75.9333 | 4
2015-08-12 16:15 | 2015-08-12 | 3 | 16 | 249 | 75.6833 | 4
2015-08-12 16:30 | 2015-08-12 | 3 | 16 | 224 | 75.4333 | 4
2015-08-12 16:45 | 2015-08-12 | 3 | 16 | 236 | 75.1833 | 4
2015-08-12 17:00 | 2015-08-12 | 3 | 17 | 227 | 74.8 | 3
2015-08-12 17:15 | 2015-08-12 | 3 | 17 | 239 | 74.05 | 3
2015-08-12 17:30 | 2015-08-12 | 3 | 17 | 228 | 73.3 | 3
2015-08-12 17:45 | 2015-08-12 | 3 | 17 | 252 | 72.55 | 3
2015-08-12 18:00 | 2015-08-12 | 3 | 18 | 222 | 71.7333 | 3
2015-08-12 18:15 | 2015-08-12 | 3 | 18 | 232 | 70.7333 | 3
2015-08-12 18:30 | 2015-08-12 | 3 | 18 | 220 | 69.7333 | 2
2015-08-12 18:45 | 2015-08-12 | 3 | 18 | 236 | 68.7333 | 2
2015-08-12 19:00 | 2015-08-12 | 3 | 19 | 228 | 67.9333 | 2
2015-08-12 19:15 | 2015-08-12 | 3 | 19 | 228 | 67.6833 | 2
2015-08-12 19:30 | 2015-08-12 | 3 | 19 | 215 | 67.4333 | 2
2015-08-12 19:45 | 2015-08-12 | 3 | 19 | 206 | 67.1833 | 2
2015-08-12 20:00 | 2015-08-12 | 3 | 20 | 207 | 67 | 2
2015-08-12 20:15 | 2015-08-12 | 3 | 20 | 199 | 67 | 2
2015-08-12 20:30 | 2015-08-12 | 3 | 20 | 210 | 67 | 2
2015-08-12 20:45 | 2015-08-12 | 3 | 20 | 212 | 67 | 2
2015-08-12 21:00 | 2015-08-12 | 3 | 21 | 200 | 66.9333 | 2
2015-08-12 21:15 | 2015-08-12 | 3 | 21 | 193 | 66.6833 | 2
2015-08-12 21:30 | 2015-08-12 | 3 | 21 | 196 | 66.4333 | 2
2015-08-12 21:45 | 2015-08-12 | 3 | 21 | 197 | 66.1833 | 2
2015-08-12 22:00 | 2015-08-12 | 3 | 22 | 209 | 66 | 2
2015-08-12 22:15 | 2015-08-12 | 3 | 22 | 184 | 66 | 2
2015-08-12 22:30 | 2015-08-12 | 3 | 22 | 198 | 66 | 2
2015-08-12 22:45 | 2015-08-12 | 3 | 22 | 208 | 66 | 2
2015-08-12 23:00 | 2015-08-12 | 3 | 23 | 213 | 66.92 | 2
2015-08-12 23:15 | 2015-08-12 | 3 | 23 | 194 | 66.62 | 2
2015-08-12 23:30 | 2015-08-12 | 3 | 23 | 191 | 66.32 | 2
2015-08-12 23:45 | 2015-08-12 | 3 | 23 | 184 | 66.02 | 2
2015-08-13 | 2015-08-13 | 4 | 0 | 199 | 66 | 2
2015-08-13 00:15 | 2015-08-13 | 4 | 0 | 185 | 66 | 2
2015-08-13 00:30 | 2015-08-13 | 4 | 0 | 172 | 66 | 2
2015-08-13 00:45 | 2015-08-13 | 4 | 0 | 175 | 66 | 2
2015-08-13 01:00 | 2015-08-13 | 4 | 1 | 191 | 65.9333 | 2
2015-08-13 01:15 | 2015-08-13 | 4 | 1 | 184 | 65.6833 | 2
2015-08-13 01:30 | 2015-08-13 | 4 | 1 | 179 | 65.4333 | 2
2015-08-13 01:45 | 2015-08-13 | 4 | 1 | 180 | 65.1833 | 2
2015-08-13 02:00 | 2015-08-13 | 4 | 2 | 177 | 64.931 | 1
2015-08-13 02:15 | 2015-08-13 | 4 | 2 | 195 | 64.6724 | 1
2015-08-13 02:30 | 2015-08-13 | 4 | 2 | 188 | 64.4138 | 1
2015-08-13 02:45 | 2015-08-13 | 4 | 2 | 175 | 64.1552 | 1
2015-08-13 03:00 | 2015-08-13 | 4 | 3 | 173 | 64.9333 | 1
2015-08-13 03:15 | 2015-08-13 | 4 | 3 | 168 | 64.6833 | 1
2015-08-13 03:30 | 2015-08-13 | 4 | 3 | 180 | 64.4333 | 1
2015-08-13 03:45 | 2015-08-13 | 4 | 3 | 174 | 64.1833 | 1
2015-08-13 04:00 | 2015-08-13 | 4 | 4 | 171 | 63.9245 | 1
2015-08-13 04:15 | 2015-08-13 | 4 | 4 | 164 | 63.6415 | 1
2015-08-13 04:30 | 2015-08-13 | 4 | 4 | 169 | 63.3585 | 1
2015-08-13 04:45 | 2015-08-13 | 4 | 4 | 180 | 63.0755 | 1
2015-08-13 05:00 | 2015-08-13 | 4 | 5 | 171 | 63 | 1
2015-08-13 05:15 | 2015-08-13 | 4 | 5 | 160 | 63 | 1
2015-08-13 05:30 | 2015-08-13 | 4 | 5 | 163 | 63 | 1
2015-08-13 05:45 | 2015-08-13 | 4 | 5 | 177 | 63 | 1
2015-08-13 06:00 | 2015-08-13 | 4 | 6 | 168 | 63 | 1
2015-08-13 06:15 | 2015-08-13 | 4 | 6 | 161 | 63 | 1
2015-08-13 06:30 | 2015-08-13 | 4 | 6 | 167 | 63 | 1
2015-08-13 06:45 | 2015-08-13 | 4 | 6 | 167 | 63 | 1
2015-08-13 07:00 | 2015-08-13 | 4 | 7 | 183 | 63.0667 | 1
2015-08-13 07:15 | 2015-08-13 | 4 | 7 | 173 | 63.3167 | 1
2015-08-13 07:30 | 2015-08-13 | 4 | 7 | 162 | 63.5667 | 1
2015-08-13 07:45 | 2015-08-13 | 4 | 7 | 166 | 63.8167 | 1
2015-08-13 08:00 | 2015-08-13 | 4 | 8 | 181 | 64.4211 | 1
2015-08-13 08:15 | 2015-08-13 | 4 | 8 | 189 | 66 | 2
2015-08-13 08:30 | 2015-08-13 | 4 | 8 | 177 | 66.7317 | 2
2015-08-13 08:45 | 2015-08-13 | 4 | 8 | 185 | 67.4634 | 2
2015-08-13 09:00 | 2015-08-13 | 4 | 9 | 183 | 68 | 2
2015-08-13 09:15 | 2015-08-13 | 4 | 9 | 198 | 68 | 2
2015-08-13 09:30 | 2015-08-13 | 4 | 9 | 190 | 68 | 2
2015-08-13 09:45 | 2015-08-13 | 4 | 9 | 186 | 68 | 2
2015-08-13 10:00 | 2015-08-13 | 4 | 10 | 195 | 68.2667 | 2
2015-08-13 10:15 | 2015-08-13 | 4 | 10 | 189 | 69.2667 | 2
2015-08-13 10:30 | 2015-08-13 | 4 | 10 | 211 | 70.2667 | 3
2015-08-13 10:45 | 2015-08-13 | 4 | 10 | 198 | 71.2667 | 3
2015-08-13 11:00 | 2015-08-13 | 4 | 11 | 205 | 72 | 3
2015-08-13 11:15 | 2015-08-13 | 4 | 11 | 200 | 72 | 3
2015-08-13 11:30 | 2015-08-13 | 4 | 11 | 208 | 72 | 3
2015-08-13 11:45 | 2015-08-13 | 4 | 11 | 225 | 72 | 3
2015-08-13 12:00 | 2015-08-13 | 4 | 12 | 221 | 72 | 3
2015-08-13 12:15 | 2015-08-13 | 4 | 12 | 211 | 72 | 3
2015-08-13 12:30 | 2015-08-13 | 4 | 12 | 217 | 72 | 3
2015-08-13 12:45 | 2015-08-13 | 4 | 12 | 229 | 72 | 3
2015-08-13 13:00 | 2015-08-13 | 4 | 13 | 221 | 72.0667 | 3
2015-08-13 13:15 | 2015-08-13 | 4 | 13 | 221 | 72.3167 | 3
2015-08-13 13:30 | 2015-08-13 | 4 | 13 | 218 | 72.5667 | 3
2015-08-13 13:45 | 2015-08-13 | 4 | 13 | 216 | 72.8167 | 3
2015-08-13 14:00 | 2015-08-13 | 4 | 14 | 234 | 73.0667 | 3
2015-08-13 14:15 | 2015-08-13 | 4 | 14 | 226 | 73.3167 | 3
2015-08-13 14:30 | 2015-08-13 | 4 | 14 | 216 | 73.5667 | 3
2015-08-13 14:45 | 2015-08-13 | 4 | 14 | 225 | 73.8167 | 3
2015-08-13 15:00 | 2015-08-13 | 4 | 15 | 214 | 73.9333 | 3
2015-08-13 15:15 | 2015-08-13 | 4 | 15 | 226 | 73.6833 | 3
2015-08-13 15:30 | 2015-08-13 | 4 | 15 | 226 | 73.4333 | 3
2015-08-13 15:45 | 2015-08-13 | 4 | 15 | 243 | 73.1833 | 3
2015-08-13 16:00 | 2015-08-13 | 4 | 16 | 229 | 72.8667 | 3
2015-08-13 16:15 | 2015-08-13 | 4 | 16 | 225 | 72.3667 | 3
2015-08-13 16:30 | 2015-08-13 | 4 | 16 | 231 | 71.8667 | 3
2015-08-13 16:45 | 2015-08-13 | 4 | 16 | 231 | 71.3667 | 3
2015-08-13 17:00 | 2015-08-13 | 4 | 17 | 234 | 70.8667 | 3
2015-08-13 17:15 | 2015-08-13 | 4 | 17 | 250 | 70.3667 | 3
2015-08-13 17:30 | 2015-08-13 | 4 | 17 | 235 | 69.8667 | 2
2015-08-13 17:45 | 2015-08-13 | 4 | 17 | 225 | 69.3667 | 2
2015-08-13 18:00 | 2015-08-13 | 4 | 18 | 229 | 68.8667 | 2
2015-08-13 18:15 | 2015-08-13 | 4 | 18 | 220 | 68.3667 | 2
2015-08-13 18:30 | 2015-08-13 | 4 | 18 | 243 | 67.8667 | 2
2015-08-13 18:45 | 2015-08-13 | 4 | 18 | 220 | 67.3667 | 2
2015-08-13 19:00 | 2015-08-13 | 4 | 19 | 236 | 66.8667 | 2
2015-08-13 19:15 | 2015-08-13 | 4 | 19 | 224 | 66.3667 | 2
2015-08-13 19:30 | 2015-08-13 | 4 | 19 | 208 | 65.8667 | 2
2015-08-13 19:45 | 2015-08-13 | 4 | 19 | 206 | 65.3667 | 2
2015-08-13 20:00 | 2015-08-13 | 4 | 20 | 218 | 64.7838 | 1
2015-08-13 20:15 | 2015-08-13 | 4 | 20 | 202 | 63.973 | 1
2015-08-13 20:30 | 2015-08-13 | 4 | 20 | 197 | 63.1622 | 1
2015-08-13 20:45 | 2015-08-13 | 4 | 20 | 199 | 63 | 1
2015-08-13 21:00 | 2015-08-13 | 4 | 21 | 191 | 63 | 1
2015-08-13 21:15 | 2015-08-13 | 4 | 21 | 204 | 63 | 1
2015-08-13 21:30 | 2015-08-13 | 4 | 21 | 186 | 63 | 1
2015-08-13 21:45 | 2015-08-13 | 4 | 21 | 192 | 63 | 1
2015-08-13 22:00 | 2015-08-13 | 4 | 22 | 183 | 63 | 1
2015-08-13 22:15 | 2015-08-13 | 4 | 22 | 200 | 63 | 1
2015-08-13 22:30 | 2015-08-13 | 4 | 22 | 193 | 63 | 1
2015-08-13 22:45 | 2015-08-13 | 4 | 22 | 186 | 63 | 1
2015-08-13 23:00 | 2015-08-13 | 4 | 23 | 192 | 62.9333 | 1
2015-08-13 23:15 | 2015-08-13 | 4 | 23 | 187 | 62.6833 | 1
2015-08-13 23:30 | 2015-08-13 | 4 | 23 | 189 | 62.4333 | 1
2015-08-13 23:45 | 2015-08-13 | 4 | 23 | 179 | 62.1833 | 1
2015-08-14 | 2015-08-14 | 5 | 0 | 173 | 62 | 1
2015-08-14 00:15 | 2015-08-14 | 5 | 0 | 180 | 62 | 1
2015-08-14 00:30 | 2015-08-14 | 5 | 0 | 186 | 62 | 1
2015-08-14 00:45 | 2015-08-14 | 5 | 0 | 166 | 62 | 1
2015-08-14 01:00 | 2015-08-14 | 5 | 1 | 172 | 62 | 1
2015-08-14 01:15 | 2015-08-14 | 5 | 1 | 171 | 62 | 1
2015-08-14 01:30 | 2015-08-14 | 5 | 1 | 174 | 62 | 1
2015-08-14 01:45 | 2015-08-14 | 5 | 1 | 176 | 62 | 1
2015-08-14 02:00 | 2015-08-14 | 5 | 2 | 163 | 62 | 1
2015-08-14 02:15 | 2015-08-14 | 5 | 2 | 160 | 62 | 1
2015-08-14 02:30 | 2015-08-14 | 5 | 2 | 169 | 62 | 1
2015-08-14 02:45 | 2015-08-14 | 5 | 2 | 178 | 62 | 1
2015-08-14 03:00 | 2015-08-14 | 5 | 3 | 160 | 62.1 | 1
2015-08-14 03:15 | 2015-08-14 | 5 | 3 | 173 | 62.475 | 1
2015-08-14 03:30 | 2015-08-14 | 5 | 3 | 163 | 62.85 | 1
2015-08-14 03:45 | 2015-08-14 | 5 | 3 | 171 | 63 | 1
2015-08-14 04:00 | 2015-08-14 | 5 | 4 | 177 | 62.9333 | 1
2015-08-14 04:15 | 2015-08-14 | 5 | 4 | 162 | 62.6833 | 1
2015-08-14 04:30 | 2015-08-14 | 5 | 4 | 162 | 62.4333 | 1
2015-08-14 04:45 | 2015-08-14 | 5 | 4 | 168 | 62.1833 | 1
2015-08-14 05:00 | 2015-08-14 | 5 | 5 | 180 | 62 | 1
2015-08-14 05:15 | 2015-08-14 | 5 | 5 | 156 | 62 | 1
2015-08-14 05:30 | 2015-08-14 | 5 | 5 | 161 | 62 | 1
2015-08-14 05:45 | 2015-08-14 | 5 | 5 | 163 | 62 | 1
2015-08-14 06:00 | 2015-08-14 | 5 | 6 | 173 | 62.3636 | 1
2015-08-14 06:15 | 2015-08-14 | 5 | 6 | 176 | 63.1633 | 1
2015-08-14 06:30 | 2015-08-14 | 5 | 6 | 165 | 63.4694 | 1
2015-08-14 06:45 | 2015-08-14 | 5 | 6 | 158 | 63.7755 | 1
2015-08-14 07:00 | 2015-08-14 | 5 | 7 | 164 | 64 | 1
2015-08-14 07:15 | 2015-08-14 | 5 | 7 | 183 | 64 | 1
2015-08-14 07:30 | 2015-08-14 | 5 | 7 | 163 | 64 | 1
2015-08-14 07:45 | 2015-08-14 | 5 | 7 | 162 | 64 | 1
2015-08-14 08:00 | 2015-08-14 | 5 | 8 | 173 | 65.1333 | 2
2015-08-14 08:15 | 2015-08-14 | 5 | 8 | 181 | 65.6333 | 2
2015-08-14 08:30 | 2015-08-14 | 5 | 8 | 185 | 66.1333 | 2
2015-08-14 08:45 | 2015-08-14 | 5 | 8 | 174 | 66.6333 | 2
2015-08-14 09:00 | 2015-08-14 | 5 | 9 | 170 | 67 | 2
2015-08-14 09:15 | 2015-08-14 | 5 | 9 | 184 | 67 | 2
2015-08-14 09:30 | 2015-08-14 | 5 | 9 | 198 | 67 | 2
2015-08-14 09:45 | 2015-08-14 | 5 | 9 | 194 | 67 | 2
2015-08-14 10:00 | 2015-08-14 | 5 | 10 | 184 | 67.1333 | 2
2015-08-14 10:15 | 2015-08-14 | 5 | 10 | 189 | 67.6333 | 2
2015-08-14 10:30 | 2015-08-14 | 5 | 10 | 191 | 68.1333 | 2
2015-08-14 10:45 | 2015-08-14 | 5 | 10 | 203 | 68.6333 | 2
2015-08-14 11:00 | 2015-08-14 | 5 | 11 | 200 | 69.2 | 2
2015-08-14 11:15 | 2015-08-14 | 5 | 11 | 196 | 69.95 | 2
2015-08-14 11:30 | 2015-08-14 | 5 | 11 | 190 | 70.7 | 3
2015-08-14 11:45 | 2015-08-14 | 5 | 11 | 200 | 71.45 | 3
2015-08-14 12:00 | 2015-08-14 | 5 | 12 | 208 | 71.9333 | 3
2015-08-14 12:15 | 2015-08-14 | 5 | 12 | 198 | 71.6833 | 3
2015-08-14 12:30 | 2015-08-14 | 5 | 12 | 201 | 71.4333 | 3
2015-08-14 12:45 | 2015-08-14 | 5 | 12 | 200 | 71.1833 | 3
2015-08-14 13:00 | 2015-08-14 | 5 | 13 | 219 | 71.1333 | 3
2015-08-14 13:15 | 2015-08-14 | 5 | 13 | 203 | 71.6333 | 3
2015-08-14 13:30 | 2015-08-14 | 5 | 13 | 211 | 72.1333 | 3
2015-08-14 13:45 | 2015-08-14 | 5 | 13 | 201 | 72.6333 | 3
2015-08-14 14:00 | 2015-08-14 | 5 | 14 | 210 | 72.9333 | 3
2015-08-14 14:15 | 2015-08-14 | 5 | 14 | 216 | 72.6833 | 3
2015-08-14 14:30 | 2015-08-14 | 5 | 14 | 231 | 72.4333 | 3
2015-08-14 14:45 | 2015-08-14 | 5 | 14 | 212 | 72.1833 | 3
2015-08-14 15:00 | 2015-08-14 | 5 | 15 | 226 | 71.9333 | 3
2015-08-14 15:15 | 2015-08-14 | 5 | 15 | 216 | 71.6833 | 3
2015-08-14 15:30 | 2015-08-14 | 5 | 15 | 236 | 71.4333 | 3
2015-08-14 15:45 | 2015-08-14 | 5 | 15 | 236 | 71.1833 | 3
2015-08-14 16:00 | 2015-08-14 | 5 | 16 | 240 | 71 | 3
2015-08-14 16:15 | 2015-08-14 | 5 | 16 | 225 | 71 | 3
2015-08-14 16:30 | 2015-08-14 | 5 | 16 | 241 | 71 | 3
2015-08-14 16:45 | 2015-08-14 | 5 | 16 | 237 | 71 | 3
2015-08-14 17:00 | 2015-08-14 | 5 | 17 | 238 | 70.8 | 3
2015-08-14 17:15 | 2015-08-14 | 5 | 17 | 228 | 70.05 | 3
2015-08-14 17:30 | 2015-08-14 | 5 | 17 | 228 | 69.3 | 2
2015-08-14 17:45 | 2015-08-14 | 5 | 17 | 232 | 68.55 | 2
2015-08-14 18:00 | 2015-08-14 | 5 | 18 | 226 | 67.8 | 2
2015-08-14 18:15 | 2015-08-14 | 5 | 18 | 216 | 67.05 | 2
2015-08-14 18:30 | 2015-08-14 | 5 | 18 | 220 | 66.3 | 2
2015-08-14 18:45 | 2015-08-14 | 5 | 18 | 219 | 65.55 | 2
2015-08-14 19:00 | 2015-08-14 | 5 | 19 | 231 | 64.9333 | 1
2015-08-14 19:15 | 2015-08-14 | 5 | 19 | 225 | 64.6833 | 1
2015-08-14 19:30 | 2015-08-14 | 5 | 19 | 205 | 64.4333 | 1
2015-08-14 19:45 | 2015-08-14 | 5 | 19 | 201 | 64.1833 | 1
2015-08-14 20:00 | 2015-08-14 | 5 | 20 | 202 | 63.9333 | 1
2015-08-14 20:15 | 2015-08-14 | 5 | 20 | 208 | 63.6833 | 1
2015-08-14 20:30 | 2015-08-14 | 5 | 20 | 206 | 63.4333 | 1
2015-08-14 20:45 | 2015-08-14 | 5 | 20 | 196 | 63.1833 | 1
2015-08-14 21:00 | 2015-08-14 | 5 | 21 | 194 | 63 | 1
2015-08-14 21:15 | 2015-08-14 | 5 | 21 | 180 | 63 | 1
2015-08-14 21:30 | 2015-08-14 | 5 | 21 | 192 | 63 | 1
2015-08-14 21:45 | 2015-08-14 | 5 | 21 | 181 | 63 | 1
2015-08-14 22:00 | 2015-08-14 | 5 | 22 | 181 | 63.0667 | 1
2015-08-14 22:15 | 2015-08-14 | 5 | 22 | 178 | 63.3167 | 1
2015-08-14 22:30 | 2015-08-14 | 5 | 22 | 184 | 63.5667 | 1
2015-08-14 22:45 | 2015-08-14 | 5 | 22 | 191 | 63.8167 | 1
2015-08-14 23:00 | 2015-08-14 | 5 | 23 | 179 | 63.9333 | 1
2015-08-14 23:15 | 2015-08-14 | 5 | 23 | 174 | 63.6833 | 1
2015-08-14 23:30 | 2015-08-14 | 5 | 23 | 174 | 63.4333 | 1
2015-08-14 23:45 | 2015-08-14 | 5 | 23 | 190 | 63.1833 | 1
2015-08-15 | 2015-08-15 | 6 | 0 | 168 | 62.8667 | 1
2015-08-15 00:15 | 2015-08-15 | 6 | 0 | 161 | 62.3667 | 1
2015-08-15 00:30 | 2015-08-15 | 6 | 0 | 168 | 61.8667 | 1
2015-08-15 00:45 | 2015-08-15 | 6 | 0 | 179 | 61.3667 | 1
2015-08-15 01:00 | 2015-08-15 | 6 | 1 | 160 | 61 | 1
2015-08-15 01:15 | 2015-08-15 | 6 | 1 | 159 | 61 | 1
2015-08-15 01:30 | 2015-08-15 | 6 | 1 | 156 | 61 | 1
2015-08-15 01:45 | 2015-08-15 | 6 | 1 | 171 | 61 | 1
2015-08-15 02:00 | 2015-08-15 | 6 | 2 | 162 | 61.0667 | 1
2015-08-15 02:15 | 2015-08-15 | 6 | 2 | 157 | 61.3167 | 1
2015-08-15 02:30 | 2015-08-15 | 6 | 2 | 151 | 61.5667 | 1
2015-08-15 02:45 | 2015-08-15 | 6 | 2 | 165 | 61.8167 | 1
2015-08-15 03:00 | 2015-08-15 | 6 | 3 | 173 | 62 | 1
2015-08-15 03:15 | 2015-08-15 | 6 | 3 | 149 | 62 | 1
2015-08-15 03:30 | 2015-08-15 | 6 | 3 | 153 | 62 | 1
2015-08-15 03:45 | 2015-08-15 | 6 | 3 | 157 | 62 | 1
2015-08-15 04:00 | 2015-08-15 | 6 | 4 | 161 | 61.9333 | 1
2015-08-15 04:15 | 2015-08-15 | 6 | 4 | 153 | 61.6833 | 1
2015-08-15 04:30 | 2015-08-15 | 6 | 4 | 153 | 61.4333 | 1
2015-08-15 04:45 | 2015-08-15 | 6 | 4 | 148 | 61.1833 | 1
2015-08-15 05:00 | 2015-08-15 | 6 | 5 | 167 | 61 | 1
2015-08-15 05:15 | 2015-08-15 | 6 | 5 | 143 | 61 | 1
2015-08-15 05:30 | 2015-08-15 | 6 | 5 | 154 | 61 | 1
2015-08-15 05:45 | 2015-08-15 | 6 | 5 | 143 | 61 | 1
2015-08-15 06:00 | 2015-08-15 | 6 | 6 | 146 | 61.3333 | 1
2015-08-15 06:15 | 2015-08-15 | 6 | 6 | 161 | 62.5833 | 1
2015-08-15 06:30 | 2015-08-15 | 6 | 6 | 149 | 63.8333 | 1
2015-08-15 06:45 | 2015-08-15 | 6 | 6 | 146 | 65.0833 | 2
2015-08-15 07:00 | 2015-08-15 | 6 | 7 | 144 | 66.2 | 2
2015-08-15 07:15 | 2015-08-15 | 6 | 7 | 156 | 66.95 | 2
2015-08-15 07:30 | 2015-08-15 | 6 | 7 | 142 | 67.7 | 2
2015-08-15 07:45 | 2015-08-15 | 6 | 7 | 170 | 68.45 | 2
2015-08-15 08:00 | 2015-08-15 | 6 | 8 | 156 | 69.0667 | 2
2015-08-15 08:15 | 2015-08-15 | 6 | 8 | 163 | 69.3167 | 2
2015-08-15 08:30 | 2015-08-15 | 6 | 8 | 153 | 69.5667 | 2
2015-08-15 08:45 | 2015-08-15 | 6 | 8 | 151 | 69.8167 | 2
2015-08-15 09:00 | 2015-08-15 | 6 | 9 | 155 | 70.1333 | 3
2015-08-15 09:15 | 2015-08-15 | 6 | 9 | 180 | 70.6333 | 3
2015-08-15 09:30 | 2015-08-15 | 6 | 9 | 164 | 71.1333 | 3
2015-08-15 09:45 | 2015-08-15 | 6 | 9 | 158 | 71.6333 | 3
2015-08-15 10:00 | 2015-08-15 | 6 | 10 | 181 | 72.2 | 3
2015-08-15 10:15 | 2015-08-15 | 6 | 10 | 170 | 72.95 | 3
2015-08-15 10:30 | 2015-08-15 | 6 | 10 | 169 | 73.7 | 3
2015-08-15 10:45 | 2015-08-15 | 6 | 10 | 175 | 74.45 | 3
2015-08-15 11:00 | 2015-08-15 | 6 | 11 | 173 | 75.2 | 4
2015-08-15 11:15 | 2015-08-15 | 6 | 11 | 181 | 75.95 | 4
2015-08-15 11:30 | 2015-08-15 | 6 | 11 | 194 | 76.7 | 4
2015-08-15 11:45 | 2015-08-15 | 6 | 11 | 180 | 77.45 | 4
2015-08-15 12:00 | 2015-08-15 | 6 | 12 | 182 | 78.3333 | 4
2015-08-15 12:15 | 2015-08-15 | 6 | 12 | 193 | 79.5833 | 4
2015-08-15 12:30 | 2015-08-15 | 6 | 12 | 187 | 80.8333 | 5
2015-08-15 12:45 | 2015-08-15 | 6 | 12 | 215 | 82.0833 | 5
2015-08-15 13:00 | 2015-08-15 | 6 | 13 | 192 | 83.6 | 5
2015-08-15 13:15 | 2015-08-15 | 6 | 13 | 203 | 85.85 | 6
2015-08-15 13:30 | 2015-08-15 | 6 | 13 | 208 | 88.1 | 6
2015-08-15 13:45 | 2015-08-15 | 6 | 13 | 217 | 90.35 | 7
2015-08-15 14:00 | 2015-08-15 | 6 | 14 | 207 | 91.8 | 7
2015-08-15 14:15 | 2015-08-15 | 6 | 14 | 211 | 91.05 | 7
2015-08-15 14:30 | 2015-08-15 | 6 | 14 | 213 | 90.3 | 7
2015-08-15 14:45 | 2015-08-15 | 6 | 14 | 216 | 89.55 | 6
2015-08-15 15:00 | 2015-08-15 | 6 | 15 | 232 | 88.5333 | 6
2015-08-15 15:15 | 2015-08-15 | 6 | 15 | 217 | 86.7833 | 6
2015-08-15 15:30 | 2015-08-15 | 6 | 15 | 228 | 85.0333 | 6
2015-08-15 15:45 | 2015-08-15 | 6 | 15 | 209 | 83.2833 | 5
2015-08-15 16:00 | 2015-08-15 | 6 | 16 | 227 | 81.8 | 5
2015-08-15 16:15 | 2015-08-15 | 6 | 16 | 239 | 81.05 | 5
2015-08-15 16:30 | 2015-08-15 | 6 | 16 | 221 | 80.3 | 5
2015-08-15 16:45 | 2015-08-15 | 6 | 16 | 228 | 79.55 | 4
2015-08-15 17:00 | 2015-08-15 | 6 | 17 | 226 | 78.6667 | 4
2015-08-15 17:15 | 2015-08-15 | 6 | 17 | 235 | 77.4167 | 4
2015-08-15 17:30 | 2015-08-15 | 6 | 17 | 247 | 76.1667 | 4
2015-08-15 17:45 | 2015-08-15 | 6 | 17 | 224 | 74.9167 | 3
2015-08-15 18:00 | 2015-08-15 | 6 | 18 | 228 | 73.8 | 3
2015-08-15 18:15 | 2015-08-15 | 6 | 18 | 216 | 73.05 | 3
2015-08-15 18:30 | 2015-08-15 | 6 | 18 | 226 | 72.3 | 3
2015-08-15 18:45 | 2015-08-15 | 6 | 18 | 234 | 71.55 | 3
2015-08-15 19:00 | 2015-08-15 | 6 | 19 | 223 | 70.6667 | 3
2015-08-15 19:15 | 2015-08-15 | 6 | 19 | 218 | 69.4167 | 2
2015-08-15 19:30 | 2015-08-15 | 6 | 19 | 207 | 68.1667 | 2
2015-08-15 19:45 | 2015-08-15 | 6 | 19 | 220 | 66.9167 | 2
2015-08-15 20:00 | 2015-08-15 | 6 | 20 | 196 | 65.8667 | 2
2015-08-15 20:15 | 2015-08-15 | 6 | 20 | 208 | 65.3667 | 2
2015-08-15 20:30 | 2015-08-15 | 6 | 20 | 192 | 64.8667 | 1
2015-08-15 20:45 | 2015-08-15 | 6 | 20 | 188 | 64.3667 | 1
2015-08-15 21:00 | 2015-08-15 | 6 | 21 | 201 | 64 | 1
2015-08-15 21:15 | 2015-08-15 | 6 | 21 | 192 | 64 | 1
2015-08-15 21:30 | 2015-08-15 | 6 | 21 | 187 | 64 | 1
2015-08-15 21:45 | 2015-08-15 | 6 | 21 | 180 | 64 | 1
2015-08-15 22:00 | 2015-08-15 | 6 | 22 | 194 | 63.9333 | 1
2015-08-15 22:15 | 2015-08-15 | 6 | 22 | 192 | 63.6833 | 1
2015-08-15 22:30 | 2015-08-15 | 6 | 22 | 180 | 63.4333 | 1
2015-08-15 22:45 | 2015-08-15 | 6 | 22 | 180 | 63.1833 | 1
2015-08-15 23:00 | 2015-08-15 | 6 | 23 | 177 | 62.9333 | 1
2015-08-15 23:15 | 2015-08-15 | 6 | 23 | 187 | 62.6833 | 1
2015-08-15 23:30 | 2015-08-15 | 6 | 23 | 176 | 62.4333 | 1
2015-08-15 23:45 | 2015-08-15 | 6 | 23 | 172 | 62.1833 | 1
2015-08-16 | 2015-08-16 | 7 | 0 | 174 | 62 | 1
2015-08-16 00:15 | 2015-08-16 | 7 | 0 | 167 | 62 | 1
2015-08-16 00:30 | 2015-08-16 | 7 | 0 | 196 | 62 | 1
2015-08-16 00:45 | 2015-08-16 | 7 | 0 | 166 | 62 | 1
2015-08-16 01:00 | 2015-08-16 | 7 | 1 | 173 | 62 | 1
2015-08-16 01:15 | 2015-08-16 | 7 | 1 | 161 | 62 | 1
2015-08-16 01:30 | 2015-08-16 | 7 | 1 | 165 | 62 | 1
2015-08-16 01:45 | 2015-08-16 | 7 | 1 | 178 | 62 | 1
2015-08-16 02:00 | 2015-08-16 | 7 | 2 | 167 | 62 | 1
2015-08-16 02:15 | 2015-08-16 | 7 | 2 | 174 | 62 | 1
2015-08-16 02:30 | 2015-08-16 | 7 | 2 | 160 | 62 | 1
2015-08-16 02:45 | 2015-08-16 | 7 | 2 | 158 | 62 | 1
2015-08-16 03:00 | 2015-08-16 | 7 | 3 | 167 | 62 | 1
2015-08-16 03:15 | 2015-08-16 | 7 | 3 | 170 | 62 | 1
2015-08-16 03:30 | 2015-08-16 | 7 | 3 | 158 | 62 | 1
2015-08-16 03:45 | 2015-08-16 | 7 | 3 | 161 | 62 | 1
2015-08-16 04:00 | 2015-08-16 | 7 | 4 | 159 | 62 | 1
2015-08-16 04:15 | 2015-08-16 | 7 | 4 | 163 | 62 | 1
2015-08-16 04:30 | 2015-08-16 | 7 | 4 | 170 | 62 | 1
2015-08-16 04:45 | 2015-08-16 | 7 | 4 | 157 | 62 | 1
2015-08-16 05:00 | 2015-08-16 | 7 | 5 | 155 | 62 | 1
2015-08-16 05:15 | 2015-08-16 | 7 | 5 | 156 | 62 | 1
2015-08-16 05:30 | 2015-08-16 | 7 | 5 | 150 | 62 | 1
2015-08-16 05:45 | 2015-08-16 | 7 | 5 | 177 | 62 | 1
2015-08-16 06:00 | 2015-08-16 | 7 | 6 | 158 | 62.3333 | 1
2015-08-16 06:15 | 2015-08-16 | 7 | 6 | 158 | 63.5833 | 1
2015-08-16 06:30 | 2015-08-16 | 7 | 6 | 171 | 64.8333 | 1
2015-08-16 06:45 | 2015-08-16 | 7 | 6 | 172 | 66.0833 | 2
2015-08-16 07:00 | 2015-08-16 | 7 | 7 | 178 | 67.1333 | 2
2015-08-16 07:15 | 2015-08-16 | 7 | 7 | 195 | 67.6333 | 2
2015-08-16 07:30 | 2015-08-16 | 7 | 7 | 169 | 68.1333 | 2
2015-08-16 07:45 | 2015-08-16 | 7 | 7 | 170 | 68.6333 | 2
2015-08-16 08:00 | 2015-08-16 | 7 | 8 | 168 | 69.1333 | 2
2015-08-16 08:15 | 2015-08-16 | 7 | 8 | 172 | 69.6333 | 2
2015-08-16 08:30 | 2015-08-16 | 7 | 8 | 176 | 70.1333 | 3
2015-08-16 08:45 | 2015-08-16 | 7 | 8 | 170 | 70.6333 | 3
2015-08-16 09:00 | 2015-08-16 | 7 | 9 | 174 | 71.2667 | 3
2015-08-16 09:15 | 2015-08-16 | 7 | 9 | 184 | 72.2667 | 3
2015-08-16 09:30 | 2015-08-16 | 7 | 9 | 191 | 73.2667 | 3
2015-08-16 09:45 | 2015-08-16 | 7 | 9 | 176 | 74.2667 | 3
2015-08-16 10:00 | 2015-08-16 | 7 | 10 | 184 | 75.1333 | 4
2015-08-16 10:15 | 2015-08-16 | 7 | 10 | 186 | 75.6333 | 4
2015-08-16 10:30 | 2015-08-16 | 7 | 10 | 207 | 76.1333 | 4
2015-08-16 10:45 | 2015-08-16 | 7 | 10 | 204 | 76.6333 | 4
2015-08-16 11:00 | 2015-08-16 | 7 | 11 | 199 | 77.0667 | 4
2015-08-16 11:15 | 2015-08-16 | 7 | 11 | 198 | 77.3167 | 4
2015-08-16 11:30 | 2015-08-16 | 7 | 11 | 200 | 77.5667 | 4
2015-08-16 11:45 | 2015-08-16 | 7 | 11 | 225 | 77.8167 | 4
2015-08-16 12:00 | 2015-08-16 | 7 | 12 | 212 | 78.1333 | 4
2015-08-16 12:15 | 2015-08-16 | 7 | 12 | 219 | 78.6333 | 4
2015-08-16 12:30 | 2015-08-16 | 7 | 12 | 216 | 79.1333 | 4
2015-08-16 12:45 | 2015-08-16 | 7 | 12 | 229 | 79.6333 | 4
2015-08-16 13:00 | 2015-08-16 | 7 | 13 | 236 | 80.6667 | 5
2015-08-16 13:15 | 2015-08-16 | 7 | 13 | 241 | 83.1667 | 5
2015-08-16 13:30 | 2015-08-16 | 7 | 13 | 230 | 85.6667 | 6
2015-08-16 13:45 | 2015-08-16 | 7 | 13 | 233 | 88.1667 | 6
2015-08-16 14:00 | 2015-08-16 | 7 | 14 | 247 | 89.7333 | 6
2015-08-16 14:15 | 2015-08-16 | 7 | 14 | 261 | 88.7333 | 6
2015-08-16 14:30 | 2015-08-16 | 7 | 14 | 244 | 87.7333 | 6
2015-08-16 14:45 | 2015-08-16 | 7 | 14 | 244 | 86.7333 | 6
2015-08-16 15:00 | 2015-08-16 | 7 | 15 | 252 | 85.9333 | 6
2015-08-16 15:15 | 2015-08-16 | 7 | 15 | 249 | 85.6833 | 6
2015-08-16 15:30 | 2015-08-16 | 7 | 15 | 267 | 85.4333 | 6
2015-08-16 15:45 | 2015-08-16 | 7 | 15 | 261 | 85.1833 | 6
2015-08-16 16:00 | 2015-08-16 | 7 | 16 | 253 | 84.8667 | 5
2015-08-16 16:15 | 2015-08-16 | 7 | 16 | 251 | 84.3667 | 5
2015-08-16 16:30 | 2015-08-16 | 7 | 16 | 265 | 83.8667 | 5
2015-08-16 16:45 | 2015-08-16 | 7 | 16 | 259 | 83.3667 | 5
2015-08-16 17:00 | 2015-08-16 | 7 | 17 | 259 | 82.9333 | 5
2015-08-16 17:15 | 2015-08-16 | 7 | 17 | 256 | 82.6833 | 5
2015-08-16 17:30 | 2015-08-16 | 7 | 17 | 250 | 82.4333 | 5
2015-08-16 17:45 | 2015-08-16 | 7 | 17 | 269 | 82.1833 | 5
2015-08-16 18:00 | 2015-08-16 | 7 | 18 | 245 | 81.7333 | 5
2015-08-16 18:15 | 2015-08-16 | 7 | 18 | 248 | 80.7333 | 5
2015-08-16 18:30 | 2015-08-16 | 7 | 18 | 252 | 79.7333 | 4
2015-08-16 18:45 | 2015-08-16 | 7 | 18 | 255 | 78.7333 | 4
2015-08-16 19:00 | 2015-08-16 | 7 | 19 | 258 | 77.6667 | 4
2015-08-16 19:15 | 2015-08-16 | 7 | 19 | 240 | 76.4167 | 4
2015-08-16 19:30 | 2015-08-16 | 7 | 19 | 236 | 75.1667 | 4
2015-08-16 19:45 | 2015-08-16 | 7 | 19 | 225 | 73.9167 | 3
2015-08-16 20:00 | 2015-08-16 | 7 | 20 | 223 | 73 | 3
2015-08-16 20:15 | 2015-08-16 | 7 | 20 | 231 | 73 | 3
2015-08-16 20:30 | 2015-08-16 | 7 | 20 | 216 | 73 | 3
2015-08-16 20:45 | 2015-08-16 | 7 | 20 | 211 | 73 | 3
2015-08-16 21:00 | 2015-08-16 | 7 | 21 | 206 | 72.6667 | 3
2015-08-16 21:15 | 2015-08-16 | 7 | 21 | 210 | 71.4167 | 3
2015-08-16 21:30 | 2015-08-16 | 7 | 21 | 207 | 70.1667 | 3
2015-08-16 21:45 | 2015-08-16 | 7 | 21 | 192 | 68.9167 | 2
2015-08-16 22:00 | 2015-08-16 | 7 | 22 | 191 | 67.8667 | 2
2015-08-16 22:15 | 2015-08-16 | 7 | 22 | 185 | 67.3667 | 2
2015-08-16 22:30 | 2015-08-16 | 7 | 22 | 211 | 66.8667 | 2
2015-08-16 22:45 | 2015-08-16 | 7 | 22 | 188 | 66.3667 | 2
2015-08-16 23:00 | 2015-08-16 | 7 | 23 | 199 | 65.8667 | 2
2015-08-16 23:15 | 2015-08-16 | 7 | 23 | 181 | 65.3667 | 2
2015-08-16 23:30 | 2015-08-16 | 7 | 23 | 197 | 64.8667 | 1
2015-08-16 23:45 | 2015-08-16 | 7 | 23 | 191 | 64.3667 | 1
2015-08-17 | 2015-08-17 | 1 | 0 | 183 | 63.8667 | 1
2015-08-17 00:15 | 2015-08-17 | 1 | 0 | 187 | 63.3667 | 1
2015-08-17 00:30 | 2015-08-17 | 1 | 0 | 183 | 62.8667 | 1
2015-08-17 00:45 | 2015-08-17 | 1 | 0 | 196 | 62.3667 | 1
2015-08-17 01:00 | 2015-08-17 | 1 | 1 | 174 | 62 | 1
2015-08-17 01:15 | 2015-08-17 | 1 | 1 | 178 | 62 | 1
2015-08-17 01:30 | 2015-08-17 | 1 | 1 | 166 | 62 | 1
2015-08-17 01:45 | 2015-08-17 | 1 | 1 | 180 | 62 | 1
2015-08-17 02:00 | 2015-08-17 | 1 | 2 | 186 | 61.9333 | 1
2015-08-17 02:15 | 2015-08-17 | 1 | 2 | 174 | 61.6833 | 1
2015-08-17 02:30 | 2015-08-17 | 1 | 2 | 180 | 61.4333 | 1
2015-08-17 02:45 | 2015-08-17 | 1 | 2 | 170 | 61.1833 | 1
2015-08-17 03:00 | 2015-08-17 | 1 | 3 | 192 | 61 | 1
2015-08-17 03:15 | 2015-08-17 | 1 | 3 | 188 | 61 | 1
2015-08-17 03:30 | 2015-08-17 | 1 | 3 | 173 | 61 | 1
2015-08-17 03:45 | 2015-08-17 | 1 | 3 | 182 | 61 | 1
2015-08-17 04:00 | 2015-08-17 | 1 | 4 | 173 | 60.9333 | 1
2015-08-17 04:15 | 2015-08-17 | 1 | 4 | 184 | 60.6833 | 1
2015-08-17 04:30 | 2015-08-17 | 1 | 4 | 188 | 60.4333 | 1
2015-08-17 04:45 | 2015-08-17 | 1 | 4 | 175 | 60.1833 | 1
2015-08-17 05:00 | 2015-08-17 | 1 | 5 | 178 | 60.2105 | 1
2015-08-17 05:15 | 2015-08-17 | 1 | 5 | 164 | 61 | 1
2015-08-17 05:30 | 2015-08-17 | 1 | 5 | 176 | 61 | 1
2015-08-17 05:45 | 2015-08-17 | 1 | 5 | 168 | 61 | 1
2015-08-17 06:00 | 2015-08-17 | 1 | 6 | 159 | 61.1333 | 1
2015-08-17 06:15 | 2015-08-17 | 1 | 6 | 160 | 61.6333 | 1
2015-08-17 06:30 | 2015-08-17 | 1 | 6 | 160 | 62.1333 | 1
2015-08-17 06:45 | 2015-08-17 | 1 | 6 | 185 | 62.6333 | 1
2015-08-17 07:00 | 2015-08-17 | 1 | 7 | 160 | 63.2667 | 1
2015-08-17 07:15 | 2015-08-17 | 1 | 7 | 167 | 64.2667 | 1
2015-08-17 07:30 | 2015-08-17 | 1 | 7 | 169 | 65.2667 | 2
2015-08-17 07:45 | 2015-08-17 | 1 | 7 | 174 | 66.2667 | 2
2015-08-17 08:00 | 2015-08-17 | 1 | 8 | 183 | 67.1333 | 2
2015-08-17 08:15 | 2015-08-17 | 1 | 8 | 186 | 67.6333 | 2
2015-08-17 08:30 | 2015-08-17 | 1 | 8 | 180 | 68.1333 | 2
2015-08-17 08:45 | 2015-08-17 | 1 | 8 | 185 | 68.6333 | 2
2015-08-17 09:00 | 2015-08-17 | 1 | 9 | 208 | 69 | 2
2015-08-17 09:15 | 2015-08-17 | 1 | 9 | 200 | 69 | 2
2015-08-17 09:30 | 2015-08-17 | 1 | 9 | 198 | 69 | 2
2015-08-17 09:45 | 2015-08-17 | 1 | 9 | 201 | 69 | 2
2015-08-17 10:00 | 2015-08-17 | 1 | 10 | 207 | 69.1333 | 2
2015-08-17 10:15 | 2015-08-17 | 1 | 10 | 216 | 69.6333 | 2
2015-08-17 10:30 | 2015-08-17 | 1 | 10 | 226 | 70.1333 | 3
2015-08-17 10:45 | 2015-08-17 | 1 | 10 | 219 | 70.6333 | 3
2015-08-17 11:00 | 2015-08-17 | 1 | 11 | 231 | 71.3333 | 3
2015-08-17 11:15 | 2015-08-17 | 1 | 11 | 231 | 72.5833 | 3
2015-08-17 11:30 | 2015-08-17 | 1 | 11 | 253 | 73.8333 | 3
2015-08-17 11:45 | 2015-08-17 | 1 | 11 | 233 | 75.0833 | 4
2015-08-17 12:00 | 2015-08-17 | 1 | 12 | 258 | 76 | 4
2015-08-17 12:15 | 2015-08-17 | 1 | 12 | 246 | 76 | 4
2015-08-17 12:30 | 2015-08-17 | 1 | 12 | 251 | 76 | 4
2015-08-17 12:45 | 2015-08-17 | 1 | 12 | 239 | 76 | 4
2015-08-17 13:00 | 2015-08-17 | 1 | 13 | 261 | 75.8667 | 4
2015-08-17 13:15 | 2015-08-17 | 1 | 13 | 259 | 75.3667 | 4
2015-08-17 13:30 | 2015-08-17 | 1 | 13 | 254 | 74.8667 | 3
2015-08-17 13:45 | 2015-08-17 | 1 | 13 | 248 | 74.3667 | 3
2015-08-17 14:00 | 2015-08-17 | 1 | 14 | 257 | 73.8667 | 3
2015-08-17 14:15 | 2015-08-17 | 1 | 14 | 261 | 73.3667 | 3
2015-08-17 14:30 | 2015-08-17 | 1 | 14 | 280 | 72.8667 | 3
2015-08-17 14:45 | 2015-08-17 | 1 | 14 | 266 | 72.3667 | 3
2015-08-17 15:00 | 2015-08-17 | 1 | 15 | 263 | 71.9333 | 3
2015-08-17 15:15 | 2015-08-17 | 1 | 15 | 257 | 71.6833 | 3
2015-08-17 15:30 | 2015-08-17 | 1 | 15 | 262 | 71.4333 | 3
2015-08-17 15:45 | 2015-08-17 | 1 | 15 | 275 | 71.1833 | 3
2015-08-17 16:00 | 2015-08-17 | 1 | 16 | 267 | 70.8 | 3
2015-08-17 16:15 | 2015-08-17 | 1 | 16 | 263 | 70.05 | 3
2015-08-17 16:30 | 2015-08-17 | 1 | 16 | 264 | 69.3 | 2
2015-08-17 16:45 | 2015-08-17 | 1 | 16 | 262 | 68.55 | 2
2015-08-17 17:00 | 2015-08-17 | 1 | 17 | 254 | 67.8 | 2
2015-08-17 17:15 | 2015-08-17 | 1 | 17 | 269 | 67.05 | 2
2015-08-17 17:30 | 2015-08-17 | 1 | 17 | 281 | 66.3 | 2
2015-08-17 17:45 | 2015-08-17 | 1 | 17 | 263 | 65.55 | 2
2015-08-17 18:00 | 2015-08-17 | 1 | 18 | 248 | 64.8 | 1
2015-08-17 18:15 | 2015-08-17 | 1 | 18 | 259 | 64.05 | 1
2015-08-17 18:30 | 2015-08-17 | 1 | 18 | 250 | 63.3 | 1
2015-08-17 18:45 | 2015-08-17 | 1 | 18 | 252 | 62.55 | 1
2015-08-17 19:00 | 2015-08-17 | 1 | 19 | 255 | 61.9333 | 1
2015-08-17 19:15 | 2015-08-17 | 1 | 19 | 239 | 61.6833 | 1
2015-08-17 19:30 | 2015-08-17 | 1 | 19 | 249 | 61.4333 | 1
2015-08-17 19:45 | 2015-08-17 | 1 | 19 | 231 | 61.1833 | 1
2015-08-17 20:00 | 2015-08-17 | 1 | 20 | 235 | 61 | 1
2015-08-17 20:15 | 2015-08-17 | 1 | 20 | 219 | 61 | 1
2015-08-17 20:30 | 2015-08-17 | 1 | 20 | 228 | 61 | 1
2015-08-17 20:45 | 2015-08-17 | 1 | 20 | 207 | 61 | 1
2015-08-17 21:00 | 2015-08-17 | 1 | 21 | 235 | 61 | 1
2015-08-17 21:15 | 2015-08-17 | 1 | 21 | 222 | 61 | 1
2015-08-17 21:30 | 2015-08-17 | 1 | 21 | 200 | 61 | 1
2015-08-17 21:45 | 2015-08-17 | 1 | 21 | 199 | 61 | 1
2015-08-17 22:00 | 2015-08-17 | 1 | 22 | 210 | 60.9333 | 1
2015-08-17 22:15 | 2015-08-17 | 1 | 22 | 209 | 60.6833 | 1
2015-08-17 22:30 | 2015-08-17 | 1 | 22 | 207 | 60.4333 | 1
2015-08-17 22:45 | 2015-08-17 | 1 | 22 | 202 | 60.1833 | 1
2015-08-17 23:00 | 2015-08-17 | 1 | 23 | 201 | 60 | 1
2015-08-17 23:15 | 2015-08-17 | 1 | 23 | 198 | 60 | 1
2015-08-17 23:30 | 2015-08-17 | 1 | 23 | 197 | 60 | 1
2015-08-17 23:45 | 2015-08-17 | 1 | 23 | 184 | 60 | 1
2015-08-18 | 2015-08-18 | 2 | 0 | 184 | 59.9333 | 1
2015-08-18 00:15 | 2015-08-18 | 2 | 0 | 177 | 59.6833 | 1
2015-08-18 00:30 | 2015-08-18 | 2 | 0 | 191 | 59.4333 | 1
2015-08-18 00:45 | 2015-08-18 | 2 | 0 | 183 | 59.1833 | 1
2015-08-18 01:00 | 2015-08-18 | 2 | 1 | 176 | 59 | 1
2015-08-18 01:15 | 2015-08-18 | 2 | 1 | 181 | 59 | 1
2015-08-18 01:30 | 2015-08-18 | 2 | 1 | 181 | 59 | 1
2015-08-18 01:45 | 2015-08-18 | 2 | 1 | 190 | 59 | 1
2015-08-18 02:00 | 2015-08-18 | 2 | 2 | 183 | 59 | 1
2015-08-18 02:15 | 2015-08-18 | 2 | 2 | 175 | 59 | 1
2015-08-18 02:30 | 2015-08-18 | 2 | 2 | 174 | 59 | 1
2015-08-18 02:45 | 2015-08-18 | 2 | 2 | 170 | 59 | 1
2015-08-18 03:00 | 2015-08-18 | 2 | 3 | 178 | 59.0667 | 1
2015-08-18 03:15 | 2015-08-18 | 2 | 3 | 185 | 59.3167 | 1
2015-08-18 03:30 | 2015-08-18 | 2 | 3 | 161 | 59.5667 | 1
2015-08-18 03:45 | 2015-08-18 | 2 | 3 | 166 | 59.8167 | 1
2015-08-18 04:00 | 2015-08-18 | 2 | 4 | 160 | 59.9333 | 1
2015-08-18 04:15 | 2015-08-18 | 2 | 4 | 172 | 59.6833 | 1
2015-08-18 04:30 | 2015-08-18 | 2 | 4 | 173 | 59.4333 | 1
2015-08-18 04:45 | 2015-08-18 | 2 | 4 | 151 | 59.1833 | 1
2015-08-18 05:00 | 2015-08-18 | 2 | 5 | 166 | 59.0667 | 1
2015-08-18 05:15 | 2015-08-18 | 2 | 5 | 166 | 59.3167 | 1
2015-08-18 05:30 | 2015-08-18 | 2 | 5 | 170 | 59.5667 | 1
2015-08-18 05:45 | 2015-08-18 | 2 | 5 | 157 | 59.8167 | 1
2015-08-18 06:00 | 2015-08-18 | 2 | 6 | 161 | 60.0667 | 1
2015-08-18 06:15 | 2015-08-18 | 2 | 6 | 158 | 60.3167 | 1
2015-08-18 06:30 | 2015-08-18 | 2 | 6 | 171 | 60.5667 | 1
2015-08-18 06:45 | 2015-08-18 | 2 | 6 | 161 | 60.8167 | 1
2015-08-18 07:00 | 2015-08-18 | 2 | 7 | 157 | 61.1333 | 1
2015-08-18 07:15 | 2015-08-18 | 2 | 7 | 160 | 61.6333 | 1
2015-08-18 07:30 | 2015-08-18 | 2 | 7 | 160 | 62.1333 | 1
2015-08-18 07:45 | 2015-08-18 | 2 | 7 | 176 | 62.6333 | 1
2015-08-18 08:00 | 2015-08-18 | 2 | 8 | 168 | 63.1905 | 1
2015-08-18 08:15 | 2015-08-18 | 2 | 8 | 168 | 63.9048 | 1
2015-08-18 08:30 | 2015-08-18 | 2 | 8 | 171 | 64.6667 | 1
2015-08-18 08:45 | 2015-08-18 | 2 | 8 | 188 | 65.4359 | 2
2015-08-18 09:00 | 2015-08-18 | 2 | 9 | 190 | 66.1333 | 2
2015-08-18 09:15 | 2015-08-18 | 2 | 9 | 177 | 66.6333 | 2
2015-08-18 09:30 | 2015-08-18 | 2 | 9 | 177 | 67.1333 | 2
2015-08-18 09:45 | 2015-08-18 | 2 | 9 | 180 | 67.6333 | 2
2015-08-18 10:00 | 2015-08-18 | 2 | 10 | 203 | 68.0667 | 2
2015-08-18 10:15 | 2015-08-18 | 2 | 10 | 191 | 68.3167 | 2
2015-08-18 10:30 | 2015-08-18 | 2 | 10 | 203 | 68.5667 | 2
2015-08-18 10:45 | 2015-08-18 | 2 | 10 | 199 | 68.8167 | 2
2015-08-18 11:00 | 2015-08-18 | 2 | 11 | 208 | 69.2 | 2
2015-08-18 11:15 | 2015-08-18 | 2 | 11 | 223 | 69.95 | 2
2015-08-18 11:30 | 2015-08-18 | 2 | 11 | 212 | 70.7 | 3
2015-08-18 11:45 | 2015-08-18 | 2 | 11 | 205 | 71.45 | 3
2015-08-18 12:00 | 2015-08-18 | 2 | 12 | 212 | 72.1333 | 3
2015-08-18 12:15 | 2015-08-18 | 2 | 12 | 223 | 72.6333 | 3
2015-08-18 12:30 | 2015-08-18 | 2 | 12 | 220 | 73.1333 | 3
2015-08-18 12:45 | 2015-08-18 | 2 | 12 | 212 | 73.6333 | 3
2015-08-18 13:00 | 2015-08-18 | 2 | 13 | 225 | 74.0667 | 3
2015-08-18 13:15 | 2015-08-18 | 2 | 13 | 219 | 74.3167 | 3
2015-08-18 13:30 | 2015-08-18 | 2 | 13 | 237 | 74.5667 | 3
2015-08-18 13:45 | 2015-08-18 | 2 | 13 | 234 | 74.8167 | 3
2015-08-18 14:00 | 2015-08-18 | 2 | 14 | 235 | 75 | 3
2015-08-18 14:15 | 2015-08-18 | 2 | 14 | 227 | 75 | 3
2015-08-18 14:30 | 2015-08-18 | 2 | 14 | 248 | 75 | 3
2015-08-18 14:45 | 2015-08-18 | 2 | 14 | 243 | 75 | 3
2015-08-18 15:00 | 2015-08-18 | 2 | 15 | 263 | 74.8667 | 3
2015-08-18 15:15 | 2015-08-18 | 2 | 15 | 248 | 74.3667 | 3
2015-08-18 15:30 | 2015-08-18 | 2 | 15 | 261 | 73.8667 | 3
2015-08-18 15:45 | 2015-08-18 | 2 | 15 | 258 | 73.3667 | 3
2015-08-18 16:00 | 2015-08-18 | 2 | 16 | 263 | 72.8 | 3
2015-08-18 16:15 | 2015-08-18 | 2 | 16 | 250 | 72.05 | 3
2015-08-18 16:30 | 2015-08-18 | 2 | 16 | 255 | 71.3 | 3
2015-08-18 16:45 | 2015-08-18 | 2 | 16 | 254 | 70.55 | 3
2015-08-18 17:00 | 2015-08-18 | 2 | 17 | 257 | 69.8667 | 2
2015-08-18 17:15 | 2015-08-18 | 2 | 17 | 264 | 69.3667 | 2
2015-08-18 17:30 | 2015-08-18 | 2 | 17 | 248 | 68.8667 | 2
2015-08-18 17:45 | 2015-08-18 | 2 | 17 | 253 | 68.3667 | 2
2015-08-18 18:00 | 2015-08-18 | 2 | 18 | 240 | 67.8 | 2
2015-08-18 18:15 | 2015-08-18 | 2 | 18 | 243 | 67.05 | 2
2015-08-18 18:30 | 2015-08-18 | 2 | 18 | 254 | 66.3 | 2
2015-08-18 18:45 | 2015-08-18 | 2 | 18 | 251 | 65.55 | 2
2015-08-18 19:00 | 2015-08-18 | 2 | 19 | 232 | 64.9333 | 1
2015-08-18 19:15 | 2015-08-18 | 2 | 19 | 228 | 64.6833 | 1
2015-08-18 19:30 | 2015-08-18 | 2 | 19 | 230 | 64.4333 | 1
2015-08-18 19:45 | 2015-08-18 | 2 | 19 | 241 | 64.1833 | 1
2015-08-18 20:00 | 2015-08-18 | 2 | 20 | 214 | 63.9333 | 1
2015-08-18 20:15 | 2015-08-18 | 2 | 20 | 222 | 63.6833 | 1
2015-08-18 20:30 | 2015-08-18 | 2 | 20 | 219 | 63.4333 | 1
2015-08-18 20:45 | 2015-08-18 | 2 | 20 | 210 | 63.1833 | 1
2015-08-18 21:00 | 2015-08-18 | 2 | 21 | 220 | 63 | 1
2015-08-18 21:15 | 2015-08-18 | 2 | 21 | 214 | 63 | 1
2015-08-18 21:30 | 2015-08-18 | 2 | 21 | 220 | 63 | 1
2015-08-18 21:45 | 2015-08-18 | 2 | 21 | 206 | 63 | 1
2015-08-18 22:00 | 2015-08-18 | 2 | 22 | 200 | 62.9333 | 1
2015-08-18 22:15 | 2015-08-18 | 2 | 22 | 192 | 62.6833 | 1
2015-08-18 22:30 | 2015-08-18 | 2 | 22 | 207 | 62.4333 | 1
2015-08-18 22:45 | 2015-08-18 | 2 | 22 | 204 | 62.1833 | 1
2015-08-18 23:00 | 2015-08-18 | 2 | 23 | 199 | 62 | 1
2015-08-18 23:15 | 2015-08-18 | 2 | 23 | 195 | 62 | 1
2015-08-18 23:30 | 2015-08-18 | 2 | 23 | 200 | 62 | 1
2015-08-18 23:45 | 2015-08-18 | 2 | 23 | 205 | 62 | 1
2015-08-19 | 2015-08-19 | 3 | 0 | 193 | 62.1111 | 1
2015-08-19 00:15 | 2015-08-19 | 3 | 0 | 191 | 62.5278 | 1
2015-08-19 00:30 | 2015-08-19 | 3 | 0 | 192 | 62.9444 | 1
2015-08-19 00:45 | 2015-08-19 | 3 | 0 | 196 | 62.4583 | 1
2015-08-19 01:00 | 2015-08-19 | 3 | 1 | 198 | 62.25 | 1
2015-08-19 01:15 | 2015-08-19 | 3 | 1 | 188 | 62.8636 | 1
2015-08-19 01:30 | 2015-08-19 | 3 | 1 | 183 | 62.1818 | 1
2015-08-19 01:45 | 2015-08-19 | 3 | 1 | 190 | 61.5 | 1
2015-08-19 02:00 | 2015-08-19 | 3 | 2 | 182 | 61 | 1
2015-08-19 02:15 | 2015-08-19 | 3 | 2 | 174 | 61 | 1
2015-08-19 02:30 | 2015-08-19 | 3 | 2 | 173 | 61 | 1
2015-08-19 02:45 | 2015-08-19 | 3 | 2 | 179 | 61 | 1
2015-08-19 03:00 | 2015-08-19 | 3 | 3 | 190 | 60.9333 | 1
2015-08-19 03:15 | 2015-08-19 | 3 | 3 | 170 | 60.6833 | 1
2015-08-19 03:30 | 2015-08-19 | 3 | 3 | 169 | 60.4333 | 1
2015-08-19 03:45 | 2015-08-19 | 3 | 3 | 178 | 60.1833 | 1
2015-08-19 04:00 | 2015-08-19 | 3 | 4 | 178 | 60 | 1
2015-08-19 04:15 | 2015-08-19 | 3 | 4 | 185 | 60 | 1
2015-08-19 04:30 | 2015-08-19 | 3 | 4 | 163 | 60 | 1
2015-08-19 04:45 | 2015-08-19 | 3 | 4 | 171 | 60 | 1
2015-08-19 05:00 | 2015-08-19 | 3 | 5 | 171 | 60.0667 | 1
2015-08-19 05:15 | 2015-08-19 | 3 | 5 | 174 | 60.3167 | 1
2015-08-19 05:30 | 2015-08-19 | 3 | 5 | 173 | 60.5667 | 1
2015-08-19 05:45 | 2015-08-19 | 3 | 5 | 162 | 60.8167 | 1
2015-08-19 06:00 | 2015-08-19 | 3 | 6 | 163 | 61.0667 | 1
2015-08-19 06:15 | 2015-08-19 | 3 | 6 | 158 | 61.3167 | 1
2015-08-19 06:30 | 2015-08-19 | 3 | 6 | 178 | 61.5667 | 1
2015-08-19 06:45 | 2015-08-19 | 3 | 6 | 174 | 61.8167 | 1
2015-08-19 07:00 | 2015-08-19 | 3 | 7 | 164 | 62.1026 | 1
2015-08-19 07:15 | 2015-08-19 | 3 | 7 | 163 | 62.4872 | 1
2015-08-19 07:30 | 2015-08-19 | 3 | 7 | 164 | 62.8718 | 1
2015-08-19 07:45 | 2015-08-19 | 3 | 7 | 183 | 63.4762 | 1
2015-08-19 08:00 | 2015-08-19 | 3 | 8 | 170 | 64 | 1
2015-08-19 08:15 | 2015-08-19 | 3 | 8 | 168 | 64 | 1
2015-08-19 08:30 | 2015-08-19 | 3 | 8 | 175 | 64 | 1
2015-08-19 08:45 | 2015-08-19 | 3 | 8 | 184 | 64 | 1
2015-08-19 09:00 | 2015-08-19 | 3 | 9 | 196 | 64.2759 | 1
2015-08-19 09:15 | 2015-08-19 | 3 | 9 | 186 | 65.3103 | 2
2015-08-19 09:30 | 2015-08-19 | 3 | 9 | 195 | 66.3448 | 2
2015-08-19 09:45 | 2015-08-19 | 3 | 9 | 192 | 67.3793 | 2
2015-08-19 10:00 | 2015-08-19 | 3 | 10 | 208 | 68.2 | 2
2015-08-19 10:15 | 2015-08-19 | 3 | 10 | 219 | 68.95 | 2
2015-08-19 10:30 | 2015-08-19 | 3 | 10 | 200 | 69.7 | 2
2015-08-19 10:45 | 2015-08-19 | 3 | 10 | 207 | 70.45 | 3
2015-08-19 11:00 | 2015-08-19 | 3 | 11 | 210 | 71.1333 | 3
2015-08-19 11:15 | 2015-08-19 | 3 | 11 | 230 | 71.6333 | 3
2015-08-19 11:30 | 2015-08-19 | 3 | 11 | 202 | 72.1333 | 3
2015-08-19 11:45 | 2015-08-19 | 3 | 11 | 212 | 72.6333 | 3
2015-08-19 12:00 | 2015-08-19 | 3 | 12 | 217 | 73 | 3
2015-08-19 12:15 | 2015-08-19 | 3 | 12 | 216 | 73 | 3
2015-08-19 12:30 | 2015-08-19 | 3 | 12 | 234 | 73 | 3
2015-08-19 12:45 | 2015-08-19 | 3 | 12 | 225 | 73 | 3
2015-08-19 13:00 | 2015-08-19 | 3 | 13 | 214 | 73 | 3
2015-08-19 13:15 | 2015-08-19 | 3 | 13 | 226 | 73 | 3
2015-08-19 13:30 | 2015-08-19 | 3 | 13 | 242 | 73 | 3
2015-08-19 13:45 | 2015-08-19 | 3 | 13 | 231 | 73 | 3
2015-08-19 14:00 | 2015-08-19 | 3 | 14 | 234 | 73 | 3
2015-08-19 14:15 | 2015-08-19 | 3 | 14 | 232 | 73 | 3
2015-08-19 14:30 | 2015-08-19 | 3 | 14 | 244 | 73 | 3
2015-08-19 14:45 | 2015-08-19 | 3 | 14 | 245 | 73 | 3
2015-08-19 15:00 | 2015-08-19 | 3 | 15 | 239 | 72.9333 | 3
2015-08-19 15:15 | 2015-08-19 | 3 | 15 | 227 | 72.6833 | 3
2015-08-19 15:30 | 2015-08-19 | 3 | 15 | 243 | 72.4333 | 3
2015-08-19 15:45 | 2015-08-19 | 3 | 15 | 230 | 72.1833 | 3
2015-08-19 16:00 | 2015-08-19 | 3 | 16 | 263 | 71.8 | 3
2015-08-19 16:15 | 2015-08-19 | 3 | 16 | 234 | 71.05 | 3
2015-08-19 16:30 | 2015-08-19 | 3 | 16 | 245 | 70.3 | 3
2015-08-19 16:45 | 2015-08-19 | 3 | 16 | 238 | 69.55 | 2
2015-08-19 17:00 | 2015-08-19 | 3 | 17 | 243 | 68.8667 | 2
2015-08-19 17:15 | 2015-08-19 | 3 | 17 | 252 | 68.3667 | 2
2015-08-19 17:30 | 2015-08-19 | 3 | 17 | 253 | 67.8667 | 2
2015-08-19 17:45 | 2015-08-19 | 3 | 17 | 236 | 67.3667 | 2
2015-08-19 18:00 | 2015-08-19 | 3 | 18 | 239 | 66.8667 | 2
2015-08-19 18:15 | 2015-08-19 | 3 | 18 | 235 | 66.3667 | 2
2015-08-19 18:30 | 2015-08-19 | 3 | 18 | 245 | 65.8667 | 2
2015-08-19 18:45 | 2015-08-19 | 3 | 18 | 239 | 65.3667 | 2
2015-08-19 19:00 | 2015-08-19 | 3 | 19 | 231 | 65 | 1
2015-08-19 19:15 | 2015-08-19 | 3 | 19 | 239 | 65 | 1
2015-08-19 19:30 | 2015-08-19 | 3 | 19 | 235 | 65 | 1
2015-08-19 19:45 | 2015-08-19 | 3 | 19 | 221 | 65 | 1
2015-08-19 20:00 | 2015-08-19 | 3 | 20 | 226 | 65 | 1
2015-08-19 20:15 | 2015-08-19 | 3 | 20 | 206 | 65 | 1
2015-08-19 20:30 | 2015-08-19 | 3 | 20 | 213 | 65 | 1
2015-08-19 20:45 | 2015-08-19 | 3 | 20 | 221 | 65 | 1
2015-08-19 21:00 | 2015-08-19 | 3 | 21 | 227 | 64.931 | 1
2015-08-19 21:15 | 2015-08-19 | 3 | 21 | 207 | 64.6724 | 1
2015-08-19 21:30 | 2015-08-19 | 3 | 21 | 198 | 64.4138 | 1
2015-08-19 21:45 | 2015-08-19 | 3 | 21 | 196 | 64.1552 | 1
2015-08-19 22:00 | 2015-08-19 | 3 | 22 | 190 | 65 | 1
2015-08-19 22:15 | 2015-08-19 | 3 | 22 | 208 | 65 | 1
2015-08-19 22:30 | 2015-08-19 | 3 | 22 | 188 | 65 | 1
2015-08-19 22:45 | 2015-08-19 | 3 | 22 | 194 | 65 | 1
2015-08-19 23:00 | 2015-08-19 | 3 | 23 | 186 | 64.9333 | 1
2015-08-19 23:15 | 2015-08-19 | 3 | 23 | 188 | 64.6833 | 1
2015-08-19 23:30 | 2015-08-19 | 3 | 23 | 196 | 64.4333 | 1
2015-08-19 23:45 | 2015-08-19 | 3 | 23 | 174 | 64.1833 | 1
2015-08-20 | 2015-08-20 | 4 | 0 | 176 | 64 | 1
2015-08-20 00:15 | 2015-08-20 | 4 | 0 | 184 | 64 | 1
2015-08-20 00:30 | 2015-08-20 | 4 | 0 | 185 | 64 | 1
2015-08-20 00:45 | 2015-08-20 | 4 | 0 | 201 | 64 | 1
2015-08-20 01:00 | 2015-08-20 | 4 | 1 | 182 | 64 | 1
2015-08-20 01:15 | 2015-08-20 | 4 | 1 | 185 | 64 | 1
2015-08-20 01:30 | 2015-08-20 | 4 | 1 | 187 | 64 | 1
2015-08-20 01:45 | 2015-08-20 | 4 | 1 | 198 | 64 | 1
2015-08-20 02:00 | 2015-08-20 | 4 | 2 | 200 | 63.9333 | 1
2015-08-20 02:15 | 2015-08-20 | 4 | 2 | 175 | 63.6833 | 1
2015-08-20 02:30 | 2015-08-20 | 4 | 2 | 184 | 63.4333 | 1
2015-08-20 02:45 | 2015-08-20 | 4 | 2 | 181 | 63.1833 | 1
2015-08-20 03:00 | 2015-08-20 | 4 | 3 | 183 | 63 | 1
2015-08-20 03:15 | 2015-08-20 | 4 | 3 | 176 | 63 | 1
2015-08-20 03:30 | 2015-08-20 | 4 | 3 | 172 | 63 | 1
2015-08-20 03:45 | 2015-08-20 | 4 | 3 | 168 | 63 | 1
2015-08-20 04:00 | 2015-08-20 | 4 | 4 | 185 | 62.9333 | 1
2015-08-20 04:15 | 2015-08-20 | 4 | 4 | 175 | 62.6833 | 1
2015-08-20 04:30 | 2015-08-20 | 4 | 4 | 173 | 62.4333 | 1
2015-08-20 04:45 | 2015-08-20 | 4 | 4 | 174 | 62.1833 | 1
2015-08-20 05:00 | 2015-08-20 | 4 | 5 | 175 | 62 | 1
2015-08-20 05:15 | 2015-08-20 | 4 | 5 | 195 | 62 | 1
2015-08-20 05:30 | 2015-08-20 | 4 | 5 | 175 | 62 | 1
2015-08-20 05:45 | 2015-08-20 | 4 | 5 | 175 | 62 | 1
2015-08-20 06:00 | 2015-08-20 | 4 | 6 | 168 | 62 | 1
2015-08-20 06:15 | 2015-08-20 | 4 | 6 | 183 | 62 | 1
2015-08-20 06:30 | 2015-08-20 | 4 | 6 | 189 | 62 | 1
2015-08-20 06:45 | 2015-08-20 | 4 | 6 | 169 | 62 | 1
2015-08-20 07:00 | 2015-08-20 | 4 | 7 | 172 | 62.0667 | 1
2015-08-20 07:15 | 2015-08-20 | 4 | 7 | 177 | 62.3167 | 1
2015-08-20 07:30 | 2015-08-20 | 4 | 7 | 191 | 62.5667 | 1
2015-08-20 07:45 | 2015-08-20 | 4 | 7 | 179 | 62.8167 | 1
2015-08-20 08:00 | 2015-08-20 | 4 | 8 | 176 | 63 | 1
2015-08-20 08:15 | 2015-08-20 | 4 | 8 | 184 | 63 | 1
2015-08-20 08:30 | 2015-08-20 | 4 | 8 | 187 | 63 | 1
2015-08-20 08:45 | 2015-08-20 | 4 | 8 | 204 | 63 | 1
2015-08-20 09:00 | 2015-08-20 | 4 | 9 | 185 | 63 | 1
2015-08-20 09:15 | 2015-08-20 | 4 | 9 | 192 | 63 | 1
2015-08-20 09:30 | 2015-08-20 | 4 | 9 | 197 | 63 | 1
2015-08-20 09:45 | 2015-08-20 | 4 | 9 | 192 | 63 | 1
2015-08-20 10:00 | 2015-08-20 | 4 | 10 | 208 | 63.2667 | 1
2015-08-20 10:15 | 2015-08-20 | 4 | 10 | 211 | 64.2667 | 1
2015-08-20 10:30 | 2015-08-20 | 4 | 10 | 208 | 65.2667 | 2
2015-08-20 10:45 | 2015-08-20 | 4 | 10 | 217 | 66.2667 | 2
2015-08-20 11:00 | 2015-08-20 | 4 | 11 | 212 | 67.0667 | 2
2015-08-20 11:15 | 2015-08-20 | 4 | 11 | 230 | 67.3167 | 2
2015-08-20 11:30 | 2015-08-20 | 4 | 11 | 223 | 67.5667 | 2
2015-08-20 11:45 | 2015-08-20 | 4 | 11 | 223 | 67.8167 | 2
2015-08-20 12:00 | 2015-08-20 | 4 | 12 | 226 | 68 | 2
2015-08-20 12:15 | 2015-08-20 | 4 | 12 | 220 | 68 | 2
2015-08-20 12:30 | 2015-08-20 | 4 | 12 | 213 | 68 | 2
2015-08-20 12:45 | 2015-08-20 | 4 | 12 | 219 | 68 | 2
2015-08-20 13:00 | 2015-08-20 | 4 | 13 | 222 | 68.0667 | 2
2015-08-20 13:15 | 2015-08-20 | 4 | 13 | 221 | 68.3167 | 2
2015-08-20 13:30 | 2015-08-20 | 4 | 13 | 222 | 68.5667 | 2
2015-08-20 13:45 | 2015-08-20 | 4 | 13 | 229 | 68.8167 | 2
2015-08-20 14:00 | 2015-08-20 | 4 | 14 | 219 | 68.9333 | 2
2015-08-20 14:15 | 2015-08-20 | 4 | 14 | 225 | 68.6833 | 2
2015-08-20 14:30 | 2015-08-20 | 4 | 14 | 218 | 68.4333 | 2
2015-08-20 14:45 | 2015-08-20 | 4 | 14 | 212 | 68.1833 | 2
2015-08-20 15:00 | 2015-08-20 | 4 | 15 | 242 | 68 | 2
2015-08-20 15:15 | 2015-08-20 | 4 | 15 | 227 | 68 | 2
2015-08-20 15:30 | 2015-08-20 | 4 | 15 | 222 | 68 | 2
2015-08-20 15:45 | 2015-08-20 | 4 | 15 | 239 | 68 | 2
2015-08-20 16:00 | 2015-08-20 | 4 | 16 | 228 | 67.9333 | 2
2015-08-20 16:15 | 2015-08-20 | 4 | 16 | 224 | 67.6833 | 2
2015-08-20 16:30 | 2015-08-20 | 4 | 16 | 217 | 67.4333 | 2
2015-08-20 16:45 | 2015-08-20 | 4 | 16 | 231 | 67.1833 | 2
2015-08-20 17:00 | 2015-08-20 | 4 | 17 | 232 | 66.8667 | 2
2015-08-20 17:15 | 2015-08-20 | 4 | 17 | 239 | 66.3667 | 2
2015-08-20 17:30 | 2015-08-20 | 4 | 17 | 226 | 65.8667 | 2
2015-08-20 17:45 | 2015-08-20 | 4 | 17 | 222 | 65.3667 | 2
2015-08-20 18:00 | 2015-08-20 | 4 | 18 | 228 | 64.8667 | 1
2015-08-20 18:15 | 2015-08-20 | 4 | 18 | 225 | 64.3667 | 1
2015-08-20 18:30 | 2015-08-20 | 4 | 18 | 221 | 63.8667 | 1
2015-08-20 18:45 | 2015-08-20 | 4 | 18 | 226 | 63.3667 | 1
2015-08-20 19:00 | 2015-08-20 | 4 | 19 | 215 | 63 | 1
2015-08-20 19:15 | 2015-08-20 | 4 | 19 | 220 | 63 | 1
2015-08-20 19:30 | 2015-08-20 | 4 | 19 | 228 | 63 | 1
2015-08-20 19:45 | 2015-08-20 | 4 | 19 | 214 | 63 | 1
2015-08-20 20:00 | 2015-08-20 | 4 | 20 | 206 | 63 | 1
2015-08-20 20:15 | 2015-08-20 | 4 | 20 | 208 | 63 | 1
2015-08-20 20:30 | 2015-08-20 | 4 | 20 | 212 | 63 | 1
2015-08-20 20:45 | 2015-08-20 | 4 | 20 | 190 | 63 | 1
2015-08-20 21:00 | 2015-08-20 | 4 | 21 | 197 | 63 | 1
2015-08-20 21:15 | 2015-08-20 | 4 | 21 | 190 | 63 | 1
2015-08-20 21:30 | 2015-08-20 | 4 | 21 | 207 | 63 | 1
2015-08-20 21:45 | 2015-08-20 | 4 | 21 | 184 | 62.44 | 1
2015-08-20 22:00 | 2015-08-20 | 4 | 22 | 185 | 61.9333 | 1
2015-08-20 22:15 | 2015-08-20 | 4 | 22 | 198 | 61.6833 | 1
2015-08-20 22:30 | 2015-08-20 | 4 | 22 | 185 | 61.4333 | 1
2015-08-20 22:45 | 2015-08-20 | 4 | 22 | 186 | 61.1833 | 1
2015-08-20 23:00 | 2015-08-20 | 4 | 23 | 184 | 61.1905 | 1
2015-08-20 23:15 | 2015-08-20 | 4 | 23 | 185 | 61.9048 | 1
2015-08-20 23:30 | 2015-08-20 | 4 | 23 | 181 | 62.619 | 1
2015-08-20 23:45 | 2015-08-20 | 4 | 23 | 176 | 62.2222 | 1
2015-08-21 | 2015-08-21 | 5 | 0 | 171 | 61 | 1
2015-08-21 00:15 | 2015-08-21 | 5 | 0 | 171 | 61 | 1
2015-08-21 00:30 | 2015-08-21 | 5 | 0 | 188 | 61 | 1
2015-08-21 00:45 | 2015-08-21 | 5 | 0 | 175 | 61 | 1
2015-08-21 01:00 | 2015-08-21 | 5 | 1 | 166 | 60.8667 | 1
2015-08-21 01:15 | 2015-08-21 | 5 | 1 | 172 | 60.3667 | 1
2015-08-21 01:30 | 2015-08-21 | 5 | 1 | 167 | 59.8667 | 1
2015-08-21 01:45 | 2015-08-21 | 5 | 1 | 183 | 59.3667 | 1
2015-08-21 02:00 | 2015-08-21 | 5 | 2 | 177 | 59 | 1
2015-08-21 02:15 | 2015-08-21 | 5 | 2 | 166 | 59 | 1
2015-08-21 02:30 | 2015-08-21 | 5 | 2 | 168 | 59 | 1
2015-08-21 02:45 | 2015-08-21 | 5 | 2 | 165 | 59 | 1
2015-08-21 03:00 | 2015-08-21 | 5 | 3 | 182 | 59 | 1
2015-08-21 03:15 | 2015-08-21 | 5 | 3 | 166 | 59 | 1
2015-08-21 03:30 | 2015-08-21 | 5 | 3 | 161 | 59 | 1
2015-08-21 03:45 | 2015-08-21 | 5 | 3 | 165 | 59 | 1
2015-08-21 04:00 | 2015-08-21 | 5 | 4 | 160 | 59 | 1
2015-08-21 04:15 | 2015-08-21 | 5 | 4 | 169 | 59 | 1
2015-08-21 04:30 | 2015-08-21 | 5 | 4 | 156 | 59 | 1
2015-08-21 04:45 | 2015-08-21 | 5 | 4 | 157 | 59 | 1
2015-08-21 05:00 | 2015-08-21 | 5 | 5 | 152 | 59.0667 | 1
2015-08-21 05:15 | 2015-08-21 | 5 | 5 | 174 | 59.3167 | 1
2015-08-21 05:30 | 2015-08-21 | 5 | 5 | 160 | 59.5667 | 1
2015-08-21 05:45 | 2015-08-21 | 5 | 5 | 155 | 59.8167 | 1
2015-08-21 06:00 | 2015-08-21 | 5 | 6 | 154 | 60.0667 | 1
2015-08-21 06:15 | 2015-08-21 | 5 | 6 | 153 | 60.3167 | 1
2015-08-21 06:30 | 2015-08-21 | 5 | 6 | 165 | 60.5667 | 1
2015-08-21 06:45 | 2015-08-21 | 5 | 6 | 176 | 60.8167 | 1
2015-08-21 07:00 | 2015-08-21 | 5 | 7 | 158 | 61.2581 | 1
2015-08-21 07:15 | 2015-08-21 | 5 | 7 | 166 | 62.2258 | 1
2015-08-21 07:30 | 2015-08-21 | 5 | 7 | 166 | 63.1034 | 1
2015-08-21 07:45 | 2015-08-21 | 5 | 7 | 172 | 63.6207 | 1
2015-08-21 08:00 | 2015-08-21 | 5 | 8 | 183 | 64 | 1
2015-08-21 08:15 | 2015-08-21 | 5 | 8 | 166 | 64 | 1
2015-08-21 08:30 | 2015-08-21 | 5 | 8 | 170 | 64 | 1
2015-08-21 08:45 | 2015-08-21 | 5 | 8 | 186 | 64 | 1
2015-08-21 09:00 | 2015-08-21 | 5 | 9 | 186 | 64.2667 | 1
2015-08-21 09:15 | 2015-08-21 | 5 | 9 | 181 | 65.2667 | 2
2015-08-21 09:30 | 2015-08-21 | 5 | 9 | 186 | 66.2667 | 2
2015-08-21 09:45 | 2015-08-21 | 5 | 9 | 191 | 67.2667 | 2
2015-08-21 10:00 | 2015-08-21 | 5 | 10 | 202 | 68.2 | 2
2015-08-21 10:15 | 2015-08-21 | 5 | 10 | 198 | 68.95 | 2
2015-08-21 10:30 | 2015-08-21 | 5 | 10 | 199 | 69.7 | 2
2015-08-21 10:45 | 2015-08-21 | 5 | 10 | 198 | 70.45 | 3
2015-08-21 11:00 | 2015-08-21 | 5 | 11 | 204 | 70.8667 | 3
2015-08-21 11:15 | 2015-08-21 | 5 | 11 | 209 | 70.3667 | 3
2015-08-21 11:30 | 2015-08-21 | 5 | 11 | 224 | 69.8667 | 2
2015-08-21 11:45 | 2015-08-21 | 5 | 11 | 210 | 69.3667 | 2
2015-08-21 12:00 | 2015-08-21 | 5 | 12 | 208 | 69 | 2
2015-08-21 12:15 | 2015-08-21 | 5 | 12 | 216 | 69 | 2
2015-08-21 12:30 | 2015-08-21 | 5 | 12 | 215 | 69 | 2
2015-08-21 12:45 | 2015-08-21 | 5 | 12 | 210 | 69 | 2
2015-08-21 13:00 | 2015-08-21 | 5 | 13 | 209 | 69 | 2
2015-08-21 13:15 | 2015-08-21 | 5 | 13 | 236 | 69 | 2
2015-08-21 13:30 | 2015-08-21 | 5 | 13 | 221 | 69 | 2
2015-08-21 13:45 | 2015-08-21 | 5 | 13 | 211 | 69 | 2
2015-08-21 14:00 | 2015-08-21 | 5 | 14 | 220 | 68.9333 | 2
2015-08-21 14:15 | 2015-08-21 | 5 | 14 | 227 | 68.6833 | 2
2015-08-21 14:30 | 2015-08-21 | 5 | 14 | 217 | 68.4333 | 2
2015-08-21 14:45 | 2015-08-21 | 5 | 14 | 234 | 68.1833 | 2
2015-08-21 15:00 | 2015-08-21 | 5 | 15 | 230 | 68 | 2
2015-08-21 15:15 | 2015-08-21 | 5 | 15 | 222 | 68 | 2
2015-08-21 15:30 | 2015-08-21 | 5 | 15 | 243 | 68 | 2
2015-08-21 15:45 | 2015-08-21 | 5 | 15 | 232 | 68 | 2
2015-08-21 16:00 | 2015-08-21 | 5 | 16 | 227 | 67.8667 | 2
2015-08-21 16:15 | 2015-08-21 | 5 | 16 | 231 | 67.3667 | 2
2015-08-21 16:30 | 2015-08-21 | 5 | 16 | 223 | 66.8667 | 2
2015-08-21 16:45 | 2015-08-21 | 5 | 16 | 232 | 66.3667 | 2
2015-08-21 17:00 | 2015-08-21 | 5 | 17 | 235 | 65.9333 | 2
2015-08-21 17:15 | 2015-08-21 | 5 | 17 | 229 | 65.6833 | 2
2015-08-21 17:30 | 2015-08-21 | 5 | 17 | 213 | 65.4333 | 2
2015-08-21 17:45 | 2015-08-21 | 5 | 17 | 222 | 65.1833 | 2
2015-08-21 18:00 | 2015-08-21 | 5 | 18 | 227 | 64.8 | 1
2015-08-21 18:15 | 2015-08-21 | 5 | 18 | 222 | 64.05 | 1
2015-08-21 18:30 | 2015-08-21 | 5 | 18 | 232 | 63.3 | 1
2015-08-21 18:45 | 2015-08-21 | 5 | 18 | 211 | 62.55 | 1
2015-08-21 19:00 | 2015-08-21 | 5 | 19 | 225 | 62 | 1
2015-08-21 19:15 | 2015-08-21 | 5 | 19 | 215 | 62 | 1
2015-08-21 19:30 | 2015-08-21 | 5 | 19 | 217 | 62 | 1
2015-08-21 19:45 | 2015-08-21 | 5 | 19 | 210 | 62 | 1
2015-08-21 20:00 | 2015-08-21 | 5 | 20 | 221 | 62 | 1
2015-08-21 20:15 | 2015-08-21 | 5 | 20 | 203 | 62 | 1
2015-08-21 20:30 | 2015-08-21 | 5 | 20 | 202 | 62 | 1
2015-08-21 20:45 | 2015-08-21 | 5 | 20 | 193 | 62 | 1
2015-08-21 21:00 | 2015-08-21 | 5 | 21 | 200 | 62 | 1
2015-08-21 21:15 | 2015-08-21 | 5 | 21 | 197 | 62 | 1
2015-08-21 21:30 | 2015-08-21 | 5 | 21 | 175 | 62 | 1
2015-08-21 21:45 | 2015-08-21 | 5 | 21 | 174 | 62 | 1
2015-08-21 22:00 | 2015-08-21 | 5 | 22 | 188 | 61.9333 | 1
2015-08-21 22:15 | 2015-08-21 | 5 | 22 | 182 | 61.6833 | 1
2015-08-21 22:30 | 2015-08-21 | 5 | 22 | 171 | 61.4333 | 1
2015-08-21 22:45 | 2015-08-21 | 5 | 22 | 172 | 61.1833 | 1
2015-08-21 23:00 | 2015-08-21 | 5 | 23 | 188 | 61 | 1
2015-08-21 23:15 | 2015-08-21 | 5 | 23 | 176 | 61 | 1
2015-08-21 23:30 | 2015-08-21 | 5 | 23 | 163 | 61 | 1
2015-08-21 23:45 | 2015-08-21 | 5 | 23 | 168 | 61 | 1
2015-08-22 | 2015-08-22 | 6 | 0 | 164 | 60.9333 | 1
2015-08-22 00:15 | 2015-08-22 | 6 | 0 | 182 | 60.6833 | 1
2015-08-22 00:30 | 2015-08-22 | 6 | 0 | 173 | 60.4333 | 1
2015-08-22 00:45 | 2015-08-22 | 6 | 0 | 164 | 60.1833 | 1
2015-08-22 01:00 | 2015-08-22 | 6 | 1 | 161 | 60.0714 | 1
2015-08-22 01:15 | 2015-08-22 | 6 | 1 | 161 | 60.3393 | 1
2015-08-22 01:30 | 2015-08-22 | 6 | 1 | 181 | 60.6071 | 1
2015-08-22 01:45 | 2015-08-22 | 6 | 1 | 165 | 60.875 | 1
2015-08-22 02:00 | 2015-08-22 | 6 | 2 | 156 | 60.0952 | 1
2015-08-22 02:15 | 2015-08-22 | 6 | 2 | 163 | 60.4524 | 1
2015-08-22 02:30 | 2015-08-22 | 6 | 2 | 171 | 60.8095 | 1
2015-08-22 02:45 | 2015-08-22 | 6 | 2 | 167 | 60.6111 | 1
2015-08-22 03:00 | 2015-08-22 | 6 | 3 | 153 | 59.9333 | 1
2015-08-22 03:15 | 2015-08-22 | 6 | 3 | 159 | 59.6833 | 1
2015-08-22 03:30 | 2015-08-22 | 6 | 3 | 154 | 59.4333 | 1
2015-08-22 03:45 | 2015-08-22 | 6 | 3 | 169 | 59.1833 | 1
2015-08-22 04:00 | 2015-08-22 | 6 | 4 | 162 | 59.3077 | 1
2015-08-22 04:15 | 2015-08-22 | 6 | 4 | 159 | 60.4615 | 1
2015-08-22 04:30 | 2015-08-22 | 6 | 4 | 155 | 61 | 1
2015-08-22 04:45 | 2015-08-22 | 6 | 4 | 157 | 61 | 1
2015-08-22 05:00 | 2015-08-22 | 6 | 5 | 173 | 61 | 1
2015-08-22 05:15 | 2015-08-22 | 6 | 5 | 153 | 61 | 1
2015-08-22 05:30 | 2015-08-22 | 6 | 5 | 157 | 61 | 1
2015-08-22 05:45 | 2015-08-22 | 6 | 5 | 155 | 61 | 1
2015-08-22 06:00 | 2015-08-22 | 6 | 6 | 157 | 61.0667 | 1
2015-08-22 06:15 | 2015-08-22 | 6 | 6 | 170 | 61.3167 | 1
2015-08-22 06:30 | 2015-08-22 | 6 | 6 | 151 | 61.5667 | 1
2015-08-22 06:45 | 2015-08-22 | 6 | 6 | 155 | 61.8167 | 1
2015-08-22 07:00 | 2015-08-22 | 6 | 7 | 153 | 62.0667 | 1
2015-08-22 07:15 | 2015-08-22 | 6 | 7 | 170 | 62.3167 | 1
2015-08-22 07:30 | 2015-08-22 | 6 | 7 | 159 | 62.5667 | 1
2015-08-22 07:45 | 2015-08-22 | 6 | 7 | 150 | 62.8167 | 1
2015-08-22 08:00 | 2015-08-22 | 6 | 8 | 153 | 63.1333 | 1
2015-08-22 08:15 | 2015-08-22 | 6 | 8 | 154 | 63.6333 | 1
2015-08-22 08:30 | 2015-08-22 | 6 | 8 | 154 | 64.1333 | 1
2015-08-22 08:45 | 2015-08-22 | 6 | 8 | 167 | 64.6333 | 1
2015-08-22 09:00 | 2015-08-22 | 6 | 9 | 148 | 65.2 | 2
2015-08-22 09:15 | 2015-08-22 | 6 | 9 | 151 | 65.95 | 2
2015-08-22 09:30 | 2015-08-22 | 6 | 9 | 154 | 66.7 | 2
2015-08-22 09:45 | 2015-08-22 | 6 | 9 | 174 | 67.45 | 2
2015-08-22 10:00 | 2015-08-22 | 6 | 10 | 165 | 68.0667 | 2
2015-08-22 10:15 | 2015-08-22 | 6 | 10 | 159 | 68.3167 | 2
2015-08-22 10:30 | 2015-08-22 | 6 | 10 | 167 | 68.5667 | 2
2015-08-22 10:45 | 2015-08-22 | 6 | 10 | 171 | 68.8167 | 2
2015-08-22 11:00 | 2015-08-22 | 6 | 11 | 175 | 69.0667 | 2
2015-08-22 11:15 | 2015-08-22 | 6 | 11 | 165 | 69.3167 | 2
2015-08-22 11:30 | 2015-08-22 | 6 | 11 | 168 | 69.5667 | 2
2015-08-22 11:45 | 2015-08-22 | 6 | 11 | 167 | 69.8167 | 2
2015-08-22 12:00 | 2015-08-22 | 6 | 12 | 183 | 70.1333 | 3
2015-08-22 12:15 | 2015-08-22 | 6 | 12 | 182 | 70.6333 | 3
2015-08-22 12:30 | 2015-08-22 | 6 | 12 | 175 | 71.1333 | 3
2015-08-22 12:45 | 2015-08-22 | 6 | 12 | 180 | 71.6333 | 3
2015-08-22 13:00 | 2015-08-22 | 6 | 13 | 181 | 72 | 3
2015-08-22 13:15 | 2015-08-22 | 6 | 13 | 191 | 72 | 3
2015-08-22 13:30 | 2015-08-22 | 6 | 13 | 190 | 72 | 3
2015-08-22 13:45 | 2015-08-22 | 6 | 13 | 179 | 72 | 3
2015-08-22 14:00 | 2015-08-22 | 6 | 14 | 180 | 72 | 3
2015-08-22 14:15 | 2015-08-22 | 6 | 14 | 183 | 72 | 3
2015-08-22 14:30 | 2015-08-22 | 6 | 14 | 198 | 72 | 3
2015-08-22 14:45 | 2015-08-22 | 6 | 14 | 206 | 72 | 3
2015-08-22 15:00 | 2015-08-22 | 6 | 15 | 194 | 71.9333 | 3
2015-08-22 15:15 | 2015-08-22 | 6 | 15 | 192 | 71.6833 | 3
2015-08-22 15:30 | 2015-08-22 | 6 | 15 | 205 | 71.4333 | 3
2015-08-22 15:45 | 2015-08-22 | 6 | 15 | 200 | 71.1833 | 3
2015-08-22 16:00 | 2015-08-22 | 6 | 16 | 221 | 70.8667 | 3
2015-08-22 16:15 | 2015-08-22 | 6 | 16 | 204 | 70.3667 | 3
2015-08-22 16:30 | 2015-08-22 | 6 | 16 | 203 | 69.8667 | 2
2015-08-22 16:45 | 2015-08-22 | 6 | 16 | 201 | 69.3667 | 2
2015-08-22 17:00 | 2015-08-22 | 6 | 17 | 205 | 68.8 | 2
2015-08-22 17:15 | 2015-08-22 | 6 | 17 | 224 | 68.05 | 2
2015-08-22 17:30 | 2015-08-22 | 6 | 17 | 198 | 67.3 | 2
2015-08-22 17:45 | 2015-08-22 | 6 | 17 | 214 | 66.55 | 2
2015-08-22 18:00 | 2015-08-22 | 6 | 18 | 205 | 65.7333 | 2
2015-08-22 18:15 | 2015-08-22 | 6 | 18 | 189 | 64.7333 | 1
2015-08-22 18:30 | 2015-08-22 | 6 | 18 | 199 | 63.7333 | 1
2015-08-22 18:45 | 2015-08-22 | 6 | 18 | 195 | 62.7333 | 1
2015-08-22 19:00 | 2015-08-22 | 6 | 19 | 205 | 62 | 1
2015-08-22 19:15 | 2015-08-22 | 6 | 19 | 189 | 62 | 1
2015-08-22 19:30 | 2015-08-22 | 6 | 19 | 192 | 62 | 1
2015-08-22 19:45 | 2015-08-22 | 6 | 19 | 186 | 62 | 1
2015-08-22 20:00 | 2015-08-22 | 6 | 20 | 185 | 62 | 1
2015-08-22 20:15 | 2015-08-22 | 6 | 20 | 195 | 62 | 1
2015-08-22 20:30 | 2015-08-22 | 6 | 20 | 191 | 62 | 1
2015-08-22 20:45 | 2015-08-22 | 6 | 20 | 176 | 62 | 1
2015-08-22 21:00 | 2015-08-22 | 6 | 21 | 179 | 61.9333 | 1
2015-08-22 21:15 | 2015-08-22 | 6 | 21 | 187 | 61.6833 | 1
2015-08-22 21:30 | 2015-08-22 | 6 | 21 | 185 | 61.4333 | 1
2015-08-22 21:45 | 2015-08-22 | 6 | 21 | 177 | 61.1833 | 1
2015-08-22 22:00 | 2015-08-22 | 6 | 22 | 178 | 61 | 1
2015-08-22 22:15 | 2015-08-22 | 6 | 22 | 166 | 61 | 1
2015-08-22 22:30 | 2015-08-22 | 6 | 22 | 184 | 61 | 1
2015-08-22 22:45 | 2015-08-22 | 6 | 22 | 175 | 61 | 1
2015-08-22 23:00 | 2015-08-22 | 6 | 23 | 163 | 61 | 1
2015-08-22 23:15 | 2015-08-22 | 6 | 23 | 162 | 61 | 1
2015-08-22 23:30 | 2015-08-22 | 6 | 23 | 174 | 61 | 1
2015-08-22 23:45 | 2015-08-22 | 6 | 23 | 177 | 61 | 1
2015-08-23 | 2015-08-23 | 7 | 0 | 158 | 61 | 1
2015-08-23 00:15 | 2015-08-23 | 7 | 0 | 160 | 61 | 1
2015-08-23 00:30 | 2015-08-23 | 7 | 0 | 158 | 61 | 1
2015-08-23 00:45 | 2015-08-23 | 7 | 0 | 166 | 61 | 1
2015-08-23 01:00 | 2015-08-23 | 7 | 1 | 161 | 61 | 1
2015-08-23 01:15 | 2015-08-23 | 7 | 1 | 157 | 60.9762 | 1
2015-08-23 01:30 | 2015-08-23 | 7 | 1 | 157 | 60.619 | 1
2015-08-23 01:45 | 2015-08-23 | 7 | 1 | 162 | 60.2619 | 1
2015-08-23 02:00 | 2015-08-23 | 7 | 2 | 164 | 60 | 1
2015-08-23 02:15 | 2015-08-23 | 7 | 2 | 154 | 60 | 1
2015-08-23 02:30 | 2015-08-23 | 7 | 2 | 148 | 60 | 1
2015-08-23 02:45 | 2015-08-23 | 7 | 2 | 147 | 60 | 1
2015-08-23 03:00 | 2015-08-23 | 7 | 3 | 164 | 60.1176 | 1
2015-08-23 03:15 | 2015-08-23 | 7 | 3 | 166 | 60.5588 | 1
2015-08-23 03:30 | 2015-08-23 | 7 | 3 | 146 | 61 | 1
2015-08-23 03:45 | 2015-08-23 | 7 | 3 | 150 | 60.4231 | 1
2015-08-23 04:00 | 2015-08-23 | 7 | 4 | 163 | 60.0667 | 1
2015-08-23 04:15 | 2015-08-23 | 7 | 4 | 162 | 60.3167 | 1
2015-08-23 04:30 | 2015-08-23 | 7 | 4 | 149 | 60.5667 | 1
2015-08-23 04:45 | 2015-08-23 | 7 | 4 | 151 | 60.8167 | 1
2015-08-23 05:00 | 2015-08-23 | 7 | 5 | 151 | 61 | 1
2015-08-23 05:15 | 2015-08-23 | 7 | 5 | 161 | 61 | 1
2015-08-23 05:30 | 2015-08-23 | 7 | 5 | 165 | 61 | 1
2015-08-23 05:45 | 2015-08-23 | 7 | 5 | 150 | 61 | 1
2015-08-23 06:00 | 2015-08-23 | 7 | 6 | 145 | 61.0667 | 1
2015-08-23 06:15 | 2015-08-23 | 7 | 6 | 151 | 61.3167 | 1
2015-08-23 06:30 | 2015-08-23 | 7 | 6 | 170 | 61.5667 | 1
2015-08-23 06:45 | 2015-08-23 | 7 | 6 | 148 | 61.8167 | 1
2015-08-23 07:00 | 2015-08-23 | 7 | 7 | 153 | 62.0667 | 1
2015-08-23 07:15 | 2015-08-23 | 7 | 7 | 155 | 62.3167 | 1
2015-08-23 07:30 | 2015-08-23 | 7 | 7 | 161 | 62.5667 | 1
2015-08-23 07:45 | 2015-08-23 | 7 | 7 | 171 | 62.8167 | 1
2015-08-23 08:00 | 2015-08-23 | 7 | 8 | 156 | 63.0889 | 1
2015-08-23 08:15 | 2015-08-23 | 7 | 8 | 159 | 63.4222 | 1
2015-08-23 08:30 | 2015-08-23 | 7 | 8 | 158 | 63.7556 | 1
2015-08-23 08:45 | 2015-08-23 | 7 | 8 | 178 | 64.2667 | 1
2015-08-23 09:00 | 2015-08-23 | 7 | 9 | 171 | 65.2 | 2
2015-08-23 09:15 | 2015-08-23 | 7 | 9 | 163 | 65.95 | 2
2015-08-23 09:30 | 2015-08-23 | 7 | 9 | 166 | 66.7 | 2
2015-08-23 09:45 | 2015-08-23 | 7 | 9 | 172 | 67.45 | 2
2015-08-23 10:00 | 2015-08-23 | 7 | 10 | 182 | 68.2 | 2
2015-08-23 10:15 | 2015-08-23 | 7 | 10 | 167 | 68.95 | 2
2015-08-23 10:30 | 2015-08-23 | 7 | 10 | 170 | 69.7 | 2
2015-08-23 10:45 | 2015-08-23 | 7 | 10 | 169 | 70.45 | 3
2015-08-23 11:00 | 2015-08-23 | 7 | 11 | 171 | 71.2 | 3
2015-08-23 11:15 | 2015-08-23 | 7 | 11 | 189 | 71.95 | 3
2015-08-23 11:30 | 2015-08-23 | 7 | 11 | 178 | 72.7 | 3
2015-08-23 11:45 | 2015-08-23 | 7 | 11 | 179 | 73.45 | 3
2015-08-23 12:00 | 2015-08-23 | 7 | 12 | 183 | 73.9333 | 3
2015-08-23 12:15 | 2015-08-23 | 7 | 12 | 187 | 73.6833 | 3
2015-08-23 12:30 | 2015-08-23 | 7 | 12 | 199 | 73.4333 | 3
2015-08-23 12:45 | 2015-08-23 | 7 | 12 | 186 | 73.1833 | 3
2015-08-23 13:00 | 2015-08-23 | 7 | 13 | 182 | 72.7333 | 3
2015-08-23 13:15 | 2015-08-23 | 7 | 13 | 184 | 71.7333 | 3
2015-08-23 13:30 | 2015-08-23 | 7 | 13 | 189 | 70.7333 | 3
2015-08-23 13:45 | 2015-08-23 | 7 | 13 | 203 | 69.7333 | 2
2015-08-23 14:00 | 2015-08-23 | 7 | 14 | 186 | 69.0667 | 2
2015-08-23 14:15 | 2015-08-23 | 7 | 14 | 188 | 69.3167 | 2
2015-08-23 14:30 | 2015-08-23 | 7 | 14 | 204 | 69.5667 | 2
2015-08-23 14:45 | 2015-08-23 | 7 | 14 | 186 | 69.8167 | 2
2015-08-23 15:00 | 2015-08-23 | 7 | 15 | 184 | 69.9333 | 2
2015-08-23 15:15 | 2015-08-23 | 7 | 15 | 199 | 69.6833 | 2
2015-08-23 15:30 | 2015-08-23 | 7 | 15 | 207 | 69.4333 | 2
2015-08-23 15:45 | 2015-08-23 | 7 | 15 | 196 | 69.1833 | 2
2015-08-23 16:00 | 2015-08-23 | 7 | 16 | 185 | 68.8667 | 2
2015-08-23 16:15 | 2015-08-23 | 7 | 16 | 194 | 68.3667 | 2
2015-08-23 16:30 | 2015-08-23 | 7 | 16 | 193 | 67.8667 | 2
2015-08-23 16:45 | 2015-08-23 | 7 | 16 | 204 | 67.3667 | 2
2015-08-23 17:00 | 2015-08-23 | 7 | 17 | 198 | 66.9333 | 2
2015-08-23 17:15 | 2015-08-23 | 7 | 17 | 191 | 66.6833 | 2
2015-08-23 17:30 | 2015-08-23 | 7 | 17 | 193 | 66.4333 | 2
2015-08-23 17:45 | 2015-08-23 | 7 | 17 | 199 | 66.1833 | 2
2015-08-23 18:00 | 2015-08-23 | 7 | 18 | 200 | 65.8 | 2
2015-08-23 18:15 | 2015-08-23 | 7 | 18 | 195 | 65.05 | 2
2015-08-23 18:30 | 2015-08-23 | 7 | 18 | 188 | 64.3 | 1
2015-08-23 18:45 | 2015-08-23 | 7 | 18 | 193 | 63.55 | 1
2015-08-23 19:00 | 2015-08-23 | 7 | 19 | 193 | 63 | 1
2015-08-23 19:15 | 2015-08-23 | 7 | 19 | 189 | 63 | 1
2015-08-23 19:30 | 2015-08-23 | 7 | 19 | 199 | 63 | 1
2015-08-23 19:45 | 2015-08-23 | 7 | 19 | 185 | 63 | 1
2015-08-23 20:00 | 2015-08-23 | 7 | 20 | 187 | 63 | 1
2015-08-23 20:15 | 2015-08-23 | 7 | 20 | 178 | 63 | 1
2015-08-23 20:30 | 2015-08-23 | 7 | 20 | 180 | 63 | 1
2015-08-23 20:45 | 2015-08-23 | 7 | 20 | 196 | 63 | 1
2015-08-23 21:00 | 2015-08-23 | 7 | 21 | 177 | 63 | 1
2015-08-23 21:15 | 2015-08-23 | 7 | 21 | 174 | 63 | 1
2015-08-23 21:30 | 2015-08-23 | 7 | 21 | 171 | 63 | 1
2015-08-23 21:45 | 2015-08-23 | 7 | 21 | 163 | 63 | 1
2015-08-23 22:00 | 2015-08-23 | 7 | 22 | 159 | 62.9333 | 1
2015-08-23 22:15 | 2015-08-23 | 7 | 22 | 167 | 62.6833 | 1
2015-08-23 22:30 | 2015-08-23 | 7 | 22 | 176 | 62.4333 | 1
2015-08-23 22:45 | 2015-08-23 | 7 | 22 | 158 | 62.1833 | 1
2015-08-23 23:00 | 2015-08-23 | 7 | 23 | 162 | 62.0755 | 1
2015-08-23 23:15 | 2015-08-23 | 7 | 23 | 159 | 62.3585 | 1
2015-08-23 23:30 | 2015-08-23 | 7 | 23 | 172 | 62.6415 | 1
2015-08-23 23:45 | 2015-08-23 | 7 | 23 | 163 | 62.9245 | 1
2015-08-24 | 2015-08-24 | 1 | 0 | 159 | 62 | 1
2015-08-24 00:15 | 2015-08-24 | 1 | 0 | 157 | 62 | 1
2015-08-24 00:30 | 2015-08-24 | 1 | 0 | 167 | 62 | 1
2015-08-24 00:45 | 2015-08-24 | 1 | 0 | 165 | 62 | 1
2015-08-24 01:00 | 2015-08-24 | 1 | 1 | 157 | 62 | 1
2015-08-24 01:15 | 2015-08-24 | 1 | 1 | 154 | 62 | 1
2015-08-24 01:30 | 2015-08-24 | 1 | 1 | 156 | 62 | 1
2015-08-24 01:45 | 2015-08-24 | 1 | 1 | 175 | 62 | 1
2015-08-24 02:00 | 2015-08-24 | 1 | 2 | 161 | 62 | 1
2015-08-24 02:15 | 2015-08-24 | 1 | 2 | 152 | 62 | 1
2015-08-24 02:30 | 2015-08-24 | 1 | 2 | 153 | 62 | 1
2015-08-24 02:45 | 2015-08-24 | 1 | 2 | 169 | 62 | 1
2015-08-24 03:00 | 2015-08-24 | 1 | 3 | 158 | 61.9333 | 1
2015-08-24 03:15 | 2015-08-24 | 1 | 3 | 152 | 61.6833 | 1
2015-08-24 03:30 | 2015-08-24 | 1 | 3 | 157 | 61.4333 | 1
2015-08-24 03:45 | 2015-08-24 | 1 | 3 | 157 | 61.1833 | 1
2015-08-24 04:00 | 2015-08-24 | 1 | 4 | 167 | 61 | 1
2015-08-24 04:15 | 2015-08-24 | 1 | 4 | 158 | 61 | 1
2015-08-24 04:30 | 2015-08-24 | 1 | 4 | 156 | 61 | 1
2015-08-24 04:45 | 2015-08-24 | 1 | 4 | 149 | 61 | 1
2015-08-24 05:00 | 2015-08-24 | 1 | 5 | 158 | 61 | 1
2015-08-24 05:15 | 2015-08-24 | 1 | 5 | 169 | 61 | 1
2015-08-24 05:30 | 2015-08-24 | 1 | 5 | 149 | 61 | 1
2015-08-24 05:45 | 2015-08-24 | 1 | 5 | 150 | 61 | 1
2015-08-24 06:00 | 2015-08-24 | 1 | 6 | 150 | 61.0667 | 1
2015-08-24 06:15 | 2015-08-24 | 1 | 6 | 152 | 61.3167 | 1
2015-08-24 06:30 | 2015-08-24 | 1 | 6 | 164 | 61.5667 | 1
2015-08-24 06:45 | 2015-08-24 | 1 | 6 | 155 | 61.8167 | 1
2015-08-24 07:00 | 2015-08-24 | 1 | 7 | 156 | 62.0667 | 1
2015-08-24 07:15 | 2015-08-24 | 1 | 7 | 151 | 62.3167 | 1
2015-08-24 07:30 | 2015-08-24 | 1 | 7 | 170 | 62.5667 | 1
2015-08-24 07:45 | 2015-08-24 | 1 | 7 | 164 | 62.8167 | 1
2015-08-24 08:00 | 2015-08-24 | 1 | 8 | 155 | 63.1333 | 1
2015-08-24 08:15 | 2015-08-24 | 1 | 8 | 162 | 63.6333 | 1
2015-08-24 08:30 | 2015-08-24 | 1 | 8 | 165 | 64.1333 | 1
2015-08-24 08:45 | 2015-08-24 | 1 | 8 | 169 | 64.6333 | 1
2015-08-24 09:00 | 2015-08-24 | 1 | 9 | 177 | 65.069 | 2
2015-08-24 09:15 | 2015-08-24 | 1 | 9 | 174 | 65.3276 | 2
2015-08-24 09:30 | 2015-08-24 | 1 | 9 | 177 | 65.5862 | 2
2015-08-24 09:45 | 2015-08-24 | 1 | 9 | 178 | 65.8448 | 2
2015-08-24 10:00 | 2015-08-24 | 1 | 10 | 195 | 67.0667 | 2
2015-08-24 10:15 | 2015-08-24 | 1 | 10 | 193 | 67.3167 | 2
2015-08-24 10:30 | 2015-08-24 | 1 | 10 | 189 | 67.5667 | 2
2015-08-24 10:45 | 2015-08-24 | 1 | 10 | 190 | 67.8167 | 2
2015-08-24 11:00 | 2015-08-24 | 1 | 11 | 208 | 68.0667 | 2
2015-08-24 11:15 | 2015-08-24 | 1 | 11 | 213 | 68.3167 | 2
2015-08-24 11:30 | 2015-08-24 | 1 | 11 | 203 | 68.5667 | 2
2015-08-24 11:45 | 2015-08-24 | 1 | 11 | 195 | 68.8167 | 2
2015-08-24 12:00 | 2015-08-24 | 1 | 12 | 203 | 69.1333 | 2
2015-08-24 12:15 | 2015-08-24 | 1 | 12 | 204 | 69.6333 | 2
2015-08-24 12:30 | 2015-08-24 | 1 | 12 | 215 | 70.1333 | 3
2015-08-24 12:45 | 2015-08-24 | 1 | 12 | 203 | 70.6333 | 3
2015-08-24 13:00 | 2015-08-24 | 1 | 13 | 202 | 71 | 3
2015-08-24 13:15 | 2015-08-24 | 1 | 13 | 209 | 71 | 3
2015-08-24 13:30 | 2015-08-24 | 1 | 13 | 223 | 71 | 3
2015-08-24 13:45 | 2015-08-24 | 1 | 13 | 203 | 71 | 3
2015-08-24 14:00 | 2015-08-24 | 1 | 14 | 208 | 71 | 3
2015-08-24 14:15 | 2015-08-24 | 1 | 14 | 209 | 71 | 3
2015-08-24 14:30 | 2015-08-24 | 1 | 14 | 221 | 71 | 3
2015-08-24 14:45 | 2015-08-24 | 1 | 14 | 235 | 71 | 3
2015-08-24 15:00 | 2015-08-24 | 1 | 15 | 218 | 70.9333 | 3
2015-08-24 15:15 | 2015-08-24 | 1 | 15 | 218 | 70.6833 | 3
2015-08-24 15:30 | 2015-08-24 | 1 | 15 | 221 | 70.4333 | 3
2015-08-24 15:45 | 2015-08-24 | 1 | 15 | 224 | 70.1833 | 3
2015-08-24 16:00 | 2015-08-24 | 1 | 16 | 247 | 69.8667 | 2
2015-08-24 16:15 | 2015-08-24 | 1 | 16 | 221 | 69.3667 | 2
2015-08-24 16:30 | 2015-08-24 | 1 | 16 | 220 | 68.8667 | 2
2015-08-24 16:45 | 2015-08-24 | 1 | 16 | 219 | 68.3667 | 2
2015-08-24 17:00 | 2015-08-24 | 1 | 17 | 233 | 67.8667 | 2
2015-08-24 17:15 | 2015-08-24 | 1 | 17 | 226 | 67.3667 | 2
2015-08-24 17:30 | 2015-08-24 | 1 | 17 | 215 | 66.8667 | 2
2015-08-24 17:45 | 2015-08-24 | 1 | 17 | 227 | 66.3667 | 2
2015-08-24 18:00 | 2015-08-24 | 1 | 18 | 210 | 65.8667 | 2
2015-08-24 18:15 | 2015-08-24 | 1 | 18 | 209 | 65.3667 | 2
2015-08-24 18:30 | 2015-08-24 | 1 | 18 | 225 | 64.8667 | 1
2015-08-24 18:45 | 2015-08-24 | 1 | 18 | 219 | 64.3667 | 1
2015-08-24 19:00 | 2015-08-24 | 1 | 19 | 200 | 63.9333 | 1
2015-08-24 19:15 | 2015-08-24 | 1 | 19 | 208 | 63.6833 | 1
2015-08-24 19:30 | 2015-08-24 | 1 | 19 | 203 | 63.4333 | 1
2015-08-24 19:45 | 2015-08-24 | 1 | 19 | 216 | 63.1833 | 1
2015-08-24 20:00 | 2015-08-24 | 1 | 20 | 200 | 62.9333 | 1
2015-08-24 20:15 | 2015-08-24 | 1 | 20 | 208 | 62.6833 | 1
2015-08-24 20:30 | 2015-08-24 | 1 | 20 | 202 | 62.4333 | 1
2015-08-24 20:45 | 2015-08-24 | 1 | 20 | 208 | 62.1833 | 1
2015-08-24 21:00 | 2015-08-24 | 1 | 21 | 195 | 62 | 1
2015-08-24 21:15 | 2015-08-24 | 1 | 21 | 206 | 62 | 1
2015-08-24 21:30 | 2015-08-24 | 1 | 21 | 205 | 62 | 1
2015-08-24 21:45 | 2015-08-24 | 1 | 21 | 187 | 62 | 1
2015-08-24 22:00 | 2015-08-24 | 1 | 22 | 194 | 61.9333 | 1
2015-08-24 22:15 | 2015-08-24 | 1 | 22 | 186 | 61.6833 | 1
2015-08-24 22:30 | 2015-08-24 | 1 | 22 | 198 | 61.4333 | 1
2015-08-24 22:45 | 2015-08-24 | 1 | 22 | 199 | 61.1833 | 1
2015-08-24 23:00 | 2015-08-24 | 1 | 23 | 178 | 60.9333 | 1
2015-08-24 23:15 | 2015-08-24 | 1 | 23 | 180 | 60.6833 | 1
2015-08-24 23:30 | 2015-08-24 | 1 | 23 | 184 | 60.4333 | 1
2015-08-24 23:45 | 2015-08-24 | 1 | 23 | 188 | 60.1833 | 1
2015-08-25 | 2015-08-25 | 2 | 0 | 191 | 60 | 1
2015-08-25 00:15 | 2015-08-25 | 2 | 0 | 183 | 60 | 1
2015-08-25 00:30 | 2015-08-25 | 2 | 0 | 176 | 60 | 1
2015-08-25 00:45 | 2015-08-25 | 2 | 0 | 172 | 60 | 1
2015-08-25 01:00 | 2015-08-25 | 2 | 1 | 182 | 59.9333 | 1
2015-08-25 01:15 | 2015-08-25 | 2 | 1 | 185 | 59.6833 | 1
2015-08-25 01:30 | 2015-08-25 | 2 | 1 | 159 | 59.4333 | 1
2015-08-25 01:45 | 2015-08-25 | 2 | 1 | 163 | 59.1833 | 1
2015-08-25 02:00 | 2015-08-25 | 2 | 2 | 162 | 59 | 1
2015-08-25 02:15 | 2015-08-25 | 2 | 2 | 174 | 59 | 1
2015-08-25 02:30 | 2015-08-25 | 2 | 2 | 160 | 59 | 1
2015-08-25 02:45 | 2015-08-25 | 2 | 2 | 158 | 59 | 1
2015-08-25 03:00 | 2015-08-25 | 2 | 3 | 165 | 59 | 1
2015-08-25 03:15 | 2015-08-25 | 2 | 3 | 170 | 59 | 1
2015-08-25 03:30 | 2015-08-25 | 2 | 3 | 162 | 59 | 1
2015-08-25 03:45 | 2015-08-25 | 2 | 3 | 159 | 59 | 1
2015-08-25 04:00 | 2015-08-25 | 2 | 4 | 156 | 58.9333 | 1
2015-08-25 04:15 | 2015-08-25 | 2 | 4 | 167 | 58.6833 | 1
2015-08-25 04:30 | 2015-08-25 | 2 | 4 | 177 | 58.4333 | 1
2015-08-25 04:45 | 2015-08-25 | 2 | 4 | 160 | 58.1833 | 1
2015-08-25 05:00 | 2015-08-25 | 2 | 5 | 160 | 58.0667 | 1
2015-08-25 05:15 | 2015-08-25 | 2 | 5 | 160 | 58.3167 | 1
2015-08-25 05:30 | 2015-08-25 | 2 | 5 | 170 | 58.5667 | 1
2015-08-25 05:45 | 2015-08-25 | 2 | 5 | 172 | 58.8167 | 1
2015-08-25 06:00 | 2015-08-25 | 2 | 6 | 156 | 59.0667 | 1
2015-08-25 06:15 | 2015-08-25 | 2 | 6 | 160 | 59.3167 | 1
2015-08-25 06:30 | 2015-08-25 | 2 | 6 | 158 | 59.5667 | 1
2015-08-25 06:45 | 2015-08-25 | 2 | 6 | 173 | 59.8167 | 1
2015-08-25 07:00 | 2015-08-25 | 2 | 7 | 162 | 60.1333 | 1
2015-08-25 07:15 | 2015-08-25 | 2 | 7 | 160 | 60.6333 | 1
2015-08-25 07:30 | 2015-08-25 | 2 | 7 | 162 | 61.1333 | 1
2015-08-25 07:45 | 2015-08-25 | 2 | 7 | 163 | 61.6333 | 1
2015-08-25 08:00 | 2015-08-25 | 2 | 8 | 188 | 62.125 | 1
2015-08-25 08:15 | 2015-08-25 | 2 | 8 | 177 | 62.5938 | 1
2015-08-25 08:30 | 2015-08-25 | 2 | 8 | 185 | 63.0714 | 1
2015-08-25 08:45 | 2015-08-25 | 2 | 8 | 181 | 63.6071 | 1
2015-08-25 09:00 | 2015-08-25 | 2 | 9 | 186 | 64.0667 | 1
2015-08-25 09:15 | 2015-08-25 | 2 | 9 | 204 | 64.3167 | 1
2015-08-25 09:30 | 2015-08-25 | 2 | 9 | 192 | 64.5667 | 1
2015-08-25 09:45 | 2015-08-25 | 2 | 9 | 193 | 64.8167 | 1
2015-08-25 10:00 | 2015-08-25 | 2 | 10 | 205 | 65.1333 | 2
2015-08-25 10:15 | 2015-08-25 | 2 | 10 | 195 | 65.6333 | 2
2015-08-25 10:30 | 2015-08-25 | 2 | 10 | 197 | 66.1333 | 2
2015-08-25 10:45 | 2015-08-25 | 2 | 10 | 196 | 66.6333 | 2
2015-08-25 11:00 | 2015-08-25 | 2 | 11 | 217 | 67.2 | 2
2015-08-25 11:15 | 2015-08-25 | 2 | 11 | 214 | 67.95 | 2
2015-08-25 11:30 | 2015-08-25 | 2 | 11 | 199 | 68.7 | 2
2015-08-25 11:45 | 2015-08-25 | 2 | 11 | 209 | 69.45 | 2
2015-08-25 12:00 | 2015-08-25 | 2 | 12 | 201 | 69.9333 | 2
2015-08-25 12:15 | 2015-08-25 | 2 | 12 | 223 | 69.6833 | 2
2015-08-25 12:30 | 2015-08-25 | 2 | 12 | 211 | 69.4333 | 2
2015-08-25 12:45 | 2015-08-25 | 2 | 12 | 207 | 69.1833 | 2
2015-08-25 13:00 | 2015-08-25 | 2 | 13 | 210 | 69 | 2
2015-08-25 13:15 | 2015-08-25 | 2 | 13 | 211 | 69 | 2
2015-08-25 13:30 | 2015-08-25 | 2 | 13 | 223 | 69 | 2
2015-08-25 13:45 | 2015-08-25 | 2 | 13 | 224 | 69 | 2
2015-08-25 14:00 | 2015-08-25 | 2 | 14 | 224 | 69 | 2
2015-08-25 14:15 | 2015-08-25 | 2 | 14 | 222 | 69 | 2
2015-08-25 14:30 | 2015-08-25 | 2 | 14 | 224 | 69 | 2
2015-08-25 14:45 | 2015-08-25 | 2 | 14 | 239 | 69 | 2
2015-08-25 15:00 | 2015-08-25 | 2 | 15 | 239 | 68.8667 | 2
2015-08-25 15:15 | 2015-08-25 | 2 | 15 | 238 | 68.3667 | 2
2015-08-25 15:30 | 2015-08-25 | 2 | 15 | 233 | 67.8667 | 2
2015-08-25 15:45 | 2015-08-25 | 2 | 15 | 240 | 67.3667 | 2
2015-08-25 16:00 | 2015-08-25 | 2 | 16 | 242 | 66.9333 | 2
2015-08-25 16:15 | 2015-08-25 | 2 | 16 | 244 | 66.6833 | 2
2015-08-25 16:30 | 2015-08-25 | 2 | 16 | 239 | 66.4333 | 2
2015-08-25 16:45 | 2015-08-25 | 2 | 16 | 241 | 66.1833 | 2
2015-08-25 17:00 | 2015-08-25 | 2 | 17 | 232 | 65.7333 | 2
2015-08-25 17:15 | 2015-08-25 | 2 | 17 | 241 | 64.7333 | 1
2015-08-25 17:30 | 2015-08-25 | 2 | 17 | 253 | 63.7333 | 1
2015-08-25 17:45 | 2015-08-25 | 2 | 17 | 227 | 62.7333 | 1
2015-08-25 18:00 | 2015-08-25 | 2 | 18 | 229 | 61.8667 | 1
2015-08-25 18:15 | 2015-08-25 | 2 | 18 | 216 | 61.3667 | 1
2015-08-25 18:30 | 2015-08-25 | 2 | 18 | 217 | 60.8667 | 1
2015-08-25 18:45 | 2015-08-25 | 2 | 18 | 233 | 60.3667 | 1
2015-08-25 19:00 | 2015-08-25 | 2 | 19 | 210 | 59.9333 | 1
2015-08-25 19:15 | 2015-08-25 | 2 | 19 | 218 | 59.6833 | 1
2015-08-25 19:30 | 2015-08-25 | 2 | 19 | 213 | 59.4333 | 1
2015-08-25 19:45 | 2015-08-25 | 2 | 19 | 210 | 59.1833 | 1
2015-08-25 20:00 | 2015-08-25 | 2 | 20 | 205 | 59 | 1
2015-08-25 20:15 | 2015-08-25 | 2 | 20 | 221 | 59 | 1
2015-08-25 20:30 | 2015-08-25 | 2 | 20 | 206 | 59 | 1
2015-08-25 20:45 | 2015-08-25 | 2 | 20 | 201 | 59 | 1
2015-08-25 21:00 | 2015-08-25 | 2 | 21 | 205 | 59 | 1
2015-08-25 21:15 | 2015-08-25 | 2 | 21 | 190 | 59 | 1
2015-08-25 21:30 | 2015-08-25 | 2 | 21 | 208 | 59 | 1
2015-08-25 21:45 | 2015-08-25 | 2 | 21 | 195 | 59 | 1
2015-08-25 22:00 | 2015-08-25 | 2 | 22 | 186 | 59 | 1
2015-08-25 22:15 | 2015-08-25 | 2 | 22 | 189 | 59 | 1
2015-08-25 22:30 | 2015-08-25 | 2 | 22 | 189 | 59 | 1
2015-08-25 22:45 | 2015-08-25 | 2 | 22 | 197 | 59 | 1
2015-08-25 23:00 | 2015-08-25 | 2 | 23 | 185 | 59 | 1
2015-08-25 23:15 | 2015-08-25 | 2 | 23 | 181 | 59 | 1
2015-08-25 23:30 | 2015-08-25 | 2 | 23 | 169 | 59 | 1
2015-08-25 23:45 | 2015-08-25 | 2 | 23 | 172 | 59 | 1
2015-08-26 | 2015-08-26 | 3 | 0 | 186 | 59 | 1
2015-08-26 00:15 | 2015-08-26 | 3 | 0 | 171 | 59 | 1
2015-08-26 00:30 | 2015-08-26 | 3 | 0 | 167 | 59 | 1
2015-08-26 00:45 | 2015-08-26 | 3 | 0 | 167 | 59 | 1
2015-08-26 01:00 | 2015-08-26 | 3 | 1 | 185 | 58.9333 | 1
2015-08-26 01:15 | 2015-08-26 | 3 | 1 | 169 | 58.6833 | 1
2015-08-26 01:30 | 2015-08-26 | 3 | 1 | 164 | 58.4333 | 1
2015-08-26 01:45 | 2015-08-26 | 3 | 1 | 170 | 58.1833 | 1
2015-08-26 02:00 | 2015-08-26 | 3 | 2 | 162 | 58 | 1
2015-08-26 02:15 | 2015-08-26 | 3 | 2 | 154 | 58 | 1
2015-08-26 02:30 | 2015-08-26 | 3 | 2 | 158 | 58 | 1
2015-08-26 02:45 | 2015-08-26 | 3 | 2 | 162 | 58 | 1
2015-08-26 03:00 | 2015-08-26 | 3 | 3 | 171 | 58 | 1
2015-08-26 03:15 | 2015-08-26 | 3 | 3 | 163 | 58 | 1
2015-08-26 03:30 | 2015-08-26 | 3 | 3 | 158 | 58 | 1
2015-08-26 03:45 | 2015-08-26 | 3 | 3 | 157 | 58 | 1
2015-08-26 04:00 | 2015-08-26 | 3 | 4 | 169 | 58 | 1
2015-08-26 04:15 | 2015-08-26 | 3 | 4 | 169 | 58 | 1
2015-08-26 04:30 | 2015-08-26 | 3 | 4 | 153 | 58 | 1
2015-08-26 04:45 | 2015-08-26 | 3 | 4 | 155 | 58 | 1
2015-08-26 05:00 | 2015-08-26 | 3 | 5 | 165 | 58.0667 | 1
2015-08-26 05:15 | 2015-08-26 | 3 | 5 | 163 | 58.3167 | 1
2015-08-26 05:30 | 2015-08-26 | 3 | 5 | 158 | 58.5667 | 1
2015-08-26 05:45 | 2015-08-26 | 3 | 5 | 155 | 58.8167 | 1
2015-08-26 06:00 | 2015-08-26 | 3 | 6 | 167 | 59 | 1
2015-08-26 06:15 | 2015-08-26 | 3 | 6 | 174 | 59 | 1
2015-08-26 06:30 | 2015-08-26 | 3 | 6 | 176 | 59 | 1
2015-08-26 06:45 | 2015-08-26 | 3 | 6 | 161 | 59 | 1
2015-08-26 07:00 | 2015-08-26 | 3 | 7 | 167 | 59.2667 | 1
2015-08-26 07:15 | 2015-08-26 | 3 | 7 | 160 | 60.2667 | 1
2015-08-26 07:30 | 2015-08-26 | 3 | 7 | 175 | 61.2667 | 1
2015-08-26 07:45 | 2015-08-26 | 3 | 7 | 168 | 62.2667 | 1
2015-08-26 08:00 | 2015-08-26 | 3 | 8 | 169 | 63.2 | 1
2015-08-26 08:15 | 2015-08-26 | 3 | 8 | 179 | 63.95 | 1
2015-08-26 08:30 | 2015-08-26 | 3 | 8 | 184 | 64.7 | 1
2015-08-26 08:45 | 2015-08-26 | 3 | 8 | 194 | 65.45 | 2
2015-08-26 09:00 | 2015-08-26 | 3 | 9 | 182 | 66.1333 | 2
2015-08-26 09:15 | 2015-08-26 | 3 | 9 | 189 | 66.6333 | 2
2015-08-26 09:30 | 2015-08-26 | 3 | 9 | 193 | 67.1333 | 2
2015-08-26 09:45 | 2015-08-26 | 3 | 9 | 195 | 67.6333 | 2
2015-08-26 10:00 | 2015-08-26 | 3 | 10 | 200 | 68.2667 | 2
2015-08-26 10:15 | 2015-08-26 | 3 | 10 | 198 | 69.2667 | 2
2015-08-26 10:30 | 2015-08-26 | 3 | 10 | 203 | 70.2667 | 3
2015-08-26 10:45 | 2015-08-26 | 3 | 10 | 206 | 71.2667 | 3
2015-08-26 11:00 | 2015-08-26 | 3 | 11 | 210 | 72.1333 | 3
2015-08-26 11:15 | 2015-08-26 | 3 | 11 | 217 | 72.6333 | 3
2015-08-26 11:30 | 2015-08-26 | 3 | 11 | 229 | 73.1333 | 3
2015-08-26 11:45 | 2015-08-26 | 3 | 11 | 222 | 73.6333 | 3
2015-08-26 12:00 | 2015-08-26 | 3 | 12 | 219 | 74.1333 | 3
2015-08-26 12:15 | 2015-08-26 | 3 | 12 | 223 | 74.6333 | 3
2015-08-26 12:30 | 2015-08-26 | 3 | 12 | 229 | 75.1333 | 4
2015-08-26 12:45 | 2015-08-26 | 3 | 12 | 220 | 75.6333 | 4
2015-08-26 13:00 | 2015-08-26 | 3 | 13 | 222 | 75.9333 | 4
2015-08-26 13:15 | 2015-08-26 | 3 | 13 | 222 | 75.6833 | 4
2015-08-26 13:30 | 2015-08-26 | 3 | 13 | 211 | 75.4333 | 4
2015-08-26 13:45 | 2015-08-26 | 3 | 13 | 232 | 75.1833 | 4
2015-08-26 14:00 | 2015-08-26 | 3 | 14 | 212 | 74.7333 | 3
2015-08-26 14:15 | 2015-08-26 | 3 | 14 | 242 | 73.7333 | 3
2015-08-26 14:30 | 2015-08-26 | 3 | 14 | 229 | 72.7333 | 3
2015-08-26 14:45 | 2015-08-26 | 3 | 14 | 220 | 71.7333 | 3
2015-08-26 15:00 | 2015-08-26 | 3 | 15 | 218 | 71 | 3
2015-08-26 15:15 | 2015-08-26 | 3 | 15 | 236 | 71 | 3
2015-08-26 15:30 | 2015-08-26 | 3 | 15 | 228 | 71 | 3
2015-08-26 15:45 | 2015-08-26 | 3 | 15 | 242 | 71 | 3
2015-08-26 16:00 | 2015-08-26 | 3 | 16 | 240 | 71.1333 | 3
2015-08-26 16:15 | 2015-08-26 | 3 | 16 | 234 | 71.6333 | 3
2015-08-26 16:30 | 2015-08-26 | 3 | 16 | 224 | 72.1333 | 3
2015-08-26 16:45 | 2015-08-26 | 3 | 16 | 230 | 72.6333 | 3
2015-08-26 17:00 | 2015-08-26 | 3 | 17 | 233 | 72.7333 | 3
2015-08-26 17:15 | 2015-08-26 | 3 | 17 | 241 | 71.7333 | 3
2015-08-26 17:30 | 2015-08-26 | 3 | 17 | 226 | 70.7333 | 3
2015-08-26 17:45 | 2015-08-26 | 3 | 17 | 215 | 69.7333 | 2
2015-08-26 18:00 | 2015-08-26 | 3 | 18 | 222 | 68.8 | 2
2015-08-26 18:15 | 2015-08-26 | 3 | 18 | 219 | 68.05 | 2
2015-08-26 18:30 | 2015-08-26 | 3 | 18 | 222 | 67.3 | 2
2015-08-26 18:45 | 2015-08-26 | 3 | 18 | 222 | 66.55 | 2
2015-08-26 19:00 | 2015-08-26 | 3 | 19 | 226 | 65.8667 | 2
2015-08-26 19:15 | 2015-08-26 | 3 | 19 | 220 | 65.3667 | 2
2015-08-26 19:30 | 2015-08-26 | 3 | 19 | 214 | 64.8667 | 1
2015-08-26 19:45 | 2015-08-26 | 3 | 19 | 206 | 64.3667 | 1
2015-08-26 20:00 | 2015-08-26 | 3 | 20 | 214 | 64 | 1
2015-08-26 20:15 | 2015-08-26 | 3 | 20 | 214 | 64 | 1
2015-08-26 20:30 | 2015-08-26 | 3 | 20 | 200 | 64 | 1
2015-08-26 20:45 | 2015-08-26 | 3 | 20 | 196 | 64 | 1
2015-08-26 21:00 | 2015-08-26 | 3 | 21 | 203 | 64 | 1
2015-08-26 21:15 | 2015-08-26 | 3 | 21 | 201 | 64 | 1
2015-08-26 21:30 | 2015-08-26 | 3 | 21 | 189 | 64 | 1
2015-08-26 21:45 | 2015-08-26 | 3 | 21 | 181 | 64 | 1
2015-08-26 22:00 | 2015-08-26 | 3 | 22 | 184 | 64 | 1
2015-08-26 22:15 | 2015-08-26 | 3 | 22 | 186 | 64 | 1
2015-08-26 22:30 | 2015-08-26 | 3 | 22 | 193 | 64 | 1
2015-08-26 22:45 | 2015-08-26 | 3 | 22 | 186 | 64 | 1
2015-08-26 23:00 | 2015-08-26 | 3 | 23 | 191 | 63.9333 | 1
2015-08-26 23:15 | 2015-08-26 | 3 | 23 | 185 | 63.6833 | 1
2015-08-26 23:30 | 2015-08-26 | 3 | 23 | 210 | 63.4333 | 1
2015-08-26 23:45 | 2015-08-26 | 3 | 23 | 201 | 63.1833 | 1
2015-08-27 | 2015-08-27 | 4 | 0 | 192 | 62.9333 | 1
2015-08-27 00:15 | 2015-08-27 | 4 | 0 | 196 | 62.6833 | 1
2015-08-27 00:30 | 2015-08-27 | 4 | 0 | 189 | 62.4333 | 1
2015-08-27 00:45 | 2015-08-27 | 4 | 0 | 195 | 62.1833 | 1
2015-08-27 01:00 | 2015-08-27 | 4 | 1 | 188 | 62 | 1
2015-08-27 01:15 | 2015-08-27 | 4 | 1 | 179 | 62 | 1
2015-08-27 01:30 | 2015-08-27 | 4 | 1 | 177 | 62 | 1
2015-08-27 01:45 | 2015-08-27 | 4 | 1 | 191 | 62 | 1
2015-08-27 02:00 | 2015-08-27 | 4 | 2 | 179 | 62 | 1
2015-08-27 02:15 | 2015-08-27 | 4 | 2 | 170 | 62 | 1
2015-08-27 02:30 | 2015-08-27 | 4 | 2 | 172 | 62 | 1
2015-08-27 02:45 | 2015-08-27 | 4 | 2 | 168 | 62 | 1
2015-08-27 03:00 | 2015-08-27 | 4 | 3 | 177 | 61.9333 | 1
2015-08-27 03:15 | 2015-08-27 | 4 | 3 | 180 | 61.6833 | 1
2015-08-27 03:30 | 2015-08-27 | 4 | 3 | 164 | 61.4333 | 1
2015-08-27 03:45 | 2015-08-27 | 4 | 3 | 166 | 61.1833 | 1
2015-08-27 04:00 | 2015-08-27 | 4 | 4 | 176 | 61 | 1
2015-08-27 04:15 | 2015-08-27 | 4 | 4 | 179 | 61 | 1
2015-08-27 04:30 | 2015-08-27 | 4 | 4 | 166 | 61 | 1
2015-08-27 04:45 | 2015-08-27 | 4 | 4 | 170 | 61 | 1
2015-08-27 05:00 | 2015-08-27 | 4 | 5 | 166 | 61 | 1
2015-08-27 05:15 | 2015-08-27 | 4 | 5 | 177 | 61 | 1
2015-08-27 05:30 | 2015-08-27 | 4 | 5 | 176 | 61 | 1
2015-08-27 05:45 | 2015-08-27 | 4 | 5 | 163 | 61 | 1
2015-08-27 06:00 | 2015-08-27 | 4 | 6 | 164 | 61.2 | 1
2015-08-27 06:15 | 2015-08-27 | 4 | 6 | 179 | 61.95 | 1
2015-08-27 06:30 | 2015-08-27 | 4 | 6 | 184 | 62.7 | 1
2015-08-27 06:45 | 2015-08-27 | 4 | 6 | 172 | 63.45 | 1
2015-08-27 07:00 | 2015-08-27 | 4 | 7 | 173 | 64.2 | 1
2015-08-27 07:15 | 2015-08-27 | 4 | 7 | 169 | 64.95 | 1
2015-08-27 07:30 | 2015-08-27 | 4 | 7 | 185 | 65.7 | 2
2015-08-27 07:45 | 2015-08-27 | 4 | 7 | 181 | 66.45 | 2
2015-08-27 08:00 | 2015-08-27 | 4 | 8 | 173 | 67.2 | 2
2015-08-27 08:15 | 2015-08-27 | 4 | 8 | 181 | 67.95 | 2
2015-08-27 08:30 | 2015-08-27 | 4 | 8 | 177 | 68.7 | 2
2015-08-27 08:45 | 2015-08-27 | 4 | 8 | 197 | 69.45 | 2
2015-08-27 09:00 | 2015-08-27 | 4 | 9 | 190 | 70.1333 | 3
2015-08-27 09:15 | 2015-08-27 | 4 | 9 | 188 | 70.6333 | 3
2015-08-27 09:30 | 2015-08-27 | 4 | 9 | 192 | 71.1333 | 3
2015-08-27 09:45 | 2015-08-27 | 4 | 9 | 201 | 71.6333 | 3
2015-08-27 10:00 | 2015-08-27 | 4 | 10 | 214 | 72.1333 | 3
2015-08-27 10:15 | 2015-08-27 | 4 | 10 | 201 | 72.6333 | 3
2015-08-27 10:30 | 2015-08-27 | 4 | 10 | 211 | 73.1333 | 3
2015-08-27 10:45 | 2015-08-27 | 4 | 10 | 204 | 73.6333 | 3
2015-08-27 11:00 | 2015-08-27 | 4 | 11 | 218 | 74.7333 | 3
2015-08-27 11:15 | 2015-08-27 | 4 | 11 | 228 | 77.4833 | 4
2015-08-27 11:30 | 2015-08-27 | 4 | 11 | 218 | 80.2333 | 5
2015-08-27 11:45 | 2015-08-27 | 4 | 11 | 220 | 82.9833 | 5
2015-08-27 12:00 | 2015-08-27 | 4 | 12 | 217 | 84.9333 | 5
2015-08-27 12:15 | 2015-08-27 | 4 | 12 | 249 | 84.6833 | 5
2015-08-27 12:30 | 2015-08-27 | 4 | 12 | 226 | 84.4333 | 5
2015-08-27 12:45 | 2015-08-27 | 4 | 12 | 220 | 84.1833 | 5
2015-08-27 13:00 | 2015-08-27 | 4 | 13 | 235 | 83.7333 | 5
2015-08-27 13:15 | 2015-08-27 | 4 | 13 | 235 | 82.7333 | 5
2015-08-27 13:30 | 2015-08-27 | 4 | 13 | 257 | 81.7333 | 5
2015-08-27 13:45 | 2015-08-27 | 4 | 13 | 242 | 80.7333 | 5
2015-08-27 14:00 | 2015-08-27 | 4 | 14 | 247 | 79.9333 | 4
2015-08-27 14:15 | 2015-08-27 | 4 | 14 | 247 | 79.6833 | 4
2015-08-27 14:30 | 2015-08-27 | 4 | 14 | 255 | 79.4333 | 4
2015-08-27 14:45 | 2015-08-27 | 4 | 14 | 260 | 79.1833 | 4
2015-08-27 15:00 | 2015-08-27 | 4 | 15 | 254 | 78.8667 | 4
2015-08-27 15:15 | 2015-08-27 | 4 | 15 | 257 | 78.3667 | 4
2015-08-27 15:30 | 2015-08-27 | 4 | 15 | 254 | 77.8667 | 4
2015-08-27 15:45 | 2015-08-27 | 4 | 15 | 261 | 77.3667 | 4
2015-08-27 16:00 | 2015-08-27 | 4 | 16 | 263 | 77 | 4
2015-08-27 16:15 | 2015-08-27 | 4 | 16 | 253 | 77 | 4
2015-08-27 16:30 | 2015-08-27 | 4 | 16 | 258 | 77 | 4
2015-08-27 16:45 | 2015-08-27 | 4 | 16 | 256 | 77 | 4
2015-08-27 17:00 | 2015-08-27 | 4 | 17 | 254 | 76.7333 | 4
2015-08-27 17:15 | 2015-08-27 | 4 | 17 | 261 | 75.7333 | 4
2015-08-27 17:30 | 2015-08-27 | 4 | 17 | 251 | 74.7333 | 3
2015-08-27 17:45 | 2015-08-27 | 4 | 17 | 242 | 73.7333 | 3
2015-08-27 18:00 | 2015-08-27 | 4 | 18 | 248 | 72.8667 | 3
2015-08-27 18:15 | 2015-08-27 | 4 | 18 | 234 | 72.3667 | 3
2015-08-27 18:30 | 2015-08-27 | 4 | 18 | 257 | 71.8667 | 3
2015-08-27 18:45 | 2015-08-27 | 4 | 18 | 235 | 71.3667 | 3
2015-08-27 19:00 | 2015-08-27 | 4 | 19 | 243 | 70.8667 | 3
2015-08-27 19:15 | 2015-08-27 | 4 | 19 | 227 | 70.3667 | 3
2015-08-27 19:30 | 2015-08-27 | 4 | 19 | 224 | 69.8667 | 2
2015-08-27 19:45 | 2015-08-27 | 4 | 19 | 223 | 69.3667 | 2
2015-08-27 20:00 | 2015-08-27 | 4 | 20 | 234 | 69.0667 | 2
2015-08-27 20:15 | 2015-08-27 | 4 | 20 | 207 | 69.3167 | 2
2015-08-27 20:30 | 2015-08-27 | 4 | 20 | 228 | 69.5667 | 2
2015-08-27 20:45 | 2015-08-27 | 4 | 20 | 203 | 69.8167 | 2
2015-08-27 21:00 | 2015-08-27 | 4 | 21 | 224 | 69.8667 | 2
2015-08-27 21:15 | 2015-08-27 | 4 | 21 | 209 | 69.3667 | 2
2015-08-27 21:30 | 2015-08-27 | 4 | 21 | 185 | 68.8667 | 2
2015-08-27 21:45 | 2015-08-27 | 4 | 21 | 191 | 68.3667 | 2
2015-08-27 22:00 | 2015-08-27 | 4 | 22 | 193 | 67.9333 | 2
2015-08-27 22:15 | 2015-08-27 | 4 | 22 | 195 | 67.6833 | 2
2015-08-27 22:30 | 2015-08-27 | 4 | 22 | 190 | 67.4333 | 2
2015-08-27 22:45 | 2015-08-27 | 4 | 22 | 182 | 67.1833 | 2
2015-08-27 23:00 | 2015-08-27 | 4 | 23 | 177 | 67 | 2
2015-08-27 23:15 | 2015-08-27 | 4 | 23 | 193 | 67 | 2
2015-08-27 23:30 | 2015-08-27 | 4 | 23 | 181 | 67 | 2
2015-08-27 23:45 | 2015-08-27 | 4 | 23 | 183 | 67 | 2
2015-08-28 | 2015-08-28 | 5 | 0 | 176 | 67 | 2
2015-08-28 00:15 | 2015-08-28 | 5 | 0 | 176 | 67 | 2
2015-08-28 00:30 | 2015-08-28 | 5 | 0 | 194 | 67 | 2
2015-08-28 00:45 | 2015-08-28 | 5 | 0 | 172 | 67 | 2
2015-08-28 01:00 | 2015-08-28 | 5 | 1 | 180 | 66.9333 | 2
2015-08-28 01:15 | 2015-08-28 | 5 | 1 | 176 | 66.6833 | 2
2015-08-28 01:30 | 2015-08-28 | 5 | 1 | 169 | 66.4333 | 2
2015-08-28 01:45 | 2015-08-28 | 5 | 1 | 187 | 66.1833 | 2
2015-08-28 02:00 | 2015-08-28 | 5 | 2 | 180 | 65.9333 | 2
2015-08-28 02:15 | 2015-08-28 | 5 | 2 | 175 | 65.6833 | 2
2015-08-28 02:30 | 2015-08-28 | 5 | 2 | 172 | 65.4333 | 2
2015-08-28 02:45 | 2015-08-28 | 5 | 2 | 163 | 65.1833 | 2
2015-08-28 03:00 | 2015-08-28 | 5 | 3 | 183 | 65 | 1
2015-08-28 03:15 | 2015-08-28 | 5 | 3 | 173 | 65 | 1
2015-08-28 03:30 | 2015-08-28 | 5 | 3 | 172 | 65 | 1
2015-08-28 03:45 | 2015-08-28 | 5 | 3 | 167 | 65 | 1
2015-08-28 04:00 | 2015-08-28 | 5 | 4 | 168 | 65 | 1
2015-08-28 04:15 | 2015-08-28 | 5 | 4 | 179 | 65 | 1
2015-08-28 04:30 | 2015-08-28 | 5 | 4 | 168 | 65 | 1
2015-08-28 04:45 | 2015-08-28 | 5 | 4 | 168 | 65 | 1
2015-08-28 05:00 | 2015-08-28 | 5 | 5 | 157 | 65.0667 | 2
2015-08-28 05:15 | 2015-08-28 | 5 | 5 | 171 | 65.3167 | 2
2015-08-28 05:30 | 2015-08-28 | 5 | 5 | 178 | 65.5667 | 2
2015-08-28 05:45 | 2015-08-28 | 5 | 5 | 164 | 65.8167 | 2
2015-08-28 06:00 | 2015-08-28 | 5 | 6 | 170 | 66.1333 | 2
2015-08-28 06:15 | 2015-08-28 | 5 | 6 | 166 | 66.6333 | 2
2015-08-28 06:30 | 2015-08-28 | 5 | 6 | 178 | 67.1333 | 2
2015-08-28 06:45 | 2015-08-28 | 5 | 6 | 182 | 67.6333 | 2
2015-08-28 07:00 | 2015-08-28 | 5 | 7 | 169 | 68.1333 | 2
2015-08-28 07:15 | 2015-08-28 | 5 | 7 | 178 | 68.6333 | 2
2015-08-28 07:30 | 2015-08-28 | 5 | 7 | 171 | 69.1333 | 2
2015-08-28 07:45 | 2015-08-28 | 5 | 7 | 183 | 69.6333 | 2
2015-08-28 08:00 | 2015-08-28 | 5 | 8 | 183 | 70.3333 | 3
2015-08-28 08:15 | 2015-08-28 | 5 | 8 | 180 | 71.5833 | 3
2015-08-28 08:30 | 2015-08-28 | 5 | 8 | 184 | 72.8333 | 3
2015-08-28 08:45 | 2015-08-28 | 5 | 8 | 192 | 74.0833 | 3
2015-08-28 09:00 | 2015-08-28 | 5 | 9 | 205 | 74.9333 | 3
2015-08-28 09:15 | 2015-08-28 | 5 | 9 | 201 | 74.6833 | 3
2015-08-28 09:30 | 2015-08-28 | 5 | 9 | 209 | 74.4333 | 3
2015-08-28 09:45 | 2015-08-28 | 5 | 9 | 198 | 74.1833 | 3
2015-08-28 10:00 | 2015-08-28 | 5 | 10 | 218 | 74.2 | 3
2015-08-28 10:15 | 2015-08-28 | 5 | 10 | 226 | 74.95 | 3
2015-08-28 10:30 | 2015-08-28 | 5 | 10 | 221 | 75.7 | 4
2015-08-28 10:45 | 2015-08-28 | 5 | 10 | 222 | 76.45 | 4
2015-08-28 11:00 | 2015-08-28 | 5 | 11 | 233 | 77.2 | 4
2015-08-28 11:15 | 2015-08-28 | 5 | 11 | 240 | 77.95 | 4
2015-08-28 11:30 | 2015-08-28 | 5 | 11 | 250 | 78.7 | 4
2015-08-28 11:45 | 2015-08-28 | 5 | 11 | 243 | 79.45 | 4
2015-08-28 12:00 | 2015-08-28 | 5 | 12 | 246 | 80.5714 | 5
2015-08-28 12:15 | 2015-08-28 | 5 | 12 | 239 | 82.7143 | 5
2015-08-28 12:30 | 2015-08-28 | 5 | 12 | 247 | 85.5 | 6
2015-08-28 12:45 | 2015-08-28 | 5 | 12 | 264 | 89.25 | 6
2015-08-28 13:00 | 2015-08-28 | 5 | 13 | 246 | 91.5333 | 7
2015-08-28 13:15 | 2015-08-28 | 5 | 13 | 252 | 89.7833 | 6
2015-08-28 13:30 | 2015-08-28 | 5 | 13 | 258 | 88.0333 | 6
2015-08-28 13:45 | 2015-08-28 | 5 | 13 | 274 | 86.2833 | 6
2015-08-28 14:00 | 2015-08-28 | 5 | 14 | 269 | 84.7333 | 5
2015-08-28 14:15 | 2015-08-28 | 5 | 14 | 267 | 83.7333 | 5
2015-08-28 14:30 | 2015-08-28 | 5 | 14 | 266 | 82.7333 | 5
2015-08-28 14:45 | 2015-08-28 | 5 | 14 | 266 | 81.7333 | 5
2015-08-28 15:00 | 2015-08-28 | 5 | 15 | 290 | 80.4667 | 5
2015-08-28 15:15 | 2015-08-28 | 5 | 15 | 272 | 78.4667 | 4
2015-08-28 15:30 | 2015-08-28 | 5 | 15 | 268 | 76.4667 | 4
2015-08-28 15:45 | 2015-08-28 | 5 | 15 | 276 | 74.4667 | 3
2015-08-28 16:00 | 2015-08-28 | 5 | 16 | 272 | 72.6667 | 3
2015-08-28 16:15 | 2015-08-28 | 5 | 16 | 243 | 71.4167 | 3
2015-08-28 16:30 | 2015-08-28 | 5 | 16 | 250 | 70.1667 | 3
2015-08-28 16:45 | 2015-08-28 | 5 | 16 | 255 | 68.9167 | 2
2015-08-28 17:00 | 2015-08-28 | 5 | 17 | 257 | 67.9333 | 2
2015-08-28 17:15 | 2015-08-28 | 5 | 17 | 247 | 67.6833 | 2
2015-08-28 17:30 | 2015-08-28 | 5 | 17 | 256 | 67.4333 | 2
2015-08-28 17:45 | 2015-08-28 | 5 | 17 | 243 | 67.1833 | 2
2015-08-28 18:00 | 2015-08-28 | 5 | 18 | 242 | 66.9333 | 2
2015-08-28 18:15 | 2015-08-28 | 5 | 18 | 245 | 66.6833 | 2
2015-08-28 18:30 | 2015-08-28 | 5 | 18 | 246 | 66.4333 | 2
2015-08-28 18:45 | 2015-08-28 | 5 | 18 | 245 | 66.1833 | 2
2015-08-28 19:00 | 2015-08-28 | 5 | 19 | 233 | 65.9333 | 2
2015-08-28 19:15 | 2015-08-28 | 5 | 19 | 240 | 65.6833 | 2
2015-08-28 19:30 | 2015-08-28 | 5 | 19 | 224 | 65.4333 | 2
2015-08-28 19:45 | 2015-08-28 | 5 | 19 | 238 | 65.1833 | 2
2015-08-28 20:00 | 2015-08-28 | 5 | 20 | 220 | 65.1111 | 2
2015-08-28 20:15 | 2015-08-28 | 5 | 20 | 213 | 65.5278 | 2
2015-08-28 20:30 | 2015-08-28 | 5 | 20 | 215 | 65.9444 | 2
2015-08-28 20:45 | 2015-08-28 | 5 | 20 | 215 | 66 | 2
2015-08-28 21:00 | 2015-08-28 | 5 | 21 | 220 | 66 | 2
2015-08-28 21:15 | 2015-08-28 | 5 | 21 | 207 | 66 | 2
2015-08-28 21:30 | 2015-08-28 | 5 | 21 | 209 | 66 | 2
2015-08-28 21:45 | 2015-08-28 | 5 | 21 | 211 | 66 | 2
2015-08-28 22:00 | 2015-08-28 | 5 | 22 | 196 | 65.75 | 2
2015-08-28 22:15 | 2015-08-28 | 5 | 22 | 203 | 64.8125 | 1
2015-08-28 22:30 | 2015-08-28 | 5 | 22 | 200 | 64.0714 | 1
2015-08-28 22:45 | 2015-08-28 | 5 | 22 | 185 | 64.6071 | 1
2015-08-28 23:00 | 2015-08-28 | 5 | 23 | 192 | 65 | 1
2015-08-28 23:15 | 2015-08-28 | 5 | 23 | 204 | 65 | 1
2015-08-28 23:30 | 2015-08-28 | 5 | 23 | 221 | 65 | 1
2015-08-28 23:45 | 2015-08-28 | 5 | 23 | 204 | 65 | 1
2015-08-29 | 2015-08-29 | 6 | 0 | 200 | 65.0667 | 2
2015-08-29 00:15 | 2015-08-29 | 6 | 0 | 195 | 65.3167 | 2
2015-08-29 00:30 | 2015-08-29 | 6 | 0 | 180 | 65.5667 | 2
2015-08-29 00:45 | 2015-08-29 | 6 | 0 | 191 | 65.8167 | 2
2015-08-29 01:00 | 2015-08-29 | 6 | 1 | 190 | 66.0667 | 2
2015-08-29 01:15 | 2015-08-29 | 6 | 1 | 183 | 66.3167 | 2
2015-08-29 01:30 | 2015-08-29 | 6 | 1 | 177 | 66.5667 | 2
2015-08-29 01:45 | 2015-08-29 | 6 | 1 | 188 | 66.8167 | 2
2015-08-29 02:00 | 2015-08-29 | 6 | 2 | 187 | 67 | 2
2015-08-29 02:15 | 2015-08-29 | 6 | 2 | 171 | 67 | 2
2015-08-29 02:30 | 2015-08-29 | 6 | 2 | 182 | 67 | 2
2015-08-29 02:45 | 2015-08-29 | 6 | 2 | 175 | 67 | 2
2015-08-29 03:00 | 2015-08-29 | 6 | 3 | 184 | 67 | 2
2015-08-29 03:15 | 2015-08-29 | 6 | 3 | 183 | 67 | 2
2015-08-29 03:30 | 2015-08-29 | 6 | 3 | 177 | 67 | 2
2015-08-29 03:45 | 2015-08-29 | 6 | 3 | 174 | 67 | 2
2015-08-29 04:00 | 2015-08-29 | 6 | 4 | 171 | 66.8519 | 2
2015-08-29 04:15 | 2015-08-29 | 6 | 4 | 195 | 66.2963 | 2
2015-08-29 04:30 | 2015-08-29 | 6 | 4 | 174 | 66.2121 | 2
2015-08-29 04:45 | 2015-08-29 | 6 | 4 | 169 | 66.6667 | 2
2015-08-29 05:00 | 2015-08-29 | 6 | 5 | 176 | 66.913 | 2
2015-08-29 05:15 | 2015-08-29 | 6 | 5 | 186 | 66.587 | 2
2015-08-29 05:30 | 2015-08-29 | 6 | 5 | 188 | 66.2609 | 2
2015-08-29 05:45 | 2015-08-29 | 6 | 5 | 169 | 66 | 2
2015-08-29 06:00 | 2015-08-29 | 6 | 6 | 171 | 66.0667 | 2
2015-08-29 06:15 | 2015-08-29 | 6 | 6 | 177 | 66.3167 | 2
2015-08-29 06:30 | 2015-08-29 | 6 | 6 | 194 | 66.5667 | 2
2015-08-29 06:45 | 2015-08-29 | 6 | 6 | 179 | 66.8167 | 2
2015-08-29 07:00 | 2015-08-29 | 6 | 7 | 173 | 67.1333 | 2
2015-08-29 07:15 | 2015-08-29 | 6 | 7 | 168 | 67.6333 | 2
2015-08-29 07:30 | 2015-08-29 | 6 | 7 | 179 | 68.1333 | 2
2015-08-29 07:45 | 2015-08-29 | 6 | 7 | 161 | 68.6333 | 2
2015-08-29 08:00 | 2015-08-29 | 6 | 8 | 169 | 69 | 2
2015-08-29 08:15 | 2015-08-29 | 6 | 8 | 154 | 69 | 2
2015-08-29 08:30 | 2015-08-29 | 6 | 8 | 152 | 69 | 2
2015-08-29 08:45 | 2015-08-29 | 6 | 8 | 161 | 69 | 2
2015-08-29 09:00 | 2015-08-29 | 6 | 9 | 169 | 69.25 | 2
2015-08-29 09:15 | 2015-08-29 | 6 | 9 | 158 | 70 | 2
2015-08-29 09:30 | 2015-08-29 | 6 | 9 | 162 | 70.037 | 3
2015-08-29 09:45 | 2015-08-29 | 6 | 9 | 178 | 70.5926 | 3
2015-08-29 10:00 | 2015-08-29 | 6 | 10 | 170 | 70.8667 | 3
2015-08-29 10:15 | 2015-08-29 | 6 | 10 | 166 | 70.3667 | 3
2015-08-29 10:30 | 2015-08-29 | 6 | 10 | 169 | 69.8667 | 2
2015-08-29 10:45 | 2015-08-29 | 6 | 10 | 178 | 69.3667 | 2
2015-08-29 11:00 | 2015-08-29 | 6 | 11 | 168 | 69.5714 | 2
2015-08-29 11:15 | 2015-08-29 | 6 | 11 | 164 | 71.7143 | 3
2015-08-29 11:30 | 2015-08-29 | 6 | 11 | 167 | 72.3333 | 3
2015-08-29 11:45 | 2015-08-29 | 6 | 11 | 168 | 72.7179 | 3
2015-08-29 12:00 | 2015-08-29 | 6 | 12 | 187 | 73.0667 | 3
2015-08-29 12:15 | 2015-08-29 | 6 | 12 | 176 | 73.3167 | 3
2015-08-29 12:30 | 2015-08-29 | 6 | 12 | 179 | 73.5667 | 3
2015-08-29 12:45 | 2015-08-29 | 6 | 12 | 176 | 73.8167 | 3
2015-08-29 13:00 | 2015-08-29 | 6 | 13 | 184 | 73.9333 | 3
2015-08-29 13:15 | 2015-08-29 | 6 | 13 | 188 | 73.6833 | 3
2015-08-29 13:30 | 2015-08-29 | 6 | 13 | 179 | 73.4333 | 3
2015-08-29 13:45 | 2015-08-29 | 6 | 13 | 176 | 73.1833 | 3
2015-08-29 14:00 | 2015-08-29 | 6 | 14 | 175 | 73.0667 | 3
2015-08-29 14:15 | 2015-08-29 | 6 | 14 | 200 | 73.3167 | 3
2015-08-29 14:30 | 2015-08-29 | 6 | 14 | 194 | 73.5667 | 3
2015-08-29 14:45 | 2015-08-29 | 6 | 14 | 189 | 73.8167 | 3
2015-08-29 15:00 | 2015-08-29 | 6 | 15 | 190 | 73.8667 | 3
2015-08-29 15:15 | 2015-08-29 | 6 | 15 | 195 | 73.3667 | 3
2015-08-29 15:30 | 2015-08-29 | 6 | 15 | 202 | 72.8667 | 3
2015-08-29 15:45 | 2015-08-29 | 6 | 15 | 184 | 72.3667 | 3
2015-08-29 16:00 | 2015-08-29 | 6 | 16 | 198 | 71.8667 | 3
2015-08-29 16:15 | 2015-08-29 | 6 | 16 | 188 | 71.3667 | 3
2015-08-29 16:30 | 2015-08-29 | 6 | 16 | 181 | 70.8667 | 3
2015-08-29 16:45 | 2015-08-29 | 6 | 16 | 193 | 70.3667 | 3
2015-08-29 17:00 | 2015-08-29 | 6 | 17 | 202 | 69.9333 | 2
2015-08-29 17:15 | 2015-08-29 | 6 | 17 | 191 | 69.6833 | 2
2015-08-29 17:30 | 2015-08-29 | 6 | 17 | 188 | 69.4333 | 2
2015-08-29 17:45 | 2015-08-29 | 6 | 17 | 186 | 69.1833 | 2
2015-08-29 18:00 | 2015-08-29 | 6 | 18 | 182 | 68.8 | 2
2015-08-29 18:15 | 2015-08-29 | 6 | 18 | 183 | 68.05 | 2
2015-08-29 18:30 | 2015-08-29 | 6 | 18 | 198 | 67.3 | 2
2015-08-29 18:45 | 2015-08-29 | 6 | 18 | 181 | 66.55 | 2
2015-08-29 19:00 | 2015-08-29 | 6 | 19 | 186 | 65.9333 | 2
2015-08-29 19:15 | 2015-08-29 | 6 | 19 | 177 | 65.6833 | 2
2015-08-29 19:30 | 2015-08-29 | 6 | 19 | 174 | 65.4333 | 2
2015-08-29 19:45 | 2015-08-29 | 6 | 19 | 169 | 65.1833 | 2
2015-08-29 20:00 | 2015-08-29 | 6 | 20 | 171 | 65 | 1
2015-08-29 20:15 | 2015-08-29 | 6 | 20 | 184 | 65 | 1
2015-08-29 20:30 | 2015-08-29 | 6 | 20 | 161 | 65 | 1
2015-08-29 20:45 | 2015-08-29 | 6 | 20 | 165 | 65 | 1
2015-08-29 21:00 | 2015-08-29 | 6 | 21 | 164 | 64.8571 | 1
2015-08-29 21:15 | 2015-08-29 | 6 | 21 | 164 | 64.3214 | 1
2015-08-29 21:30 | 2015-08-29 | 6 | 21 | 176 | 64.1875 | 1
2015-08-29 21:45 | 2015-08-29 | 6 | 21 | 165 | 64.6562 | 1
2015-08-29 22:00 | 2015-08-29 | 6 | 22 | 156 | 65.069 | 2
2015-08-29 22:15 | 2015-08-29 | 6 | 22 | 161 | 65.3276 | 2
2015-08-29 22:30 | 2015-08-29 | 6 | 22 | 179 | 65.5862 | 2
2015-08-29 22:45 | 2015-08-29 | 6 | 22 | 147 | 65.8448 | 2
2015-08-29 23:00 | 2015-08-29 | 6 | 23 | 157 | 65.9333 | 2
2015-08-29 23:15 | 2015-08-29 | 6 | 23 | 151 | 65.6833 | 2
2015-08-29 23:30 | 2015-08-29 | 6 | 23 | 159 | 65.4333 | 2
2015-08-29 23:45 | 2015-08-29 | 6 | 23 | 161 | 65.1833 | 2
2015-08-30 | 2015-08-30 | 7 | 0 | 144 | 65 | 1
2015-08-30 00:15 | 2015-08-30 | 7 | 0 | 145 | 65 | 1
2015-08-30 00:30 | 2015-08-30 | 7 | 0 | 159 | 65 | 1
2015-08-30 00:45 | 2015-08-30 | 7 | 0 | 153 | 65 | 1
2015-08-30 01:00 | 2015-08-30 | 7 | 1 | 140 | 64.8621 | 1
2015-08-30 01:15 | 2015-08-30 | 7 | 1 | 146 | 64.3448 | 1
2015-08-30 01:30 | 2015-08-30 | 7 | 1 | 144 | 63.8276 | 1
2015-08-30 01:45 | 2015-08-30 | 7 | 1 | 160 | 63.3103 | 1
2015-08-30 02:00 | 2015-08-30 | 7 | 2 | 137 | 63.1905 | 1
2015-08-30 02:15 | 2015-08-30 | 7 | 2 | 147 | 63.9048 | 1
2015-08-30 02:30 | 2015-08-30 | 7 | 2 | 135 | 63.6486 | 1
2015-08-30 02:45 | 2015-08-30 | 7 | 2 | 157 | 63.2432 | 1
2015-08-30 03:00 | 2015-08-30 | 7 | 3 | 146 | 63 | 1
2015-08-30 03:15 | 2015-08-30 | 7 | 3 | 146 | 63 | 1
2015-08-30 03:30 | 2015-08-30 | 7 | 3 | 136 | 63 | 1
2015-08-30 03:45 | 2015-08-30 | 7 | 3 | 158 | 63 | 1
2015-08-30 04:00 | 2015-08-30 | 7 | 4 | 147 | 63.0667 | 1
2015-08-30 04:15 | 2015-08-30 | 7 | 4 | 145 | 63.3167 | 1
2015-08-30 04:30 | 2015-08-30 | 7 | 4 | 138 | 63.5667 | 1
2015-08-30 04:45 | 2015-08-30 | 7 | 4 | 145 | 63.8167 | 1
2015-08-30 05:00 | 2015-08-30 | 7 | 5 | 152 | 63.9024 | 1
2015-08-30 05:15 | 2015-08-30 | 7 | 5 | 146 | 63.5366 | 1
2015-08-30 05:30 | 2015-08-30 | 7 | 5 | 142 | 63.1707 | 1
2015-08-30 05:45 | 2015-08-30 | 7 | 5 | 144 | 63 | 1
2015-08-30 06:00 | 2015-08-30 | 7 | 6 | 149 | 63 | 1
2015-08-30 06:15 | 2015-08-30 | 7 | 6 | 160 | 63.0682 | 1
2015-08-30 06:30 | 2015-08-30 | 7 | 6 | 138 | 63.4091 | 1
2015-08-30 06:45 | 2015-08-30 | 7 | 6 | 147 | 63.75 | 1
2015-08-30 07:00 | 2015-08-30 | 7 | 7 | 150 | 64 | 1
2015-08-30 07:15 | 2015-08-30 | 7 | 7 | 162 | 64 | 1
2015-08-30 07:30 | 2015-08-30 | 7 | 7 | 162 | 64 | 1
2015-08-30 07:45 | 2015-08-30 | 7 | 7 | 155 | 64 | 1
2015-08-30 08:00 | 2015-08-30 | 7 | 8 | 157 | 64.2667 | 1
2015-08-30 08:15 | 2015-08-30 | 7 | 8 | 150 | 65.2667 | 2
2015-08-30 08:30 | 2015-08-30 | 7 | 8 | 163 | 66.2667 | 2
2015-08-30 08:45 | 2015-08-30 | 7 | 8 | 165 | 67.2667 | 2
2015-08-30 09:00 | 2015-08-30 | 7 | 9 | 171 | 68.1333 | 2
2015-08-30 09:15 | 2015-08-30 | 7 | 9 | 158 | 68.6333 | 2
2015-08-30 09:30 | 2015-08-30 | 7 | 9 | 158 | 69.1333 | 2
2015-08-30 09:45 | 2015-08-30 | 7 | 9 | 162 | 69.6333 | 2
2015-08-30 10:00 | 2015-08-30 | 7 | 10 | 162 | 70.0667 | 3
2015-08-30 10:15 | 2015-08-30 | 7 | 10 | 173 | 70.3167 | 3
2015-08-30 10:30 | 2015-08-30 | 7 | 10 | 168 | 70.5667 | 3
2015-08-30 10:45 | 2015-08-30 | 7 | 10 | 162 | 70.8167 | 3
2015-08-30 11:00 | 2015-08-30 | 7 | 11 | 163 | 71.1333 | 3
2015-08-30 11:15 | 2015-08-30 | 7 | 11 | 185 | 71.6333 | 3
2015-08-30 11:30 | 2015-08-30 | 7 | 11 | 183 | 72.1333 | 3
2015-08-30 11:45 | 2015-08-30 | 7 | 11 | 177 | 72.6333 | 3
2015-08-30 12:00 | 2015-08-30 | 7 | 12 | 174 | 73.0667 | 3
2015-08-30 12:15 | 2015-08-30 | 7 | 12 | 173 | 73.3167 | 3
2015-08-30 12:30 | 2015-08-30 | 7 | 12 | 189 | 73.5667 | 3
2015-08-30 12:45 | 2015-08-30 | 7 | 12 | 183 | 73.8167 | 3
2015-08-30 13:00 | 2015-08-30 | 7 | 13 | 174 | 73.9333 | 3
2015-08-30 13:15 | 2015-08-30 | 7 | 13 | 178 | 73.6833 | 3
2015-08-30 13:30 | 2015-08-30 | 7 | 13 | 175 | 73.4333 | 3
2015-08-30 13:45 | 2015-08-30 | 7 | 13 | 188 | 73.1833 | 3
2015-08-30 14:00 | 2015-08-30 | 7 | 14 | 194 | 72.9333 | 3
2015-08-30 14:15 | 2015-08-30 | 7 | 14 | 176 | 72.6833 | 3
2015-08-30 14:30 | 2015-08-30 | 7 | 14 | 179 | 72.4333 | 3
2015-08-30 14:45 | 2015-08-30 | 7 | 14 | 188 | 72.1833 | 3
2015-08-30 15:00 | 2015-08-30 | 7 | 15 | 201 | 72 | 3
2015-08-30 15:15 | 2015-08-30 | 7 | 15 | 191 | 72 | 3
2015-08-30 15:30 | 2015-08-30 | 7 | 15 | 190 | 72 | 3
2015-08-30 15:45 | 2015-08-30 | 7 | 15 | 200 | 72 | 3
2015-08-30 16:00 | 2015-08-30 | 7 | 16 | 202 | 71.9333 | 3
2015-08-30 16:15 | 2015-08-30 | 7 | 16 | 204 | 71.6833 | 3
2015-08-30 16:30 | 2015-08-30 | 7 | 16 | 204 | 71.4333 | 3
2015-08-30 16:45 | 2015-08-30 | 7 | 16 | 190 | 71.1833 | 3
2015-08-30 17:00 | 2015-08-30 | 7 | 17 | 198 | 70.8667 | 3
2015-08-30 17:15 | 2015-08-30 | 7 | 17 | 213 | 70.3667 | 3
2015-08-30 17:30 | 2015-08-30 | 7 | 17 | 205 | 69.8667 | 2
2015-08-30 17:45 | 2015-08-30 | 7 | 17 | 195 | 69.3667 | 2
2015-08-30 18:00 | 2015-08-30 | 7 | 18 | 210 | 68.8667 | 2
2015-08-30 18:15 | 2015-08-30 | 7 | 18 | 189 | 68.3667 | 2
2015-08-30 18:30 | 2015-08-30 | 7 | 18 | 193 | 67.8667 | 2
2015-08-30 18:45 | 2015-08-30 | 7 | 18 | 183 | 67.3667 | 2
2015-08-30 19:00 | 2015-08-30 | 7 | 19 | 202 | 66.8667 | 2
2015-08-30 19:15 | 2015-08-30 | 7 | 19 | 193 | 66.3667 | 2
2015-08-30 19:30 | 2015-08-30 | 7 | 19 | 180 | 65.8667 | 2
2015-08-30 19:45 | 2015-08-30 | 7 | 19 | 173 | 65.3667 | 2
2015-08-30 20:00 | 2015-08-30 | 7 | 20 | 172 | 64.9333 | 1
2015-08-30 20:15 | 2015-08-30 | 7 | 20 | 186 | 64.6833 | 1
2015-08-30 20:30 | 2015-08-30 | 7 | 20 | 179 | 64.4333 | 1
2015-08-30 20:45 | 2015-08-30 | 7 | 20 | 167 | 64.1833 | 1
2015-08-30 21:00 | 2015-08-30 | 7 | 21 | 174 | 64.0667 | 1
2015-08-30 21:15 | 2015-08-30 | 7 | 21 | 180 | 64.3167 | 1
2015-08-30 21:30 | 2015-08-30 | 7 | 21 | 169 | 64.5667 | 1
2015-08-30 21:45 | 2015-08-30 | 7 | 21 | 163 | 64.8167 | 1
2015-08-30 22:00 | 2015-08-30 | 7 | 22 | 167 | 64.8667 | 1
2015-08-30 22:15 | 2015-08-30 | 7 | 22 | 153 | 64.3667 | 1
2015-08-30 22:30 | 2015-08-30 | 7 | 22 | 166 | 63.8667 | 1
2015-08-30 22:45 | 2015-08-30 | 7 | 22 | 170 | 63.3667 | 1
2015-08-30 23:00 | 2015-08-30 | 7 | 23 | 151 | 63 | 1
2015-08-30 23:15 | 2015-08-30 | 7 | 23 | 162 | 63 | 1
2015-08-30 23:30 | 2015-08-30 | 7 | 23 | 172 | 63 | 1
2015-08-30 23:45 | 2015-08-30 | 7 | 23 | 159 | 63 | 1
2015-08-31 | 2015-08-31 | 1 | 0 | 155 | 62.9333 | 1
2015-08-31 00:15 | 2015-08-31 | 1 | 0 | 158 | 62.6833 | 1
2015-08-31 00:30 | 2015-08-31 | 1 | 0 | 161 | 62.4333 | 1
2015-08-31 00:45 | 2015-08-31 | 1 | 0 | 164 | 62.1833 | 1
2015-08-31 01:00 | 2015-08-31 | 1 | 1 | 155 | 61.9333 | 1
2015-08-31 01:15 | 2015-08-31 | 1 | 1 | 153 | 61.6833 | 1
2015-08-31 01:30 | 2015-08-31 | 1 | 1 | 147 | 61.4333 | 1
2015-08-31 01:45 | 2015-08-31 | 1 | 1 | 161 | 61.1833 | 1
2015-08-31 02:00 | 2015-08-31 | 1 | 2 | 167 | 60.9333 | 1
2015-08-31 02:15 | 2015-08-31 | 1 | 2 | 146 | 60.6833 | 1
2015-08-31 02:30 | 2015-08-31 | 1 | 2 | 149 | 60.4333 | 1
2015-08-31 02:45 | 2015-08-31 | 1 | 2 | 151 | 60.1833 | 1
2015-08-31 03:00 | 2015-08-31 | 1 | 3 | 150 | 60 | 1
2015-08-31 03:15 | 2015-08-31 | 1 | 3 | 167 | 60 | 1
2015-08-31 03:30 | 2015-08-31 | 1 | 3 | 143 | 60 | 1
2015-08-31 03:45 | 2015-08-31 | 1 | 3 | 143 | 60 | 1
2015-08-31 04:00 | 2015-08-31 | 1 | 4 | 147 | 60 | 1
2015-08-31 04:15 | 2015-08-31 | 1 | 4 | 140 | 60 | 1
2015-08-31 04:30 | 2015-08-31 | 1 | 4 | 166 | 60 | 1
2015-08-31 04:45 | 2015-08-31 | 1 | 4 | 145 | 60 | 1
2015-08-31 05:00 | 2015-08-31 | 1 | 5 | 147 | 60.069 | 1
2015-08-31 05:15 | 2015-08-31 | 1 | 5 | 143 | 60.3276 | 1
2015-08-31 05:30 | 2015-08-31 | 1 | 5 | 144 | 60.5862 | 1
2015-08-31 05:45 | 2015-08-31 | 1 | 5 | 164 | 60.8448 | 1
2015-08-31 06:00 | 2015-08-31 | 1 | 6 | 145 | 60.2 | 1
2015-08-31 06:15 | 2015-08-31 | 1 | 6 | 144 | 60.95 | 1
2015-08-31 06:30 | 2015-08-31 | 1 | 6 | 142 | 61.7 | 1
2015-08-31 06:45 | 2015-08-31 | 1 | 6 | 141 | 62.45 | 1
2015-08-31 07:00 | 2015-08-31 | 1 | 7 | 158 | 63.2 | 1
2015-08-31 07:15 | 2015-08-31 | 1 | 7 | 146 | 63.95 | 1
2015-08-31 07:30 | 2015-08-31 | 1 | 7 | 141 | 64.7 | 1
2015-08-31 07:45 | 2015-08-31 | 1 | 7 | 144 | 65.45 | 2
2015-08-31 08:00 | 2015-08-31 | 1 | 8 | 154 | 66.0667 | 2
2015-08-31 08:15 | 2015-08-31 | 1 | 8 | 159 | 66.3167 | 2
2015-08-31 08:30 | 2015-08-31 | 1 | 8 | 179 | 66.5667 | 2
2015-08-31 08:45 | 2015-08-31 | 1 | 8 | 164 | 66.8167 | 2
2015-08-31 09:00 | 2015-08-31 | 1 | 9 | 171 | 67.2 | 2
2015-08-31 09:15 | 2015-08-31 | 1 | 9 | 165 | 67.95 | 2
2015-08-31 09:30 | 2015-08-31 | 1 | 9 | 178 | 68.7 | 2
2015-08-31 09:45 | 2015-08-31 | 1 | 9 | 186 | 69.45 | 2
2015-08-31 10:00 | 2015-08-31 | 1 | 10 | 191 | 70.2667 | 3
2015-08-31 10:15 | 2015-08-31 | 1 | 10 | 190 | 71.2667 | 3
2015-08-31 10:30 | 2015-08-31 | 1 | 10 | 197 | 72.2667 | 3
2015-08-31 10:45 | 2015-08-31 | 1 | 10 | 212 | 73.2667 | 3
2015-08-31 11:00 | 2015-08-31 | 1 | 11 | 199 | 74 | 3
2015-08-31 11:15 | 2015-08-31 | 1 | 11 | 196 | 74 | 3
2015-08-31 11:30 | 2015-08-31 | 1 | 11 | 198 | 74 | 3
2015-08-31 11:45 | 2015-08-31 | 1 | 11 | 191 | 74 | 3
2015-08-31 12:00 | 2015-08-31 | 1 | 12 | 218 | 74.0667 | 3
2015-08-31 12:15 | 2015-08-31 | 1 | 12 | 205 | 74.3167 | 3
2015-08-31 12:30 | 2015-08-31 | 1 | 12 | 203 | 74.5667 | 3
2015-08-31 12:45 | 2015-08-31 | 1 | 12 | 202 | 74.8167 | 3
2015-08-31 13:00 | 2015-08-31 | 1 | 13 | 201 | 75 | 3
2015-08-31 13:15 | 2015-08-31 | 1 | 13 | 222 | 75 | 3
2015-08-31 13:30 | 2015-08-31 | 1 | 13 | 218 | 75 | 3
2015-08-31 13:45 | 2015-08-31 | 1 | 13 | 226 | 75 | 3
2015-08-31 14:00 | 2015-08-31 | 1 | 14 | 214 | 74.8 | 3
2015-08-31 14:15 | 2015-08-31 | 1 | 14 | 233 | 74.05 | 3
2015-08-31 14:30 | 2015-08-31 | 1 | 14 | 238 | 73.3 | 3
2015-08-31 14:45 | 2015-08-31 | 1 | 14 | 228 | 72.55 | 3
2015-08-31 15:00 | 2015-08-31 | 1 | 15 | 226 | 71.9333 | 3
2015-08-31 15:15 | 2015-08-31 | 1 | 15 | 234 | 71.6833 | 3
2015-08-31 15:30 | 2015-08-31 | 1 | 15 | 238 | 71.4333 | 3
2015-08-31 15:45 | 2015-08-31 | 1 | 15 | 249 | 71.1833 | 3
2015-08-31 16:00 | 2015-08-31 | 1 | 16 | 231 | 70.8 | 3
2015-08-31 16:15 | 2015-08-31 | 1 | 16 | 231 | 70.05 | 3
2015-08-31 16:30 | 2015-08-31 | 1 | 16 | 240 | 69.3 | 2
2015-08-31 16:45 | 2015-08-31 | 1 | 16 | 238 | 68.55 | 2
2015-08-31 17:00 | 2015-08-31 | 1 | 17 | 262 | 67.8 | 2
2015-08-31 17:15 | 2015-08-31 | 1 | 17 | 230 | 67.05 | 2
2015-08-31 17:30 | 2015-08-31 | 1 | 17 | 234 | 66.3 | 2
2015-08-31 17:45 | 2015-08-31 | 1 | 17 | 227 | 65.55 | 2
2015-08-31 18:00 | 2015-08-31 | 1 | 18 | 229 | 64.9333 | 1
2015-08-31 18:15 | 2015-08-31 | 1 | 18 | 227 | 64.6833 | 1
2015-08-31 18:30 | 2015-08-31 | 1 | 18 | 231 | 64.4333 | 1
2015-08-31 18:45 | 2015-08-31 | 1 | 18 | 224 | 64.1833 | 1
2015-08-31 19:00 | 2015-08-31 | 1 | 19 | 218 | 63.9333 | 1
2015-08-31 19:15 | 2015-08-31 | 1 | 19 | 208 | 63.6833 | 1
2015-08-31 19:30 | 2015-08-31 | 1 | 19 | 220 | 63.4333 | 1
2015-08-31 19:45 | 2015-08-31 | 1 | 19 | 204 | 63.1833 | 1
2015-08-31 20:00 | 2015-08-31 | 1 | 20 | 202 | 63 | 1
2015-08-31 20:15 | 2015-08-31 | 1 | 20 | 196 | 63 | 1
2015-08-31 20:30 | 2015-08-31 | 1 | 20 | 210 | 63 | 1
2015-08-31 20:45 | 2015-08-31 | 1 | 20 | 198 | 63 | 1
2015-08-31 21:00 | 2015-08-31 | 1 | 21 | 195 | 63 | 1
2015-08-31 21:15 | 2015-08-31 | 1 | 21 | 185 | 63 | 1
2015-08-31 21:30 | 2015-08-31 | 1 | 21 | 204 | 63 | 1
2015-08-31 21:45 | 2015-08-31 | 1 | 21 | 193 | 63 | 1
2015-08-31 22:00 | 2015-08-31 | 1 | 22 | 196 | 62.9333 | 1
2015-08-31 22:15 | 2015-08-31 | 1 | 22 | 192 | 62.6833 | 1
2015-08-31 22:30 | 2015-08-31 | 1 | 22 | 185 | 62.4333 | 1
2015-08-31 22:45 | 2015-08-31 | 1 | 22 | 200 | 62.1833 | 1
2015-08-31 23:00 | 2015-08-31 | 1 | 23 | 195 | 61.9333 | 1
2015-08-31 23:15 | 2015-08-31 | 1 | 23 | 180 | 61.6833 | 1
2015-08-31 23:30 | 2015-08-31 | 1 | 23 | 178 | 61.4333 | 1
2015-08-31 23:45 | 2015-08-31 | 1 | 23 | 177 | 61.1833 | 1
2015-09-01 | 2015-09-01 | 2 | 0 | 184 | 61 | 1
2015-09-01 00:15 | 2015-09-01 | 2 | 0 | 176 | 61 | 1
2015-09-01 00:30 | 2015-09-01 | 2 | 0 | 168 | 61 | 1
2015-09-01 00:45 | 2015-09-01 | 2 | 0 | 171 | 61 | 1
2015-09-01 01:00 | 2015-09-01 | 2 | 1 | 170 | 61 | 1
2015-09-01 01:15 | 2015-09-01 | 2 | 1 | 168 | 61 | 1
2015-09-01 01:30 | 2015-09-01 | 2 | 1 | 164 | 61 | 1
2015-09-01 01:45 | 2015-09-01 | 2 | 1 | 179 | 61 | 1
2015-09-01 02:00 | 2015-09-01 | 2 | 2 | 166 | 60.9333 | 1
2015-09-01 02:15 | 2015-09-01 | 2 | 2 | 159 | 60.6833 | 1
2015-09-01 02:30 | 2015-09-01 | 2 | 2 | 160 | 60.4333 | 1
2015-09-01 02:45 | 2015-09-01 | 2 | 2 | 163 | 60.1833 | 1
2015-09-01 03:00 | 2015-09-01 | 2 | 3 | 173 | 60 | 1
2015-09-01 03:15 | 2015-09-01 | 2 | 3 | 163 | 60 | 1
2015-09-01 03:30 | 2015-09-01 | 2 | 3 | 161 | 60 | 1
2015-09-01 03:45 | 2015-09-01 | 2 | 3 | 154 | 60 | 1
2015-09-01 04:00 | 2015-09-01 | 2 | 4 | 173 | 60 | 1
2015-09-01 04:15 | 2015-09-01 | 2 | 4 | 159 | 60 | 1
2015-09-01 04:30 | 2015-09-01 | 2 | 4 | 154 | 60 | 1
2015-09-01 04:45 | 2015-09-01 | 2 | 4 | 158 | 60 | 1
2015-09-01 05:00 | 2015-09-01 | 2 | 5 | 157 | 60 | 1
2015-09-01 05:15 | 2015-09-01 | 2 | 5 | 167 | 60 | 1
2015-09-01 05:30 | 2015-09-01 | 2 | 5 | 151 | 60 | 1
2015-09-01 05:45 | 2015-09-01 | 2 | 5 | 150 | 60 | 1
2015-09-01 06:00 | 2015-09-01 | 2 | 6 | 150 | 60.1333 | 1
2015-09-01 06:15 | 2015-09-01 | 2 | 6 | 152 | 60.6333 | 1
2015-09-01 06:30 | 2015-09-01 | 2 | 6 | 162 | 61.1333 | 1
2015-09-01 06:45 | 2015-09-01 | 2 | 6 | 155 | 61.6333 | 1
2015-09-01 07:00 | 2015-09-01 | 2 | 7 | 159 | 62.2667 | 1
2015-09-01 07:15 | 2015-09-01 | 2 | 7 | 150 | 63.2667 | 1
2015-09-01 07:30 | 2015-09-01 | 2 | 7 | 156 | 64.2667 | 1
2015-09-01 07:45 | 2015-09-01 | 2 | 7 | 167 | 65.2667 | 2
2015-09-01 08:00 | 2015-09-01 | 2 | 8 | 152 | 66.1333 | 2
2015-09-01 08:15 | 2015-09-01 | 2 | 8 | 162 | 66.6333 | 2
2015-09-01 08:30 | 2015-09-01 | 2 | 8 | 166 | 67.1333 | 2
2015-09-01 08:45 | 2015-09-01 | 2 | 8 | 181 | 67.6333 | 2
2015-09-01 09:00 | 2015-09-01 | 2 | 9 | 187 | 68.2 | 2
2015-09-01 09:15 | 2015-09-01 | 2 | 9 | 180 | 68.95 | 2
2015-09-01 09:30 | 2015-09-01 | 2 | 9 | 188 | 69.7 | 2
2015-09-01 09:45 | 2015-09-01 | 2 | 9 | 182 | 70.45 | 3
2015-09-01 10:00 | 2015-09-01 | 2 | 10 | 198 | 71.0667 | 3
2015-09-01 10:15 | 2015-09-01 | 2 | 10 | 205 | 71.3167 | 3
2015-09-01 10:30 | 2015-09-01 | 2 | 10 | 185 | 71.5667 | 3
2015-09-01 10:45 | 2015-09-01 | 2 | 10 | 194 | 71.8167 | 3
2015-09-01 11:00 | 2015-09-01 | 2 | 11 | 194 | 72.1333 | 3
2015-09-01 11:15 | 2015-09-01 | 2 | 11 | 210 | 72.6333 | 3
2015-09-01 11:30 | 2015-09-01 | 2 | 11 | 205 | 73.1333 | 3
2015-09-01 11:45 | 2015-09-01 | 2 | 11 | 203 | 73.6333 | 3
2015-09-01 12:00 | 2015-09-01 | 2 | 12 | 209 | 74 | 3
2015-09-01 12:15 | 2015-09-01 | 2 | 12 | 203 | 74 | 3
2015-09-01 12:30 | 2015-09-01 | 2 | 12 | 219 | 74 | 3
2015-09-01 12:45 | 2015-09-01 | 2 | 12 | 211 | 74 | 3
2015-09-01 13:00 | 2015-09-01 | 2 | 13 | 212 | 74.1333 | 3
2015-09-01 13:15 | 2015-09-01 | 2 | 13 | 210 | 74.6333 | 3
2015-09-01 13:30 | 2015-09-01 | 2 | 13 | 214 | 75.1333 | 4
2015-09-01 13:45 | 2015-09-01 | 2 | 13 | 234 | 75.6333 | 4
2015-09-01 14:00 | 2015-09-01 | 2 | 14 | 231 | 75.9333 | 4
2015-09-01 14:15 | 2015-09-01 | 2 | 14 | 218 | 75.6833 | 4
2015-09-01 14:30 | 2015-09-01 | 2 | 14 | 231 | 75.4333 | 4
2015-09-01 14:45 | 2015-09-01 | 2 | 14 | 226 | 75.1833 | 4
2015-09-01 15:00 | 2015-09-01 | 2 | 15 | 242 | 74.8667 | 3
2015-09-01 15:15 | 2015-09-01 | 2 | 15 | 234 | 74.3667 | 3
2015-09-01 15:30 | 2015-09-01 | 2 | 15 | 240 | 73.8667 | 3
2015-09-01 15:45 | 2015-09-01 | 2 | 15 | 229 | 73.3667 | 3
2015-09-01 16:00 | 2015-09-01 | 2 | 16 | 235 | 72.7333 | 3
2015-09-01 16:15 | 2015-09-01 | 2 | 16 | 242 | 71.7333 | 3
2015-09-01 16:30 | 2015-09-01 | 2 | 16 | 250 | 70.7333 | 3
2015-09-01 16:45 | 2015-09-01 | 2 | 16 | 237 | 69.7333 | 2
2015-09-01 17:00 | 2015-09-01 | 2 | 17 | 250 | 68.7333 | 2
2015-09-01 17:15 | 2015-09-01 | 2 | 17 | 227 | 67.7333 | 2
2015-09-01 17:30 | 2015-09-01 | 2 | 17 | 248 | 66.7333 | 2
2015-09-01 17:45 | 2015-09-01 | 2 | 17 | 243 | 65.7333 | 2
2015-09-01 18:00 | 2015-09-01 | 2 | 18 | 228 | 64.9333 | 1
2015-09-01 18:15 | 2015-09-01 | 2 | 18 | 231 | 64.6833 | 1
2015-09-01 18:30 | 2015-09-01 | 2 | 18 | 219 | 64.4333 | 1
2015-09-01 18:45 | 2015-09-01 | 2 | 18 | 227 | 64.1833 | 1
2015-09-01 19:00 | 2015-09-01 | 2 | 19 | 238 | 63.9333 | 1
2015-09-01 19:15 | 2015-09-01 | 2 | 19 | 211 | 63.6833 | 1
2015-09-01 19:30 | 2015-09-01 | 2 | 19 | 210 | 63.4333 | 1
2015-09-01 19:45 | 2015-09-01 | 2 | 19 | 202 | 63.1833 | 1
2015-09-01 20:00 | 2015-09-01 | 2 | 20 | 203 | 63 | 1
2015-09-01 20:15 | 2015-09-01 | 2 | 20 | 209 | 63 | 1
2015-09-01 20:30 | 2015-09-01 | 2 | 20 | 201 | 63 | 1
2015-09-01 20:45 | 2015-09-01 | 2 | 20 | 209 | 63 | 1
2015-09-01 21:00 | 2015-09-01 | 2 | 21 | 207 | 63 | 1
2015-09-01 21:15 | 2015-09-01 | 2 | 21 | 192 | 63 | 1
2015-09-01 21:30 | 2015-09-01 | 2 | 21 | 198 | 63 | 1
2015-09-01 21:45 | 2015-09-01 | 2 | 21 | 193 | 63 | 1
2015-09-01 22:00 | 2015-09-01 | 2 | 22 | 192 | 63 | 1
2015-09-01 22:15 | 2015-09-01 | 2 | 22 | 181 | 63 | 1
2015-09-01 22:30 | 2015-09-01 | 2 | 22 | 192 | 63 | 1
2015-09-01 22:45 | 2015-09-01 | 2 | 22 | 201 | 63 | 1
2015-09-01 23:00 | 2015-09-01 | 2 | 23 | 181 | 63 | 1
2015-09-01 23:15 | 2015-09-01 | 2 | 23 | 183 | 63 | 1
2015-09-01 23:30 | 2015-09-01 | 2 | 23 | 177 | 63 | 1
2015-09-01 23:45 | 2015-09-01 | 2 | 23 | 184 | 63 | 1
2015-09-02 | 2015-09-02 | 3 | 0 | 183 | 63 | 1
2015-09-02 00:15 | 2015-09-02 | 3 | 0 | 173 | 63 | 1
2015-09-02 00:30 | 2015-09-02 | 3 | 0 | 163 | 63 | 1
2015-09-02 00:45 | 2015-09-02 | 3 | 0 | 169 | 63 | 1
2015-09-02 01:00 | 2015-09-02 | 3 | 1 | 172 | 62.9333 | 1
2015-09-02 01:15 | 2015-09-02 | 3 | 1 | 184 | 62.6833 | 1
2015-09-02 01:30 | 2015-09-02 | 3 | 1 | 168 | 62.4333 | 1
2015-09-02 01:45 | 2015-09-02 | 3 | 1 | 171 | 62.1833 | 1
2015-09-02 02:00 | 2015-09-02 | 3 | 2 | 167 | 62.0667 | 1
2015-09-02 02:15 | 2015-09-02 | 3 | 2 | 163 | 62.3167 | 1
2015-09-02 02:30 | 2015-09-02 | 3 | 2 | 181 | 62.5667 | 1
2015-09-02 02:45 | 2015-09-02 | 3 | 2 | 162 | 62.8167 | 1
2015-09-02 03:00 | 2015-09-02 | 3 | 3 | 155 | 63 | 1
2015-09-02 03:15 | 2015-09-02 | 3 | 3 | 162 | 63 | 1
2015-09-02 03:30 | 2015-09-02 | 3 | 3 | 170 | 63 | 1
2015-09-02 03:45 | 2015-09-02 | 3 | 3 | 167 | 63 | 1
2015-09-02 04:00 | 2015-09-02 | 3 | 4 | 158 | 63 | 1
2015-09-02 04:15 | 2015-09-02 | 3 | 4 | 154 | 63 | 1
2015-09-02 04:30 | 2015-09-02 | 3 | 4 | 164 | 63 | 1
2015-09-02 04:45 | 2015-09-02 | 3 | 4 | 178 | 63 | 1
2015-09-02 05:00 | 2015-09-02 | 3 | 5 | 163 | 63 | 1
2015-09-02 05:15 | 2015-09-02 | 3 | 5 | 162 | 63 | 1
2015-09-02 05:30 | 2015-09-02 | 3 | 5 | 153 | 63 | 1
2015-09-02 05:45 | 2015-09-02 | 3 | 5 | 160 | 63 | 1
2015-09-02 06:00 | 2015-09-02 | 3 | 6 | 174 | 63 | 1
2015-09-02 06:15 | 2015-09-02 | 3 | 6 | 157 | 63 | 1
2015-09-02 06:30 | 2015-09-02 | 3 | 6 | 166 | 63 | 1
2015-09-02 06:45 | 2015-09-02 | 3 | 6 | 157 | 63 | 1
2015-09-02 07:00 | 2015-09-02 | 3 | 7 | 172 | 63 | 1
2015-09-02 07:15 | 2015-09-02 | 3 | 7 | 175 | 63 | 1
2015-09-02 07:30 | 2015-09-02 | 3 | 7 | 160 | 63 | 1
2015-09-02 07:45 | 2015-09-02 | 3 | 7 | 160 | 63 | 1
2015-09-02 08:00 | 2015-09-02 | 3 | 8 | 165 | 63.1333 | 1
2015-09-02 08:15 | 2015-09-02 | 3 | 8 | 179 | 63.6333 | 1
2015-09-02 08:30 | 2015-09-02 | 3 | 8 | 180 | 64.1333 | 1
2015-09-02 08:45 | 2015-09-02 | 3 | 8 | 182 | 64.6333 | 1
2015-09-02 09:00 | 2015-09-02 | 3 | 9 | 173 | 65.2 | 2
2015-09-02 09:15 | 2015-09-02 | 3 | 9 | 189 | 65.95 | 2
2015-09-02 09:30 | 2015-09-02 | 3 | 9 | 198 | 66.7 | 2
2015-09-02 09:45 | 2015-09-02 | 3 | 9 | 181 | 67.45 | 2
2015-09-02 10:00 | 2015-09-02 | 3 | 10 | 185 | 66.8571 | 2
2015-09-02 10:15 | 2015-09-02 | 3 | 10 | 192 | 66.9057 | 2
2015-09-02 10:30 | 2015-09-02 | 3 | 10 | 211 | 68.0377 | 2
2015-09-02 10:45 | 2015-09-02 | 3 | 10 | 194 | 69.1698 | 2
2015-09-02 11:00 | 2015-09-02 | 3 | 11 | 201 | 69.9333 | 2
2015-09-02 11:15 | 2015-09-02 | 3 | 11 | 208 | 69.6833 | 2
2015-09-02 11:30 | 2015-09-02 | 3 | 11 | 205 | 69.4333 | 2
2015-09-02 11:45 | 2015-09-02 | 3 | 11 | 227 | 69.1833 | 2
2015-09-02 12:00 | 2015-09-02 | 3 | 12 | 213 | 69.2 | 2
2015-09-02 12:15 | 2015-09-02 | 3 | 12 | 212 | 69.95 | 2
2015-09-02 12:30 | 2015-09-02 | 3 | 12 | 205 | 70.7 | 3
2015-09-02 12:45 | 2015-09-02 | 3 | 12 | 211 | 71.45 | 3
2015-09-02 13:00 | 2015-09-02 | 3 | 13 | 217 | 71.8667 | 3
2015-09-02 13:15 | 2015-09-02 | 3 | 13 | 233 | 71.3667 | 3
2015-09-02 13:30 | 2015-09-02 | 3 | 13 | 221 | 70.8667 | 3
2015-09-02 13:45 | 2015-09-02 | 3 | 13 | 224 | 70.3667 | 3
2015-09-02 14:00 | 2015-09-02 | 3 | 14 | 227 | 70 | 2
2015-09-02 14:15 | 2015-09-02 | 3 | 14 | 232 | 70 | 2
2015-09-02 14:30 | 2015-09-02 | 3 | 14 | 225 | 70 | 2
2015-09-02 14:45 | 2015-09-02 | 3 | 14 | 251 | 70 | 2
2015-09-02 15:00 | 2015-09-02 | 3 | 15 | 221 | 68.9333 | 2
2015-09-02 15:15 | 2015-09-02 | 3 | 15 | 228 | 68.6833 | 2
2015-09-02 15:30 | 2015-09-02 | 3 | 15 | 229 | 68.4333 | 2
2015-09-02 15:45 | 2015-09-02 | 3 | 15 | 222 | 68.1833 | 2
2015-09-02 16:00 | 2015-09-02 | 3 | 16 | 235 | 67.9333 | 2
2015-09-02 16:15 | 2015-09-02 | 3 | 16 | 236 | 67.6833 | 2
2015-09-02 16:30 | 2015-09-02 | 3 | 16 | 223 | 67.4333 | 2
2015-09-02 16:45 | 2015-09-02 | 3 | 16 | 233 | 67.1833 | 2
2015-09-02 17:00 | 2015-09-02 | 3 | 17 | 229 | 66.8667 | 2
2015-09-02 17:15 | 2015-09-02 | 3 | 17 | 223 | 66.3667 | 2
2015-09-02 17:30 | 2015-09-02 | 3 | 17 | 225 | 65.8667 | 2
2015-09-02 17:45 | 2015-09-02 | 3 | 17 | 215 | 65.3667 | 2
2015-09-02 18:00 | 2015-09-02 | 3 | 18 | 217 | 64.9333 | 1
2015-09-02 18:15 | 2015-09-02 | 3 | 18 | 215 | 64.6833 | 1
2015-09-02 18:30 | 2015-09-02 | 3 | 18 | 215 | 64.4333 | 1
2015-09-02 18:45 | 2015-09-02 | 3 | 18 | 228 | 64.1833 | 1
2015-09-02 19:00 | 2015-09-02 | 3 | 19 | 212 | 63.9333 | 1
2015-09-02 19:15 | 2015-09-02 | 3 | 19 | 204 | 63.6833 | 1
2015-09-02 19:30 | 2015-09-02 | 3 | 19 | 197 | 63.4333 | 1
2015-09-02 19:45 | 2015-09-02 | 3 | 19 | 214 | 63.1833 | 1
2015-09-02 20:00 | 2015-09-02 | 3 | 20 | 204 | 63 | 1
2015-09-02 20:15 | 2015-09-02 | 3 | 20 | 206 | 63 | 1
2015-09-02 20:30 | 2015-09-02 | 3 | 20 | 192 | 63 | 1
2015-09-02 20:45 | 2015-09-02 | 3 | 20 | 192 | 63 | 1
2015-09-02 21:00 | 2015-09-02 | 3 | 21 | 205 | 63 | 1
2015-09-02 21:15 | 2015-09-02 | 3 | 21 | 197 | 63 | 1
2015-09-02 21:30 | 2015-09-02 | 3 | 21 | 185 | 63 | 1
2015-09-02 21:45 | 2015-09-02 | 3 | 21 | 186 | 63 | 1
2015-09-02 22:00 | 2015-09-02 | 3 | 22 | 186 | 62.9333 | 1
2015-09-02 22:15 | 2015-09-02 | 3 | 22 | 196 | 62.6833 | 1
2015-09-02 22:30 | 2015-09-02 | 3 | 22 | 182 | 62.4333 | 1
2015-09-02 22:45 | 2015-09-02 | 3 | 22 | 186 | 62.1833 | 1
2015-09-02 23:00 | 2015-09-02 | 3 | 23 | 184 | 62 | 1
2015-09-02 23:15 | 2015-09-02 | 3 | 23 | 184 | 62 | 1
2015-09-02 23:30 | 2015-09-02 | 3 | 23 | 188 | 62 | 1
2015-09-02 23:45 | 2015-09-02 | 3 | 23 | 171 | 62 | 1
2015-09-03 | 2015-09-03 | 4 | 0 | 177 | 61.9333 | 1
2015-09-03 00:15 | 2015-09-03 | 4 | 0 | 165 | 61.6833 | 1
2015-09-03 00:30 | 2015-09-03 | 4 | 0 | 182 | 61.4333 | 1
2015-09-03 00:45 | 2015-09-03 | 4 | 0 | 165 | 61.1833 | 1
2015-09-03 01:00 | 2015-09-03 | 4 | 1 | 161 | 61 | 1
2015-09-03 01:15 | 2015-09-03 | 4 | 1 | 178 | 61 | 1
2015-09-03 01:30 | 2015-09-03 | 4 | 1 | 163 | 61 | 1
2015-09-03 01:45 | 2015-09-03 | 4 | 1 | 158 | 61 | 1
2015-09-03 02:00 | 2015-09-03 | 4 | 2 | 158 | 61 | 1
2015-09-03 02:15 | 2015-09-03 | 4 | 2 | 173 | 61 | 1
2015-09-03 02:30 | 2015-09-03 | 4 | 2 | 160 | 61 | 1
2015-09-03 02:45 | 2015-09-03 | 4 | 2 | 164 | 61 | 1
2015-09-03 03:00 | 2015-09-03 | 4 | 3 | 156 | 61 | 1
2015-09-03 03:15 | 2015-09-03 | 4 | 3 | 162 | 61 | 1
2015-09-03 03:30 | 2015-09-03 | 4 | 3 | 177 | 61 | 1
2015-09-03 03:45 | 2015-09-03 | 4 | 3 | 153 | 61 | 1
2015-09-03 04:00 | 2015-09-03 | 4 | 4 | 162 | 61 | 1
2015-09-03 04:15 | 2015-09-03 | 4 | 4 | 149 | 61 | 1
2015-09-03 04:30 | 2015-09-03 | 4 | 4 | 166 | 61 | 1
2015-09-03 04:45 | 2015-09-03 | 4 | 4 | 166 | 61 | 1
2015-09-03 05:00 | 2015-09-03 | 4 | 5 | 154 | 61 | 1
2015-09-03 05:15 | 2015-09-03 | 4 | 5 | 159 | 61 | 1
2015-09-03 05:30 | 2015-09-03 | 4 | 5 | 152 | 61 | 1
2015-09-03 05:45 | 2015-09-03 | 4 | 5 | 164 | 61 | 1
2015-09-03 06:00 | 2015-09-03 | 4 | 6 | 168 | 61.0667 | 1
2015-09-03 06:15 | 2015-09-03 | 4 | 6 | 161 | 61.3167 | 1
2015-09-03 06:30 | 2015-09-03 | 4 | 6 | 158 | 61.5667 | 1
2015-09-03 06:45 | 2015-09-03 | 4 | 6 | 157 | 61.8167 | 1
2015-09-03 07:00 | 2015-09-03 | 4 | 7 | 174 | 62.0667 | 1
2015-09-03 07:15 | 2015-09-03 | 4 | 7 | 156 | 62.3167 | 1
2015-09-03 07:30 | 2015-09-03 | 4 | 7 | 162 | 62.5667 | 1
2015-09-03 07:45 | 2015-09-03 | 4 | 7 | 154 | 62.8167 | 1
2015-09-03 08:00 | 2015-09-03 | 4 | 8 | 164 | 63.1333 | 1
2015-09-03 08:15 | 2015-09-03 | 4 | 8 | 179 | 63.6333 | 1
2015-09-03 08:30 | 2015-09-03 | 4 | 8 | 167 | 64.1333 | 1
2015-09-03 08:45 | 2015-09-03 | 4 | 8 | 167 | 64.6333 | 1
2015-09-03 09:00 | 2015-09-03 | 4 | 9 | 167 | 65.1333 | 2
2015-09-03 09:15 | 2015-09-03 | 4 | 9 | 175 | 65.6333 | 2
2015-09-03 09:30 | 2015-09-03 | 4 | 9 | 189 | 66.1333 | 2
2015-09-03 09:45 | 2015-09-03 | 4 | 9 | 181 | 66.6333 | 2
2015-09-03 10:00 | 2015-09-03 | 4 | 10 | 188 | 67 | 2
2015-09-03 10:15 | 2015-09-03 | 4 | 10 | 180 | 67 | 2
2015-09-03 10:30 | 2015-09-03 | 4 | 10 | 186 | 67 | 2
2015-09-03 10:45 | 2015-09-03 | 4 | 10 | 204 | 67 | 2
2015-09-03 11:00 | 2015-09-03 | 4 | 11 | 192 | 67 | 2
2015-09-03 11:15 | 2015-09-03 | 4 | 11 | 193 | 67 | 2
2015-09-03 11:30 | 2015-09-03 | 4 | 11 | 195 | 67 | 2
2015-09-03 11:45 | 2015-09-03 | 4 | 11 | 206 | 67 | 2
2015-09-03 12:00 | 2015-09-03 | 4 | 12 | 212 | 67 | 2
2015-09-03 12:15 | 2015-09-03 | 4 | 12 | 202 | 67 | 2
2015-09-03 12:30 | 2015-09-03 | 4 | 12 | 198 | 67 | 2
2015-09-03 12:45 | 2015-09-03 | 4 | 12 | 209 | 67 | 2
2015-09-03 13:00 | 2015-09-03 | 4 | 13 | 205 | 67 | 2
2015-09-03 13:15 | 2015-09-03 | 4 | 13 | 214 | 67 | 2
2015-09-03 13:30 | 2015-09-03 | 4 | 13 | 198 | 67 | 2
2015-09-03 13:45 | 2015-09-03 | 4 | 13 | 207 | 67 | 2
2015-09-03 14:00 | 2015-09-03 | 4 | 14 | 204 | 66.9333 | 2
2015-09-03 14:15 | 2015-09-03 | 4 | 14 | 210 | 66.6833 | 2
2015-09-03 14:30 | 2015-09-03 | 4 | 14 | 209 | 66.4333 | 2
2015-09-03 14:45 | 2015-09-03 | 4 | 14 | 207 | 66.1833 | 2
2015-09-03 15:00 | 2015-09-03 | 4 | 15 | 212 | 66 | 2
2015-09-03 15:15 | 2015-09-03 | 4 | 15 | 212 | 66 | 2
2015-09-03 15:30 | 2015-09-03 | 4 | 15 | 207 | 66 | 2
2015-09-03 15:45 | 2015-09-03 | 4 | 15 | 228 | 66 | 2
2015-09-03 16:00 | 2015-09-03 | 4 | 16 | 224 | 65.8667 | 2
2015-09-03 16:15 | 2015-09-03 | 4 | 16 | 215 | 65.3667 | 2
2015-09-03 16:30 | 2015-09-03 | 4 | 16 | 203 | 64.8667 | 1
2015-09-03 16:45 | 2015-09-03 | 4 | 16 | 229 | 64.3667 | 1
2015-09-03 17:00 | 2015-09-03 | 4 | 17 | 216 | 63.8667 | 1
2015-09-03 17:15 | 2015-09-03 | 4 | 17 | 226 | 63.3667 | 1
2015-09-03 17:30 | 2015-09-03 | 4 | 17 | 215 | 62.8667 | 1
2015-09-03 17:45 | 2015-09-03 | 4 | 17 | 203 | 62.3667 | 1
2015-09-03 18:00 | 2015-09-03 | 4 | 18 | 212 | 61.9333 | 1
2015-09-03 18:15 | 2015-09-03 | 4 | 18 | 212 | 61.6833 | 1
2015-09-03 18:30 | 2015-09-03 | 4 | 18 | 204 | 61.4333 | 1
2015-09-03 18:45 | 2015-09-03 | 4 | 18 | 214 | 61.1833 | 1
2015-09-03 19:00 | 2015-09-03 | 4 | 19 | 193 | 61 | 1
2015-09-03 19:15 | 2015-09-03 | 4 | 19 | 208 | 61 | 1
2015-09-03 19:30 | 2015-09-03 | 4 | 19 | 202 | 61 | 1
2015-09-03 19:45 | 2015-09-03 | 4 | 19 | 195 | 61 | 1
2015-09-03 20:00 | 2015-09-03 | 4 | 20 | 192 | 60.9333 | 1
2015-09-03 20:15 | 2015-09-03 | 4 | 20 | 183 | 60.6833 | 1
2015-09-03 20:30 | 2015-09-03 | 4 | 20 | 184 | 60.4333 | 1
2015-09-03 20:45 | 2015-09-03 | 4 | 20 | 182 | 60.1833 | 1
2015-09-03 21:00 | 2015-09-03 | 4 | 21 | 183 | 60 | 1
2015-09-03 21:15 | 2015-09-03 | 4 | 21 | 179 | 60 | 1
2015-09-03 21:30 | 2015-09-03 | 4 | 21 | 165 | 60 | 1
2015-09-03 21:45 | 2015-09-03 | 4 | 21 | 168 | 60 | 1
2015-09-03 22:00 | 2015-09-03 | 4 | 22 | 162 | 60 | 1
2015-09-03 22:15 | 2015-09-03 | 4 | 22 | 170 | 60 | 1
2015-09-03 22:30 | 2015-09-03 | 4 | 22 | 165 | 60 | 1
2015-09-03 22:45 | 2015-09-03 | 4 | 22 | 175 | 60 | 1
2015-09-03 23:00 | 2015-09-03 | 4 | 23 | 164 | 59.9333 | 1
2015-09-03 23:15 | 2015-09-03 | 4 | 23 | 161 | 59.6833 | 1
2015-09-03 23:30 | 2015-09-03 | 4 | 23 | 161 | 59.4333 | 1
2015-09-03 23:45 | 2015-09-03 | 4 | 23 | 147 | 59.1833 | 1
2015-09-04 | 2015-09-04 | 5 | 0 | 154 | 59 | 1
2015-09-04 00:15 | 2015-09-04 | 5 | 0 | 147 | 59 | 1
2015-09-04 00:30 | 2015-09-04 | 5 | 0 | 147 | 59 | 1
2015-09-04 00:45 | 2015-09-04 | 5 | 0 | 140 | 59 | 1
2015-09-04 01:00 | 2015-09-04 | 5 | 1 | 143 | 58.9333 | 1
2015-09-04 01:15 | 2015-09-04 | 5 | 1 | 142 | 58.6833 | 1
2015-09-04 01:30 | 2015-09-04 | 5 | 1 | 148 | 58.4333 | 1
2015-09-04 01:45 | 2015-09-04 | 5 | 1 | 140 | 58.1833 | 1
2015-09-04 02:00 | 2015-09-04 | 5 | 2 | 140 | 57.9333 | 1
2015-09-04 02:15 | 2015-09-04 | 5 | 2 | 140 | 57.6833 | 1
2015-09-04 02:30 | 2015-09-04 | 5 | 2 | 140 | 57.4333 | 1
2015-09-04 02:45 | 2015-09-04 | 5 | 2 | 140 | 57.1833 | 1
2015-09-04 03:00 | 2015-09-04 | 5 | 3 | 141 | 57 | 1
2015-09-04 03:15 | 2015-09-04 | 5 | 3 | 139 | 57 | 1
2015-09-04 03:30 | 2015-09-04 | 5 | 3 | 140 | 57 | 1
2015-09-04 03:45 | 2015-09-04 | 5 | 3 | 139 | 57 | 1
2015-09-04 04:00 | 2015-09-04 | 5 | 4 | 133 | 57 | 1
2015-09-04 04:15 | 2015-09-04 | 5 | 4 | 129 | 57 | 1
2015-09-04 04:30 | 2015-09-04 | 5 | 4 | 125 | 57 | 1
2015-09-04 04:45 | 2015-09-04 | 5 | 4 | 128 | 57 | 1
2015-09-04 05:00 | 2015-09-04 | 5 | 5 | 125 | 56.9333 | 1
2015-09-04 05:15 | 2015-09-04 | 5 | 5 | 127 | 56.6833 | 1
2015-09-04 05:30 | 2015-09-04 | 5 | 5 | 126 | 56.4333 | 1
2015-09-04 05:45 | 2015-09-04 | 5 | 5 | 129 | 56.1833 | 1
2015-09-04 06:00 | 2015-09-04 | 5 | 6 | 129 | 56.1333 | 1
2015-09-04 06:15 | 2015-09-04 | 5 | 6 | 128 | 56.6333 | 1
2015-09-04 06:30 | 2015-09-04 | 5 | 6 | 130 | 57.1333 | 1
2015-09-04 06:45 | 2015-09-04 | 5 | 6 | 126 | 57.6333 | 1
2015-09-04 07:00 | 2015-09-04 | 5 | 7 | 128 | 58.1333 | 1
2015-09-04 07:15 | 2015-09-04 | 5 | 7 | 132 | 58.6333 | 1
2015-09-04 07:30 | 2015-09-04 | 5 | 7 | 131 | 59.1333 | 1
2015-09-04 07:45 | 2015-09-04 | 5 | 7 | 144 | 59.6333 | 1
2015-09-04 08:00 | 2015-09-04 | 5 | 8 | 147 | 60.2 | 1
2015-09-04 08:15 | 2015-09-04 | 5 | 8 | 157 | 60.95 | 1
2015-09-04 08:30 | 2015-09-04 | 5 | 8 | 157 | 61.7 | 1
2015-09-04 08:45 | 2015-09-04 | 5 | 8 | 158 | 62.45 | 1
2015-09-04 09:00 | 2015-09-04 | 5 | 9 | 157 | 63.1333 | 1
2015-09-04 09:15 | 2015-09-04 | 5 | 9 | 163 | 63.6333 | 1
2015-09-04 09:30 | 2015-09-04 | 5 | 9 | 174 | 64.1333 | 1
2015-09-04 09:45 | 2015-09-04 | 5 | 9 | 181 | 64.6333 | 1
2015-09-04 10:00 | 2015-09-04 | 5 | 10 | 174 | 65.1333 | 2
2015-09-04 10:15 | 2015-09-04 | 5 | 10 | 182 | 65.6333 | 2
2015-09-04 10:30 | 2015-09-04 | 5 | 10 | 181 | 66.1333 | 2
2015-09-04 10:45 | 2015-09-04 | 5 | 10 | 185 | 66.6333 | 2
2015-09-04 11:00 | 2015-09-04 | 5 | 11 | 189 | 67 | 2
2015-09-04 11:15 | 2015-09-04 | 5 | 11 | 187 | 67 | 2
2015-09-04 11:30 | 2015-09-04 | 5 | 11 | 184 | 67 | 2
2015-09-04 11:45 | 2015-09-04 | 5 | 11 | 196 | 67 | 2
2015-09-04 12:00 | 2015-09-04 | 5 | 12 | 185 | 67.0667 | 2
2015-09-04 12:15 | 2015-09-04 | 5 | 12 | 198 | 67.3167 | 2
2015-09-04 12:30 | 2015-09-04 | 5 | 12 | 196 | 67.5667 | 2
2015-09-04 12:45 | 2015-09-04 | 5 | 12 | 183 | 67.8167 | 2
2015-09-04 13:00 | 2015-09-04 | 5 | 13 | 196 | 68 | 2
2015-09-04 13:15 | 2015-09-04 | 5 | 13 | 182 | 68 | 2
2015-09-04 13:30 | 2015-09-04 | 5 | 13 | 194 | 68 | 2
2015-09-04 13:45 | 2015-09-04 | 5 | 13 | 197 | 68 | 2
2015-09-04 14:00 | 2015-09-04 | 5 | 14 | 190 | 67.8667 | 2
2015-09-04 14:15 | 2015-09-04 | 5 | 14 | 199 | 67.3667 | 2
2015-09-04 14:30 | 2015-09-04 | 5 | 14 | 200 | 66.8667 | 2
2015-09-04 14:45 | 2015-09-04 | 5 | 14 | 203 | 66.3667 | 2
2015-09-04 15:00 | 2015-09-04 | 5 | 15 | 211 | 65.9333 | 2
2015-09-04 15:15 | 2015-09-04 | 5 | 15 | 208 | 65.6833 | 2
2015-09-04 15:30 | 2015-09-04 | 5 | 15 | 200 | 65.4333 | 2
2015-09-04 15:45 | 2015-09-04 | 5 | 15 | 217 | 65.1833 | 2
2015-09-04 16:00 | 2015-09-04 | 5 | 16 | 217 | 64.8667 | 1
2015-09-04 16:15 | 2015-09-04 | 5 | 16 | 205 | 64.3667 | 1
2015-09-04 16:30 | 2015-09-04 | 5 | 16 | 221 | 63.8667 | 1
2015-09-04 16:45 | 2015-09-04 | 5 | 16 | 209 | 63.3667 | 1
2015-09-04 17:00 | 2015-09-04 | 5 | 17 | 203 | 62.8667 | 1
2015-09-04 17:15 | 2015-09-04 | 5 | 17 | 209 | 62.3667 | 1
2015-09-04 17:30 | 2015-09-04 | 5 | 17 | 200 | 61.8667 | 1
2015-09-04 17:45 | 2015-09-04 | 5 | 17 | 201 | 61.3667 | 1
2015-09-04 18:00 | 2015-09-04 | 5 | 18 | 199 | 60.9333 | 1
2015-09-04 18:15 | 2015-09-04 | 5 | 18 | 196 | 60.6833 | 1
2015-09-04 18:30 | 2015-09-04 | 5 | 18 | 188 | 60.4333 | 1
2015-09-04 18:45 | 2015-09-04 | 5 | 18 | 188 | 60.1833 | 1
2015-09-04 19:00 | 2015-09-04 | 5 | 19 | 181 | 59.9333 | 1
2015-09-04 19:15 | 2015-09-04 | 5 | 19 | 184 | 59.6833 | 1
2015-09-04 19:30 | 2015-09-04 | 5 | 19 | 179 | 59.4333 | 1
2015-09-04 19:45 | 2015-09-04 | 5 | 19 | 171 | 59.1833 | 1
2015-09-04 20:00 | 2015-09-04 | 5 | 20 | 179 | 59 | 1
2015-09-04 20:15 | 2015-09-04 | 5 | 20 | 176 | 59 | 1
2015-09-04 20:30 | 2015-09-04 | 5 | 20 | 176 | 59 | 1
2015-09-04 20:45 | 2015-09-04 | 5 | 20 | 178 | 59 | 1
2015-09-04 21:00 | 2015-09-04 | 5 | 21 | 170 | 58.9333 | 1
2015-09-04 21:15 | 2015-09-04 | 5 | 21 | 166 | 58.6833 | 1
2015-09-04 21:30 | 2015-09-04 | 5 | 21 | 158 | 58.4333 | 1
2015-09-04 21:45 | 2015-09-04 | 5 | 21 | 165 | 58.1833 | 1
2015-09-04 22:00 | 2015-09-04 | 5 | 22 | 163 | 58 | 1
2015-09-04 22:15 | 2015-09-04 | 5 | 22 | 166 | 58 | 1
2015-09-04 22:30 | 2015-09-04 | 5 | 22 | 162 | 58 | 1
2015-09-04 22:45 | 2015-09-04 | 5 | 22 | 155 | 58 | 1
2015-09-04 23:00 | 2015-09-04 | 5 | 23 | 163 | 57.9333 | 1
2015-09-04 23:15 | 2015-09-04 | 5 | 23 | 163 | 57.6833 | 1
2015-09-04 23:30 | 2015-09-04 | 5 | 23 | 157 | 57.4333 | 1
2015-09-04 23:45 | 2015-09-04 | 5 | 23 | 156 | 57.1833 | 1
2015-09-05 | 2015-09-05 | 6 | 0 | 146 | 57.0667 | 1
2015-09-05 00:15 | 2015-09-05 | 6 | 0 | 135 | 57.3167 | 1
2015-09-05 00:30 | 2015-09-05 | 6 | 0 | 139 | 57.5667 | 1
2015-09-05 00:45 | 2015-09-05 | 6 | 0 | 130 | 57.8167 | 1
2015-09-05 01:00 | 2015-09-05 | 6 | 1 | 131 | 57.8 | 1
2015-09-05 01:15 | 2015-09-05 | 6 | 1 | 125 | 57.05 | 1
2015-09-05 01:30 | 2015-09-05 | 6 | 1 | 125 | 56.3 | 1
2015-09-05 01:45 | 2015-09-05 | 6 | 1 | 127 | 55.55 | 1
2015-09-05 02:00 | 2015-09-05 | 6 | 2 | 128 | 55 | 1
2015-09-05 02:15 | 2015-09-05 | 6 | 2 | 132 | 55 | 1
2015-09-05 02:30 | 2015-09-05 | 6 | 2 | 119 | 55 | 1
2015-09-05 02:45 | 2015-09-05 | 6 | 2 | 115 | 55 | 1
2015-09-05 03:00 | 2015-09-05 | 6 | 3 | 120 | 54.9333 | 1
2015-09-05 03:15 | 2015-09-05 | 6 | 3 | 117 | 54.6833 | 1
2015-09-05 03:30 | 2015-09-05 | 6 | 3 | 115 | 54.4333 | 1
2015-09-05 03:45 | 2015-09-05 | 6 | 3 | 116 | 54.1833 | 1
2015-09-05 04:00 | 2015-09-05 | 6 | 4 | 110 | 54 | 1
2015-09-05 04:15 | 2015-09-05 | 6 | 4 | 113 | 54 | 1
2015-09-05 04:30 | 2015-09-05 | 6 | 4 | 113 | 54 | 1
2015-09-05 04:45 | 2015-09-05 | 6 | 4 | 115 | 54 | 1
2015-09-05 05:00 | 2015-09-05 | 6 | 5 | 118 | 54 | 1
2015-09-05 05:15 | 2015-09-05 | 6 | 5 | 112 | 54 | 1
2015-09-05 05:30 | 2015-09-05 | 6 | 5 | 111 | 54 | 1
2015-09-05 05:45 | 2015-09-05 | 6 | 5 | 112 | 54 | 1
2015-09-05 06:00 | 2015-09-05 | 6 | 6 | 113 | 54.2667 | 1
2015-09-05 06:15 | 2015-09-05 | 6 | 6 | 110 | 55.2667 | 1
2015-09-05 06:30 | 2015-09-05 | 6 | 6 | 118 | 56.2667 | 1
2015-09-05 06:45 | 2015-09-05 | 6 | 6 | 112 | 57.2667 | 1
2015-09-05 07:00 | 2015-09-05 | 6 | 7 | 111 | 58.2 | 1
2015-09-05 07:15 | 2015-09-05 | 6 | 7 | 110 | 58.95 | 1
2015-09-05 07:30 | 2015-09-05 | 6 | 7 | 118 | 59.7 | 1
2015-09-05 07:45 | 2015-09-05 | 6 | 7 | 121 | 60.45 | 1
2015-09-05 08:00 | 2015-09-05 | 6 | 8 | 132 | 61.2 | 1
2015-09-05 08:15 | 2015-09-05 | 6 | 8 | 128 | 61.95 | 1
2015-09-05 08:30 | 2015-09-05 | 6 | 8 | 120 | 62.7 | 1
2015-09-05 08:45 | 2015-09-05 | 6 | 8 | 130 | 63.45 | 1
2015-09-05 09:00 | 2015-09-05 | 6 | 9 | 138 | 64.2 | 1
2015-09-05 09:15 | 2015-09-05 | 6 | 9 | 137 | 64.95 | 1
2015-09-05 09:30 | 2015-09-05 | 6 | 9 | 139 | 65.7 | 2
2015-09-05 09:45 | 2015-09-05 | 6 | 9 | 138 | 66.45 | 2
2015-09-05 10:00 | 2015-09-05 | 6 | 10 | 139 | 67.2 | 2
2015-09-05 10:15 | 2015-09-05 | 6 | 10 | 142 | 67.95 | 2
2015-09-05 10:30 | 2015-09-05 | 6 | 10 | 138 | 68.7 | 2
2015-09-05 10:45 | 2015-09-05 | 6 | 10 | 146 | 69.45 | 2
2015-09-05 11:00 | 2015-09-05 | 6 | 11 | 149 | 70.1333 | 3
2015-09-05 11:15 | 2015-09-05 | 6 | 11 | 141 | 70.6333 | 3
2015-09-05 11:30 | 2015-09-05 | 6 | 11 | 147 | 71.1333 | 3
2015-09-05 11:45 | 2015-09-05 | 6 | 11 | 148 | 71.6333 | 3
2015-09-05 12:00 | 2015-09-05 | 6 | 12 | 140 | 72.2667 | 3
2015-09-05 12:15 | 2015-09-05 | 6 | 12 | 162 | 73.2667 | 3
2015-09-05 12:30 | 2015-09-05 | 6 | 12 | 153 | 74.2667 | 3
2015-09-05 12:45 | 2015-09-05 | 6 | 12 | 146 | 75.2667 | 4
2015-09-05 13:00 | 2015-09-05 | 6 | 13 | 152 | 76 | 4
2015-09-05 13:15 | 2015-09-05 | 6 | 13 | 150 | 76 | 4
2015-09-05 13:30 | 2015-09-05 | 6 | 13 | 149 | 76 | 4
2015-09-05 13:45 | 2015-09-05 | 6 | 13 | 167 | 76 | 4
2015-09-05 14:00 | 2015-09-05 | 6 | 14 | 146 | 75.8 | 4
2015-09-05 14:15 | 2015-09-05 | 6 | 14 | 158 | 75.05 | 4
2015-09-05 14:30 | 2015-09-05 | 6 | 14 | 161 | 74.3 | 3
2015-09-05 14:45 | 2015-09-05 | 6 | 14 | 157 | 73.55 | 3
2015-09-05 15:00 | 2015-09-05 | 6 | 15 | 164 | 73 | 3
2015-09-05 15:15 | 2015-09-05 | 6 | 15 | 174 | 73 | 3
2015-09-05 15:30 | 2015-09-05 | 6 | 15 | 161 | 73 | 3
2015-09-05 15:45 | 2015-09-05 | 6 | 15 | 172 | 73 | 3
2015-09-05 16:00 | 2015-09-05 | 6 | 16 | 168 | 72.8667 | 3
2015-09-05 16:15 | 2015-09-05 | 6 | 16 | 169 | 72.3667 | 3
2015-09-05 16:30 | 2015-09-05 | 6 | 16 | 174 | 71.8667 | 3
2015-09-05 16:45 | 2015-09-05 | 6 | 16 | 178 | 71.3667 | 3
2015-09-05 17:00 | 2015-09-05 | 6 | 17 | 163 | 70.8 | 3
2015-09-05 17:15 | 2015-09-05 | 6 | 17 | 175 | 70.05 | 3
2015-09-05 17:30 | 2015-09-05 | 6 | 17 | 178 | 69.3 | 2
2015-09-05 17:45 | 2015-09-05 | 6 | 17 | 169 | 68.55 | 2
2015-09-05 18:00 | 2015-09-05 | 6 | 18 | 174 | 67.7333 | 2
2015-09-05 18:15 | 2015-09-05 | 6 | 18 | 177 | 66.7333 | 2
2015-09-05 18:30 | 2015-09-05 | 6 | 18 | 165 | 65.7333 | 2
2015-09-05 18:45 | 2015-09-05 | 6 | 18 | 171 | 64.7333 | 1
2015-09-05 19:00 | 2015-09-05 | 6 | 19 | 170 | 63.8667 | 1
2015-09-05 19:15 | 2015-09-05 | 6 | 19 | 154 | 63.3667 | 1
2015-09-05 19:30 | 2015-09-05 | 6 | 19 | 160 | 62.8667 | 1
2015-09-05 19:45 | 2015-09-05 | 6 | 19 | 163 | 62.3667 | 1
2015-09-05 20:00 | 2015-09-05 | 6 | 20 | 153 | 62 | 1
2015-09-05 20:15 | 2015-09-05 | 6 | 20 | 163 | 62 | 1
2015-09-05 20:30 | 2015-09-05 | 6 | 20 | 152 | 62 | 1
2015-09-05 20:45 | 2015-09-05 | 6 | 20 | 160 | 62 | 1
2015-09-05 21:00 | 2015-09-05 | 6 | 21 | 148 | 62.1333 | 1
2015-09-05 21:15 | 2015-09-05 | 6 | 21 | 154 | 62.6333 | 1
2015-09-05 21:30 | 2015-09-05 | 6 | 21 | 143 | 63.1333 | 1
2015-09-05 21:45 | 2015-09-05 | 6 | 21 | 152 | 63.6333 | 1
2015-09-05 22:00 | 2015-09-05 | 6 | 22 | 145 | 63.8667 | 1
2015-09-05 22:15 | 2015-09-05 | 6 | 22 | 151 | 63.3667 | 1
2015-09-05 22:30 | 2015-09-05 | 6 | 22 | 140 | 62.8667 | 1
2015-09-05 22:45 | 2015-09-05 | 6 | 22 | 148 | 62.3667 | 1
2015-09-05 23:00 | 2015-09-05 | 6 | 23 | 142 | 62 | 1
2015-09-05 23:15 | 2015-09-05 | 6 | 23 | 145 | 62 | 1
2015-09-05 23:30 | 2015-09-05 | 6 | 23 | 143 | 62 | 1
2015-09-05 23:45 | 2015-09-05 | 6 | 23 | 145 | 62 | 1
2015-09-06 | 2015-09-06 | 7 | 0 | 144 | 61.8667 | 1
2015-09-06 00:15 | 2015-09-06 | 7 | 0 | 145 | 61.3667 | 1
2015-09-06 00:30 | 2015-09-06 | 7 | 0 | 140 | 60.8667 | 1
2015-09-06 00:45 | 2015-09-06 | 7 | 0 | 139 | 60.3667 | 1
2015-09-06 01:00 | 2015-09-06 | 7 | 1 | 140 | 60 | 1
2015-09-06 01:15 | 2015-09-06 | 7 | 1 | 138 | 60 | 1
2015-09-06 01:30 | 2015-09-06 | 7 | 1 | 137 | 60 | 1
2015-09-06 01:45 | 2015-09-06 | 7 | 1 | 146 | 60 | 1
2015-09-06 02:00 | 2015-09-06 | 7 | 2 | 133 | 59.8 | 1
2015-09-06 02:15 | 2015-09-06 | 7 | 2 | 138 | 59.05 | 1
2015-09-06 02:30 | 2015-09-06 | 7 | 2 | 130 | 58.3 | 1
2015-09-06 02:45 | 2015-09-06 | 7 | 2 | 139 | 57.55 | 1
2015-09-06 03:00 | 2015-09-06 | 7 | 3 | 133 | 56.9333 | 1
2015-09-06 03:15 | 2015-09-06 | 7 | 3 | 137 | 56.6833 | 1
2015-09-06 03:30 | 2015-09-06 | 7 | 3 | 130 | 56.4333 | 1
2015-09-06 03:45 | 2015-09-06 | 7 | 3 | 136 | 56.1833 | 1
2015-09-06 04:00 | 2015-09-06 | 7 | 4 | 132 | 56.0667 | 1
2015-09-06 04:15 | 2015-09-06 | 7 | 4 | 132 | 56.3167 | 1
2015-09-06 04:30 | 2015-09-06 | 7 | 4 | 134 | 56.5667 | 1
2015-09-06 04:45 | 2015-09-06 | 7 | 4 | 126 | 56.8167 | 1
2015-09-06 05:00 | 2015-09-06 | 7 | 5 | 129 | 57 | 1
2015-09-06 05:15 | 2015-09-06 | 7 | 5 | 128 | 57 | 1
2015-09-06 05:30 | 2015-09-06 | 7 | 5 | 129 | 57 | 1
2015-09-06 05:45 | 2015-09-06 | 7 | 5 | 130 | 57 | 1
2015-09-06 06:00 | 2015-09-06 | 7 | 6 | 126 | 57.2 | 1
2015-09-06 06:15 | 2015-09-06 | 7 | 6 | 123 | 57.95 | 1
2015-09-06 06:30 | 2015-09-06 | 7 | 6 | 131 | 58.7 | 1
2015-09-06 06:45 | 2015-09-06 | 7 | 6 | 131 | 59.45 | 1
2015-09-06 07:00 | 2015-09-06 | 7 | 7 | 138 | 60.3333 | 1
2015-09-06 07:15 | 2015-09-06 | 7 | 7 | 134 | 61.5833 | 1
2015-09-06 07:30 | 2015-09-06 | 7 | 7 | 139 | 62.8333 | 1
2015-09-06 07:45 | 2015-09-06 | 7 | 7 | 143 | 64.0833 | 1
2015-09-06 08:00 | 2015-09-06 | 7 | 8 | 139 | 65.1333 | 2
2015-09-06 08:15 | 2015-09-06 | 7 | 8 | 139 | 65.6333 | 2
2015-09-06 08:30 | 2015-09-06 | 7 | 8 | 144 | 66.1333 | 2
2015-09-06 08:45 | 2015-09-06 | 7 | 8 | 152 | 66.6333 | 2
2015-09-06 09:00 | 2015-09-06 | 7 | 9 | 144 | 67.1333 | 2
2015-09-06 09:15 | 2015-09-06 | 7 | 9 | 151 | 67.6333 | 2
2015-09-06 09:30 | 2015-09-06 | 7 | 9 | 150 | 68.1333 | 2
2015-09-06 09:45 | 2015-09-06 | 7 | 9 | 152 | 68.6333 | 2
2015-09-06 10:00 | 2015-09-06 | 7 | 10 | 157 | 69.1333 | 2
2015-09-06 10:15 | 2015-09-06 | 7 | 10 | 155 | 69.6333 | 2
2015-09-06 10:30 | 2015-09-06 | 7 | 10 | 151 | 70.1333 | 3
2015-09-06 10:45 | 2015-09-06 | 7 | 10 | 161 | 70.6333 | 3
2015-09-06 11:00 | 2015-09-06 | 7 | 11 | 160 | 71.2 | 3
2015-09-06 11:15 | 2015-09-06 | 7 | 11 | 162 | 71.95 | 3
2015-09-06 11:30 | 2015-09-06 | 7 | 11 | 156 | 72.7 | 3
2015-09-06 11:45 | 2015-09-06 | 7 | 11 | 172 | 73.45 | 3
2015-09-06 12:00 | 2015-09-06 | 7 | 12 | 169 | 74.5333 | 3
2015-09-06 12:15 | 2015-09-06 | 7 | 12 | 166 | 76.5333 | 4
2015-09-06 12:30 | 2015-09-06 | 7 | 12 | 171 | 78.5333 | 4
2015-09-06 12:45 | 2015-09-06 | 7 | 12 | 174 | 80.5333 | 5
2015-09-06 13:00 | 2015-09-06 | 7 | 13 | 174 | 82.2 | 5
2015-09-06 13:15 | 2015-09-06 | 7 | 13 | 177 | 82.95 | 5
2015-09-06 13:30 | 2015-09-06 | 7 | 13 | 180 | 83.7 | 5
2015-09-06 13:45 | 2015-09-06 | 7 | 13 | 169 | 84.45 | 5
2015-09-06 14:00 | 2015-09-06 | 7 | 14 | 174 | 84.8667 | 5
2015-09-06 14:15 | 2015-09-06 | 7 | 14 | 192 | 84.3667 | 5
2015-09-06 14:30 | 2015-09-06 | 7 | 14 | 180 | 83.8667 | 5
2015-09-06 14:45 | 2015-09-06 | 7 | 14 | 185 | 83.3667 | 5
2015-09-06 15:00 | 2015-09-06 | 7 | 15 | 195 | 82.8 | 5
2015-09-06 15:15 | 2015-09-06 | 7 | 15 | 200 | 82.05 | 5
2015-09-06 15:30 | 2015-09-06 | 7 | 15 | 183 | 81.3 | 5
2015-09-06 15:45 | 2015-09-06 | 7 | 15 | 200 | 80.55 | 5
2015-09-06 16:00 | 2015-09-06 | 7 | 16 | 189 | 79.8 | 4
2015-09-06 16:15 | 2015-09-06 | 7 | 16 | 191 | 79.05 | 4
2015-09-06 16:30 | 2015-09-06 | 7 | 16 | 200 | 78.3 | 4
2015-09-06 16:45 | 2015-09-06 | 7 | 16 | 191 | 77.55 | 4
2015-09-06 17:00 | 2015-09-06 | 7 | 17 | 188 | 76.5333 | 4
2015-09-06 17:15 | 2015-09-06 | 7 | 17 | 206 | 74.7833 | 3
2015-09-06 17:30 | 2015-09-06 | 7 | 17 | 193 | 73.0333 | 3
2015-09-06 17:45 | 2015-09-06 | 7 | 17 | 201 | 71.2833 | 3
2015-09-06 18:00 | 2015-09-06 | 7 | 18 | 194 | 69.6667 | 2
2015-09-06 18:15 | 2015-09-06 | 7 | 18 | 195 | 68.4167 | 2
2015-09-06 18:30 | 2015-09-06 | 7 | 18 | 187 | 67.1667 | 2
2015-09-06 18:45 | 2015-09-06 | 7 | 18 | 198 | 65.9167 | 2
2015-09-06 19:00 | 2015-09-06 | 7 | 19 | 197 | 64.8667 | 1
2015-09-06 19:15 | 2015-09-06 | 7 | 19 | 177 | 64.3667 | 1
2015-09-06 19:30 | 2015-09-06 | 7 | 19 | 178 | 63.8667 | 1
2015-09-06 19:45 | 2015-09-06 | 7 | 19 | 180 | 63.3667 | 1
2015-09-06 20:00 | 2015-09-06 | 7 | 20 | 172 | 63.0667 | 1
2015-09-06 20:15 | 2015-09-06 | 7 | 20 | 174 | 63.3167 | 1
2015-09-06 20:30 | 2015-09-06 | 7 | 20 | 177 | 63.5667 | 1
2015-09-06 20:45 | 2015-09-06 | 7 | 20 | 171 | 63.8167 | 1
2015-09-06 21:00 | 2015-09-06 | 7 | 21 | 177 | 64 | 1
2015-09-06 21:15 | 2015-09-06 | 7 | 21 | 160 | 64 | 1
2015-09-06 21:30 | 2015-09-06 | 7 | 21 | 161 | 64 | 1
2015-09-06 21:45 | 2015-09-06 | 7 | 21 | 168 | 64 | 1
2015-09-06 22:00 | 2015-09-06 | 7 | 22 | 152 | 63.8667 | 1
2015-09-06 22:15 | 2015-09-06 | 7 | 22 | 163 | 63.3667 | 1
2015-09-06 22:30 | 2015-09-06 | 7 | 22 | 152 | 62.8667 | 1
2015-09-06 22:45 | 2015-09-06 | 7 | 22 | 154 | 62.3667 | 1
2015-09-06 23:00 | 2015-09-06 | 7 | 23 | 160 | 61.8667 | 1
2015-09-06 23:15 | 2015-09-06 | 7 | 23 | 145 | 61.3667 | 1
2015-09-06 23:30 | 2015-09-06 | 7 | 23 | 152 | 60.8667 | 1
2015-09-06 23:45 | 2015-09-06 | 7 | 23 | 152 | 60.3667 | 1
2015-09-07 | 2015-09-07 | 0 | 0 | 147 | 60 | 1
2015-09-07 00:15 | 2015-09-07 | 0 | 0 | 154 | 60 | 1
2015-09-07 00:30 | 2015-09-07 | 0 | 0 | 144 | 60 | 1
2015-09-07 00:45 | 2015-09-07 | 0 | 0 | 147 | 60 | 1
2015-09-07 01:00 | 2015-09-07 | 0 | 1 | 146 | 59.9333 | 1
2015-09-07 01:15 | 2015-09-07 | 0 | 1 | 141 | 59.6833 | 1
2015-09-07 01:30 | 2015-09-07 | 0 | 1 | 148 | 59.4333 | 1
2015-09-07 01:45 | 2015-09-07 | 0 | 1 | 137 | 59.1833 | 1
2015-09-07 02:00 | 2015-09-07 | 0 | 2 | 143 | 59.0667 | 1
2015-09-07 02:15 | 2015-09-07 | 0 | 2 | 146 | 59.3167 | 1
2015-09-07 02:30 | 2015-09-07 | 0 | 2 | 141 | 59.5667 | 1
2015-09-07 02:45 | 2015-09-07 | 0 | 2 | 143 | 59.8167 | 1
2015-09-07 03:00 | 2015-09-07 | 0 | 3 | 139 | 59.9333 | 1
2015-09-07 03:15 | 2015-09-07 | 0 | 3 | 145 | 59.6833 | 1
2015-09-07 03:30 | 2015-09-07 | 0 | 3 | 137 | 59.4333 | 1
2015-09-07 03:45 | 2015-09-07 | 0 | 3 | 142 | 59.1833 | 1
2015-09-07 04:00 | 2015-09-07 | 0 | 4 | 131 | 58.9333 | 1
2015-09-07 04:15 | 2015-09-07 | 0 | 4 | 145 | 58.6833 | 1
2015-09-07 04:30 | 2015-09-07 | 0 | 4 | 138 | 58.4333 | 1
2015-09-07 04:45 | 2015-09-07 | 0 | 4 | 139 | 58.1833 | 1
2015-09-07 05:00 | 2015-09-07 | 0 | 5 | 139 | 58 | 1
2015-09-07 05:15 | 2015-09-07 | 0 | 5 | 138 | 58 | 1
2015-09-07 05:30 | 2015-09-07 | 0 | 5 | 134 | 58 | 1
2015-09-07 05:45 | 2015-09-07 | 0 | 5 | 140 | 58 | 1
2015-09-07 06:00 | 2015-09-07 | 0 | 6 | 134 | 58.5333 | 1
2015-09-07 06:15 | 2015-09-07 | 0 | 6 | 136 | 60.5333 | 1
2015-09-07 06:30 | 2015-09-07 | 0 | 6 | 139 | 62.5333 | 1
2015-09-07 06:45 | 2015-09-07 | 0 | 6 | 134 | 64.5333 | 1
2015-09-07 07:00 | 2015-09-07 | 0 | 7 | 134 | 66.1333 | 2
2015-09-07 07:15 | 2015-09-07 | 0 | 7 | 137 | 66.6333 | 2
2015-09-07 07:30 | 2015-09-07 | 0 | 7 | 137 | 67.1333 | 2
2015-09-07 07:45 | 2015-09-07 | 0 | 7 | 138 | 67.6333 | 2
2015-09-07 08:00 | 2015-09-07 | 0 | 8 | 147 | 68.1333 | 2
2015-09-07 08:15 | 2015-09-07 | 0 | 8 | 138 | 68.6333 | 2
2015-09-07 08:30 | 2015-09-07 | 0 | 8 | 149 | 69.1333 | 2
2015-09-07 08:45 | 2015-09-07 | 0 | 8 | 139 | 69.6333 | 2
2015-09-07 09:00 | 2015-09-07 | 0 | 9 | 147 | 70.1333 | 3
2015-09-07 09:15 | 2015-09-07 | 0 | 9 | 151 | 70.6333 | 3
2015-09-07 09:30 | 2015-09-07 | 0 | 9 | 146 | 71.1333 | 3
2015-09-07 09:45 | 2015-09-07 | 0 | 9 | 155 | 71.6333 | 3
2015-09-07 10:00 | 2015-09-07 | 0 | 10 | 152 | 72.2667 | 3
2015-09-07 10:15 | 2015-09-07 | 0 | 10 | 146 | 73.2667 | 3
2015-09-07 10:30 | 2015-09-07 | 0 | 10 | 155 | 74.2667 | 3
2015-09-07 10:45 | 2015-09-07 | 0 | 10 | 156 | 75.2667 | 4
2015-09-07 11:00 | 2015-09-07 | 0 | 11 | 159 | 76.3333 | 4
2015-09-07 11:15 | 2015-09-07 | 0 | 11 | 157 | 77.5833 | 4
2015-09-07 11:30 | 2015-09-07 | 0 | 11 | 174 | 78.8333 | 4
2015-09-07 11:45 | 2015-09-07 | 0 | 11 | 170 | 80.0833 | 5
2015-09-07 12:00 | 2015-09-07 | 0 | 12 | 167 | 80.9333 | 5
2015-09-07 12:15 | 2015-09-07 | 0 | 12 | 179 | 80.6833 | 5
2015-09-07 12:30 | 2015-09-07 | 0 | 12 | 167 | 80.4333 | 5
2015-09-07 12:45 | 2015-09-07 | 0 | 12 | 173 | 80.1833 | 5
2015-09-07 13:00 | 2015-09-07 | 0 | 13 | 175 | 80.1333 | 5
2015-09-07 13:15 | 2015-09-07 | 0 | 13 | 177 | 80.6333 | 5
2015-09-07 13:30 | 2015-09-07 | 0 | 13 | 178 | 81.1333 | 5
2015-09-07 13:45 | 2015-09-07 | 0 | 13 | 194 | 81.6333 | 5
2015-09-07 14:00 | 2015-09-07 | 0 | 14 | 185 | 82.4 | 5
2015-09-07 14:15 | 2015-09-07 | 0 | 14 | 180 | 83.9 | 5
2015-09-07 14:30 | 2015-09-07 | 0 | 14 | 217 | 85.4 | 6
2015-09-07 14:45 | 2015-09-07 | 0 | 14 | 188 | 86.9 | 6
2015-09-07 15:00 | 2015-09-07 | 0 | 15 | 204 | 87.8 | 6
2015-09-07 15:15 | 2015-09-07 | 0 | 15 | 209 | 87.05 | 6
2015-09-07 15:30 | 2015-09-07 | 0 | 15 | 207 | 86.3 | 6
2015-09-07 15:45 | 2015-09-07 | 0 | 15 | 216 | 85.55 | 6
2015-09-07 16:00 | 2015-09-07 | 0 | 16 | 209 | 84.7333 | 5
2015-09-07 16:15 | 2015-09-07 | 0 | 16 | 209 | 83.7333 | 5
2015-09-07 16:30 | 2015-09-07 | 0 | 16 | 209 | 82.7333 | 5
2015-09-07 16:45 | 2015-09-07 | 0 | 16 | 207 | 81.7333 | 5
2015-09-07 17:00 | 2015-09-07 | 0 | 17 | 216 | 80.9333 | 5
2015-09-07 17:15 | 2015-09-07 | 0 | 17 | 206 | 80.6833 | 5
2015-09-07 17:30 | 2015-09-07 | 0 | 17 | 217 | 80.4333 | 5
2015-09-07 17:45 | 2015-09-07 | 0 | 17 | 214 | 80.1833 | 5
2015-09-07 18:00 | 2015-09-07 | 0 | 18 | 201 | 79.8 | 4
2015-09-07 18:15 | 2015-09-07 | 0 | 18 | 204 | 79.05 | 4
2015-09-07 18:30 | 2015-09-07 | 0 | 18 | 198 | 78.3 | 4
2015-09-07 18:45 | 2015-09-07 | 0 | 18 | 204 | 77.55 | 4
2015-09-07 19:00 | 2015-09-07 | 0 | 19 | 202 | 76.9333 | 4
2015-09-07 19:15 | 2015-09-07 | 0 | 19 | 194 | 76.6833 | 4
2015-09-07 19:30 | 2015-09-07 | 0 | 19 | 186 | 76.4333 | 4
2015-09-07 19:45 | 2015-09-07 | 0 | 19 | 199 | 76.1833 | 4
2015-09-07 20:00 | 2015-09-07 | 0 | 20 | 174 | 75.8667 | 4
2015-09-07 20:15 | 2015-09-07 | 0 | 20 | 177 | 75.3667 | 4
2015-09-07 20:30 | 2015-09-07 | 0 | 20 | 180 | 74.8667 | 3
2015-09-07 20:45 | 2015-09-07 | 0 | 20 | 178 | 74.3667 | 3
2015-09-07 21:00 | 2015-09-07 | 0 | 21 | 165 | 73.8 | 3
2015-09-07 21:15 | 2015-09-07 | 0 | 21 | 173 | 73.05 | 3
2015-09-07 21:30 | 2015-09-07 | 0 | 21 | 171 | 72.3 | 3
2015-09-07 21:45 | 2015-09-07 | 0 | 21 | 153 | 71.55 | 3
2015-09-07 22:00 | 2015-09-07 | 0 | 22 | 167 | 71 | 3
2015-09-07 22:15 | 2015-09-07 | 0 | 22 | 164 | 71 | 3
2015-09-07 22:30 | 2015-09-07 | 0 | 22 | 159 | 71 | 3
2015-09-07 22:45 | 2015-09-07 | 0 | 22 | 164 | 71 | 3
2015-09-07 23:00 | 2015-09-07 | 0 | 23 | 160 | 70.8667 | 3
2015-09-07 23:15 | 2015-09-07 | 0 | 23 | 158 | 70.3667 | 3
2015-09-07 23:30 | 2015-09-07 | 0 | 23 | 157 | 69.8667 | 2
2015-09-07 23:45 | 2015-09-07 | 0 | 23 | 152 | 69.3667 | 2
2015-09-08 | 2015-09-08 | 2 | 0 | 158 | 68.8667 | 2
2015-09-08 00:15 | 2015-09-08 | 2 | 0 | 159 | 68.3667 | 2
2015-09-08 00:30 | 2015-09-08 | 2 | 0 | 145 | 67.8667 | 2
2015-09-08 00:45 | 2015-09-08 | 2 | 0 | 159 | 67.3667 | 2
2015-09-08 01:00 | 2015-09-08 | 2 | 1 | 149 | 66.8667 | 2
2015-09-08 01:15 | 2015-09-08 | 2 | 1 | 154 | 66.3667 | 2
2015-09-08 01:30 | 2015-09-08 | 2 | 1 | 157 | 65.8667 | 2
2015-09-08 01:45 | 2015-09-08 | 2 | 1 | 143 | 65.3667 | 2
2015-09-08 02:00 | 2015-09-08 | 2 | 2 | 153 | 65 | 1
2015-09-08 02:15 | 2015-09-08 | 2 | 2 | 145 | 65 | 1
2015-09-08 02:30 | 2015-09-08 | 2 | 2 | 152 | 65 | 1
2015-09-08 02:45 | 2015-09-08 | 2 | 2 | 149 | 65 | 1
2015-09-08 03:00 | 2015-09-08 | 2 | 3 | 143 | 64.9333 | 1
2015-09-08 03:15 | 2015-09-08 | 2 | 3 | 151 | 64.6833 | 1
2015-09-08 03:30 | 2015-09-08 | 2 | 3 | 141 | 64.4333 | 1
2015-09-08 03:45 | 2015-09-08 | 2 | 3 | 145 | 64.1833 | 1
2015-09-08 04:00 | 2015-09-08 | 2 | 4 | 144 | 63.9333 | 1
2015-09-08 04:15 | 2015-09-08 | 2 | 4 | 144 | 63.6833 | 1
2015-09-08 04:30 | 2015-09-08 | 2 | 4 | 138 | 63.4333 | 1
2015-09-08 04:45 | 2015-09-08 | 2 | 4 | 148 | 63.1833 | 1
2015-09-08 05:00 | 2015-09-08 | 2 | 5 | 135 | 63.2 | 1
2015-09-08 05:15 | 2015-09-08 | 2 | 5 | 150 | 63.95 | 1
2015-09-08 05:30 | 2015-09-08 | 2 | 5 | 136 | 64.7 | 1
2015-09-08 05:45 | 2015-09-08 | 2 | 5 | 145 | 65.45 | 2
2015-09-08 06:00 | 2015-09-08 | 2 | 6 | 138 | 66.0667 | 2
2015-09-08 06:15 | 2015-09-08 | 2 | 6 | 143 | 66.3167 | 2
2015-09-08 06:30 | 2015-09-08 | 2 | 6 | 138 | 66.5667 | 2
2015-09-08 06:45 | 2015-09-08 | 2 | 6 | 150 | 66.8167 | 2
2015-09-08 07:00 | 2015-09-08 | 2 | 7 | 135 | 67.2 | 2
2015-09-08 07:15 | 2015-09-08 | 2 | 7 | 147 | 67.95 | 2
2015-09-08 07:30 | 2015-09-08 | 2 | 7 | 143 | 68.7 | 2
2015-09-08 07:45 | 2015-09-08 | 2 | 7 | 145 | 69.45 | 2
2015-09-08 08:00 | 2015-09-08 | 2 | 8 | 157 | 70.2 | 3
2015-09-08 08:15 | 2015-09-08 | 2 | 8 | 162 | 70.95 | 3
2015-09-08 08:30 | 2015-09-08 | 2 | 8 | 159 | 71.7 | 3
2015-09-08 08:45 | 2015-09-08 | 2 | 8 | 167 | 72.45 | 3
2015-09-08 09:00 | 2015-09-08 | 2 | 9 | 163 | 72.9333 | 3
2015-09-08 09:15 | 2015-09-08 | 2 | 9 | 166 | 72.6833 | 3
2015-09-08 09:30 | 2015-09-08 | 2 | 9 | 171 | 72.4333 | 3
2015-09-08 09:45 | 2015-09-08 | 2 | 9 | 182 | 72.1833 | 3
2015-09-08 10:00 | 2015-09-08 | 2 | 10 | 189 | 72.3333 | 3
2015-09-08 10:15 | 2015-09-08 | 2 | 10 | 186 | 73.5833 | 3
2015-09-08 10:30 | 2015-09-08 | 2 | 10 | 202 | 74.8333 | 3
2015-09-08 10:45 | 2015-09-08 | 2 | 10 | 201 | 76.0833 | 4
2015-09-08 11:00 | 2015-09-08 | 2 | 11 | 195 | 77.1333 | 4
2015-09-08 11:15 | 2015-09-08 | 2 | 11 | 206 | 77.6333 | 4
2015-09-08 11:30 | 2015-09-08 | 2 | 11 | 213 | 78.1333 | 4
2015-09-08 11:45 | 2015-09-08 | 2 | 11 | 210 | 78.6333 | 4
2015-09-08 12:00 | 2015-09-08 | 2 | 12 | 220 | 79.0667 | 4
2015-09-08 12:15 | 2015-09-08 | 2 | 12 | 233 | 79.3167 | 4
2015-09-08 12:30 | 2015-09-08 | 2 | 12 | 214 | 79.5667 | 4
2015-09-08 12:45 | 2015-09-08 | 2 | 12 | 223 | 79.8167 | 4
2015-09-08 13:00 | 2015-09-08 | 2 | 13 | 235 | 80.2 | 5
2015-09-08 13:15 | 2015-09-08 | 2 | 13 | 216 | 80.95 | 5
2015-09-08 13:30 | 2015-09-08 | 2 | 13 | 250 | 81.7 | 5
2015-09-08 13:45 | 2015-09-08 | 2 | 13 | 224 | 82.45 | 5
2015-09-08 14:00 | 2015-09-08 | 2 | 14 | 250 | 83.5333 | 5
2015-09-08 14:15 | 2015-09-08 | 2 | 14 | 243 | 85.5333 | 6
2015-09-08 14:30 | 2015-09-08 | 2 | 14 | 240 | 87.5333 | 6
2015-09-08 14:45 | 2015-09-08 | 2 | 14 | 254 | 89.5333 | 6
2015-09-08 15:00 | 2015-09-08 | 2 | 15 | 243 | 90.8 | 7
2015-09-08 15:15 | 2015-09-08 | 2 | 15 | 257 | 90.05 | 7
2015-09-08 15:30 | 2015-09-08 | 2 | 15 | 248 | 89.3 | 6
2015-09-08 15:45 | 2015-09-08 | 2 | 15 | 257 | 88.55 | 6
2015-09-08 16:00 | 2015-09-08 | 2 | 16 | 257 | 87.8667 | 6
2015-09-08 16:15 | 2015-09-08 | 2 | 16 | 253 | 87.3667 | 6
2015-09-08 16:30 | 2015-09-08 | 2 | 16 | 257 | 86.8667 | 6
2015-09-08 16:45 | 2015-09-08 | 2 | 16 | 251 | 86.3667 | 6
2015-09-08 17:00 | 2015-09-08 | 2 | 17 | 251 | 85.6667 | 6
2015-09-08 17:15 | 2015-09-08 | 2 | 17 | 252 | 84.4167 | 5
2015-09-08 17:30 | 2015-09-08 | 2 | 17 | 249 | 83.1667 | 5
2015-09-08 17:45 | 2015-09-08 | 2 | 17 | 252 | 81.9167 | 5
2015-09-08 18:00 | 2015-09-08 | 2 | 18 | 239 | 80.7333 | 5
2015-09-08 18:15 | 2015-09-08 | 2 | 18 | 247 | 79.7333 | 4
2015-09-08 18:30 | 2015-09-08 | 2 | 18 | 245 | 78.7333 | 4
2015-09-08 18:45 | 2015-09-08 | 2 | 18 | 231 | 77.7333 | 4
2015-09-08 19:00 | 2015-09-08 | 2 | 19 | 234 | 76.9333 | 4
2015-09-08 19:15 | 2015-09-08 | 2 | 19 | 230 | 76.6833 | 4
2015-09-08 19:30 | 2015-09-08 | 2 | 19 | 221 | 76.4333 | 4
2015-09-08 19:45 | 2015-09-08 | 2 | 19 | 228 | 76.1833 | 4
2015-09-08 20:00 | 2015-09-08 | 2 | 20 | 215 | 76 | 4
2015-09-08 20:15 | 2015-09-08 | 2 | 20 | 215 | 76 | 4
2015-09-08 20:30 | 2015-09-08 | 2 | 20 | 212 | 76 | 4
2015-09-08 20:45 | 2015-09-08 | 2 | 20 | 211 | 76 | 4
2015-09-08 21:00 | 2015-09-08 | 2 | 21 | 201 | 76 | 4
2015-09-08 21:15 | 2015-09-08 | 2 | 21 | 204 | 76 | 4
2015-09-08 21:30 | 2015-09-08 | 2 | 21 | 191 | 76 | 4
2015-09-08 21:45 | 2015-09-08 | 2 | 21 | 188 | 76 | 4
2015-09-08 22:00 | 2015-09-08 | 2 | 22 | 195 | 75.7333 | 4
2015-09-08 22:15 | 2015-09-08 | 2 | 22 | 191 | 74.7333 | 3
2015-09-08 22:30 | 2015-09-08 | 2 | 22 | 182 | 73.7333 | 3
2015-09-08 22:45 | 2015-09-08 | 2 | 22 | 184 | 72.7333 | 3
2015-09-08 23:00 | 2015-09-08 | 2 | 23 | 192 | 72 | 3
2015-09-08 23:15 | 2015-09-08 | 2 | 23 | 175 | 72 | 3
2015-09-08 23:30 | 2015-09-08 | 2 | 23 | 178 | 72 | 3
2015-09-08 23:45 | 2015-09-08 | 2 | 23 | 179 | 72 | 3
2015-09-09 | 2015-09-09 | 3 | 0 | 169 | 71.8667 | 3
2015-09-09 00:15 | 2015-09-09 | 3 | 0 | 172 | 71.3667 | 3
2015-09-09 00:30 | 2015-09-09 | 3 | 0 | 173 | 70.8667 | 3
2015-09-09 00:45 | 2015-09-09 | 3 | 0 | 170 | 70.3667 | 3
2015-09-09 01:00 | 2015-09-09 | 3 | 1 | 172 | 69.8667 | 2
2015-09-09 01:15 | 2015-09-09 | 3 | 1 | 174 | 69.3667 | 2
2015-09-09 01:30 | 2015-09-09 | 3 | 1 | 164 | 68.8667 | 2
2015-09-09 01:45 | 2015-09-09 | 3 | 1 | 171 | 68.3667 | 2
2015-09-09 02:00 | 2015-09-09 | 3 | 2 | 170 | 67.9333 | 2
2015-09-09 02:15 | 2015-09-09 | 3 | 2 | 161 | 67.6833 | 2
2015-09-09 02:30 | 2015-09-09 | 3 | 2 | 177 | 67.4333 | 2
2015-09-09 02:45 | 2015-09-09 | 3 | 2 | 161 | 67.1833 | 2
2015-09-09 03:00 | 2015-09-09 | 3 | 3 | 160 | 66.8667 | 2
2015-09-09 03:15 | 2015-09-09 | 3 | 3 | 169 | 66.3667 | 2
2015-09-09 03:30 | 2015-09-09 | 3 | 3 | 159 | 65.8667 | 2
2015-09-09 03:45 | 2015-09-09 | 3 | 3 | 167 | 65.3667 | 2
2015-09-09 04:00 | 2015-09-09 | 3 | 4 | 165 | 65 | 1
2015-09-09 04:15 | 2015-09-09 | 3 | 4 | 157 | 65 | 1
2015-09-09 04:30 | 2015-09-09 | 3 | 4 | 166 | 65 | 1
2015-09-09 04:45 | 2015-09-09 | 3 | 4 | 156 | 65 | 1
2015-09-09 05:00 | 2015-09-09 | 3 | 5 | 169 | 65 | 1
2015-09-09 05:15 | 2015-09-09 | 3 | 5 | 158 | 65 | 1
2015-09-09 05:30 | 2015-09-09 | 3 | 5 | 163 | 65 | 1
2015-09-09 05:45 | 2015-09-09 | 3 | 5 | 165 | 65 | 1
2015-09-09 06:00 | 2015-09-09 | 3 | 6 | 160 | 65.3333 | 2
2015-09-09 06:15 | 2015-09-09 | 3 | 6 | 166 | 66.5833 | 2
2015-09-09 06:30 | 2015-09-09 | 3 | 6 | 156 | 67.8333 | 2
2015-09-09 06:45 | 2015-09-09 | 3 | 6 | 163 | 69.0833 | 2
2015-09-09 07:00 | 2015-09-09 | 3 | 7 | 155 | 70.1333 | 3
2015-09-09 07:15 | 2015-09-09 | 3 | 7 | 160 | 70.6333 | 3
2015-09-09 07:30 | 2015-09-09 | 3 | 7 | 152 | 71.1333 | 3
2015-09-09 07:45 | 2015-09-09 | 3 | 7 | 162 | 71.6333 | 3
2015-09-09 08:00 | 2015-09-09 | 3 | 8 | 162 | 72.1333 | 3
2015-09-09 08:15 | 2015-09-09 | 3 | 8 | 181 | 72.6333 | 3
2015-09-09 08:30 | 2015-09-09 | 3 | 8 | 181 | 73.1333 | 3
2015-09-09 08:45 | 2015-09-09 | 3 | 8 | 180 | 73.6333 | 3
2015-09-09 09:00 | 2015-09-09 | 3 | 9 | 181 | 74.0667 | 3
2015-09-09 09:15 | 2015-09-09 | 3 | 9 | 197 | 74.3167 | 3
2015-09-09 09:30 | 2015-09-09 | 3 | 9 | 184 | 74.5667 | 3
2015-09-09 09:45 | 2015-09-09 | 3 | 9 | 197 | 74.8167 | 3
2015-09-09 10:00 | 2015-09-09 | 3 | 10 | 210 | 75.1333 | 4
2015-09-09 10:15 | 2015-09-09 | 3 | 10 | 200 | 75.6333 | 4
2015-09-09 10:30 | 2015-09-09 | 3 | 10 | 216 | 76.1333 | 4
2015-09-09 10:45 | 2015-09-09 | 3 | 10 | 218 | 76.6333 | 4
2015-09-09 11:00 | 2015-09-09 | 3 | 11 | 218 | 77.2 | 4
2015-09-09 11:15 | 2015-09-09 | 3 | 11 | 235 | 77.95 | 4
2015-09-09 11:30 | 2015-09-09 | 3 | 11 | 239 | 78.7 | 4
2015-09-09 11:45 | 2015-09-09 | 3 | 11 | 228 | 79.45 | 4
2015-09-09 12:00 | 2015-09-09 | 3 | 12 | 247 | 80.7111 | 5
2015-09-09 12:15 | 2015-09-09 | 3 | 12 | 234 | 83.3778 | 5
2015-09-09 12:30 | 2015-09-09 | 3 | 12 | 253 | 86.0444 | 6
2015-09-09 12:45 | 2015-09-09 | 3 | 12 | 236 | 88 | 6
2015-09-09 13:00 | 2015-09-09 | 3 | 13 | 252 | 88.1333 | 6
2015-09-09 13:15 | 2015-09-09 | 3 | 13 | 240 | 88.6333 | 6
2015-09-09 13:30 | 2015-09-09 | 3 | 13 | 248 | 89.1333 | 6
2015-09-09 13:45 | 2015-09-09 | 3 | 13 | 256 | 89.6333 | 6
2015-09-09 14:00 | 2015-09-09 | 3 | 14 | 258 | 90 | 6
2015-09-09 14:15 | 2015-09-09 | 3 | 14 | 268 | 90 | 6
2015-09-09 14:30 | 2015-09-09 | 3 | 14 | 263 | 90 | 6
2015-09-09 14:45 | 2015-09-09 | 3 | 14 | 273 | 90 | 6
2015-09-09 15:00 | 2015-09-09 | 3 | 15 | 267 | 89.8 | 6
2015-09-09 15:15 | 2015-09-09 | 3 | 15 | 270 | 89.05 | 6
2015-09-09 15:30 | 2015-09-09 | 3 | 15 | 273 | 88.3 | 6
2015-09-09 15:45 | 2015-09-09 | 3 | 15 | 264 | 87.55 | 6
2015-09-09 16:00 | 2015-09-09 | 3 | 16 | 270 | 86.4667 | 6
2015-09-09 16:15 | 2015-09-09 | 3 | 16 | 260 | 84.4667 | 5
2015-09-09 16:30 | 2015-09-09 | 3 | 16 | 274 | 82.4667 | 5
2015-09-09 16:45 | 2015-09-09 | 3 | 16 | 246 | 80.4667 | 5
2015-09-09 17:00 | 2015-09-09 | 3 | 17 | 270 | 78.7333 | 4
2015-09-09 17:15 | 2015-09-09 | 3 | 17 | 255 | 77.7333 | 4
2015-09-09 17:30 | 2015-09-09 | 3 | 17 | 258 | 76.7333 | 4
2015-09-09 17:45 | 2015-09-09 | 3 | 17 | 244 | 75.7333 | 4
2015-09-09 18:00 | 2015-09-09 | 3 | 18 | 248 | 74.8 | 3
2015-09-09 18:15 | 2015-09-09 | 3 | 18 | 245 | 74.05 | 3
2015-09-09 18:30 | 2015-09-09 | 3 | 18 | 239 | 73.3 | 3
2015-09-09 18:45 | 2015-09-09 | 3 | 18 | 245 | 72.55 | 3
2015-09-09 19:00 | 2015-09-09 | 3 | 19 | 235 | 71.8 | 3
2015-09-09 19:15 | 2015-09-09 | 3 | 19 | 228 | 71.05 | 3
2015-09-09 19:30 | 2015-09-09 | 3 | 19 | 233 | 70.3 | 3
2015-09-09 19:45 | 2015-09-09 | 3 | 19 | 225 | 69.55 | 2
2015-09-09 20:00 | 2015-09-09 | 3 | 20 | 224 | 69 | 2
2015-09-09 20:15 | 2015-09-09 | 3 | 20 | 216 | 69 | 2
2015-09-09 20:30 | 2015-09-09 | 3 | 20 | 208 | 69 | 2
2015-09-09 20:45 | 2015-09-09 | 3 | 20 | 213 | 69 | 2
2015-09-09 21:00 | 2015-09-09 | 3 | 21 | 203 | 68.8 | 2
2015-09-09 21:15 | 2015-09-09 | 3 | 21 | 192 | 68.05 | 2
2015-09-09 21:30 | 2015-09-09 | 3 | 21 | 206 | 67.3 | 2
2015-09-09 21:45 | 2015-09-09 | 3 | 21 | 191 | 66.55 | 2
2015-09-09 22:00 | 2015-09-09 | 3 | 22 | 202 | 65.9333 | 2
2015-09-09 22:15 | 2015-09-09 | 3 | 22 | 194 | 65.6833 | 2
2015-09-09 22:30 | 2015-09-09 | 3 | 22 | 184 | 65.4333 | 2
2015-09-09 22:45 | 2015-09-09 | 3 | 22 | 197 | 65.1833 | 2
2015-09-09 23:00 | 2015-09-09 | 3 | 23 | 192 | 64.6667 | 1
2015-09-09 23:15 | 2015-09-09 | 3 | 23 | 190 | 63.4167 | 1
2015-09-09 23:30 | 2015-09-09 | 3 | 23 | 191 | 62.1667 | 1
2015-09-09 23:45 | 2015-09-09 | 3 | 23 | 184 | 60.9167 | 1
2015-09-10 | 2015-09-10 | 4 | 0 | 179 | 60.0667 | 1
2015-09-10 00:15 | 2015-09-10 | 4 | 0 | 190 | 60.3167 | 1
2015-09-10 00:30 | 2015-09-10 | 4 | 0 | 175 | 60.5667 | 1
2015-09-10 00:45 | 2015-09-10 | 4 | 0 | 185 | 60.8167 | 1
2015-09-10 01:00 | 2015-09-10 | 4 | 1 | 176 | 60.8667 | 1
2015-09-10 01:15 | 2015-09-10 | 4 | 1 | 170 | 60.3667 | 1
2015-09-10 01:30 | 2015-09-10 | 4 | 1 | 175 | 59.8667 | 1
2015-09-10 01:45 | 2015-09-10 | 4 | 1 | 163 | 59.3667 | 1
2015-09-10 02:00 | 2015-09-10 | 4 | 2 | 171 | 59 | 1
2015-09-10 02:15 | 2015-09-10 | 4 | 2 | 168 | 59 | 1
2015-09-10 02:30 | 2015-09-10 | 4 | 2 | 162 | 59 | 1
2015-09-10 02:45 | 2015-09-10 | 4 | 2 | 176 | 59 | 1
2015-09-10 03:00 | 2015-09-10 | 4 | 3 | 164 | 58.9333 | 1
2015-09-10 03:15 | 2015-09-10 | 4 | 3 | 178 | 58.6833 | 1
2015-09-10 03:30 | 2015-09-10 | 4 | 3 | 163 | 58.4333 | 1
2015-09-10 03:45 | 2015-09-10 | 4 | 3 | 174 | 58.1833 | 1
2015-09-10 04:00 | 2015-09-10 | 4 | 4 | 162 | 57.9286 | 1
2015-09-10 04:15 | 2015-09-10 | 4 | 4 | 175 | 57.6607 | 1
2015-09-10 04:30 | 2015-09-10 | 4 | 4 | 170 | 57.3929 | 1
2015-09-10 04:45 | 2015-09-10 | 4 | 4 | 168 | 57.125 | 1
2015-09-10 05:00 | 2015-09-10 | 4 | 5 | 168 | 57.0667 | 1
2015-09-10 05:15 | 2015-09-10 | 4 | 5 | 158 | 57.3167 | 1
2015-09-10 05:30 | 2015-09-10 | 4 | 5 | 168 | 57.5667 | 1
2015-09-10 05:45 | 2015-09-10 | 4 | 5 | 158 | 57.8167 | 1
2015-09-10 06:00 | 2015-09-10 | 4 | 6 | 171 | 58.3333 | 1
2015-09-10 06:15 | 2015-09-10 | 4 | 6 | 162 | 59.5833 | 1
2015-09-10 06:30 | 2015-09-10 | 4 | 6 | 170 | 60.8333 | 1
2015-09-10 06:45 | 2015-09-10 | 4 | 6 | 155 | 62.0833 | 1
2015-09-10 07:00 | 2015-09-10 | 4 | 7 | 169 | 63.2667 | 1
2015-09-10 07:15 | 2015-09-10 | 4 | 7 | 161 | 64.2667 | 1
2015-09-10 07:30 | 2015-09-10 | 4 | 7 | 167 | 65.2667 | 2
2015-09-10 07:45 | 2015-09-10 | 4 | 7 | 173 | 66.2667 | 2
2015-09-10 08:00 | 2015-09-10 | 4 | 8 | 177 | 67.2 | 2
2015-09-10 08:15 | 2015-09-10 | 4 | 8 | 175 | 67.95 | 2
2015-09-10 08:30 | 2015-09-10 | 4 | 8 | 180 | 68.7 | 2
2015-09-10 08:45 | 2015-09-10 | 4 | 8 | 184 | 69.45 | 2
2015-09-10 09:00 | 2015-09-10 | 4 | 9 | 199 | 70.2 | 3
2015-09-10 09:15 | 2015-09-10 | 4 | 9 | 198 | 70.95 | 3
2015-09-10 09:30 | 2015-09-10 | 4 | 9 | 194 | 71.7 | 3
2015-09-10 09:45 | 2015-09-10 | 4 | 9 | 214 | 72.45 | 3
2015-09-10 10:00 | 2015-09-10 | 4 | 10 | 210 | 73.0667 | 3
2015-09-10 10:15 | 2015-09-10 | 4 | 10 | 212 | 73.3167 | 3
2015-09-10 10:30 | 2015-09-10 | 4 | 10 | 230 | 73.5667 | 3
2015-09-10 10:45 | 2015-09-10 | 4 | 10 | 212 | 73.8167 | 3
2015-09-10 11:00 | 2015-09-10 | 4 | 11 | 235 | 74.2 | 3
2015-09-10 11:15 | 2015-09-10 | 4 | 11 | 238 | 74.95 | 3
2015-09-10 11:30 | 2015-09-10 | 4 | 11 | 256 | 75.7 | 4
2015-09-10 11:45 | 2015-09-10 | 4 | 11 | 247 | 76.45 | 4
2015-09-10 12:00 | 2015-09-10 | 4 | 12 | 236 | 77.2 | 4
2015-09-10 12:15 | 2015-09-10 | 4 | 12 | 255 | 77.95 | 4
2015-09-10 12:30 | 2015-09-10 | 4 | 12 | 250 | 78.7 | 4
2015-09-10 12:45 | 2015-09-10 | 4 | 12 | 279 | 79.45 | 4
2015-09-10 13:00 | 2015-09-10 | 4 | 13 | 261 | 80.0667 | 5
2015-09-10 13:15 | 2015-09-10 | 4 | 13 | 270 | 80.3167 | 5
2015-09-10 13:30 | 2015-09-10 | 4 | 13 | 257 | 80.5667 | 5
2015-09-10 13:45 | 2015-09-10 | 4 | 13 | 277 | 80.8167 | 5
2015-09-10 14:00 | 2015-09-10 | 4 | 14 | 276 | 80.9333 | 5
2015-09-10 14:15 | 2015-09-10 | 4 | 14 | 273 | 80.6833 | 5
2015-09-10 14:30 | 2015-09-10 | 4 | 14 | 269 | 80.4333 | 5
2015-09-10 14:45 | 2015-09-10 | 4 | 14 | 274 | 80.1833 | 5
2015-09-10 15:00 | 2015-09-10 | 4 | 15 | 276 | 80 | 4
2015-09-10 15:15 | 2015-09-10 | 4 | 15 | 288 | 80 | 4
2015-09-10 15:30 | 2015-09-10 | 4 | 15 | 275 | 80 | 4
2015-09-10 15:45 | 2015-09-10 | 4 | 15 | 267 | 80 | 4
2015-09-10 16:00 | 2015-09-10 | 4 | 16 | 246 | 79.6 | 4
2015-09-10 16:15 | 2015-09-10 | 4 | 16 | 272 | 78.1 | 4
2015-09-10 16:30 | 2015-09-10 | 4 | 16 | 274 | 76.6 | 4
2015-09-10 16:45 | 2015-09-10 | 4 | 16 | 258 | 75.1 | 4
2015-09-10 17:00 | 2015-09-10 | 4 | 17 | 253 | 73.7333 | 3
2015-09-10 17:15 | 2015-09-10 | 4 | 17 | 250 | 72.7333 | 3
2015-09-10 17:30 | 2015-09-10 | 4 | 17 | 248 | 71.7333 | 3
2015-09-10 17:45 | 2015-09-10 | 4 | 17 | 253 | 70.7333 | 3
2015-09-10 18:00 | 2015-09-10 | 4 | 18 | 252 | 69.6667 | 2
2015-09-10 18:15 | 2015-09-10 | 4 | 18 | 241 | 68.4167 | 2
2015-09-10 18:30 | 2015-09-10 | 4 | 18 | 246 | 67.1667 | 2
2015-09-10 18:45 | 2015-09-10 | 4 | 18 | 238 | 65.9167 | 2
2015-09-10 19:00 | 2015-09-10 | 4 | 19 | 248 | 64.9333 | 1
2015-09-10 19:15 | 2015-09-10 | 4 | 19 | 228 | 64.6833 | 1
2015-09-10 19:30 | 2015-09-10 | 4 | 19 | 224 | 64.4333 | 1
2015-09-10 19:45 | 2015-09-10 | 4 | 19 | 214 | 64.1833 | 1
2015-09-10 20:00 | 2015-09-10 | 4 | 20 | 220 | 63.9333 | 1
2015-09-10 20:15 | 2015-09-10 | 4 | 20 | 214 | 63.6833 | 1
2015-09-10 20:30 | 2015-09-10 | 4 | 20 | 214 | 63.4333 | 1
2015-09-10 20:45 | 2015-09-10 | 4 | 20 | 205 | 63.1833 | 1
2015-09-10 21:00 | 2015-09-10 | 4 | 21 | 203 | 63 | 1
2015-09-10 21:15 | 2015-09-10 | 4 | 21 | 207 | 63 | 1
2015-09-10 21:30 | 2015-09-10 | 4 | 21 | 202 | 63 | 1
2015-09-10 21:45 | 2015-09-10 | 4 | 21 | 193 | 63 | 1
2015-09-10 22:00 | 2015-09-10 | 4 | 22 | 202 | 62.8667 | 1
2015-09-10 22:15 | 2015-09-10 | 4 | 22 | 202 | 62.3667 | 1
2015-09-10 22:30 | 2015-09-10 | 4 | 22 | 195 | 61.8667 | 1
2015-09-10 22:45 | 2015-09-10 | 4 | 22 | 198 | 61.3667 | 1
2015-09-10 23:00 | 2015-09-10 | 4 | 23 | 184 | 60.8667 | 1
2015-09-10 23:15 | 2015-09-10 | 4 | 23 | 184 | 60.3667 | 1
2015-09-10 23:30 | 2015-09-10 | 4 | 23 | 185 | 59.8667 | 1
2015-09-10 23:45 | 2015-09-10 | 4 | 23 | 186 | 59.3667 | 1
2015-09-11 | 2015-09-11 | 5 | 0 | 184 | 59 | 1
2015-09-11 00:15 | 2015-09-11 | 5 | 0 | 176 | 59 | 1
2015-09-11 00:30 | 2015-09-11 | 5 | 0 | 174 | 59 | 1
2015-09-11 00:45 | 2015-09-11 | 5 | 0 | 182 | 59 | 1
2015-09-11 01:00 | 2015-09-11 | 5 | 1 | 176 | 58.9333 | 1
2015-09-11 01:15 | 2015-09-11 | 5 | 1 | 172 | 58.6833 | 1
2015-09-11 01:30 | 2015-09-11 | 5 | 1 | 170 | 58.4333 | 1
2015-09-11 01:45 | 2015-09-11 | 5 | 1 | 170 | 58.1833 | 1
2015-09-11 02:00 | 2015-09-11 | 5 | 2 | 183 | 58 | 1
2015-09-11 02:15 | 2015-09-11 | 5 | 2 | 168 | 58 | 1
2015-09-11 02:30 | 2015-09-11 | 5 | 2 | 169 | 58 | 1
2015-09-11 02:45 | 2015-09-11 | 5 | 2 | 171 | 58 | 1
2015-09-11 03:00 | 2015-09-11 | 5 | 3 | 169 | 57.9333 | 1
2015-09-11 03:15 | 2015-09-11 | 5 | 3 | 167 | 57.6833 | 1
2015-09-11 03:30 | 2015-09-11 | 5 | 3 | 179 | 57.4333 | 1
2015-09-11 03:45 | 2015-09-11 | 5 | 3 | 171 | 57.1833 | 1
2015-09-11 04:00 | 2015-09-11 | 5 | 4 | 158 | 57 | 1
2015-09-11 04:15 | 2015-09-11 | 5 | 4 | 174 | 57 | 1
2015-09-11 04:30 | 2015-09-11 | 5 | 4 | 166 | 57 | 1
2015-09-11 04:45 | 2015-09-11 | 5 | 4 | 160 | 57 | 1
2015-09-11 05:00 | 2015-09-11 | 5 | 5 | 181 | 57 | 1
2015-09-11 05:15 | 2015-09-11 | 5 | 5 | 158 | 57 | 1
2015-09-11 05:30 | 2015-09-11 | 5 | 5 | 170 | 57 | 1
2015-09-11 05:45 | 2015-09-11 | 5 | 5 | 164 | 57 | 1
2015-09-11 06:00 | 2015-09-11 | 5 | 6 | 167 | 57.0667 | 1
2015-09-11 06:15 | 2015-09-11 | 5 | 6 | 175 | 57.3167 | 1
2015-09-11 06:30 | 2015-09-11 | 5 | 6 | 166 | 57.5667 | 1
2015-09-11 06:45 | 2015-09-11 | 5 | 6 | 172 | 57.8167 | 1
2015-09-11 07:00 | 2015-09-11 | 5 | 7 | 173 | 58.1333 | 1
2015-09-11 07:15 | 2015-09-11 | 5 | 7 | 185 | 58.6333 | 1
2015-09-11 07:30 | 2015-09-11 | 5 | 7 | 181 | 59.1333 | 1
2015-09-11 07:45 | 2015-09-11 | 5 | 7 | 182 | 59.6333 | 1
2015-09-11 08:00 | 2015-09-11 | 5 | 8 | 192 | 60.3333 | 1
2015-09-11 08:15 | 2015-09-11 | 5 | 8 | 189 | 61.5833 | 1
2015-09-11 08:30 | 2015-09-11 | 5 | 8 | 197 | 62.8333 | 1
2015-09-11 08:45 | 2015-09-11 | 5 | 8 | 196 | 64.0833 | 1
2015-09-11 09:00 | 2015-09-11 | 5 | 9 | 191 | 65.2 | 2
2015-09-11 09:15 | 2015-09-11 | 5 | 9 | 196 | 65.95 | 2
2015-09-11 09:30 | 2015-09-11 | 5 | 9 | 217 | 66.7 | 2
2015-09-11 09:45 | 2015-09-11 | 5 | 9 | 224 | 67.45 | 2
2015-09-11 10:00 | 2015-09-11 | 5 | 10 | 225 | 68.0667 | 2
2015-09-11 10:15 | 2015-09-11 | 5 | 10 | 228 | 68.3167 | 2
2015-09-11 10:30 | 2015-09-11 | 5 | 10 | 241 | 68.5667 | 2
2015-09-11 10:45 | 2015-09-11 | 5 | 10 | 257 | 68.8167 | 2
2015-09-11 11:00 | 2015-09-11 | 5 | 11 | 245 | 69.2 | 2
2015-09-11 11:15 | 2015-09-11 | 5 | 11 | 254 | 69.95 | 2
2015-09-11 11:30 | 2015-09-11 | 5 | 11 | 254 | 70.7 | 3
2015-09-11 11:45 | 2015-09-11 | 5 | 11 | 261 | 71.45 | 3
2015-09-11 12:00 | 2015-09-11 | 5 | 12 | 262 | 72.1333 | 3
2015-09-11 12:15 | 2015-09-11 | 5 | 12 | 255 | 72.6333 | 3
2015-09-11 12:30 | 2015-09-11 | 5 | 12 | 262 | 73.1333 | 3
2015-09-11 12:45 | 2015-09-11 | 5 | 12 | 248 | 73.6333 | 3
2015-09-11 13:00 | 2015-09-11 | 5 | 13 | 275 | 74 | 3
2015-09-11 13:15 | 2015-09-11 | 5 | 13 | 256 | 74 | 3
2015-09-11 13:30 | 2015-09-11 | 5 | 13 | 263 | 74 | 3
2015-09-11 13:45 | 2015-09-11 | 5 | 13 | 263 | 74 | 3
2015-09-11 14:00 | 2015-09-11 | 5 | 14 | 265 | 74 | 3
2015-09-11 14:15 | 2015-09-11 | 5 | 14 | 271 | 74 | 3
2015-09-11 14:30 | 2015-09-11 | 5 | 14 | 276 | 74 | 3
2015-09-11 14:45 | 2015-09-11 | 5 | 14 | 278 | 74 | 3
2015-09-11 15:00 | 2015-09-11 | 5 | 15 | 263 | 74.0667 | 3
2015-09-11 15:15 | 2015-09-11 | 5 | 15 | 275 | 74.3167 | 3
2015-09-11 15:30 | 2015-09-11 | 5 | 15 | 273 | 74.5667 | 3
2015-09-11 15:45 | 2015-09-11 | 5 | 15 | 270 | 74.8167 | 3
2015-09-11 16:00 | 2015-09-11 | 5 | 16 | 278 | 74.6667 | 3
2015-09-11 16:15 | 2015-09-11 | 5 | 16 | 264 | 73.4167 | 3
2015-09-11 16:30 | 2015-09-11 | 5 | 16 | 261 | 72.1667 | 3
2015-09-11 16:45 | 2015-09-11 | 5 | 16 | 255 | 70.9167 | 3
2015-09-11 17:00 | 2015-09-11 | 5 | 17 | 266 | 69.6667 | 2
2015-09-11 17:15 | 2015-09-11 | 5 | 17 | 269 | 68.4167 | 2
2015-09-11 17:30 | 2015-09-11 | 5 | 17 | 262 | 67.1667 | 2
2015-09-11 17:45 | 2015-09-11 | 5 | 17 | 263 | 65.9167 | 2
2015-09-11 18:00 | 2015-09-11 | 5 | 18 | 261 | 64.8667 | 1
2015-09-11 18:15 | 2015-09-11 | 5 | 18 | 267 | 64.3667 | 1
2015-09-11 18:30 | 2015-09-11 | 5 | 18 | 249 | 63.8667 | 1
2015-09-11 18:45 | 2015-09-11 | 5 | 18 | 250 | 63.3667 | 1
2015-09-11 19:00 | 2015-09-11 | 5 | 19 | 242 | 62.8 | 1
2015-09-11 19:15 | 2015-09-11 | 5 | 19 | 259 | 62.05 | 1
2015-09-11 19:30 | 2015-09-11 | 5 | 19 | 226 | 61.3 | 1
2015-09-11 19:45 | 2015-09-11 | 5 | 19 | 233 | 60.55 | 1
2015-09-11 20:00 | 2015-09-11 | 5 | 20 | 228 | 59.9333 | 1
2015-09-11 20:15 | 2015-09-11 | 5 | 20 | 219 | 59.6833 | 1
2015-09-11 20:30 | 2015-09-11 | 5 | 20 | 226 | 59.4333 | 1
2015-09-11 20:45 | 2015-09-11 | 5 | 20 | 219 | 59.1833 | 1
2015-09-11 21:00 | 2015-09-11 | 5 | 21 | 211 | 59 | 1
2015-09-11 21:15 | 2015-09-11 | 5 | 21 | 202 | 59 | 1
2015-09-11 21:30 | 2015-09-11 | 5 | 21 | 205 | 59 | 1
2015-09-11 21:45 | 2015-09-11 | 5 | 21 | 192 | 59 | 1
2015-09-11 22:00 | 2015-09-11 | 5 | 22 | 187 | 59 | 1
2015-09-11 22:15 | 2015-09-11 | 5 | 22 | 188 | 59 | 1
2015-09-11 22:30 | 2015-09-11 | 5 | 22 | 191 | 59 | 1
2015-09-11 22:45 | 2015-09-11 | 5 | 22 | 197 | 59 | 1
2015-09-11 23:00 | 2015-09-11 | 5 | 23 | 188 | 58.9333 | 1
2015-09-11 23:15 | 2015-09-11 | 5 | 23 | 188 | 58.6833 | 1
2015-09-11 23:30 | 2015-09-11 | 5 | 23 | 197 | 58.4333 | 1
2015-09-11 23:45 | 2015-09-11 | 5 | 23 | 203 | 58.1833 | 1
2015-09-12 | 2015-09-12 | 6 | 0 | 185 | 58 | 1
2015-09-12 00:15 | 2015-09-12 | 6 | 0 | 183 | 58 | 1
2015-09-12 00:30 | 2015-09-12 | 6 | 0 | 183 | 58 | 1
2015-09-12 00:45 | 2015-09-12 | 6 | 0 | 189 | 58 | 1
2015-09-12 01:00 | 2015-09-12 | 6 | 1 | 186 | 57.92 | 1
2015-09-12 01:15 | 2015-09-12 | 6 | 1 | 178 | 57.62 | 1
2015-09-12 01:30 | 2015-09-12 | 6 | 1 | 180 | 57.32 | 1
2015-09-12 01:45 | 2015-09-12 | 6 | 1 | 189 | 57.02 | 1
2015-09-12 02:00 | 2015-09-12 | 6 | 2 | 178 | 57.9333 | 1
2015-09-12 02:15 | 2015-09-12 | 6 | 2 | 175 | 57.6833 | 1
2015-09-12 02:30 | 2015-09-12 | 6 | 2 | 171 | 57.4333 | 1
2015-09-12 02:45 | 2015-09-12 | 6 | 2 | 175 | 57.1833 | 1
2015-09-12 03:00 | 2015-09-12 | 6 | 3 | 191 | 57 | 1
2015-09-12 03:15 | 2015-09-12 | 6 | 3 | 168 | 57 | 1
2015-09-12 03:30 | 2015-09-12 | 6 | 3 | 168 | 57 | 1
2015-09-12 03:45 | 2015-09-12 | 6 | 3 | 169 | 57 | 1
2015-09-12 04:00 | 2015-09-12 | 6 | 4 | 186 | 57 | 1
2015-09-12 04:15 | 2015-09-12 | 6 | 4 | 172 | 57 | 1
2015-09-12 04:30 | 2015-09-12 | 6 | 4 | 165 | 57 | 1
2015-09-12 04:45 | 2015-09-12 | 6 | 4 | 172 | 57.0833 | 1
2015-09-12 05:00 | 2015-09-12 | 6 | 5 | 169 | 58 | 1
2015-09-12 05:15 | 2015-09-12 | 6 | 5 | 184 | 58 | 1
2015-09-12 05:30 | 2015-09-12 | 6 | 5 | 165 | 58 | 1
2015-09-12 05:45 | 2015-09-12 | 6 | 5 | 169 | 58 | 1
2015-09-12 06:00 | 2015-09-12 | 6 | 6 | 168 | 58 | 1
2015-09-12 06:15 | 2015-09-12 | 6 | 6 | 188 | 58 | 1
2015-09-12 06:30 | 2015-09-12 | 6 | 6 | 175 | 58 | 1
2015-09-12 06:45 | 2015-09-12 | 6 | 6 | 171 | 58 | 1
2015-09-12 07:00 | 2015-09-12 | 6 | 7 | 177 | 58.5 | 1
2015-09-12 07:15 | 2015-09-12 | 6 | 7 | 171 | 59.2115 | 1
2015-09-12 07:30 | 2015-09-12 | 6 | 7 | 185 | 59.5 | 1
2015-09-12 07:45 | 2015-09-12 | 6 | 7 | 169 | 59.7885 | 1
2015-09-12 08:00 | 2015-09-12 | 6 | 8 | 168 | 60.0667 | 1
2015-09-12 08:15 | 2015-09-12 | 6 | 8 | 165 | 60.3167 | 1
2015-09-12 08:30 | 2015-09-12 | 6 | 8 | 186 | 60.5667 | 1
2015-09-12 08:45 | 2015-09-12 | 6 | 8 | 177 | 60.8167 | 1
2015-09-12 09:00 | 2015-09-12 | 6 | 9 | 169 | 61.1333 | 1
2015-09-12 09:15 | 2015-09-12 | 6 | 9 | 175 | 61.6333 | 1
2015-09-12 09:30 | 2015-09-12 | 6 | 9 | 174 | 62.1333 | 1
2015-09-12 09:45 | 2015-09-12 | 6 | 9 | 191 | 62.6333 | 1
2015-09-12 10:00 | 2015-09-12 | 6 | 10 | 182 | 62.75 | 1
2015-09-12 10:15 | 2015-09-12 | 6 | 10 | 174 | 61.8125 | 1
2015-09-12 10:30 | 2015-09-12 | 6 | 10 | 175 | 61 | 1
2015-09-12 10:45 | 2015-09-12 | 6 | 10 | 181 | 61 | 1
2015-09-12 11:00 | 2015-09-12 | 6 | 11 | 196 | 60.9333 | 1
2015-09-12 11:15 | 2015-09-12 | 6 | 11 | 176 | 60.6833 | 1
2015-09-12 11:30 | 2015-09-12 | 6 | 11 | 178 | 60.4333 | 1
2015-09-12 11:45 | 2015-09-12 | 6 | 11 | 181 | 60.1833 | 1
2015-09-12 12:00 | 2015-09-12 | 6 | 12 | 176 | 60.125 | 1
2015-09-12 12:15 | 2015-09-12 | 6 | 12 | 192 | 60.5938 | 1
2015-09-12 12:30 | 2015-09-12 | 6 | 12 | 186 | 61 | 1
2015-09-12 12:45 | 2015-09-12 | 6 | 12 | 183 | 61 | 1
2015-09-12 13:00 | 2015-09-12 | 6 | 13 | 181 | 61.0667 | 1
2015-09-12 13:15 | 2015-09-12 | 6 | 13 | 189 | 61.3167 | 1
2015-09-12 13:30 | 2015-09-12 | 6 | 13 | 197 | 61.5667 | 1
2015-09-12 13:45 | 2015-09-12 | 6 | 13 | 175 | 61.8167 | 1
2015-09-12 14:00 | 2015-09-12 | 6 | 14 | 174 | 62.1333 | 1
2015-09-12 14:15 | 2015-09-12 | 6 | 14 | 185 | 62.6333 | 1
2015-09-12 14:30 | 2015-09-12 | 6 | 14 | 197 | 63.1333 | 1
2015-09-12 14:45 | 2015-09-12 | 6 | 14 | 187 | 63.6333 | 1
2015-09-12 15:00 | 2015-09-12 | 6 | 15 | 182 | 64.4667 | 1
2015-09-12 15:15 | 2015-09-12 | 6 | 15 | 190 | 66.2167 | 2
2015-09-12 15:30 | 2015-09-12 | 6 | 15 | 189 | 67.9667 | 2
2015-09-12 15:45 | 2015-09-12 | 6 | 15 | 193 | 69.7167 | 2
2015-09-12 16:00 | 2015-09-12 | 6 | 16 | 199 | 71 | 3
2015-09-12 16:15 | 2015-09-12 | 6 | 16 | 184 | 71 | 3
2015-09-12 16:30 | 2015-09-12 | 6 | 16 | 186 | 71 | 3
2015-09-12 16:45 | 2015-09-12 | 6 | 16 | 196 | 71 | 3
2015-09-12 17:00 | 2015-09-12 | 6 | 17 | 200 | 71.1333 | 3
2015-09-12 17:15 | 2015-09-12 | 6 | 17 | 180 | 71.6333 | 3
2015-09-12 17:30 | 2015-09-12 | 6 | 17 | 187 | 72.1333 | 3
2015-09-12 17:45 | 2015-09-12 | 6 | 17 | 180 | 72.6333 | 3
2015-09-12 18:00 | 2015-09-12 | 6 | 18 | 199 | 72.6667 | 3
2015-09-12 18:15 | 2015-09-12 | 6 | 18 | 200 | 71.4167 | 3
2015-09-12 18:30 | 2015-09-12 | 6 | 18 | 185 | 70.1667 | 3
2015-09-12 18:45 | 2015-09-12 | 6 | 18 | 185 | 68.9167 | 2
2015-09-12 19:00 | 2015-09-12 | 6 | 19 | 179 | 67.8 | 2
2015-09-12 19:15 | 2015-09-12 | 6 | 19 | 192 | 67.05 | 2
2015-09-12 19:30 | 2015-09-12 | 6 | 19 | 195 | 66.3 | 2
2015-09-12 19:45 | 2015-09-12 | 6 | 19 | 177 | 65.55 | 2
2015-09-12 20:00 | 2015-09-12 | 6 | 20 | 176 | 64.9333 | 1
2015-09-12 20:15 | 2015-09-12 | 6 | 20 | 195 | 64.6833 | 1
2015-09-12 20:30 | 2015-09-12 | 6 | 20 | 181 | 64.4333 | 1
2015-09-12 20:45 | 2015-09-12 | 6 | 20 | 177 | 64.1833 | 1
2015-09-12 21:00 | 2015-09-12 | 6 | 21 | 179 | 63.931 | 1
2015-09-12 21:15 | 2015-09-12 | 6 | 21 | 191 | 63.6724 | 1
2015-09-12 21:30 | 2015-09-12 | 6 | 21 | 171 | 63.4138 | 1
2015-09-12 21:45 | 2015-09-12 | 6 | 21 | 173 | 63.1552 | 1
2015-09-12 22:00 | 2015-09-12 | 6 | 22 | 174 | 62.9333 | 1
2015-09-12 22:15 | 2015-09-12 | 6 | 22 | 183 | 62.6833 | 1
2015-09-12 22:30 | 2015-09-12 | 6 | 22 | 172 | 62.4333 | 1
2015-09-12 22:45 | 2015-09-12 | 6 | 22 | 176 | 62.1833 | 1
2015-09-12 23:00 | 2015-09-12 | 6 | 23 | 171 | 61.9333 | 1
2015-09-12 23:15 | 2015-09-12 | 6 | 23 | 182 | 61.6833 | 1
2015-09-12 23:30 | 2015-09-12 | 6 | 23 | 174 | 61.4333 | 1
2015-09-12 23:45 | 2015-09-12 | 6 | 23 | 173 | 61.1833 | 1
2015-09-13 | 2015-09-13 | 7 | 0 | 171 | 61 | 1
2015-09-13 00:15 | 2015-09-13 | 7 | 0 | 176 | 61 | 1
2015-09-13 00:30 | 2015-09-13 | 7 | 0 | 188 | 61 | 1
2015-09-13 00:45 | 2015-09-13 | 7 | 0 | 175 | 61 | 1
2015-09-13 01:00 | 2015-09-13 | 7 | 1 | 172 | 60.9333 | 1
2015-09-13 01:15 | 2015-09-13 | 7 | 1 | 165 | 60.6833 | 1
2015-09-13 01:30 | 2015-09-13 | 7 | 1 | 172 | 60.4333 | 1
2015-09-13 01:45 | 2015-09-13 | 7 | 1 | 183 | 60.1833 | 1
2015-09-13 02:00 | 2015-09-13 | 7 | 2 | 169 | 60 | 1
2015-09-13 02:15 | 2015-09-13 | 7 | 2 | 169 | 60 | 1
2015-09-13 02:30 | 2015-09-13 | 7 | 2 | 168 | 60 | 1
2015-09-13 02:45 | 2015-09-13 | 7 | 2 | 174 | 60 | 1
2015-09-13 03:00 | 2015-09-13 | 7 | 3 | 183 | 60 | 1
2015-09-13 03:15 | 2015-09-13 | 7 | 3 | 173 | 60 | 1
2015-09-13 03:30 | 2015-09-13 | 7 | 3 | 169 | 60 | 1
2015-09-13 03:45 | 2015-09-13 | 7 | 3 | 165 | 60 | 1
2015-09-13 04:00 | 2015-09-13 | 7 | 4 | 167 | 60 | 1
2015-09-13 04:15 | 2015-09-13 | 7 | 4 | 185 | 60 | 1
2015-09-13 04:30 | 2015-09-13 | 7 | 4 | 168 | 60 | 1
2015-09-13 04:45 | 2015-09-13 | 7 | 4 | 168 | 60 | 1
2015-09-13 05:00 | 2015-09-13 | 7 | 5 | 177 | 59.9333 | 1
2015-09-13 05:15 | 2015-09-13 | 7 | 5 | 175 | 59.6833 | 1
2015-09-13 05:30 | 2015-09-13 | 7 | 5 | 163 | 59.4333 | 1
2015-09-13 05:45 | 2015-09-13 | 7 | 5 | 169 | 59.1833 | 1
2015-09-13 06:00 | 2015-09-13 | 7 | 6 | 161 | 59.0667 | 1
2015-09-13 06:15 | 2015-09-13 | 7 | 6 | 171 | 59.3167 | 1
2015-09-13 06:30 | 2015-09-13 | 7 | 6 | 184 | 59.5667 | 1
2015-09-13 06:45 | 2015-09-13 | 7 | 6 | 174 | 59.8167 | 1
2015-09-13 07:00 | 2015-09-13 | 7 | 7 | 172 | 60.2 | 1
2015-09-13 07:15 | 2015-09-13 | 7 | 7 | 179 | 60.95 | 1
2015-09-13 07:30 | 2015-09-13 | 7 | 7 | 189 | 61.7 | 1
2015-09-13 07:45 | 2015-09-13 | 7 | 7 | 183 | 62.45 | 1
2015-09-13 08:00 | 2015-09-13 | 7 | 8 | 183 | 63.1333 | 1
2015-09-13 08:15 | 2015-09-13 | 7 | 8 | 176 | 63.6333 | 1
2015-09-13 08:30 | 2015-09-13 | 7 | 8 | 175 | 64.1333 | 1
2015-09-13 08:45 | 2015-09-13 | 7 | 8 | 175 | 64.6333 | 1
2015-09-13 09:00 | 2015-09-13 | 7 | 9 | 195 | 65.0667 | 2
2015-09-13 09:15 | 2015-09-13 | 7 | 9 | 184 | 65.3167 | 2
2015-09-13 09:30 | 2015-09-13 | 7 | 9 | 178 | 65.5667 | 2
2015-09-13 09:45 | 2015-09-13 | 7 | 9 | 180 | 65.8167 | 2
2015-09-13 10:00 | 2015-09-13 | 7 | 10 | 183 | 66.0667 | 2
2015-09-13 10:15 | 2015-09-13 | 7 | 10 | 175 | 66.3167 | 2
2015-09-13 10:30 | 2015-09-13 | 7 | 10 | 170 | 66.5667 | 2
2015-09-13 10:45 | 2015-09-13 | 7 | 10 | 181 | 66.8167 | 2
2015-09-13 11:00 | 2015-09-13 | 7 | 11 | 184 | 67.2667 | 2
2015-09-13 11:15 | 2015-09-13 | 7 | 11 | 179 | 68.2667 | 2
2015-09-13 11:30 | 2015-09-13 | 7 | 11 | 172 | 69.2667 | 2
2015-09-13 11:45 | 2015-09-13 | 7 | 11 | 169 | 70.2667 | 3
2015-09-13 12:00 | 2015-09-13 | 7 | 12 | 184 | 70.9333 | 3
2015-09-13 12:15 | 2015-09-13 | 7 | 12 | 181 | 70.6833 | 3
2015-09-13 12:30 | 2015-09-13 | 7 | 12 | 171 | 70.4333 | 3
2015-09-13 12:45 | 2015-09-13 | 7 | 12 | 183 | 70.1833 | 3
2015-09-13 13:00 | 2015-09-13 | 7 | 13 | 187 | 69.8667 | 2
2015-09-13 13:15 | 2015-09-13 | 7 | 13 | 189 | 69.3667 | 2
2015-09-13 13:30 | 2015-09-13 | 7 | 13 | 179 | 68.8667 | 2
2015-09-13 13:45 | 2015-09-13 | 7 | 13 | 187 | 68.3667 | 2
2015-09-13 14:00 | 2015-09-13 | 7 | 14 | 188 | 67.8667 | 2
2015-09-13 14:15 | 2015-09-13 | 7 | 14 | 199 | 67.3667 | 2
2015-09-13 14:30 | 2015-09-13 | 7 | 14 | 191 | 66.8667 | 2
2015-09-13 14:45 | 2015-09-13 | 7 | 14 | 191 | 66.3667 | 2
2015-09-13 15:00 | 2015-09-13 | 7 | 15 | 191 | 65.8667 | 2
2015-09-13 15:15 | 2015-09-13 | 7 | 15 | 194 | 65.3667 | 2
2015-09-13 15:30 | 2015-09-13 | 7 | 15 | 221 | 64.8667 | 1
2015-09-13 15:45 | 2015-09-13 | 7 | 15 | 203 | 64.3667 | 1
2015-09-13 16:00 | 2015-09-13 | 7 | 16 | 201 | 63.8 | 1
2015-09-13 16:15 | 2015-09-13 | 7 | 16 | 205 | 63.05 | 1
2015-09-13 16:30 | 2015-09-13 | 7 | 16 | 203 | 62.3 | 1
2015-09-13 16:45 | 2015-09-13 | 7 | 16 | 219 | 61.55 | 1
2015-09-13 17:00 | 2015-09-13 | 7 | 17 | 203 | 60.8667 | 1
2015-09-13 17:15 | 2015-09-13 | 7 | 17 | 209 | 60.3667 | 1
2015-09-13 17:30 | 2015-09-13 | 7 | 17 | 196 | 59.8667 | 1
2015-09-13 17:45 | 2015-09-13 | 7 | 17 | 195 | 59.3667 | 1
2015-09-13 18:00 | 2015-09-13 | 7 | 18 | 203 | 59 | 1
2015-09-13 18:15 | 2015-09-13 | 7 | 18 | 205 | 59 | 1
2015-09-13 18:30 | 2015-09-13 | 7 | 18 | 184 | 59 | 1
2015-09-13 18:45 | 2015-09-13 | 7 | 18 | 191 | 59 | 1
2015-09-13 19:00 | 2015-09-13 | 7 | 19 | 182 | 59.0667 | 1
2015-09-13 19:15 | 2015-09-13 | 7 | 19 | 191 | 59.3167 | 1
2015-09-13 19:30 | 2015-09-13 | 7 | 19 | 200 | 59.5667 | 1
2015-09-13 19:45 | 2015-09-13 | 7 | 19 | 187 | 59.8167 | 1
2015-09-13 20:00 | 2015-09-13 | 7 | 20 | 187 | 60 | 1
2015-09-13 20:15 | 2015-09-13 | 7 | 20 | 194 | 60 | 1
2015-09-13 20:30 | 2015-09-13 | 7 | 20 | 180 | 60 | 1
2015-09-13 20:45 | 2015-09-13 | 7 | 20 | 181 | 60 | 1
2015-09-13 21:00 | 2015-09-13 | 7 | 21 | 189 | 60 | 1
2015-09-13 21:15 | 2015-09-13 | 7 | 21 | 186 | 60 | 1
2015-09-13 21:30 | 2015-09-13 | 7 | 21 | 168 | 60 | 1
2015-09-13 21:45 | 2015-09-13 | 7 | 21 | 168 | 60 | 1
2015-09-13 22:00 | 2015-09-13 | 7 | 22 | 168 | 60 | 1
2015-09-13 22:15 | 2015-09-13 | 7 | 22 | 176 | 60 | 1
2015-09-13 22:30 | 2015-09-13 | 7 | 22 | 168 | 60 | 1
2015-09-13 22:45 | 2015-09-13 | 7 | 22 | 181 | 60 | 1
2015-09-13 23:00 | 2015-09-13 | 7 | 23 | 177 | 60 | 1
2015-09-13 23:15 | 2015-09-13 | 7 | 23 | 163 | 60 | 1
2015-09-13 23:30 | 2015-09-13 | 7 | 23 | 173 | 60 | 1
2015-09-13 23:45 | 2015-09-13 | 7 | 23 | 169 | 60 | 1
2015-09-14 | 2015-09-14 | 1 | 0 | 185 | 59.9333 | 1
2015-09-14 00:15 | 2015-09-14 | 1 | 0 | 165 | 59.6833 | 1
2015-09-14 00:30 | 2015-09-14 | 1 | 0 | 163 | 59.4333 | 1
2015-09-14 00:45 | 2015-09-14 | 1 | 0 | 166 | 59.1833 | 1
2015-09-14 01:00 | 2015-09-14 | 1 | 1 | 174 | 59 | 1
2015-09-14 01:15 | 2015-09-14 | 1 | 1 | 173 | 59 | 1
2015-09-14 01:30 | 2015-09-14 | 1 | 1 | 163 | 59 | 1
2015-09-14 01:45 | 2015-09-14 | 1 | 1 | 166 | 59 | 1
2015-09-14 02:00 | 2015-09-14 | 1 | 2 | 161 | 59 | 1
2015-09-14 02:15 | 2015-09-14 | 1 | 2 | 170 | 59 | 1
2015-09-14 02:30 | 2015-09-14 | 1 | 2 | 176 | 59 | 1
2015-09-14 02:45 | 2015-09-14 | 1 | 2 | 168 | 59 | 1
2015-09-14 03:00 | 2015-09-14 | 1 | 3 | 158 | 59 | 1
2015-09-14 03:15 | 2015-09-14 | 1 | 3 | 170 | 59 | 1
2015-09-14 03:30 | 2015-09-14 | 1 | 3 | 176 | 59 | 1
2015-09-14 03:45 | 2015-09-14 | 1 | 3 | 156 | 59 | 1
2015-09-14 04:00 | 2015-09-14 | 1 | 4 | 156 | 59.0667 | 1
2015-09-14 04:15 | 2015-09-14 | 1 | 4 | 159 | 59.3167 | 1
2015-09-14 04:30 | 2015-09-14 | 1 | 4 | 163 | 59.5667 | 1
2015-09-14 04:45 | 2015-09-14 | 1 | 4 | 164 | 59.8167 | 1
2015-09-14 05:00 | 2015-09-14 | 1 | 5 | 160 | 60.2353 | 1
2015-09-14 05:15 | 2015-09-14 | 1 | 5 | 155 | 61 | 1
2015-09-14 05:30 | 2015-09-14 | 1 | 5 | 157 | 61 | 1
2015-09-14 05:45 | 2015-09-14 | 1 | 5 | 161 | 61 | 1
2015-09-14 06:00 | 2015-09-14 | 1 | 6 | 172 | 61.1379 | 1
2015-09-14 06:15 | 2015-09-14 | 1 | 6 | 161 | 61.6552 | 1
2015-09-14 06:30 | 2015-09-14 | 1 | 6 | 159 | 62.1724 | 1
2015-09-14 06:45 | 2015-09-14 | 1 | 6 | 163 | 62.6897 | 1
2015-09-14 07:00 | 2015-09-14 | 1 | 7 | 171 | 62.1379 | 1
2015-09-14 07:15 | 2015-09-14 | 1 | 7 | 157 | 62.6552 | 1
2015-09-14 07:30 | 2015-09-14 | 1 | 7 | 152 | 63.1724 | 1
2015-09-14 07:45 | 2015-09-14 | 1 | 7 | 160 | 63.6897 | 1
2015-09-14 08:00 | 2015-09-14 | 1 | 8 | 186 | 64 | 1
2015-09-14 08:15 | 2015-09-14 | 1 | 8 | 177 | 64 | 1
2015-09-14 08:30 | 2015-09-14 | 1 | 8 | 175 | 64 | 1
2015-09-14 08:45 | 2015-09-14 | 1 | 8 | 181 | 64 | 1
2015-09-14 09:00 | 2015-09-14 | 1 | 9 | 177 | 64.0667 | 1
2015-09-14 09:15 | 2015-09-14 | 1 | 9 | 201 | 64.3167 | 1
2015-09-14 09:30 | 2015-09-14 | 1 | 9 | 202 | 64.5667 | 1
2015-09-14 09:45 | 2015-09-14 | 1 | 9 | 190 | 64.8167 | 1
2015-09-14 10:00 | 2015-09-14 | 1 | 10 | 188 | 65 | 1
2015-09-14 10:15 | 2015-09-14 | 1 | 10 | 203 | 65 | 1
2015-09-14 10:30 | 2015-09-14 | 1 | 10 | 201 | 65 | 1
2015-09-14 10:45 | 2015-09-14 | 1 | 10 | 193 | 65 | 1
2015-09-14 11:00 | 2015-09-14 | 1 | 11 | 196 | 65 | 1
2015-09-14 11:15 | 2015-09-14 | 1 | 11 | 202 | 65 | 1
2015-09-14 11:30 | 2015-09-14 | 1 | 11 | 216 | 65 | 1
2015-09-14 11:45 | 2015-09-14 | 1 | 11 | 197 | 65 | 1
2015-09-14 12:00 | 2015-09-14 | 1 | 12 | 200 | 65.2 | 2
2015-09-14 12:15 | 2015-09-14 | 1 | 12 | 199 | 65.95 | 2
2015-09-14 12:30 | 2015-09-14 | 1 | 12 | 208 | 66.7 | 2
2015-09-14 12:45 | 2015-09-14 | 1 | 12 | 207 | 67.45 | 2
2015-09-14 13:00 | 2015-09-14 | 1 | 13 | 202 | 67.9333 | 2
2015-09-14 13:15 | 2015-09-14 | 1 | 13 | 190 | 67.6833 | 2
2015-09-14 13:30 | 2015-09-14 | 1 | 13 | 202 | 67.4333 | 2
2015-09-14 13:45 | 2015-09-14 | 1 | 13 | 208 | 67.1833 | 2
2015-09-14 14:00 | 2015-09-14 | 1 | 14 | 192 | 67 | 2
2015-09-14 14:15 | 2015-09-14 | 1 | 14 | 192 | 67 | 2
2015-09-14 14:30 | 2015-09-14 | 1 | 14 | 199 | 67 | 2
2015-09-14 14:45 | 2015-09-14 | 1 | 14 | 223 | 67 | 2
2015-09-14 15:00 | 2015-09-14 | 1 | 15 | 194 | 66.9333 | 2
2015-09-14 15:15 | 2015-09-14 | 1 | 15 | 204 | 66.6833 | 2
2015-09-14 15:30 | 2015-09-14 | 1 | 15 | 206 | 66.4333 | 2
2015-09-14 15:45 | 2015-09-14 | 1 | 15 | 209 | 66.1833 | 2
2015-09-14 16:00 | 2015-09-14 | 1 | 16 | 197 | 65.8667 | 2
2015-09-14 16:15 | 2015-09-14 | 1 | 16 | 195 | 65.3667 | 2
2015-09-14 16:30 | 2015-09-14 | 1 | 16 | 199 | 64.8667 | 1
2015-09-14 16:45 | 2015-09-14 | 1 | 16 | 188 | 64.3667 | 1
2015-09-14 17:00 | 2015-09-14 | 1 | 17 | 211 | 63.9333 | 1
2015-09-14 17:15 | 2015-09-14 | 1 | 17 | 211 | 63.6833 | 1
2015-09-14 17:30 | 2015-09-14 | 1 | 17 | 199 | 63.4333 | 1
2015-09-14 17:45 | 2015-09-14 | 1 | 17 | 201 | 63.1833 | 1
2015-09-14 18:00 | 2015-09-14 | 1 | 18 | 192 | 62.9333 | 1
2015-09-14 18:15 | 2015-09-14 | 1 | 18 | 207 | 62.6833 | 1
2015-09-14 18:30 | 2015-09-14 | 1 | 18 | 204 | 62.4333 | 1
2015-09-14 18:45 | 2015-09-14 | 1 | 18 | 198 | 62.1833 | 1
2015-09-14 19:00 | 2015-09-14 | 1 | 19 | 201 | 62 | 1
2015-09-14 19:15 | 2015-09-14 | 1 | 19 | 194 | 62 | 1
2015-09-14 19:30 | 2015-09-14 | 1 | 19 | 199 | 62 | 1
2015-09-14 19:45 | 2015-09-14 | 1 | 19 | 204 | 62 | 1
2015-09-14 20:00 | 2015-09-14 | 1 | 20 | 191 | 61.8667 | 1
2015-09-14 20:15 | 2015-09-14 | 1 | 20 | 194 | 61.3667 | 1
2015-09-14 20:30 | 2015-09-14 | 1 | 20 | 188 | 60.8667 | 1
2015-09-14 20:45 | 2015-09-14 | 1 | 20 | 194 | 60.3667 | 1
2015-09-14 21:00 | 2015-09-14 | 1 | 21 | 203 | 60.0667 | 1
2015-09-14 21:15 | 2015-09-14 | 1 | 21 | 184 | 60.3167 | 1
2015-09-14 21:30 | 2015-09-14 | 1 | 21 | 184 | 60.5667 | 1
2015-09-14 21:45 | 2015-09-14 | 1 | 21 | 192 | 60.8167 | 1
2015-09-14 22:00 | 2015-09-14 | 1 | 22 | 186 | 61 | 1
2015-09-14 22:15 | 2015-09-14 | 1 | 22 | 190 | 61 | 1
2015-09-14 22:30 | 2015-09-14 | 1 | 22 | 186 | 61 | 1
2015-09-14 22:45 | 2015-09-14 | 1 | 22 | 201 | 61 | 1
2015-09-14 23:00 | 2015-09-14 | 1 | 23 | 184 | 60.8667 | 1
2015-09-14 23:15 | 2015-09-14 | 1 | 23 | 184 | 60.3667 | 1
2015-09-14 23:30 | 2015-09-14 | 1 | 23 | 171 | 59.8667 | 1
2015-09-14 23:45 | 2015-09-14 | 1 | 23 | 182 | 59.3667 | 1
2015-09-15 | 2015-09-15 | 2 | 0 | 175 | 59 | 1
2015-09-15 00:15 | 2015-09-15 | 2 | 0 | 164 | 59 | 1
2015-09-15 00:30 | 2015-09-15 | 2 | 0 | 164 | 59 | 1
2015-09-15 00:45 | 2015-09-15 | 2 | 0 | 177 | 59 | 1
2015-09-15 01:00 | 2015-09-15 | 2 | 1 | 170 | 58.9333 | 1
2015-09-15 01:15 | 2015-09-15 | 2 | 1 | 159 | 58.6833 | 1
2015-09-15 01:30 | 2015-09-15 | 2 | 1 | 166 | 58.4333 | 1
2015-09-15 01:45 | 2015-09-15 | 2 | 1 | 167 | 58.1833 | 1
2015-09-15 02:00 | 2015-09-15 | 2 | 2 | 171 | 57.8824 | 1
2015-09-15 02:15 | 2015-09-15 | 2 | 2 | 165 | 57.4412 | 1
2015-09-15 02:30 | 2015-09-15 | 2 | 2 | 161 | 57 | 1
2015-09-15 02:45 | 2015-09-15 | 2 | 2 | 153 | 57 | 1
2015-09-15 03:00 | 2015-09-15 | 2 | 3 | 165 | 57 | 1
2015-09-15 03:15 | 2015-09-15 | 2 | 3 | 172 | 57 | 1
2015-09-15 03:30 | 2015-09-15 | 2 | 3 | 152 | 57 | 1
2015-09-15 03:45 | 2015-09-15 | 2 | 3 | 160 | 57 | 1
2015-09-15 04:00 | 2015-09-15 | 2 | 4 | 154 | 57 | 1
2015-09-15 04:15 | 2015-09-15 | 2 | 4 | 165 | 57 | 1
2015-09-15 04:30 | 2015-09-15 | 2 | 4 | 166 | 57 | 1
2015-09-15 04:45 | 2015-09-15 | 2 | 4 | 156 | 57 | 1
2015-09-15 05:00 | 2015-09-15 | 2 | 5 | 154 | 57 | 1
2015-09-15 05:15 | 2015-09-15 | 2 | 5 | 157 | 57 | 1
2015-09-15 05:30 | 2015-09-15 | 2 | 5 | 160 | 57 | 1
2015-09-15 05:45 | 2015-09-15 | 2 | 5 | 157 | 57 | 1
2015-09-15 06:00 | 2015-09-15 | 2 | 6 | 151 | 58.0667 | 1
2015-09-15 06:15 | 2015-09-15 | 2 | 6 | 151 | 58.3167 | 1
2015-09-15 06:30 | 2015-09-15 | 2 | 6 | 156 | 58.5667 | 1
2015-09-15 06:45 | 2015-09-15 | 2 | 6 | 164 | 58.8167 | 1
2015-09-15 07:00 | 2015-09-15 | 2 | 7 | 145 | 59 | 1
2015-09-15 07:15 | 2015-09-15 | 2 | 7 | 149 | 59 | 1
2015-09-15 07:30 | 2015-09-15 | 2 | 7 | 140 | 59 | 1
2015-09-15 07:45 | 2015-09-15 | 2 | 7 | 160 | 59 | 1
2015-09-15 08:00 | 2015-09-15 | 2 | 8 | 166 | 59.2 | 1
2015-09-15 08:15 | 2015-09-15 | 2 | 8 | 158 | 59.95 | 1
2015-09-15 08:30 | 2015-09-15 | 2 | 8 | 158 | 60.7 | 1
2015-09-15 08:45 | 2015-09-15 | 2 | 8 | 160 | 61.45 | 1
2015-09-15 09:00 | 2015-09-15 | 2 | 9 | 189 | 62.2 | 1
2015-09-15 09:15 | 2015-09-15 | 2 | 9 | 178 | 62.95 | 1
2015-09-15 09:30 | 2015-09-15 | 2 | 9 | 180 | 63.7 | 1
2015-09-15 09:45 | 2015-09-15 | 2 | 9 | 180 | 64.45 | 1
2015-09-15 10:00 | 2015-09-15 | 2 | 10 | 189 | 64.9333 | 1
2015-09-15 10:15 | 2015-09-15 | 2 | 10 | 203 | 64.6833 | 1
2015-09-15 10:30 | 2015-09-15 | 2 | 10 | 189 | 64.4333 | 1
2015-09-15 10:45 | 2015-09-15 | 2 | 10 | 194 | 64.1833 | 1
2015-09-15 11:00 | 2015-09-15 | 2 | 11 | 194 | 64.0667 | 1
2015-09-15 11:15 | 2015-09-15 | 2 | 11 | 196 | 64.3167 | 1
2015-09-15 11:30 | 2015-09-15 | 2 | 11 | 204 | 64.5667 | 1
2015-09-15 11:45 | 2015-09-15 | 2 | 11 | 193 | 64.8167 | 1
2015-09-15 12:00 | 2015-09-15 | 2 | 12 | 184 | 65.1333 | 2
2015-09-15 12:15 | 2015-09-15 | 2 | 12 | 186 | 65.6333 | 2
2015-09-15 12:30 | 2015-09-15 | 2 | 12 | 208 | 66.1333 | 2
2015-09-15 12:45 | 2015-09-15 | 2 | 12 | 194 | 66.6333 | 2
2015-09-15 13:00 | 2015-09-15 | 2 | 13 | 191 | 67 | 2
2015-09-15 13:15 | 2015-09-15 | 2 | 13 | 202 | 67 | 2
2015-09-15 13:30 | 2015-09-15 | 2 | 13 | 187 | 67 | 2
2015-09-15 13:45 | 2015-09-15 | 2 | 13 | 210 | 67 | 2
2015-09-15 14:00 | 2015-09-15 | 2 | 14 | 201 | 66.8 | 2
2015-09-15 14:15 | 2015-09-15 | 2 | 14 | 207 | 66.05 | 2
2015-09-15 14:30 | 2015-09-15 | 2 | 14 | 194 | 65.3 | 2
2015-09-15 14:45 | 2015-09-15 | 2 | 14 | 215 | 64.55 | 1
2015-09-15 15:00 | 2015-09-15 | 2 | 15 | 210 | 63.9333 | 1
2015-09-15 15:15 | 2015-09-15 | 2 | 15 | 197 | 63.6833 | 1
2015-09-15 15:30 | 2015-09-15 | 2 | 15 | 210 | 63.4333 | 1
2015-09-15 15:45 | 2015-09-15 | 2 | 15 | 198 | 63.1833 | 1
2015-09-15 16:00 | 2015-09-15 | 2 | 16 | 212 | 62.8667 | 1
2015-09-15 16:15 | 2015-09-15 | 2 | 16 | 208 | 62.3667 | 1
2015-09-15 16:30 | 2015-09-15 | 2 | 16 | 196 | 61.8667 | 1
2015-09-15 16:45 | 2015-09-15 | 2 | 16 | 198 | 61.3667 | 1
2015-09-15 17:00 | 2015-09-15 | 2 | 17 | 221 | 61 | 1
2015-09-15 17:15 | 2015-09-15 | 2 | 17 | 195 | 61 | 1
2015-09-15 17:30 | 2015-09-15 | 2 | 17 | 203 | 61 | 1
2015-09-15 17:45 | 2015-09-15 | 2 | 17 | 195 | 61 | 1
2015-09-15 18:00 | 2015-09-15 | 2 | 18 | 186 | 60.9333 | 1
2015-09-15 18:15 | 2015-09-15 | 2 | 18 | 205 | 60.6833 | 1
2015-09-15 18:30 | 2015-09-15 | 2 | 18 | 191 | 60.4333 | 1
2015-09-15 18:45 | 2015-09-15 | 2 | 18 | 187 | 60.1833 | 1
2015-09-15 19:00 | 2015-09-15 | 2 | 19 | 178 | 59.9333 | 1
2015-09-15 19:15 | 2015-09-15 | 2 | 19 | 183 | 59.6833 | 1
2015-09-15 19:30 | 2015-09-15 | 2 | 19 | 178 | 59.4333 | 1
2015-09-15 19:45 | 2015-09-15 | 2 | 19 | 189 | 59.1833 | 1
2015-09-15 20:00 | 2015-09-15 | 2 | 20 | 189 | 59 | 1
2015-09-15 20:15 | 2015-09-15 | 2 | 20 | 174 | 59 | 1
2015-09-15 20:30 | 2015-09-15 | 2 | 20 | 181 | 59 | 1
2015-09-15 20:45 | 2015-09-15 | 2 | 20 | 171 | 59 | 1
2015-09-15 21:00 | 2015-09-15 | 2 | 21 | 180 | 59 | 1
2015-09-15 21:15 | 2015-09-15 | 2 | 21 | 165 | 59 | 1
2015-09-15 21:30 | 2015-09-15 | 2 | 21 | 178 | 59 | 1
2015-09-15 21:45 | 2015-09-15 | 2 | 21 | 166 | 59 | 1
2015-09-15 22:00 | 2015-09-15 | 2 | 22 | 164 | 59 | 1
2015-09-15 22:15 | 2015-09-15 | 2 | 22 | 165 | 59 | 1
2015-09-15 22:30 | 2015-09-15 | 2 | 22 | 161 | 59 | 1
2015-09-15 22:45 | 2015-09-15 | 2 | 22 | 163 | 59 | 1
2015-09-15 23:00 | 2015-09-15 | 2 | 23 | 160 | 59 | 1
2015-09-15 23:15 | 2015-09-15 | 2 | 23 | 161 | 59 | 1
2015-09-15 23:30 | 2015-09-15 | 2 | 23 | 150 | 59 | 1
2015-09-15 23:45 | 2015-09-15 | 2 | 23 | 150 | 59 | 1
2015-09-16 | 2015-09-16 | 3 | 0 | 141 | 59.0667 | 1
2015-09-16 00:15 | 2015-09-16 | 3 | 0 | 142 | 59.3167 | 1
2015-09-16 00:30 | 2015-09-16 | 3 | 0 | 136 | 59.5667 | 1
2015-09-16 00:45 | 2015-09-16 | 3 | 0 | 137 | 59.8167 | 1
2015-09-16 01:00 | 2015-09-16 | 3 | 1 | 139 | 59.7647 | 1
2015-09-16 01:15 | 2015-09-16 | 3 | 1 | 139 | 59 | 1
2015-09-16 01:30 | 2015-09-16 | 3 | 1 | 142 | 59 | 1
2015-09-16 01:45 | 2015-09-16 | 3 | 1 | 138 | 59 | 1
2015-09-16 02:00 | 2015-09-16 | 3 | 2 | 137 | 58.9333 | 1
2015-09-16 02:15 | 2015-09-16 | 3 | 2 | 143 | 58.6833 | 1
2015-09-16 02:30 | 2015-09-16 | 3 | 2 | 142 | 58.4333 | 1
2015-09-16 02:45 | 2015-09-16 | 3 | 2 | 145 | 58.1833 | 1
2015-09-16 03:00 | 2015-09-16 | 3 | 3 | 147 | 58.0667 | 1
2015-09-16 03:15 | 2015-09-16 | 3 | 3 | 137 | 58.3167 | 1
2015-09-16 03:30 | 2015-09-16 | 3 | 3 | 133 | 58.5667 | 1
2015-09-16 03:45 | 2015-09-16 | 3 | 3 | 130 | 58.8167 | 1
2015-09-16 04:00 | 2015-09-16 | 3 | 4 | 131 | 59 | 1
2015-09-16 04:15 | 2015-09-16 | 3 | 4 | 125 | 59 | 1
2015-09-16 04:30 | 2015-09-16 | 3 | 4 | 129 | 59 | 1
2015-09-16 04:45 | 2015-09-16 | 3 | 4 | 130 | 59 | 1
2015-09-16 05:00 | 2015-09-16 | 3 | 5 | 130 | 59 | 1
2015-09-16 05:15 | 2015-09-16 | 3 | 5 | 124 | 59 | 1
2015-09-16 05:30 | 2015-09-16 | 3 | 5 | 124 | 59 | 1
2015-09-16 05:45 | 2015-09-16 | 3 | 5 | 127 | 59 | 1
2015-09-16 06:00 | 2015-09-16 | 3 | 6 | 128 | 59 | 1
2015-09-16 06:15 | 2015-09-16 | 3 | 6 | 126 | 59 | 1
2015-09-16 06:30 | 2015-09-16 | 3 | 6 | 127 | 59 | 1
2015-09-16 06:45 | 2015-09-16 | 3 | 6 | 127 | 59 | 1
2015-09-16 07:00 | 2015-09-16 | 3 | 7 | 139 | 59.2667 | 1
2015-09-16 07:15 | 2015-09-16 | 3 | 7 | 126 | 60.2667 | 1
2015-09-16 07:30 | 2015-09-16 | 3 | 7 | 127 | 61.2667 | 1
2015-09-16 07:45 | 2015-09-16 | 3 | 7 | 137 | 62.2667 | 1
2015-09-16 08:00 | 2015-09-16 | 3 | 8 | 144 | 63.0667 | 1
2015-09-16 08:15 | 2015-09-16 | 3 | 8 | 153 | 63.3167 | 1
2015-09-16 08:30 | 2015-09-16 | 3 | 8 | 151 | 63.5667 | 1
2015-09-16 08:45 | 2015-09-16 | 3 | 8 | 173 | 63.8167 | 1
2015-09-16 09:00 | 2015-09-16 | 3 | 9 | 164 | 64.2 | 1
2015-09-16 09:15 | 2015-09-16 | 3 | 9 | 170 | 64.95 | 1
2015-09-16 09:30 | 2015-09-16 | 3 | 9 | 170 | 65.7 | 2
2015-09-16 09:45 | 2015-09-16 | 3 | 9 | 177 | 66.45 | 2
2015-09-16 10:00 | 2015-09-16 | 3 | 10 | 169 | 67.0667 | 2
2015-09-16 10:15 | 2015-09-16 | 3 | 10 | 196 | 67.3167 | 2
2015-09-16 10:30 | 2015-09-16 | 3 | 10 | 175 | 67.5667 | 2
2015-09-16 10:45 | 2015-09-16 | 3 | 10 | 184 | 67.8167 | 2
2015-09-16 11:00 | 2015-09-16 | 3 | 11 | 184 | 68.1333 | 2
2015-09-16 11:15 | 2015-09-16 | 3 | 11 | 186 | 68.6333 | 2
2015-09-16 11:30 | 2015-09-16 | 3 | 11 | 191 | 69.1333 | 2
2015-09-16 11:45 | 2015-09-16 | 3 | 11 | 185 | 69.6333 | 2
2015-09-16 12:00 | 2015-09-16 | 3 | 12 | 181 | 69.9333 | 2
2015-09-16 12:15 | 2015-09-16 | 3 | 12 | 189 | 69.6833 | 2
2015-09-16 12:30 | 2015-09-16 | 3 | 12 | 194 | 69.4333 | 2
2015-09-16 12:45 | 2015-09-16 | 3 | 12 | 182 | 69.1833 | 2
2015-09-16 13:00 | 2015-09-16 | 3 | 13 | 188 | 69 | 2
2015-09-16 13:15 | 2015-09-16 | 3 | 13 | 172 | 69 | 2
2015-09-16 13:30 | 2015-09-16 | 3 | 13 | 182 | 69 | 2
2015-09-16 13:45 | 2015-09-16 | 3 | 13 | 182 | 69 | 2
2015-09-16 14:00 | 2015-09-16 | 3 | 14 | 185 | 69 | 2
2015-09-16 14:15 | 2015-09-16 | 3 | 14 | 190 | 69 | 2
2015-09-16 14:30 | 2015-09-16 | 3 | 14 | 191 | 69 | 2
2015-09-16 14:45 | 2015-09-16 | 3 | 14 | 183 | 69 | 2
2015-09-16 15:00 | 2015-09-16 | 3 | 15 | 185 | 68.8667 | 2
2015-09-16 15:15 | 2015-09-16 | 3 | 15 | 202 | 68.3667 | 2
2015-09-16 15:30 | 2015-09-16 | 3 | 15 | 194 | 67.8667 | 2
2015-09-16 15:45 | 2015-09-16 | 3 | 15 | 196 | 67.3667 | 2
2015-09-16 16:00 | 2015-09-16 | 3 | 16 | 192 | 66.9333 | 2
2015-09-16 16:15 | 2015-09-16 | 3 | 16 | 206 | 66.6833 | 2
2015-09-16 16:30 | 2015-09-16 | 3 | 16 | 201 | 66.4333 | 2
2015-09-16 16:45 | 2015-09-16 | 3 | 16 | 190 | 66.1833 | 2
2015-09-16 17:00 | 2015-09-16 | 3 | 17 | 197 | 65.7333 | 2
2015-09-16 17:15 | 2015-09-16 | 3 | 17 | 180 | 64.7333 | 1
2015-09-16 17:30 | 2015-09-16 | 3 | 17 | 188 | 63.7333 | 1
2015-09-16 17:45 | 2015-09-16 | 3 | 17 | 205 | 62.7333 | 1
2015-09-16 18:00 | 2015-09-16 | 3 | 18 | 179 | 62.1333 | 1
2015-09-16 18:15 | 2015-09-16 | 3 | 18 | 193 | 62.6333 | 1
2015-09-16 18:30 | 2015-09-16 | 3 | 18 | 187 | 63.1333 | 1
2015-09-16 18:45 | 2015-09-16 | 3 | 18 | 181 | 63.6333 | 1
2015-09-16 19:00 | 2015-09-16 | 3 | 19 | 195 | 63.7778 | 1
2015-09-16 19:15 | 2015-09-16 | 3 | 19 | 179 | 63 | 1
2015-09-16 19:30 | 2015-09-16 | 3 | 19 | 180 | 63 | 1
2015-09-16 19:45 | 2015-09-16 | 3 | 19 | 176 | 63 | 1
2015-09-16 20:00 | 2015-09-16 | 3 | 20 | 184 | 63 | 1
2015-09-16 20:15 | 2015-09-16 | 3 | 20 | 192 | 63 | 1
2015-09-16 20:30 | 2015-09-16 | 3 | 20 | 177 | 63 | 1
2015-09-16 20:45 | 2015-09-16 | 3 | 20 | 173 | 63 | 1
2015-09-16 21:00 | 2015-09-16 | 3 | 21 | 184 | 63.069 | 1
2015-09-16 21:15 | 2015-09-16 | 3 | 21 | 180 | 63.3276 | 1
2015-09-16 21:30 | 2015-09-16 | 3 | 21 | 175 | 63.5862 | 1
2015-09-16 21:45 | 2015-09-16 | 3 | 21 | 175 | 63.8448 | 1
2015-09-16 22:00 | 2015-09-16 | 3 | 22 | 168 | 63.9333 | 1
2015-09-16 22:15 | 2015-09-16 | 3 | 22 | 176 | 63.6833 | 1
2015-09-16 22:30 | 2015-09-16 | 3 | 22 | 179 | 63.4333 | 1
2015-09-16 22:45 | 2015-09-16 | 3 | 22 | 178 | 63.1833 | 1
2015-09-16 23:00 | 2015-09-16 | 3 | 23 | 167 | 63 | 1
2015-09-16 23:15 | 2015-09-16 | 3 | 23 | 167 | 63 | 1
2015-09-16 23:30 | 2015-09-16 | 3 | 23 | 158 | 63 | 1
2015-09-16 23:45 | 2015-09-16 | 3 | 23 | 172 | 62.55 | 1
2015-09-17 | 2015-09-17 | 4 | 0 | 160 | 62 | 1
2015-09-17 00:15 | 2015-09-17 | 4 | 0 | 154 | 62 | 1
2015-09-17 00:30 | 2015-09-17 | 4 | 0 | 155 | 62 | 1
2015-09-17 00:45 | 2015-09-17 | 4 | 0 | 160 | 62 | 1
2015-09-17 01:00 | 2015-09-17 | 4 | 1 | 166 | 61.9111 | 1
2015-09-17 01:15 | 2015-09-17 | 4 | 1 | 154 | 61.5778 | 1
2015-09-17 01:30 | 2015-09-17 | 4 | 1 | 157 | 61.2444 | 1
2015-09-17 01:45 | 2015-09-17 | 4 | 1 | 153 | 60.7333 | 1
2015-09-17 02:00 | 2015-09-17 | 4 | 2 | 157 | 60.2222 | 1
2015-09-17 02:15 | 2015-09-17 | 4 | 2 | 169 | 60.9762 | 1
2015-09-17 02:30 | 2015-09-17 | 4 | 2 | 155 | 60.619 | 1
2015-09-17 02:45 | 2015-09-17 | 4 | 2 | 152 | 60.2619 | 1
2015-09-17 03:00 | 2015-09-17 | 4 | 3 | 159 | 60.1212 | 1
2015-09-17 03:15 | 2015-09-17 | 4 | 3 | 161 | 60.5758 | 1
2015-09-17 03:30 | 2015-09-17 | 4 | 3 | 158 | 61 | 1
2015-09-17 03:45 | 2015-09-17 | 4 | 3 | 150 | 61 | 1
2015-09-17 04:00 | 2015-09-17 | 4 | 4 | 150 | 60 | 1
2015-09-17 04:15 | 2015-09-17 | 4 | 4 | 146 | 60 | 1
2015-09-17 04:30 | 2015-09-17 | 4 | 4 | 160 | 60 | 1
2015-09-17 04:45 | 2015-09-17 | 4 | 4 | 157 | 60 | 1
2015-09-17 05:00 | 2015-09-17 | 4 | 5 | 145 | 59.931 | 1
2015-09-17 05:15 | 2015-09-17 | 4 | 5 | 148 | 59.6724 | 1
2015-09-17 05:30 | 2015-09-17 | 4 | 5 | 146 | 59.4138 | 1
2015-09-17 05:45 | 2015-09-17 | 4 | 5 | 159 | 59.1552 | 1
2015-09-17 06:00 | 2015-09-17 | 4 | 6 | 149 | 59 | 1
2015-09-17 06:15 | 2015-09-17 | 4 | 6 | 147 | 59 | 1
2015-09-17 06:30 | 2015-09-17 | 4 | 6 | 144 | 59 | 1
2015-09-17 06:45 | 2015-09-17 | 4 | 6 | 150 | 59 | 1
2015-09-17 07:00 | 2015-09-17 | 4 | 7 | 165 | 59.1379 | 1
2015-09-17 07:15 | 2015-09-17 | 4 | 7 | 151 | 59.6552 | 1
2015-09-17 07:30 | 2015-09-17 | 4 | 7 | 146 | 60.1724 | 1
2015-09-17 07:45 | 2015-09-17 | 4 | 7 | 145 | 60.6897 | 1
2015-09-17 08:00 | 2015-09-17 | 4 | 8 | 152 | 61.8 | 1
2015-09-17 08:15 | 2015-09-17 | 4 | 8 | 187 | 62.82 | 1
2015-09-17 08:30 | 2015-09-17 | 4 | 8 | 161 | 62.52 | 1
2015-09-17 08:45 | 2015-09-17 | 4 | 8 | 167 | 62.22 | 1
2015-09-17 09:00 | 2015-09-17 | 4 | 9 | 168 | 62.0667 | 1
2015-09-17 09:15 | 2015-09-17 | 4 | 9 | 174 | 62.3167 | 1
2015-09-17 09:30 | 2015-09-17 | 4 | 9 | 184 | 62.5667 | 1
2015-09-17 09:45 | 2015-09-17 | 4 | 9 | 173 | 62.8167 | 1
2015-09-17 10:00 | 2015-09-17 | 4 | 10 | 179 | 63.069 | 1
2015-09-17 10:15 | 2015-09-17 | 4 | 10 | 181 | 63.3276 | 1
2015-09-17 10:30 | 2015-09-17 | 4 | 10 | 200 | 63.5862 | 1
2015-09-17 10:45 | 2015-09-17 | 4 | 10 | 194 | 63.8448 | 1
2015-09-17 11:00 | 2015-09-17 | 4 | 11 | 184 | 66 | 2
2015-09-17 11:15 | 2015-09-17 | 4 | 11 | 183 | 66 | 2
2015-09-17 11:30 | 2015-09-17 | 4 | 11 | 184 | 66 | 2
2015-09-17 11:45 | 2015-09-17 | 4 | 11 | 203 | 66 | 2
2015-09-17 12:00 | 2015-09-17 | 4 | 12 | 189 | 66.2 | 2
2015-09-17 12:15 | 2015-09-17 | 4 | 12 | 181 | 66.95 | 2
2015-09-17 12:30 | 2015-09-17 | 4 | 12 | 181 | 67.7 | 2
2015-09-17 12:45 | 2015-09-17 | 4 | 12 | 183 | 68.45 | 2
2015-09-17 13:00 | 2015-09-17 | 4 | 13 | 200 | 68.9333 | 2
2015-09-17 13:15 | 2015-09-17 | 4 | 13 | 188 | 68.6833 | 2
2015-09-17 13:30 | 2015-09-17 | 4 | 13 | 189 | 68.4333 | 2
2015-09-17 13:45 | 2015-09-17 | 4 | 13 | 183 | 68.1833 | 2
2015-09-17 14:00 | 2015-09-17 | 4 | 14 | 189 | 68 | 2
2015-09-17 14:15 | 2015-09-17 | 4 | 14 | 203 | 68 | 2
2015-09-17 14:30 | 2015-09-17 | 4 | 14 | 192 | 68 | 2
2015-09-17 14:45 | 2015-09-17 | 4 | 14 | 194 | 68 | 2
2015-09-17 15:00 | 2015-09-17 | 4 | 15 | 202 | 67.7333 | 2
2015-09-17 15:15 | 2015-09-17 | 4 | 15 | 214 | 66.7333 | 2
2015-09-17 15:30 | 2015-09-17 | 4 | 15 | 202 | 65.7333 | 2
2015-09-17 15:45 | 2015-09-17 | 4 | 15 | 207 | 64.7333 | 1
2015-09-17 16:00 | 2015-09-17 | 4 | 16 | 194 | 63.9333 | 1
2015-09-17 16:15 | 2015-09-17 | 4 | 16 | 205 | 63.6833 | 1
2015-09-17 16:30 | 2015-09-17 | 4 | 16 | 215 | 63.4333 | 1
2015-09-17 16:45 | 2015-09-17 | 4 | 16 | 189 | 63.1833 | 1
2015-09-17 17:00 | 2015-09-17 | 4 | 17 | 205 | 62.8 | 1
2015-09-17 17:15 | 2015-09-17 | 4 | 17 | 199 | 62.05 | 1
2015-09-17 17:30 | 2015-09-17 | 4 | 17 | 204 | 61.3 | 1
2015-09-17 17:45 | 2015-09-17 | 4 | 17 | 212 | 60.55 | 1
2015-09-17 18:00 | 2015-09-17 | 4 | 18 | 187 | 60 | 1
2015-09-17 18:15 | 2015-09-17 | 4 | 18 | 196 | 60 | 1
2015-09-17 18:30 | 2015-09-17 | 4 | 18 | 191 | 60 | 1
2015-09-17 18:45 | 2015-09-17 | 4 | 18 | 203 | 60 | 1
2015-09-17 19:00 | 2015-09-17 | 4 | 19 | 195 | 60 | 1
2015-09-17 19:15 | 2015-09-17 | 4 | 19 | 182 | 60 | 1
2015-09-17 19:30 | 2015-09-17 | 4 | 19 | 194 | 60 | 1
2015-09-17 19:45 | 2015-09-17 | 4 | 19 | 200 | 60 | 1
2015-09-17 20:00 | 2015-09-17 | 4 | 20 | 179 | 60 | 1
2015-09-17 20:15 | 2015-09-17 | 4 | 20 | 182 | 60 | 1
2015-09-17 20:30 | 2015-09-17 | 4 | 20 | 185 | 60 | 1
2015-09-17 20:45 | 2015-09-17 | 4 | 20 | 180 | 60 | 1
2015-09-17 21:00 | 2015-09-17 | 4 | 21 | 195 | 60 | 1
2015-09-17 21:15 | 2015-09-17 | 4 | 21 | 179 | 60 | 1
2015-09-17 21:30 | 2015-09-17 | 4 | 21 | 167 | 60 | 1
2015-09-17 21:45 | 2015-09-17 | 4 | 21 | 171 | 60 | 1
2015-09-17 22:00 | 2015-09-17 | 4 | 22 | 185 | 59.9333 | 1
2015-09-17 22:15 | 2015-09-17 | 4 | 22 | 176 | 59.6833 | 1
2015-09-17 22:30 | 2015-09-17 | 4 | 22 | 165 | 59.4333 | 1
2015-09-17 22:45 | 2015-09-17 | 4 | 22 | 166 | 59.1833 | 1
2015-09-17 23:00 | 2015-09-17 | 4 | 23 | 168 | 58.9333 | 1
2015-09-17 23:15 | 2015-09-17 | 4 | 23 | 175 | 58.6833 | 1
2015-09-17 23:30 | 2015-09-17 | 4 | 23 | 157 | 58.4333 | 1
2015-09-17 23:45 | 2015-09-17 | 4 | 23 | 154 | 58.1833 | 1
2015-09-18 | 2015-09-18 | 5 | 0 | 145 | 58.0667 | 1
2015-09-18 00:15 | 2015-09-18 | 5 | 0 | 149 | 58.3167 | 1
2015-09-18 00:30 | 2015-09-18 | 5 | 0 | 169 | 58.5667 | 1
2015-09-18 00:45 | 2015-09-18 | 5 | 0 | 148 | 58.8167 | 1
2015-09-18 01:00 | 2015-09-18 | 5 | 1 | 152 | 58.9333 | 1
2015-09-18 01:15 | 2015-09-18 | 5 | 1 | 154 | 58.6833 | 1
2015-09-18 01:30 | 2015-09-18 | 5 | 1 | 153 | 58.4333 | 1
2015-09-18 01:45 | 2015-09-18 | 5 | 1 | 164 | 58.1833 | 1
2015-09-18 02:00 | 2015-09-18 | 5 | 2 | 145 | 58 | 1
2015-09-18 02:15 | 2015-09-18 | 5 | 2 | 145 | 58 | 1
2015-09-18 02:30 | 2015-09-18 | 5 | 2 | 144 | 58 | 1
2015-09-18 02:45 | 2015-09-18 | 5 | 2 | 145 | 58 | 1
2015-09-18 03:00 | 2015-09-18 | 5 | 3 | 159 | 57.9333 | 1
2015-09-18 03:15 | 2015-09-18 | 5 | 3 | 141 | 57.6833 | 1
2015-09-18 03:30 | 2015-09-18 | 5 | 3 | 145 | 57.4333 | 1
2015-09-18 03:45 | 2015-09-18 | 5 | 3 | 140 | 57.1833 | 1
2015-09-18 04:00 | 2015-09-18 | 5 | 4 | 143 | 57 | 1
2015-09-18 04:15 | 2015-09-18 | 5 | 4 | 158 | 57 | 1
2015-09-18 04:30 | 2015-09-18 | 5 | 4 | 139 | 57 | 1
2015-09-18 04:45 | 2015-09-18 | 5 | 4 | 144 | 57 | 1
2015-09-18 05:00 | 2015-09-18 | 5 | 5 | 133 | 57.0667 | 1
2015-09-18 05:15 | 2015-09-18 | 5 | 5 | 144 | 57.3167 | 1
2015-09-18 05:30 | 2015-09-18 | 5 | 5 | 148 | 57.5667 | 1
2015-09-18 05:45 | 2015-09-18 | 5 | 5 | 143 | 57.8167 | 1
2015-09-18 06:00 | 2015-09-18 | 5 | 6 | 142 | 58.2 | 1
2015-09-18 06:15 | 2015-09-18 | 5 | 6 | 149 | 58.95 | 1
2015-09-18 06:30 | 2015-09-18 | 5 | 6 | 145 | 59.7 | 1
2015-09-18 06:45 | 2015-09-18 | 5 | 6 | 170 | 60.45 | 1
2015-09-18 07:00 | 2015-09-18 | 5 | 7 | 145 | 61.1333 | 1
2015-09-18 07:15 | 2015-09-18 | 5 | 7 | 152 | 61.6333 | 1
2015-09-18 07:30 | 2015-09-18 | 5 | 7 | 137 | 62.1333 | 1
2015-09-18 07:45 | 2015-09-18 | 5 | 7 | 148 | 62.6333 | 1
2015-09-18 08:00 | 2015-09-18 | 5 | 8 | 159 | 63.1333 | 1
2015-09-18 08:15 | 2015-09-18 | 5 | 8 | 174 | 63.6333 | 1
2015-09-18 08:30 | 2015-09-18 | 5 | 8 | 165 | 64.1333 | 1
2015-09-18 08:45 | 2015-09-18 | 5 | 8 | 172 | 64.6333 | 1
2015-09-18 09:00 | 2015-09-18 | 5 | 9 | 173 | 65.2 | 2
2015-09-18 09:15 | 2015-09-18 | 5 | 9 | 185 | 65.95 | 2
2015-09-18 09:30 | 2015-09-18 | 5 | 9 | 173 | 66.7 | 2
2015-09-18 09:45 | 2015-09-18 | 5 | 9 | 176 | 67.45 | 2
2015-09-18 10:00 | 2015-09-18 | 5 | 10 | 174 | 68.1333 | 2
2015-09-18 10:15 | 2015-09-18 | 5 | 10 | 175 | 68.6333 | 2
2015-09-18 10:30 | 2015-09-18 | 5 | 10 | 199 | 69.1333 | 2
2015-09-18 10:45 | 2015-09-18 | 5 | 10 | 185 | 69.6333 | 2
2015-09-18 11:00 | 2015-09-18 | 5 | 11 | 186 | 70.2 | 3
2015-09-18 11:15 | 2015-09-18 | 5 | 11 | 190 | 70.95 | 3
2015-09-18 11:30 | 2015-09-18 | 5 | 11 | 207 | 71.7 | 3
2015-09-18 11:45 | 2015-09-18 | 5 | 11 | 201 | 72.45 | 3
2015-09-18 12:00 | 2015-09-18 | 5 | 12 | 198 | 73.3333 | 3
2015-09-18 12:15 | 2015-09-18 | 5 | 12 | 201 | 74.5833 | 3
2015-09-18 12:30 | 2015-09-18 | 5 | 12 | 205 | 75.8333 | 4
2015-09-18 12:45 | 2015-09-18 | 5 | 12 | 214 | 77.0833 | 4
2015-09-18 13:00 | 2015-09-18 | 5 | 13 | 206 | 77.6667 | 4
2015-09-18 13:15 | 2015-09-18 | 5 | 13 | 201 | 76.4167 | 4
2015-09-18 13:30 | 2015-09-18 | 5 | 13 | 198 | 75.1667 | 4
2015-09-18 13:45 | 2015-09-18 | 5 | 13 | 201 | 73.9167 | 3
2015-09-18 14:00 | 2015-09-18 | 5 | 14 | 216 | 73 | 3
2015-09-18 14:15 | 2015-09-18 | 5 | 14 | 208 | 73 | 3
2015-09-18 14:30 | 2015-09-18 | 5 | 14 | 205 | 73 | 3
2015-09-18 14:45 | 2015-09-18 | 5 | 14 | 212 | 73 | 3
2015-09-18 15:00 | 2015-09-18 | 5 | 15 | 243 | 72.8667 | 3
2015-09-18 15:15 | 2015-09-18 | 5 | 15 | 223 | 72.3667 | 3
2015-09-18 15:30 | 2015-09-18 | 5 | 15 | 227 | 71.8667 | 3
2015-09-18 15:45 | 2015-09-18 | 5 | 15 | 218 | 71.3667 | 3
2015-09-18 16:00 | 2015-09-18 | 5 | 16 | 212 | 70.8667 | 3
2015-09-18 16:15 | 2015-09-18 | 5 | 16 | 231 | 70.3667 | 3
2015-09-18 16:30 | 2015-09-18 | 5 | 16 | 225 | 69.8667 | 2
2015-09-18 16:45 | 2015-09-18 | 5 | 16 | 215 | 69.3667 | 2
2015-09-18 17:00 | 2015-09-18 | 5 | 17 | 212 | 68.6 | 2
2015-09-18 17:15 | 2015-09-18 | 5 | 17 | 209 | 67.1 | 2
2015-09-18 17:30 | 2015-09-18 | 5 | 17 | 220 | 65.6 | 2
2015-09-18 17:45 | 2015-09-18 | 5 | 17 | 224 | 64.1 | 1
2015-09-18 18:00 | 2015-09-18 | 5 | 18 | 209 | 62.9333 | 1
2015-09-18 18:15 | 2015-09-18 | 5 | 18 | 204 | 62.6833 | 1
2015-09-18 18:30 | 2015-09-18 | 5 | 18 | 217 | 62.4333 | 1
2015-09-18 18:45 | 2015-09-18 | 5 | 18 | 215 | 62.1833 | 1
2015-09-18 19:00 | 2015-09-18 | 5 | 19 | 199 | 61.9333 | 1
2015-09-18 19:15 | 2015-09-18 | 5 | 19 | 196 | 61.6833 | 1
2015-09-18 19:30 | 2015-09-18 | 5 | 19 | 193 | 61.4333 | 1
2015-09-18 19:45 | 2015-09-18 | 5 | 19 | 208 | 61.1833 | 1
2015-09-18 20:00 | 2015-09-18 | 5 | 20 | 194 | 60.9333 | 1
2015-09-18 20:15 | 2015-09-18 | 5 | 20 | 188 | 60.6833 | 1
2015-09-18 20:30 | 2015-09-18 | 5 | 20 | 190 | 60.4333 | 1
2015-09-18 20:45 | 2015-09-18 | 5 | 20 | 190 | 60.1833 | 1
2015-09-18 21:00 | 2015-09-18 | 5 | 21 | 199 | 60 | 1
2015-09-18 21:15 | 2015-09-18 | 5 | 21 | 185 | 60 | 1
2015-09-18 21:30 | 2015-09-18 | 5 | 21 | 169 | 60 | 1
2015-09-18 21:45 | 2015-09-18 | 5 | 21 | 163 | 60 | 1
2015-09-18 22:00 | 2015-09-18 | 5 | 22 | 175 | 59.9333 | 1
2015-09-18 22:15 | 2015-09-18 | 5 | 22 | 180 | 59.6833 | 1
2015-09-18 22:30 | 2015-09-18 | 5 | 22 | 159 | 59.4333 | 1
2015-09-18 22:45 | 2015-09-18 | 5 | 22 | 162 | 59.1833 | 1
2015-09-18 23:00 | 2015-09-18 | 5 | 23 | 163 | 58.9333 | 1
2015-09-18 23:15 | 2015-09-18 | 5 | 23 | 170 | 58.6833 | 1
2015-09-18 23:30 | 2015-09-18 | 5 | 23 | 165 | 58.4333 | 1
2015-09-18 23:45 | 2015-09-18 | 5 | 23 | 158 | 58.1833 | 1
2015-09-19 | 2015-09-19 | 6 | 0 | 161 | 58 | 1
2015-09-19 00:15 | 2015-09-19 | 6 | 0 | 155 | 58 | 1
2015-09-19 00:30 | 2015-09-19 | 6 | 0 | 174 | 58 | 1
2015-09-19 00:45 | 2015-09-19 | 6 | 0 | 155 | 58 | 1
2015-09-19 01:00 | 2015-09-19 | 6 | 1 | 152 | 57.9333 | 1
2015-09-19 01:15 | 2015-09-19 | 6 | 1 | 146 | 57.6833 | 1
2015-09-19 01:30 | 2015-09-19 | 6 | 1 | 159 | 57.4333 | 1
2015-09-19 01:45 | 2015-09-19 | 6 | 1 | 154 | 57.1833 | 1
2015-09-19 02:00 | 2015-09-19 | 6 | 2 | 143 | 56.9333 | 1
2015-09-19 02:15 | 2015-09-19 | 6 | 2 | 146 | 56.6833 | 1
2015-09-19 02:30 | 2015-09-19 | 6 | 2 | 135 | 56.4333 | 1
2015-09-19 02:45 | 2015-09-19 | 6 | 2 | 153 | 56.1833 | 1
2015-09-19 03:00 | 2015-09-19 | 6 | 3 | 142 | 56 | 1
2015-09-19 03:15 | 2015-09-19 | 6 | 3 | 139 | 56 | 1
2015-09-19 03:30 | 2015-09-19 | 6 | 3 | 138 | 56 | 1
2015-09-19 03:45 | 2015-09-19 | 6 | 3 | 131 | 56 | 1
2015-09-19 04:00 | 2015-09-19 | 6 | 4 | 143 | 56 | 1
2015-09-19 04:15 | 2015-09-19 | 6 | 4 | 136 | 56 | 1
2015-09-19 04:30 | 2015-09-19 | 6 | 4 | 135 | 56 | 1
2015-09-19 04:45 | 2015-09-19 | 6 | 4 | 128 | 56 | 1
2015-09-19 05:00 | 2015-09-19 | 6 | 5 | 136 | 56 | 1
2015-09-19 05:15 | 2015-09-19 | 6 | 5 | 135 | 56 | 1
2015-09-19 05:30 | 2015-09-19 | 6 | 5 | 137 | 56 | 1
2015-09-19 05:45 | 2015-09-19 | 6 | 5 | 142 | 56 | 1
2015-09-19 06:00 | 2015-09-19 | 6 | 6 | 130 | 56.3333 | 1
2015-09-19 06:15 | 2015-09-19 | 6 | 6 | 128 | 57.5833 | 1
2015-09-19 06:30 | 2015-09-19 | 6 | 6 | 131 | 58.8333 | 1
2015-09-19 06:45 | 2015-09-19 | 6 | 6 | 139 | 60.0833 | 1
2015-09-19 07:00 | 2015-09-19 | 6 | 7 | 140 | 61.2667 | 1
2015-09-19 07:15 | 2015-09-19 | 6 | 7 | 137 | 62.2667 | 1
2015-09-19 07:30 | 2015-09-19 | 6 | 7 | 129 | 63.2667 | 1
2015-09-19 07:45 | 2015-09-19 | 6 | 7 | 132 | 64.2667 | 1
2015-09-19 08:00 | 2015-09-19 | 6 | 8 | 127 | 65.1333 | 2
2015-09-19 08:15 | 2015-09-19 | 6 | 8 | 136 | 65.6333 | 2
2015-09-19 08:30 | 2015-09-19 | 6 | 8 | 134 | 66.1333 | 2
2015-09-19 08:45 | 2015-09-19 | 6 | 8 | 154 | 66.6333 | 2
2015-09-19 09:00 | 2015-09-19 | 6 | 9 | 141 | 67.1333 | 2
2015-09-19 09:15 | 2015-09-19 | 6 | 9 | 148 | 67.6333 | 2
2015-09-19 09:30 | 2015-09-19 | 6 | 9 | 141 | 68.1333 | 2
2015-09-19 09:45 | 2015-09-19 | 6 | 9 | 151 | 68.6333 | 2
2015-09-19 10:00 | 2015-09-19 | 6 | 10 | 148 | 69.1333 | 2
2015-09-19 10:15 | 2015-09-19 | 6 | 10 | 146 | 69.6333 | 2
2015-09-19 10:30 | 2015-09-19 | 6 | 10 | 152 | 70.1333 | 3
2015-09-19 10:45 | 2015-09-19 | 6 | 10 | 158 | 70.6333 | 3
2015-09-19 11:00 | 2015-09-19 | 6 | 11 | 163 | 71.2 | 3
2015-09-19 11:15 | 2015-09-19 | 6 | 11 | 157 | 71.95 | 3
2015-09-19 11:30 | 2015-09-19 | 6 | 11 | 163 | 72.7 | 3
2015-09-19 11:45 | 2015-09-19 | 6 | 11 | 152 | 73.45 | 3
2015-09-19 12:00 | 2015-09-19 | 6 | 12 | 156 | 74.1333 | 3
2015-09-19 12:15 | 2015-09-19 | 6 | 12 | 176 | 74.6333 | 3
2015-09-19 12:30 | 2015-09-19 | 6 | 12 | 167 | 75.1333 | 4
2015-09-19 12:45 | 2015-09-19 | 6 | 12 | 172 | 75.6333 | 4
2015-09-19 13:00 | 2015-09-19 | 6 | 13 | 168 | 76.5333 | 4
2015-09-19 13:15 | 2015-09-19 | 6 | 13 | 170 | 78.5333 | 4
2015-09-19 13:30 | 2015-09-19 | 6 | 13 | 174 | 80.5333 | 5
2015-09-19 13:45 | 2015-09-19 | 6 | 13 | 182 | 82.5333 | 5
2015-09-19 14:00 | 2015-09-19 | 6 | 14 | 173 | 83.9333 | 5
2015-09-19 14:15 | 2015-09-19 | 6 | 14 | 174 | 83.6833 | 5
2015-09-19 14:30 | 2015-09-19 | 6 | 14 | 184 | 83.4333 | 5
2015-09-19 14:45 | 2015-09-19 | 6 | 14 | 182 | 83.1833 | 5
2015-09-19 15:00 | 2015-09-19 | 6 | 15 | 190 | 82.9333 | 5
2015-09-19 15:15 | 2015-09-19 | 6 | 15 | 197 | 82.6833 | 5
2015-09-19 15:30 | 2015-09-19 | 6 | 15 | 190 | 82.4333 | 5
2015-09-19 15:45 | 2015-09-19 | 6 | 15 | 193 | 82.1833 | 5
2015-09-19 16:00 | 2015-09-19 | 6 | 16 | 190 | 81.9333 | 5
2015-09-19 16:15 | 2015-09-19 | 6 | 16 | 225 | 81.6833 | 5
2015-09-19 16:30 | 2015-09-19 | 6 | 16 | 186 | 81.4333 | 5
2015-09-19 16:45 | 2015-09-19 | 6 | 16 | 201 | 81.1833 | 5
2015-09-19 17:00 | 2015-09-19 | 6 | 17 | 201 | 80.8 | 5
2015-09-19 17:15 | 2015-09-19 | 6 | 17 | 201 | 80.05 | 5
2015-09-19 17:30 | 2015-09-19 | 6 | 17 | 204 | 79.3 | 4
2015-09-19 17:45 | 2015-09-19 | 6 | 17 | 203 | 78.55 | 4
2015-09-19 18:00 | 2015-09-19 | 6 | 18 | 190 | 77.6667 | 4
2015-09-19 18:15 | 2015-09-19 | 6 | 18 | 197 | 76.4167 | 4
2015-09-19 18:30 | 2015-09-19 | 6 | 18 | 204 | 75.1667 | 4
2015-09-19 18:45 | 2015-09-19 | 6 | 18 | 190 | 73.9167 | 3
2015-09-19 19:00 | 2015-09-19 | 6 | 19 | 194 | 72.8667 | 3
2015-09-19 19:15 | 2015-09-19 | 6 | 19 | 168 | 72.3667 | 3
2015-09-19 19:30 | 2015-09-19 | 6 | 19 | 176 | 71.8667 | 3
2015-09-19 19:45 | 2015-09-19 | 6 | 19 | 191 | 71.3667 | 3
2015-09-19 20:00 | 2015-09-19 | 6 | 20 | 163 | 71 | 3
2015-09-19 20:15 | 2015-09-19 | 6 | 20 | 175 | 71 | 3
2015-09-19 20:30 | 2015-09-19 | 6 | 20 | 163 | 71 | 3
2015-09-19 20:45 | 2015-09-19 | 6 | 20 | 163 | 71 | 3
2015-09-19 21:00 | 2015-09-19 | 6 | 21 | 175 | 70.9333 | 3
2015-09-19 21:15 | 2015-09-19 | 6 | 21 | 160 | 70.6833 | 3
2015-09-19 21:30 | 2015-09-19 | 6 | 21 | 158 | 70.4333 | 3
2015-09-19 21:45 | 2015-09-19 | 6 | 21 | 158 | 70.1833 | 3
2015-09-19 22:00 | 2015-09-19 | 6 | 22 | 155 | 70 | 2
2015-09-19 22:15 | 2015-09-19 | 6 | 22 | 171 | 70 | 2
2015-09-19 22:30 | 2015-09-19 | 6 | 22 | 152 | 70 | 2
2015-09-19 22:45 | 2015-09-19 | 6 | 22 | 160 | 70 | 2
2015-09-19 23:00 | 2015-09-19 | 6 | 23 | 152 | 69.8 | 2
2015-09-19 23:15 | 2015-09-19 | 6 | 23 | 150 | 69.05 | 2
2015-09-19 23:30 | 2015-09-19 | 6 | 23 | 154 | 68.3 | 2
2015-09-19 23:45 | 2015-09-19 | 6 | 23 | 156 | 67.55 | 2
2015-09-20 | 2015-09-20 | 7 | 0 | 147 | 66.8667 | 2
2015-09-20 00:15 | 2015-09-20 | 7 | 0 | 155 | 66.3667 | 2
2015-09-20 00:30 | 2015-09-20 | 7 | 0 | 154 | 65.8667 | 2
2015-09-20 00:45 | 2015-09-20 | 7 | 0 | 149 | 65.3667 | 2
2015-09-20 01:00 | 2015-09-20 | 7 | 1 | 159 | 64.9333 | 1
2015-09-20 01:15 | 2015-09-20 | 7 | 1 | 154 | 64.6833 | 1
2015-09-20 01:30 | 2015-09-20 | 7 | 1 | 153 | 64.4333 | 1
2015-09-20 01:45 | 2015-09-20 | 7 | 1 | 142 | 64.1833 | 1
2015-09-20 02:00 | 2015-09-20 | 7 | 2 | 150 | 64 | 1
2015-09-20 02:15 | 2015-09-20 | 7 | 2 | 141 | 64 | 1
2015-09-20 02:30 | 2015-09-20 | 7 | 2 | 155 | 64 | 1
2015-09-20 02:45 | 2015-09-20 | 7 | 2 | 139 | 64 | 1
2015-09-20 03:00 | 2015-09-20 | 7 | 3 | 150 | 63.8667 | 1
2015-09-20 03:15 | 2015-09-20 | 7 | 3 | 137 | 63.3667 | 1
2015-09-20 03:30 | 2015-09-20 | 7 | 3 | 147 | 62.8667 | 1
2015-09-20 03:45 | 2015-09-20 | 7 | 3 | 140 | 62.3667 | 1
2015-09-20 04:00 | 2015-09-20 | 7 | 4 | 144 | 61.9333 | 1
2015-09-20 04:15 | 2015-09-20 | 7 | 4 | 143 | 61.6833 | 1
2015-09-20 04:30 | 2015-09-20 | 7 | 4 | 145 | 61.4333 | 1
2015-09-20 04:45 | 2015-09-20 | 7 | 4 | 140 | 61.1833 | 1
2015-09-20 05:00 | 2015-09-20 | 7 | 5 | 135 | 61.1333 | 1
2015-09-20 05:15 | 2015-09-20 | 7 | 5 | 146 | 61.6333 | 1
2015-09-20 05:30 | 2015-09-20 | 7 | 5 | 136 | 62.1333 | 1
2015-09-20 05:45 | 2015-09-20 | 7 | 5 | 148 | 62.6333 | 1
2015-09-20 06:00 | 2015-09-20 | 7 | 6 | 130 | 63.1333 | 1
2015-09-20 06:15 | 2015-09-20 | 7 | 6 | 152 | 63.6333 | 1
2015-09-20 06:30 | 2015-09-20 | 7 | 6 | 139 | 64.1333 | 1
2015-09-20 06:45 | 2015-09-20 | 7 | 6 | 144 | 64.6333 | 1
2015-09-20 07:00 | 2015-09-20 | 7 | 7 | 143 | 65.2667 | 2
2015-09-20 07:15 | 2015-09-20 | 7 | 7 | 138 | 66.2667 | 2
2015-09-20 07:30 | 2015-09-20 | 7 | 7 | 145 | 67.2667 | 2
2015-09-20 07:45 | 2015-09-20 | 7 | 7 | 139 | 68.2667 | 2
2015-09-20 08:00 | 2015-09-20 | 7 | 8 | 146 | 69.1333 | 2
2015-09-20 08:15 | 2015-09-20 | 7 | 8 | 138 | 69.6333 | 2
2015-09-20 08:30 | 2015-09-20 | 7 | 8 | 142 | 70.1333 | 3
2015-09-20 08:45 | 2015-09-20 | 7 | 8 | 146 | 70.6333 | 3
2015-09-20 09:00 | 2015-09-20 | 7 | 9 | 147 | 71.1333 | 3
2015-09-20 09:15 | 2015-09-20 | 7 | 9 | 151 | 71.6333 | 3
2015-09-20 09:30 | 2015-09-20 | 7 | 9 | 153 | 72.1333 | 3
2015-09-20 09:45 | 2015-09-20 | 7 | 9 | 149 | 72.6333 | 3
2015-09-20 10:00 | 2015-09-20 | 7 | 10 | 161 | 73.2 | 3
2015-09-20 10:15 | 2015-09-20 | 7 | 10 | 153 | 73.95 | 3
2015-09-20 10:30 | 2015-09-20 | 7 | 10 | 155 | 74.7 | 3
2015-09-20 10:45 | 2015-09-20 | 7 | 10 | 166 | 75.45 | 4
2015-09-20 11:00 | 2015-09-20 | 7 | 11 | 158 | 76.0667 | 4
2015-09-20 11:15 | 2015-09-20 | 7 | 11 | 168 | 76.3167 | 4
2015-09-20 11:30 | 2015-09-20 | 7 | 11 | 169 | 76.5667 | 4
2015-09-20 11:45 | 2015-09-20 | 7 | 11 | 169 | 76.8167 | 4
2015-09-20 12:00 | 2015-09-20 | 7 | 12 | 179 | 77.1333 | 4
2015-09-20 12:15 | 2015-09-20 | 7 | 12 | 170 | 77.6333 | 4
2015-09-20 12:30 | 2015-09-20 | 7 | 12 | 185 | 78.1333 | 4
2015-09-20 12:45 | 2015-09-20 | 7 | 12 | 193 | 78.6333 | 4
2015-09-20 13:00 | 2015-09-20 | 7 | 13 | 181 | 79.3333 | 4
2015-09-20 13:15 | 2015-09-20 | 7 | 13 | 209 | 80.5833 | 5
2015-09-20 13:30 | 2015-09-20 | 7 | 13 | 193 | 81.8333 | 5
2015-09-20 13:45 | 2015-09-20 | 7 | 13 | 205 | 83.0833 | 5
2015-09-20 14:00 | 2015-09-20 | 7 | 14 | 192 | 84.3333 | 5
2015-09-20 14:15 | 2015-09-20 | 7 | 14 | 205 | 85.5833 | 6
2015-09-20 14:30 | 2015-09-20 | 7 | 14 | 205 | 86.8333 | 6
2015-09-20 14:45 | 2015-09-20 | 7 | 14 | 210 | 88.0833 | 6
2015-09-20 15:00 | 2015-09-20 | 7 | 15 | 219 | 89 | 6
2015-09-20 15:15 | 2015-09-20 | 7 | 15 | 214 | 89 | 6
2015-09-20 15:30 | 2015-09-20 | 7 | 15 | 222 | 89 | 6
2015-09-20 15:45 | 2015-09-20 | 7 | 15 | 212 | 89 | 6
2015-09-20 16:00 | 2015-09-20 | 7 | 16 | 231 | 88.6667 | 6
2015-09-20 16:15 | 2015-09-20 | 7 | 16 | 216 | 87.4167 | 6
2015-09-20 16:30 | 2015-09-20 | 7 | 16 | 224 | 86.1667 | 6
2015-09-20 16:45 | 2015-09-20 | 7 | 16 | 216 | 84.9167 | 5
2015-09-20 17:00 | 2015-09-20 | 7 | 17 | 213 | 83.8 | 5
2015-09-20 17:15 | 2015-09-20 | 7 | 17 | 227 | 83.05 | 5
2015-09-20 17:30 | 2015-09-20 | 7 | 17 | 209 | 82.3 | 5
2015-09-20 17:45 | 2015-09-20 | 7 | 17 | 221 | 81.55 | 5
2015-09-20 18:00 | 2015-09-20 | 7 | 18 | 212 | 80.7333 | 5
2015-09-20 18:15 | 2015-09-20 | 7 | 18 | 214 | 79.7333 | 4
2015-09-20 18:30 | 2015-09-20 | 7 | 18 | 206 | 78.7333 | 4
2015-09-20 18:45 | 2015-09-20 | 7 | 18 | 217 | 77.7333 | 4
2015-09-20 19:00 | 2015-09-20 | 7 | 19 | 199 | 77 | 4
2015-09-20 19:15 | 2015-09-20 | 7 | 19 | 194 | 77 | 4
2015-09-20 19:30 | 2015-09-20 | 7 | 19 | 191 | 77 | 4
2015-09-20 19:45 | 2015-09-20 | 7 | 19 | 183 | 77 | 4
2015-09-20 20:00 | 2015-09-20 | 7 | 20 | 192 | 77 | 4
2015-09-20 20:15 | 2015-09-20 | 7 | 20 | 181 | 77 | 4
2015-09-20 20:30 | 2015-09-20 | 7 | 20 | 172 | 77 | 4
2015-09-20 20:45 | 2015-09-20 | 7 | 20 | 182 | 77 | 4
2015-09-20 21:00 | 2015-09-20 | 7 | 21 | 179 | 76.9333 | 4
2015-09-20 21:15 | 2015-09-20 | 7 | 21 | 166 | 76.6833 | 4
2015-09-20 21:30 | 2015-09-20 | 7 | 21 | 171 | 76.4333 | 4
2015-09-20 21:45 | 2015-09-20 | 7 | 21 | 175 | 76.1833 | 4
2015-09-20 22:00 | 2015-09-20 | 7 | 22 | 164 | 75.9333 | 4
2015-09-20 22:15 | 2015-09-20 | 7 | 22 | 165 | 75.6833 | 4
2015-09-20 22:30 | 2015-09-20 | 7 | 22 | 171 | 75.4333 | 4
2015-09-20 22:45 | 2015-09-20 | 7 | 22 | 159 | 75.1833 | 4
2015-09-20 23:00 | 2015-09-20 | 7 | 23 | 170 | 74.8 | 3
2015-09-20 23:15 | 2015-09-20 | 7 | 23 | 166 | 74.05 | 3
2015-09-20 23:30 | 2015-09-20 | 7 | 23 | 152 | 73.3 | 3
2015-09-20 23:45 | 2015-09-20 | 7 | 23 | 166 | 72.55 | 3
2015-09-21 | 2015-09-21 | 1 | 0 | 161 | 71.9333 | 3
2015-09-21 00:15 | 2015-09-21 | 1 | 0 | 157 | 71.6833 | 3
2015-09-21 00:30 | 2015-09-21 | 1 | 0 | 163 | 71.4333 | 3
2015-09-21 00:45 | 2015-09-21 | 1 | 0 | 156 | 71.1833 | 3
2015-09-21 01:00 | 2015-09-21 | 1 | 1 | 159 | 70.8667 | 3
2015-09-21 01:15 | 2015-09-21 | 1 | 1 | 153 | 70.3667 | 3
2015-09-21 01:30 | 2015-09-21 | 1 | 1 | 157 | 69.8667 | 2
2015-09-21 01:45 | 2015-09-21 | 1 | 1 | 160 | 69.3667 | 2
2015-09-21 02:00 | 2015-09-21 | 1 | 2 | 153 | 69 | 2
2015-09-21 02:15 | 2015-09-21 | 1 | 2 | 161 | 69 | 2
2015-09-21 02:30 | 2015-09-21 | 1 | 2 | 150 | 69 | 2
2015-09-21 02:45 | 2015-09-21 | 1 | 2 | 159 | 69 | 2
2015-09-21 03:00 | 2015-09-21 | 1 | 3 | 155 | 68.8667 | 2
2015-09-21 03:15 | 2015-09-21 | 1 | 3 | 150 | 68.3667 | 2
2015-09-21 03:30 | 2015-09-21 | 1 | 3 | 158 | 67.8667 | 2
2015-09-21 03:45 | 2015-09-21 | 1 | 3 | 150 | 67.3667 | 2
2015-09-21 04:00 | 2015-09-21 | 1 | 4 | 154 | 67.0667 | 2
2015-09-21 04:15 | 2015-09-21 | 1 | 4 | 155 | 67.3167 | 2
2015-09-21 04:30 | 2015-09-21 | 1 | 4 | 147 | 67.5667 | 2
2015-09-21 04:45 | 2015-09-21 | 1 | 4 | 158 | 67.8167 | 2
2015-09-21 05:00 | 2015-09-21 | 1 | 5 | 146 | 67.9333 | 2
2015-09-21 05:15 | 2015-09-21 | 1 | 5 | 151 | 67.6833 | 2
2015-09-21 05:30 | 2015-09-21 | 1 | 5 | 157 | 67.4333 | 2
2015-09-21 05:45 | 2015-09-21 | 1 | 5 | 143 | 67.1833 | 2
2015-09-21 06:00 | 2015-09-21 | 1 | 6 | 154 | 67.2 | 2
2015-09-21 06:15 | 2015-09-21 | 1 | 6 | 155 | 67.95 | 2
2015-09-21 06:30 | 2015-09-21 | 1 | 6 | 143 | 68.7 | 2
2015-09-21 06:45 | 2015-09-21 | 1 | 6 | 155 | 69.45 | 2
2015-09-21 07:00 | 2015-09-21 | 1 | 7 | 152 | 70.1333 | 3
2015-09-21 07:15 | 2015-09-21 | 1 | 7 | 149 | 70.6333 | 3
2015-09-21 07:30 | 2015-09-21 | 1 | 7 | 150 | 71.1333 | 3
2015-09-21 07:45 | 2015-09-21 | 1 | 7 | 143 | 71.6333 | 3
2015-09-21 08:00 | 2015-09-21 | 1 | 8 | 164 | 72.1333 | 3
2015-09-21 08:15 | 2015-09-21 | 1 | 8 | 167 | 72.6333 | 3
2015-09-21 08:30 | 2015-09-21 | 1 | 8 | 168 | 73.1333 | 3
2015-09-21 08:45 | 2015-09-21 | 1 | 8 | 180 | 73.6333 | 3
2015-09-21 09:00 | 2015-09-21 | 1 | 9 | 163 | 74.0667 | 3
2015-09-21 09:15 | 2015-09-21 | 1 | 9 | 187 | 74.3167 | 3
2015-09-21 09:30 | 2015-09-21 | 1 | 9 | 185 | 74.5667 | 3
2015-09-21 09:45 | 2015-09-21 | 1 | 9 | 196 | 74.8167 | 3
2015-09-21 10:00 | 2015-09-21 | 1 | 10 | 202 | 75.1333 | 4
2015-09-21 10:15 | 2015-09-21 | 1 | 10 | 193 | 75.6333 | 4
2015-09-21 10:30 | 2015-09-21 | 1 | 10 | 205 | 76.1333 | 4
2015-09-21 10:45 | 2015-09-21 | 1 | 10 | 206 | 76.6333 | 4
2015-09-21 11:00 | 2015-09-21 | 1 | 11 | 206 | 77.2 | 4
2015-09-21 11:15 | 2015-09-21 | 1 | 11 | 227 | 77.95 | 4
2015-09-21 11:30 | 2015-09-21 | 1 | 11 | 208 | 78.7 | 4
2015-09-21 11:45 | 2015-09-21 | 1 | 11 | 225 | 79.45 | 4
2015-09-21 12:00 | 2015-09-21 | 1 | 12 | 217 | 80.5333 | 5
2015-09-21 12:15 | 2015-09-21 | 1 | 12 | 227 | 82.5333 | 5
2015-09-21 12:30 | 2015-09-21 | 1 | 12 | 230 | 84.5333 | 5
2015-09-21 12:45 | 2015-09-21 | 1 | 12 | 245 | 86.5333 | 6
2015-09-21 13:00 | 2015-09-21 | 1 | 13 | 233 | 87.9333 | 6
2015-09-21 13:15 | 2015-09-21 | 1 | 13 | 244 | 87.6833 | 6
2015-09-21 13:30 | 2015-09-21 | 1 | 13 | 246 | 87.4333 | 6
2015-09-21 13:45 | 2015-09-21 | 1 | 13 | 253 | 87.1833 | 6
2015-09-21 14:00 | 2015-09-21 | 1 | 14 | 258 | 86.6 | 6
2015-09-21 14:15 | 2015-09-21 | 1 | 14 | 254 | 85.1 | 6
2015-09-21 14:30 | 2015-09-21 | 1 | 14 | 257 | 83.6 | 5
2015-09-21 14:45 | 2015-09-21 | 1 | 14 | 260 | 82.1 | 5
2015-09-21 15:00 | 2015-09-21 | 1 | 15 | 258 | 80.8 | 5
2015-09-21 15:15 | 2015-09-21 | 1 | 15 | 274 | 80.05 | 5
2015-09-21 15:30 | 2015-09-21 | 1 | 15 | 260 | 79.3 | 4
2015-09-21 15:45 | 2015-09-21 | 1 | 15 | 268 | 78.55 | 4
2015-09-21 16:00 | 2015-09-21 | 1 | 16 | 263 | 77.5333 | 4
2015-09-21 16:15 | 2015-09-21 | 1 | 16 | 263 | 75.7833 | 4
2015-09-21 16:30 | 2015-09-21 | 1 | 16 | 264 | 74.0333 | 3
2015-09-21 16:45 | 2015-09-21 | 1 | 16 | 267 | 72.2833 | 3
2015-09-21 17:00 | 2015-09-21 | 1 | 17 | 256 | 70.6667 | 3
2015-09-21 17:15 | 2015-09-21 | 1 | 17 | 250 | 69.4167 | 2
2015-09-21 17:30 | 2015-09-21 | 1 | 17 | 258 | 68.1667 | 2
2015-09-21 17:45 | 2015-09-21 | 1 | 17 | 248 | 66.9167 | 2
2015-09-21 18:00 | 2015-09-21 | 1 | 18 | 242 | 65.8 | 2
2015-09-21 18:15 | 2015-09-21 | 1 | 18 | 244 | 65.05 | 2
2015-09-21 18:30 | 2015-09-21 | 1 | 18 | 237 | 64.3 | 1
2015-09-21 18:45 | 2015-09-21 | 1 | 18 | 237 | 63.55 | 1
2015-09-21 19:00 | 2015-09-21 | 1 | 19 | 232 | 63 | 1
2015-09-21 19:15 | 2015-09-21 | 1 | 19 | 222 | 63 | 1
2015-09-21 19:30 | 2015-09-21 | 1 | 19 | 213 | 63 | 1
2015-09-21 19:45 | 2015-09-21 | 1 | 19 | 214 | 63 | 1
2015-09-21 20:00 | 2015-09-21 | 1 | 20 | 223 | 62.9333 | 1
2015-09-21 20:15 | 2015-09-21 | 1 | 20 | 207 | 62.6833 | 1
2015-09-21 20:30 | 2015-09-21 | 1 | 20 | 199 | 62.4333 | 1
2015-09-21 20:45 | 2015-09-21 | 1 | 20 | 200 | 62.1833 | 1
2015-09-21 21:00 | 2015-09-21 | 1 | 21 | 193 | 61.9333 | 1
2015-09-21 21:15 | 2015-09-21 | 1 | 21 | 200 | 61.6833 | 1
2015-09-21 21:30 | 2015-09-21 | 1 | 21 | 188 | 61.4333 | 1
2015-09-21 21:45 | 2015-09-21 | 1 | 21 | 185 | 61.1833 | 1
2015-09-21 22:00 | 2015-09-21 | 1 | 22 | 183 | 61 | 1
2015-09-21 22:15 | 2015-09-21 | 1 | 22 | 185 | 61 | 1
2015-09-21 22:30 | 2015-09-21 | 1 | 22 | 204 | 61 | 1
2015-09-21 22:45 | 2015-09-21 | 1 | 22 | 188 | 61 | 1
2015-09-21 23:00 | 2015-09-21 | 1 | 23 | 192 | 60.9333 | 1
2015-09-21 23:15 | 2015-09-21 | 1 | 23 | 186 | 60.6833 | 1
2015-09-21 23:30 | 2015-09-21 | 1 | 23 | 189 | 60.4333 | 1
2015-09-21 23:45 | 2015-09-21 | 1 | 23 | 201 | 60.1833 | 1
2015-09-22 | 2015-09-22 | 2 | 0 | 183 | 60 | 1
2015-09-22 00:15 | 2015-09-22 | 2 | 0 | 185 | 60 | 1
2015-09-22 00:30 | 2015-09-22 | 2 | 0 | 181 | 60 | 1
2015-09-22 00:45 | 2015-09-22 | 2 | 0 | 180 | 60 | 1
2015-09-22 01:00 | 2015-09-22 | 2 | 1 | 191 | 59.9333 | 1
2015-09-22 01:15 | 2015-09-22 | 2 | 1 | 175 | 59.6833 | 1
2015-09-22 01:30 | 2015-09-22 | 2 | 1 | 171 | 59.4333 | 1
2015-09-22 01:45 | 2015-09-22 | 2 | 1 | 175 | 59.1833 | 1
2015-09-22 02:00 | 2015-09-22 | 2 | 2 | 187 | 59 | 1
2015-09-22 02:15 | 2015-09-22 | 2 | 2 | 175 | 59 | 1
2015-09-22 02:30 | 2015-09-22 | 2 | 2 | 173 | 59 | 1
2015-09-22 02:45 | 2015-09-22 | 2 | 2 | 167 | 59 | 1
2015-09-22 03:00 | 2015-09-22 | 2 | 3 | 169 | 59.0667 | 1
2015-09-22 03:15 | 2015-09-22 | 2 | 3 | 182 | 59.3167 | 1
2015-09-22 03:30 | 2015-09-22 | 2 | 3 | 165 | 59.5667 | 1
2015-09-22 03:45 | 2015-09-22 | 2 | 3 | 165 | 59.8167 | 1
2015-09-22 04:00 | 2015-09-22 | 2 | 4 | 156 | 59.9333 | 1
2015-09-22 04:15 | 2015-09-22 | 2 | 4 | 170 | 59.6833 | 1
2015-09-22 04:30 | 2015-09-22 | 2 | 4 | 162 | 59.4333 | 1
2015-09-22 04:45 | 2015-09-22 | 2 | 4 | 158 | 59.1833 | 1
2015-09-22 05:00 | 2015-09-22 | 2 | 5 | 153 | 58.8621 | 1
2015-09-22 05:15 | 2015-09-22 | 2 | 5 | 162 | 58.3448 | 1
2015-09-22 05:30 | 2015-09-22 | 2 | 5 | 173 | 57.8276 | 1
2015-09-22 05:45 | 2015-09-22 | 2 | 5 | 157 | 57.3103 | 1
2015-09-22 06:00 | 2015-09-22 | 2 | 6 | 158 | 58.1333 | 1
2015-09-22 06:15 | 2015-09-22 | 2 | 6 | 157 | 58.6333 | 1
2015-09-22 06:30 | 2015-09-22 | 2 | 6 | 159 | 59.1333 | 1
2015-09-22 06:45 | 2015-09-22 | 2 | 6 | 174 | 59.6333 | 1
2015-09-22 07:00 | 2015-09-22 | 2 | 7 | 156 | 60.0667 | 1
2015-09-22 07:15 | 2015-09-22 | 2 | 7 | 157 | 60.3167 | 1
2015-09-22 07:30 | 2015-09-22 | 2 | 7 | 153 | 60.5667 | 1
2015-09-22 07:45 | 2015-09-22 | 2 | 7 | 167 | 60.8167 | 1
2015-09-22 08:00 | 2015-09-22 | 2 | 8 | 173 | 61.1379 | 1
2015-09-22 08:15 | 2015-09-22 | 2 | 8 | 163 | 61.6552 | 1
2015-09-22 08:30 | 2015-09-22 | 2 | 8 | 169 | 62.1724 | 1
2015-09-22 08:45 | 2015-09-22 | 2 | 8 | 171 | 62.6897 | 1
2015-09-22 09:00 | 2015-09-22 | 2 | 9 | 192 | 63.0667 | 1
2015-09-22 09:15 | 2015-09-22 | 2 | 9 | 181 | 63.3167 | 1
2015-09-22 09:30 | 2015-09-22 | 2 | 9 | 184 | 63.5667 | 1
2015-09-22 09:45 | 2015-09-22 | 2 | 9 | 179 | 63.8167 | 1
2015-09-22 10:00 | 2015-09-22 | 2 | 10 | 176 | 64 | 1
2015-09-22 10:15 | 2015-09-22 | 2 | 10 | 198 | 64 | 1
2015-09-22 10:30 | 2015-09-22 | 2 | 10 | 193 | 64 | 1
2015-09-22 10:45 | 2015-09-22 | 2 | 10 | 182 | 64 | 1
2015-09-22 11:00 | 2015-09-22 | 2 | 11 | 191 | 64 | 1
2015-09-22 11:15 | 2015-09-22 | 2 | 11 | 191 | 64 | 1
2015-09-22 11:30 | 2015-09-22 | 2 | 11 | 215 | 64 | 1
2015-09-22 11:45 | 2015-09-22 | 2 | 11 | 207 | 64 | 1
2015-09-22 12:00 | 2015-09-22 | 2 | 12 | 206 | 64 | 1
2015-09-22 12:15 | 2015-09-22 | 2 | 12 | 206 | 64 | 1
2015-09-22 12:30 | 2015-09-22 | 2 | 12 | 205 | 64 | 1
2015-09-22 12:45 | 2015-09-22 | 2 | 12 | 225 | 64 | 1
2015-09-22 13:00 | 2015-09-22 | 2 | 13 | 217 | 64 | 1
2015-09-22 13:15 | 2015-09-22 | 2 | 13 | 215 | 64 | 1
2015-09-22 13:30 | 2015-09-22 | 2 | 13 | 212 | 64 | 1
2015-09-22 13:45 | 2015-09-22 | 2 | 13 | 226 | 64 | 1
2015-09-22 14:00 | 2015-09-22 | 2 | 14 | 226 | 64 | 1
2015-09-22 14:15 | 2015-09-22 | 2 | 14 | 213 | 64 | 1
2015-09-22 14:30 | 2015-09-22 | 2 | 14 | 228 | 64 | 1
2015-09-22 14:45 | 2015-09-22 | 2 | 14 | 224 | 64 | 1
2015-09-22 15:00 | 2015-09-22 | 2 | 15 | 230 | 63.8 | 1
2015-09-22 15:15 | 2015-09-22 | 2 | 15 | 203 | 63.05 | 1
2015-09-22 15:30 | 2015-09-22 | 2 | 15 | 218 | 62.3 | 1
2015-09-22 15:45 | 2015-09-22 | 2 | 15 | 215 | 61.55 | 1
2015-09-22 16:00 | 2015-09-22 | 2 | 16 | 226 | 61.0667 | 1
2015-09-22 16:15 | 2015-09-22 | 2 | 16 | 218 | 61.3167 | 1
2015-09-22 16:30 | 2015-09-22 | 2 | 16 | 209 | 61.5667 | 1
2015-09-22 16:45 | 2015-09-22 | 2 | 16 | 207 | 61.8167 | 1
2015-09-22 17:00 | 2015-09-22 | 2 | 17 | 213 | 61.8667 | 1
2015-09-22 17:15 | 2015-09-22 | 2 | 17 | 221 | 61.3667 | 1
2015-09-22 17:30 | 2015-09-22 | 2 | 17 | 206 | 60.8667 | 1
2015-09-22 17:45 | 2015-09-22 | 2 | 17 | 207 | 60.3667 | 1
2015-09-22 18:00 | 2015-09-22 | 2 | 18 | 199 | 59.9333 | 1
2015-09-22 18:15 | 2015-09-22 | 2 | 18 | 204 | 59.6833 | 1
2015-09-22 18:30 | 2015-09-22 | 2 | 18 | 208 | 59.4333 | 1
2015-09-22 18:45 | 2015-09-22 | 2 | 18 | 197 | 59.1833 | 1
2015-09-22 19:00 | 2015-09-22 | 2 | 19 | 185 | 59 | 1
2015-09-22 19:15 | 2015-09-22 | 2 | 19 | 128 | 59 | 1
2015-09-22 19:30 | 2015-09-22 | 2 | 19 | 125 | 59 | 1
2015-09-22 19:45 | 2015-09-22 | 2 | 19 | 142 | 59 | 1
2015-09-22 20:00 | 2015-09-22 | 2 | 20 | 129 | 59 | 1
2015-09-22 20:15 | 2015-09-22 | 2 | 20 | 127 | 59 | 1
2015-09-22 20:30 | 2015-09-22 | 2 | 20 | 129 | 59 | 1
2015-09-22 20:45 | 2015-09-22 | 2 | 20 | 128 | 59 | 1
2015-09-22 21:00 | 2015-09-22 | 2 | 21 | 139 | 59 | 1
2015-09-22 21:15 | 2015-09-22 | 2 | 21 | 120 | 59 | 1
2015-09-22 21:30 | 2015-09-22 | 2 | 21 | 111 | 59 | 1
2015-09-22 21:45 | 2015-09-22 | 2 | 21 | 112 | 59 | 1
2015-09-22 22:00 | 2015-09-22 | 2 | 22 | 124 | 58.9333 | 1
2015-09-22 22:15 | 2015-09-22 | 2 | 22 | 117 | 58.6833 | 1
2015-09-22 22:30 | 2015-09-22 | 2 | 22 | 119 | 58.4333 | 1
2015-09-22 22:45 | 2015-09-22 | 2 | 22 | 116 | 58.1833 | 1
2015-09-22 23:00 | 2015-09-22 | 2 | 23 | 114 | 58 | 1
2015-09-22 23:15 | 2015-09-22 | 2 | 23 | 128 | 58 | 1
2015-09-22 23:30 | 2015-09-22 | 2 | 23 | 114 | 58 | 1
2015-09-22 23:45 | 2015-09-22 | 2 | 23 | 112 | 58 | 1
2015-09-23 | 2015-09-23 | 3 | 0 | 108 | 58 | 1
2015-09-23 00:15 | 2015-09-23 | 3 | 0 | 108 | 58 | 1
2015-09-23 00:30 | 2015-09-23 | 3 | 0 | 110 | 58 | 1
2015-09-23 00:45 | 2015-09-23 | 3 | 0 | 106 | 58 | 1
2015-09-23 01:00 | 2015-09-23 | 3 | 1 | 117 | 57.8667 | 1
2015-09-23 01:15 | 2015-09-23 | 3 | 1 | 113 | 57.3667 | 1
2015-09-23 01:30 | 2015-09-23 | 3 | 1 | 108 | 56.8667 | 1
2015-09-23 01:45 | 2015-09-23 | 3 | 1 | 109 | 56.3667 | 1
2015-09-23 02:00 | 2015-09-23 | 3 | 2 | 115 | 56 | 1
2015-09-23 02:15 | 2015-09-23 | 3 | 2 | 110 | 56 | 1
2015-09-23 02:30 | 2015-09-23 | 3 | 2 | 110 | 56 | 1
2015-09-23 02:45 | 2015-09-23 | 3 | 2 | 106 | 56 | 1
2015-09-23 03:00 | 2015-09-23 | 3 | 3 | 108 | 56 | 1
2015-09-23 03:15 | 2015-09-23 | 3 | 3 | 117 | 56 | 1
2015-09-23 03:30 | 2015-09-23 | 3 | 3 | 107 | 56 | 1
2015-09-23 03:45 | 2015-09-23 | 3 | 3 | 110 | 56 | 1
2015-09-23 04:00 | 2015-09-23 | 3 | 4 | 104 | 56 | 1
2015-09-23 04:15 | 2015-09-23 | 3 | 4 | 117 | 56 | 1
2015-09-23 04:30 | 2015-09-23 | 3 | 4 | 111 | 56 | 1
2015-09-23 04:45 | 2015-09-23 | 3 | 4 | 108 | 56 | 1
2015-09-23 05:00 | 2015-09-23 | 3 | 5 | 108 | 55.931 | 1
2015-09-23 05:15 | 2015-09-23 | 3 | 5 | 108 | 55.6724 | 1
2015-09-23 05:30 | 2015-09-23 | 3 | 5 | 116 | 55.4138 | 1
2015-09-23 05:45 | 2015-09-23 | 3 | 5 | 107 | 55.1552 | 1
2015-09-23 06:00 | 2015-09-23 | 3 | 6 | 107 | 57 | 1
2015-09-23 06:15 | 2015-09-23 | 3 | 6 | 111 | 57 | 1
2015-09-23 06:30 | 2015-09-23 | 3 | 6 | 115 | 57 | 1
2015-09-23 06:45 | 2015-09-23 | 3 | 6 | 113 | 57 | 1
2015-09-23 07:00 | 2015-09-23 | 3 | 7 | 113 | 57.3333 | 1
2015-09-23 07:15 | 2015-09-23 | 3 | 7 | 145 | 58.5833 | 1
2015-09-23 07:30 | 2015-09-23 | 3 | 7 | 149 | 59.8333 | 1
2015-09-23 07:45 | 2015-09-23 | 3 | 7 | 150 | 61.0833 | 1
2015-09-23 08:00 | 2015-09-23 | 3 | 8 | 150 | 62 | 1
2015-09-23 08:15 | 2015-09-23 | 3 | 8 | 152 | 62 | 1
2015-09-23 08:30 | 2015-09-23 | 3 | 8 | 163 | 62 | 1
2015-09-23 08:45 | 2015-09-23 | 3 | 8 | 164 | 62 | 1
2015-09-23 09:00 | 2015-09-23 | 3 | 9 | 165 | 62.1333 | 1
2015-09-23 09:15 | 2015-09-23 | 3 | 9 | 173 | 62.6333 | 1
2015-09-23 09:30 | 2015-09-23 | 3 | 9 | 176 | 63.1333 | 1
2015-09-23 09:45 | 2015-09-23 | 3 | 9 | 194 | 63.6333 | 1
2015-09-23 10:00 | 2015-09-23 | 3 | 10 | 184 | 64.1333 | 1
2015-09-23 10:15 | 2015-09-23 | 3 | 10 | 190 | 64.6333 | 1
2015-09-23 10:30 | 2015-09-23 | 3 | 10 | 202 | 65.1333 | 2
2015-09-23 10:45 | 2015-09-23 | 3 | 10 | 210 | 65.6333 | 2
2015-09-23 11:00 | 2015-09-23 | 3 | 11 | 208 | 66.4 | 2
2015-09-23 11:15 | 2015-09-23 | 3 | 11 | 214 | 67.9 | 2
2015-09-23 11:30 | 2015-09-23 | 3 | 11 | 213 | 69.4 | 2
2015-09-23 11:45 | 2015-09-23 | 3 | 11 | 205 | 70.9 | 3
2015-09-23 12:00 | 2015-09-23 | 3 | 12 | 217 | 72.0667 | 3
2015-09-23 12:15 | 2015-09-23 | 3 | 12 | 215 | 72.3167 | 3
2015-09-23 12:30 | 2015-09-23 | 3 | 12 | 209 | 72.5667 | 3
2015-09-23 12:45 | 2015-09-23 | 3 | 12 | 211 | 72.8167 | 3
2015-09-23 13:00 | 2015-09-23 | 3 | 13 | 197 | 73 | 3
2015-09-23 13:15 | 2015-09-23 | 3 | 13 | 215 | 73 | 3
2015-09-23 13:30 | 2015-09-23 | 3 | 13 | 215 | 73 | 3
2015-09-23 13:45 | 2015-09-23 | 3 | 13 | 208 | 73 | 3
2015-09-23 14:00 | 2015-09-23 | 3 | 14 | 219 | 72.9333 | 3
2015-09-23 14:15 | 2015-09-23 | 3 | 14 | 221 | 72.6833 | 3
2015-09-23 14:30 | 2015-09-23 | 3 | 14 | 218 | 72.4333 | 3
2015-09-23 14:45 | 2015-09-23 | 3 | 14 | 224 | 72.1833 | 3
2015-09-23 15:00 | 2015-09-23 | 3 | 15 | 220 | 71.9333 | 3
2015-09-23 15:15 | 2015-09-23 | 3 | 15 | 231 | 71.6833 | 3
2015-09-23 15:30 | 2015-09-23 | 3 | 15 | 229 | 71.4333 | 3
2015-09-23 15:45 | 2015-09-23 | 3 | 15 | 231 | 71.1833 | 3
2015-09-23 16:00 | 2015-09-23 | 3 | 16 | 221 | 70.7333 | 3
2015-09-23 16:15 | 2015-09-23 | 3 | 16 | 230 | 69.7333 | 2
2015-09-23 16:30 | 2015-09-23 | 3 | 16 | 213 | 68.7333 | 2
2015-09-23 16:45 | 2015-09-23 | 3 | 16 | 235 | 67.7333 | 2
2015-09-23 17:00 | 2015-09-23 | 3 | 17 | 223 | 66.9333 | 2
2015-09-23 17:15 | 2015-09-23 | 3 | 17 | 219 | 66.6833 | 2
2015-09-23 17:30 | 2015-09-23 | 3 | 17 | 219 | 66.4333 | 2
2015-09-23 17:45 | 2015-09-23 | 3 | 17 | 224 | 66.1833 | 2
2015-09-23 18:00 | 2015-09-23 | 3 | 18 | 218 | 65.9333 | 2
2015-09-23 18:15 | 2015-09-23 | 3 | 18 | 217 | 65.6833 | 2
2015-09-23 18:30 | 2015-09-23 | 3 | 18 | 208 | 65.4333 | 2
2015-09-23 18:45 | 2015-09-23 | 3 | 18 | 197 | 65.1833 | 2
2015-09-23 19:00 | 2015-09-23 | 3 | 19 | 214 | 64.9333 | 1
2015-09-23 19:15 | 2015-09-23 | 3 | 19 | 122 | 64.6833 | 1
2015-09-23 19:30 | 2015-09-23 | 3 | 19 | 125 | 64.4333 | 1
2015-09-23 19:45 | 2015-09-23 | 3 | 19 | 122 | 64.1833 | 1
2015-09-23 20:00 | 2015-09-23 | 3 | 20 | 122 | 63.9333 | 1
2015-09-23 20:15 | 2015-09-23 | 3 | 20 | 129 | 63.6833 | 1
2015-09-23 20:30 | 2015-09-23 | 3 | 20 | 123 | 63.4333 | 1
2015-09-23 20:45 | 2015-09-23 | 3 | 20 | 122 | 63.1833 | 1
2015-09-23 21:00 | 2015-09-23 | 3 | 21 | 121 | 62.9333 | 1
2015-09-23 21:15 | 2015-09-23 | 3 | 21 | 122 | 62.6833 | 1
2015-09-23 21:30 | 2015-09-23 | 3 | 21 | 117 | 62.4333 | 1
2015-09-23 21:45 | 2015-09-23 | 3 | 21 | 118 | 62.1833 | 1
2015-09-23 22:00 | 2015-09-23 | 3 | 22 | 116 | 61.9333 | 1
2015-09-23 22:15 | 2015-09-23 | 3 | 22 | 116 | 61.6833 | 1
2015-09-23 22:30 | 2015-09-23 | 3 | 22 | 120 | 61.4333 | 1
2015-09-23 22:45 | 2015-09-23 | 3 | 22 | 123 | 61.1833 | 1
2015-09-23 23:00 | 2015-09-23 | 3 | 23 | 124 | 61.0667 | 1
2015-09-23 23:15 | 2015-09-23 | 3 | 23 | 123 | 61.3167 | 1
2015-09-23 23:30 | 2015-09-23 | 3 | 23 | 117 | 61.5667 | 1
2015-09-23 23:45 | 2015-09-23 | 3 | 23 | 121 | 61.8167 | 1
2015-09-24 | 2015-09-24 | 4 | 0 | 121 | 62 | 1
2015-09-24 00:15 | 2015-09-24 | 4 | 0 | 110 | 62 | 1
2015-09-24 00:30 | 2015-09-24 | 4 | 0 | 121 | 62 | 1
2015-09-24 00:45 | 2015-09-24 | 4 | 0 | 113 | 62 | 1
2015-09-24 01:00 | 2015-09-24 | 4 | 1 | 112 | 61.9333 | 1
2015-09-24 01:15 | 2015-09-24 | 4 | 1 | 106 | 61.6833 | 1
2015-09-24 01:30 | 2015-09-24 | 4 | 1 | 114 | 61.4333 | 1
2015-09-24 01:45 | 2015-09-24 | 4 | 1 | 108 | 61.1833 | 1
2015-09-24 02:00 | 2015-09-24 | 4 | 2 | 116 | 61 | 1
2015-09-24 02:15 | 2015-09-24 | 4 | 2 | 106 | 61 | 1
2015-09-24 02:30 | 2015-09-24 | 4 | 2 | 112 | 61 | 1
2015-09-24 02:45 | 2015-09-24 | 4 | 2 | 106 | 61 | 1
2015-09-24 03:00 | 2015-09-24 | 4 | 3 | 112 | 61 | 1
2015-09-24 03:15 | 2015-09-24 | 4 | 3 | 110 | 61 | 1
2015-09-24 03:30 | 2015-09-24 | 4 | 3 | 107 | 61 | 1
2015-09-24 03:45 | 2015-09-24 | 4 | 3 | 109 | 61 | 1
2015-09-24 04:00 | 2015-09-24 | 4 | 4 | 112 | 61 | 1
2015-09-24 04:15 | 2015-09-24 | 4 | 4 | 109 | 61 | 1
2015-09-24 04:30 | 2015-09-24 | 4 | 4 | 107 | 61 | 1
2015-09-24 04:45 | 2015-09-24 | 4 | 4 | 107 | 61 | 1
2015-09-24 05:00 | 2015-09-24 | 4 | 5 | 110 | 61.0667 | 1
2015-09-24 05:15 | 2015-09-24 | 4 | 5 | 109 | 61.3167 | 1
2015-09-24 05:30 | 2015-09-24 | 4 | 5 | 108 | 61.5667 | 1
2015-09-24 05:45 | 2015-09-24 | 4 | 5 | 106 | 61.8167 | 1
2015-09-24 06:00 | 2015-09-24 | 4 | 6 | 107 | 62.0667 | 1
2015-09-24 06:15 | 2015-09-24 | 4 | 6 | 113 | 62.3167 | 1
2015-09-24 06:30 | 2015-09-24 | 4 | 6 | 112 | 62.5667 | 1
2015-09-24 06:45 | 2015-09-24 | 4 | 6 | 117 | 62.8167 | 1
2015-09-24 07:00 | 2015-09-24 | 4 | 7 | 112 | 63.2667 | 1
2015-09-24 07:15 | 2015-09-24 | 4 | 7 | 200 | 64.2667 | 1
2015-09-24 07:30 | 2015-09-24 | 4 | 7 | 179 | 65.2667 | 2
2015-09-24 07:45 | 2015-09-24 | 4 | 7 | 170 | 66.2667 | 2
2015-09-24 08:00 | 2015-09-24 | 4 | 8 | 168 | 67.0667 | 2
2015-09-24 08:15 | 2015-09-24 | 4 | 8 | 178 | 67.3167 | 2
2015-09-24 08:30 | 2015-09-24 | 4 | 8 | 182 | 67.5667 | 2
2015-09-24 08:45 | 2015-09-24 | 4 | 8 | 189 | 67.8167 | 2
2015-09-24 09:00 | 2015-09-24 | 4 | 9 | 189 | 68.1333 | 2
2015-09-24 09:15 | 2015-09-24 | 4 | 9 | 191 | 68.6333 | 2
2015-09-24 09:30 | 2015-09-24 | 4 | 9 | 200 | 69.1333 | 2
2015-09-24 09:45 | 2015-09-24 | 4 | 9 | 208 | 69.6333 | 2
2015-09-24 10:00 | 2015-09-24 | 4 | 10 | 203 | 70.2 | 3
2015-09-24 10:15 | 2015-09-24 | 4 | 10 | 214 | 70.95 | 3
2015-09-24 10:30 | 2015-09-24 | 4 | 10 | 217 | 71.7 | 3
2015-09-24 10:45 | 2015-09-24 | 4 | 10 | 213 | 72.45 | 3
2015-09-24 11:00 | 2015-09-24 | 4 | 11 | 211 | 73.1333 | 3
2015-09-24 11:15 | 2015-09-24 | 4 | 11 | 209 | 73.6333 | 3
2015-09-24 11:30 | 2015-09-24 | 4 | 11 | 220 | 74.1333 | 3
2015-09-24 11:45 | 2015-09-24 | 4 | 11 | 227 | 74.6333 | 3
2015-09-24 12:00 | 2015-09-24 | 4 | 12 | 217 | 75.1333 | 4
2015-09-24 12:15 | 2015-09-24 | 4 | 12 | 226 | 75.6333 | 4
2015-09-24 12:30 | 2015-09-24 | 4 | 12 | 228 | 76.1333 | 4
2015-09-24 12:45 | 2015-09-24 | 4 | 12 | 226 | 76.6333 | 4
2015-09-24 13:00 | 2015-09-24 | 4 | 13 | 245 | 77.0667 | 4
2015-09-24 13:15 | 2015-09-24 | 4 | 13 | 242 | 77.3167 | 4
2015-09-24 13:30 | 2015-09-24 | 4 | 13 | 230 | 77.5667 | 4
2015-09-24 13:45 | 2015-09-24 | 4 | 13 | 239 | 77.8167 | 4
2015-09-24 14:00 | 2015-09-24 | 4 | 14 | 250 | 78 | 4
2015-09-24 14:15 | 2015-09-24 | 4 | 14 | 250 | 78 | 4
2015-09-24 14:30 | 2015-09-24 | 4 | 14 | 246 | 78 | 4
2015-09-24 14:45 | 2015-09-24 | 4 | 14 | 252 | 78 | 4
2015-09-24 15:00 | 2015-09-24 | 4 | 15 | 245 | 78 | 4
2015-09-24 15:15 | 2015-09-24 | 4 | 15 | 259 | 78 | 4
2015-09-24 15:30 | 2015-09-24 | 4 | 15 | 250 | 78 | 4
2015-09-24 15:45 | 2015-09-24 | 4 | 15 | 261 | 78 | 4
2015-09-24 16:00 | 2015-09-24 | 4 | 16 | 242 | 77.6 | 4
2015-09-24 16:15 | 2015-09-24 | 4 | 16 | 263 | 76.1 | 4
2015-09-24 16:30 | 2015-09-24 | 4 | 16 | 238 | 74.6 | 3
2015-09-24 16:45 | 2015-09-24 | 4 | 16 | 253 | 73.1 | 3
2015-09-24 17:00 | 2015-09-24 | 4 | 17 | 240 | 72 | 3
2015-09-24 17:15 | 2015-09-24 | 4 | 17 | 254 | 72 | 3
2015-09-24 17:30 | 2015-09-24 | 4 | 17 | 242 | 72 | 3
2015-09-24 17:45 | 2015-09-24 | 4 | 17 | 254 | 72 | 3
2015-09-24 18:00 | 2015-09-24 | 4 | 18 | 245 | 71.7333 | 3
2015-09-24 18:15 | 2015-09-24 | 4 | 18 | 240 | 70.7333 | 3
2015-09-24 18:30 | 2015-09-24 | 4 | 18 | 241 | 69.7333 | 2
2015-09-24 18:45 | 2015-09-24 | 4 | 18 | 232 | 68.7333 | 2
2015-09-24 19:00 | 2015-09-24 | 4 | 19 | 218 | 67.9333 | 2
2015-09-24 19:15 | 2015-09-24 | 4 | 19 | 143 | 67.6833 | 2
2015-09-24 19:30 | 2015-09-24 | 4 | 19 | 126 | 67.4333 | 2
2015-09-24 19:45 | 2015-09-24 | 4 | 19 | 131 | 67.1833 | 2
2015-09-24 20:00 | 2015-09-24 | 4 | 20 | 127 | 66.8667 | 2
2015-09-24 20:15 | 2015-09-24 | 4 | 20 | 128 | 66.3667 | 2
2015-09-24 20:30 | 2015-09-24 | 4 | 20 | 139 | 65.8667 | 2
2015-09-24 20:45 | 2015-09-24 | 4 | 20 | 128 | 65.3667 | 2
2015-09-24 21:00 | 2015-09-24 | 4 | 21 | 129 | 64.9333 | 1
2015-09-24 21:15 | 2015-09-24 | 4 | 21 | 116 | 64.6833 | 1
2015-09-24 21:30 | 2015-09-24 | 4 | 21 | 119 | 64.4333 | 1
2015-09-24 21:45 | 2015-09-24 | 4 | 21 | 115 | 64.1833 | 1
2015-09-24 22:00 | 2015-09-24 | 4 | 22 | 114 | 63.8667 | 1
2015-09-24 22:15 | 2015-09-24 | 4 | 22 | 114 | 63.3667 | 1
2015-09-24 22:30 | 2015-09-24 | 4 | 22 | 119 | 62.8667 | 1
2015-09-24 22:45 | 2015-09-24 | 4 | 22 | 117 | 62.3667 | 1
2015-09-24 23:00 | 2015-09-24 | 4 | 23 | 128 | 62 | 1
2015-09-24 23:15 | 2015-09-24 | 4 | 23 | 119 | 62 | 1
2015-09-24 23:30 | 2015-09-24 | 4 | 23 | 116 | 62 | 1
2015-09-24 23:45 | 2015-09-24 | 4 | 23 | 115 | 62 | 1
2015-09-25 | 2015-09-25 | 5 | 0 | 112 | 61.9333 | 1
2015-09-25 00:15 | 2015-09-25 | 5 | 0 | 116 | 61.6833 | 1
2015-09-25 00:30 | 2015-09-25 | 5 | 0 | 111 | 61.4333 | 1
2015-09-25 00:45 | 2015-09-25 | 5 | 0 | 116 | 61.1833 | 1
2015-09-25 01:00 | 2015-09-25 | 5 | 1 | 111 | 60.9333 | 1
2015-09-25 01:15 | 2015-09-25 | 5 | 1 | 115 | 60.6833 | 1
2015-09-25 01:30 | 2015-09-25 | 5 | 1 | 106 | 60.4333 | 1
2015-09-25 01:45 | 2015-09-25 | 5 | 1 | 112 | 60.1833 | 1
2015-09-25 02:00 | 2015-09-25 | 5 | 2 | 110 | 59.9333 | 1
2015-09-25 02:15 | 2015-09-25 | 5 | 2 | 110 | 59.6833 | 1
2015-09-25 02:30 | 2015-09-25 | 5 | 2 | 105 | 59.4333 | 1
2015-09-25 02:45 | 2015-09-25 | 5 | 2 | 112 | 59.1833 | 1
2015-09-25 03:00 | 2015-09-25 | 5 | 3 | 111 | 59 | 1
2015-09-25 03:15 | 2015-09-25 | 5 | 3 | 109 | 59 | 1
2015-09-25 03:30 | 2015-09-25 | 5 | 3 | 109 | 59 | 1
2015-09-25 03:45 | 2015-09-25 | 5 | 3 | 106 | 59 | 1
2015-09-25 04:00 | 2015-09-25 | 5 | 4 | 113 | 59.0667 | 1
2015-09-25 04:15 | 2015-09-25 | 5 | 4 | 111 | 59.3167 | 1
2015-09-25 04:30 | 2015-09-25 | 5 | 4 | 109 | 59.5667 | 1
2015-09-25 04:45 | 2015-09-25 | 5 | 4 | 108 | 59.8167 | 1
2015-09-25 05:00 | 2015-09-25 | 5 | 5 | 109 | 60 | 1
2015-09-25 05:15 | 2015-09-25 | 5 | 5 | 110 | 60 | 1
2015-09-25 05:30 | 2015-09-25 | 5 | 5 | 108 | 60 | 1
2015-09-25 05:45 | 2015-09-25 | 5 | 5 | 103 | 60 | 1
2015-09-25 06:00 | 2015-09-25 | 5 | 6 | 109 | 59.9333 | 1
2015-09-25 06:15 | 2015-09-25 | 5 | 6 | 111 | 59.6833 | 1
2015-09-25 06:30 | 2015-09-25 | 5 | 6 | 115 | 59.4333 | 1
2015-09-25 06:45 | 2015-09-25 | 5 | 6 | 113 | 59.1833 | 1
2015-09-25 07:00 | 2015-09-25 | 5 | 7 | 114 | 59.2667 | 1
2015-09-25 07:15 | 2015-09-25 | 5 | 7 | 216 | 60.2667 | 1
2015-09-25 07:30 | 2015-09-25 | 5 | 7 | 204 | 61.2667 | 1
2015-09-25 07:45 | 2015-09-25 | 5 | 7 | 174 | 62.2667 | 1
2015-09-25 08:00 | 2015-09-25 | 5 | 8 | 185 | 63.3333 | 1
2015-09-25 08:15 | 2015-09-25 | 5 | 8 | 191 | 64.5833 | 1
2015-09-25 08:30 | 2015-09-25 | 5 | 8 | 185 | 65.8333 | 2
2015-09-25 08:45 | 2015-09-25 | 5 | 8 | 181 | 67.0833 | 2
2015-09-25 09:00 | 2015-09-25 | 5 | 9 | 189 | 68.0667 | 2
2015-09-25 09:15 | 2015-09-25 | 5 | 9 | 210 | 68.3167 | 2
2015-09-25 09:30 | 2015-09-25 | 5 | 9 | 205 | 68.5667 | 2
2015-09-25 09:45 | 2015-09-25 | 5 | 9 | 210 | 68.8167 | 2
2015-09-25 10:00 | 2015-09-25 | 5 | 10 | 202 | 69.2 | 2
2015-09-25 10:15 | 2015-09-25 | 5 | 10 | 205 | 69.95 | 2
2015-09-25 10:30 | 2015-09-25 | 5 | 10 | 207 | 70.7 | 3
2015-09-25 10:45 | 2015-09-25 | 5 | 10 | 213 | 71.45 | 3
2015-09-25 11:00 | 2015-09-25 | 5 | 11 | 209 | 72.0667 | 3
2015-09-25 11:15 | 2015-09-25 | 5 | 11 | 204 | 72.3167 | 3
2015-09-25 11:30 | 2015-09-25 | 5 | 11 | 221 | 72.5667 | 3
2015-09-25 11:45 | 2015-09-25 | 5 | 11 | 215 | 72.8167 | 3
2015-09-25 12:00 | 2015-09-25 | 5 | 12 | 227 | 72.9333 | 3
2015-09-25 12:15 | 2015-09-25 | 5 | 12 | 223 | 72.6833 | 3
2015-09-25 12:30 | 2015-09-25 | 5 | 12 | 217 | 72.4333 | 3
2015-09-25 12:45 | 2015-09-25 | 5 | 12 | 237 | 72.1833 | 3
2015-09-25 13:00 | 2015-09-25 | 5 | 13 | 235 | 72.0667 | 3
2015-09-25 13:15 | 2015-09-25 | 5 | 13 | 234 | 72.3167 | 3
2015-09-25 13:30 | 2015-09-25 | 5 | 13 | 229 | 72.5667 | 3
2015-09-25 13:45 | 2015-09-25 | 5 | 13 | 242 | 72.8167 | 3
2015-09-25 14:00 | 2015-09-25 | 5 | 14 | 243 | 72.8 | 3
2015-09-25 14:15 | 2015-09-25 | 5 | 14 | 255 | 72.05 | 3
2015-09-25 14:30 | 2015-09-25 | 5 | 14 | 251 | 71.3 | 3
2015-09-25 14:45 | 2015-09-25 | 5 | 14 | 243 | 70.55 | 3
2015-09-25 15:00 | 2015-09-25 | 5 | 15 | 238 | 70.1333 | 3
2015-09-25 15:15 | 2015-09-25 | 5 | 15 | 243 | 70.6333 | 3
2015-09-25 15:30 | 2015-09-25 | 5 | 15 | 242 | 71.1333 | 3
2015-09-25 15:45 | 2015-09-25 | 5 | 15 | 252 | 71.6333 | 3
2015-09-25 16:00 | 2015-09-25 | 5 | 16 | 236 | 71.8 | 3
2015-09-25 16:15 | 2015-09-25 | 5 | 16 | 231 | 71.05 | 3
2015-09-25 16:30 | 2015-09-25 | 5 | 16 | 208 | 70.3 | 3
2015-09-25 16:45 | 2015-09-25 | 5 | 16 | 208 | 69.55 | 2
2015-09-25 17:00 | 2015-09-25 | 5 | 17 | 232 | 68.7333 | 2
2015-09-25 17:15 | 2015-09-25 | 5 | 17 | 222 | 67.7333 | 2
2015-09-25 17:30 | 2015-09-25 | 5 | 17 | 219 | 66.7333 | 2
2015-09-25 17:45 | 2015-09-25 | 5 | 17 | 217 | 65.7333 | 2
2015-09-25 18:00 | 2015-09-25 | 5 | 18 | 229 | 64.8667 | 1
2015-09-25 18:15 | 2015-09-25 | 5 | 18 | 221 | 64.3667 | 1
2015-09-25 18:30 | 2015-09-25 | 5 | 18 | 204 | 63.8667 | 1
2015-09-25 18:45 | 2015-09-25 | 5 | 18 | 207 | 63.3667 | 1
2015-09-25 19:00 | 2015-09-25 | 5 | 19 | 197 | 62.9333 | 1
2015-09-25 19:15 | 2015-09-25 | 5 | 19 | 132 | 62.6833 | 1
2015-09-25 19:30 | 2015-09-25 | 5 | 19 | 120 | 62.4333 | 1
2015-09-25 19:45 | 2015-09-25 | 5 | 19 | 120 | 62.1833 | 1
2015-09-25 20:00 | 2015-09-25 | 5 | 20 | 116 | 62 | 1
2015-09-25 20:15 | 2015-09-25 | 5 | 20 | 126 | 62 | 1
2015-09-25 20:30 | 2015-09-25 | 5 | 20 | 123 | 62 | 1
2015-09-25 20:45 | 2015-09-25 | 5 | 20 | 123 | 62 | 1
2015-09-25 21:00 | 2015-09-25 | 5 | 21 | 122 | 62 | 1
2015-09-25 21:15 | 2015-09-25 | 5 | 21 | 111 | 62 | 1
2015-09-25 21:30 | 2015-09-25 | 5 | 21 | 111 | 62 | 1
2015-09-25 21:45 | 2015-09-25 | 5 | 21 | 113 | 62 | 1
2015-09-25 22:00 | 2015-09-25 | 5 | 22 | 107 | 61.9333 | 1
2015-09-25 22:15 | 2015-09-25 | 5 | 22 | 108 | 61.6833 | 1
2015-09-25 22:30 | 2015-09-25 | 5 | 22 | 112 | 61.4333 | 1
2015-09-25 22:45 | 2015-09-25 | 5 | 22 | 114 | 61.1833 | 1
2015-09-25 23:00 | 2015-09-25 | 5 | 23 | 110 | 61 | 1
2015-09-25 23:15 | 2015-09-25 | 5 | 23 | 110 | 61 | 1
2015-09-25 23:30 | 2015-09-25 | 5 | 23 | 106 | 61 | 1
2015-09-25 23:45 | 2015-09-25 | 5 | 23 | 109 | 61 | 1
2015-09-26 | 2015-09-26 | 6 | 0 | 109 | 60.9333 | 1
2015-09-26 00:15 | 2015-09-26 | 6 | 0 | 106 | 60.6833 | 1
2015-09-26 00:30 | 2015-09-26 | 6 | 0 | 113 | 60.4333 | 1
2015-09-26 00:45 | 2015-09-26 | 6 | 0 | 115 | 60.1833 | 1
2015-09-26 01:00 | 2015-09-26 | 6 | 1 | 105 | 59.9333 | 1
2015-09-26 01:15 | 2015-09-26 | 6 | 1 | 108 | 59.6833 | 1
2015-09-26 01:30 | 2015-09-26 | 6 | 1 | 114 | 59.4333 | 1
2015-09-26 01:45 | 2015-09-26 | 6 | 1 | 112 | 59.1833 | 1
2015-09-26 02:00 | 2015-09-26 | 6 | 2 | 109 | 58.9333 | 1
2015-09-26 02:15 | 2015-09-26 | 6 | 2 | 107 | 58.6833 | 1
2015-09-26 02:30 | 2015-09-26 | 6 | 2 | 107 | 58.4333 | 1
2015-09-26 02:45 | 2015-09-26 | 6 | 2 | 115 | 58.1833 | 1
2015-09-26 03:00 | 2015-09-26 | 6 | 3 | 105 | 57.9333 | 1
2015-09-26 03:15 | 2015-09-26 | 6 | 3 | 110 | 57.6833 | 1
2015-09-26 03:30 | 2015-09-26 | 6 | 3 | 105 | 57.4333 | 1
2015-09-26 03:45 | 2015-09-26 | 6 | 3 | 112 | 57.1833 | 1
2015-09-26 04:00 | 2015-09-26 | 6 | 4 | 107 | 57 | 1
2015-09-26 04:15 | 2015-09-26 | 6 | 4 | 112 | 57 | 1
2015-09-26 04:30 | 2015-09-26 | 6 | 4 | 110 | 57 | 1
2015-09-26 04:45 | 2015-09-26 | 6 | 4 | 107 | 57 | 1
2015-09-26 05:00 | 2015-09-26 | 6 | 5 | 105 | 57 | 1
2015-09-26 05:15 | 2015-09-26 | 6 | 5 | 116 | 57 | 1
2015-09-26 05:30 | 2015-09-26 | 6 | 5 | 107 | 57 | 1
2015-09-26 05:45 | 2015-09-26 | 6 | 5 | 107 | 57 | 1
2015-09-26 06:00 | 2015-09-26 | 6 | 6 | 105 | 57.0667 | 1
2015-09-26 06:15 | 2015-09-26 | 6 | 6 | 105 | 57.3167 | 1
2015-09-26 06:30 | 2015-09-26 | 6 | 6 | 109 | 57.5667 | 1
2015-09-26 06:45 | 2015-09-26 | 6 | 6 | 111 | 57.8167 | 1
2015-09-26 07:00 | 2015-09-26 | 6 | 7 | 110 | 58.2 | 1
2015-09-26 07:15 | 2015-09-26 | 6 | 7 | 110 | 58.95 | 1
2015-09-26 07:30 | 2015-09-26 | 6 | 7 | 109 | 59.7 | 1
2015-09-26 07:45 | 2015-09-26 | 6 | 7 | 108 | 60.45 | 1
2015-09-26 08:00 | 2015-09-26 | 6 | 8 | 102 | 61.1333 | 1
2015-09-26 08:15 | 2015-09-26 | 6 | 8 | 104 | 61.6333 | 1
2015-09-26 08:30 | 2015-09-26 | 6 | 8 | 108 | 62.1333 | 1
2015-09-26 08:45 | 2015-09-26 | 6 | 8 | 105 | 62.6333 | 1
2015-09-26 09:00 | 2015-09-26 | 6 | 9 | 108 | 63.0667 | 1
2015-09-26 09:15 | 2015-09-26 | 6 | 9 | 107 | 63.3167 | 1
2015-09-26 09:30 | 2015-09-26 | 6 | 9 | 105 | 63.5667 | 1
2015-09-26 09:45 | 2015-09-26 | 6 | 9 | 110 | 63.8167 | 1
2015-09-26 10:00 | 2015-09-26 | 6 | 10 | 109 | 64.3333 | 1
2015-09-26 10:15 | 2015-09-26 | 6 | 10 | 104 | 65.5833 | 2
2015-09-26 10:30 | 2015-09-26 | 6 | 10 | 107 | 66.8333 | 2
2015-09-26 10:45 | 2015-09-26 | 6 | 10 | 112 | 68.0833 | 2
2015-09-26 11:00 | 2015-09-26 | 6 | 11 | 107 | 69 | 2
2015-09-26 11:15 | 2015-09-26 | 6 | 11 | 104 | 69 | 2
2015-09-26 11:30 | 2015-09-26 | 6 | 11 | 111 | 69 | 2
2015-09-26 11:45 | 2015-09-26 | 6 | 11 | 104 | 69 | 2
2015-09-26 12:00 | 2015-09-26 | 6 | 12 | 107 | 69.0667 | 2
2015-09-26 12:15 | 2015-09-26 | 6 | 12 | 112 | 69.3167 | 2
2015-09-26 12:30 | 2015-09-26 | 6 | 12 | 107 | 69.5667 | 2
2015-09-26 12:45 | 2015-09-26 | 6 | 12 | 109 | 69.8167 | 2
2015-09-26 13:00 | 2015-09-26 | 6 | 13 | 107 | 70 | 2
2015-09-26 13:15 | 2015-09-26 | 6 | 13 | 118 | 70 | 2
2015-09-26 13:30 | 2015-09-26 | 6 | 13 | 110 | 70 | 2
2015-09-26 13:45 | 2015-09-26 | 6 | 13 | 110 | 70 | 2
2015-09-26 14:00 | 2015-09-26 | 6 | 14 | 110 | 70 | 2
2015-09-26 14:15 | 2015-09-26 | 6 | 14 | 113 | 70 | 2
2015-09-26 14:30 | 2015-09-26 | 6 | 14 | 107 | 70 | 2
2015-09-26 14:45 | 2015-09-26 | 6 | 14 | 111 | 70 | 2
2015-09-26 15:00 | 2015-09-26 | 6 | 15 | 107 | 70 | 2
2015-09-26 15:15 | 2015-09-26 | 6 | 15 | 113 | 70 | 2
2015-09-26 15:30 | 2015-09-26 | 6 | 15 | 110 | 70 | 2
2015-09-26 15:45 | 2015-09-26 | 6 | 15 | 106 | 70 | 2
2015-09-26 16:00 | 2015-09-26 | 6 | 16 | 105 | 69.8 | 2
2015-09-26 16:15 | 2015-09-26 | 6 | 16 | 105 | 69.05 | 2
2015-09-26 16:30 | 2015-09-26 | 6 | 16 | 107 | 68.3 | 2
2015-09-26 16:45 | 2015-09-26 | 6 | 16 | 109 | 67.55 | 2
2015-09-26 17:00 | 2015-09-26 | 6 | 17 | 109 | 66.7333 | 2
2015-09-26 17:15 | 2015-09-26 | 6 | 17 | 110 | 65.7333 | 2
2015-09-26 17:30 | 2015-09-26 | 6 | 17 | 106 | 64.7333 | 1
2015-09-26 17:45 | 2015-09-26 | 6 | 17 | 116 | 63.7333 | 1
2015-09-26 18:00 | 2015-09-26 | 6 | 18 | 109 | 62.9333 | 1
2015-09-26 18:15 | 2015-09-26 | 6 | 18 | 107 | 62.6833 | 1
2015-09-26 18:30 | 2015-09-26 | 6 | 18 | 106 | 62.4333 | 1
2015-09-26 18:45 | 2015-09-26 | 6 | 18 | 109 | 62.1833 | 1
2015-09-26 19:00 | 2015-09-26 | 6 | 19 | 113 | 61.9333 | 1
2015-09-26 19:15 | 2015-09-26 | 6 | 19 | 109 | 61.6833 | 1
2015-09-26 19:30 | 2015-09-26 | 6 | 19 | 115 | 61.4333 | 1
2015-09-26 19:45 | 2015-09-26 | 6 | 19 | 107 | 61.1833 | 1
2015-09-26 20:00 | 2015-09-26 | 6 | 20 | 109 | 60.9333 | 1
2015-09-26 20:15 | 2015-09-26 | 6 | 20 | 114 | 60.6833 | 1
2015-09-26 20:30 | 2015-09-26 | 6 | 20 | 110 | 60.4333 | 1
2015-09-26 20:45 | 2015-09-26 | 6 | 20 | 109 | 60.1833 | 1
2015-09-26 21:00 | 2015-09-26 | 6 | 21 | 108 | 60 | 1
2015-09-26 21:15 | 2015-09-26 | 6 | 21 | 108 | 60 | 1
2015-09-26 21:30 | 2015-09-26 | 6 | 21 | 111 | 60 | 1
2015-09-26 21:45 | 2015-09-26 | 6 | 21 | 110 | 60 | 1
2015-09-26 22:00 | 2015-09-26 | 6 | 22 | 108 | 59.9333 | 1
2015-09-26 22:15 | 2015-09-26 | 6 | 22 | 107 | 59.6833 | 1
2015-09-26 22:30 | 2015-09-26 | 6 | 22 | 113 | 59.4333 | 1
2015-09-26 22:45 | 2015-09-26 | 6 | 22 | 108 | 59.1833 | 1
2015-09-26 23:00 | 2015-09-26 | 6 | 23 | 110 | 59 | 1
2015-09-26 23:15 | 2015-09-26 | 6 | 23 | 106 | 59 | 1
2015-09-26 23:30 | 2015-09-26 | 6 | 23 | 108 | 59 | 1
2015-09-26 23:45 | 2015-09-26 | 6 | 23 | 107 | 59 | 1
2015-09-27 | 2015-09-27 | 7 | 0 | 110 | 59 | 1
2015-09-27 00:15 | 2015-09-27 | 7 | 0 | 112 | 59 | 1
2015-09-27 00:30 | 2015-09-27 | 7 | 0 | 111 | 59 | 1
2015-09-27 00:45 | 2015-09-27 | 7 | 0 | 110 | 59 | 1
2015-09-27 01:00 | 2015-09-27 | 7 | 1 | 108 | 58.9333 | 1
2015-09-27 01:15 | 2015-09-27 | 7 | 1 | 112 | 58.6833 | 1
2015-09-27 01:30 | 2015-09-27 | 7 | 1 | 109 | 58.4333 | 1
2015-09-27 01:45 | 2015-09-27 | 7 | 1 | 108 | 58.1833 | 1
2015-09-27 02:00 | 2015-09-27 | 7 | 2 | 105 | 58 | 1
2015-09-27 02:15 | 2015-09-27 | 7 | 2 | 112 | 58 | 1
2015-09-27 02:30 | 2015-09-27 | 7 | 2 | 110 | 58 | 1
2015-09-27 02:45 | 2015-09-27 | 7 | 2 | 110 | 58 | 1
2015-09-27 03:00 | 2015-09-27 | 7 | 3 | 108 | 58 | 1
2015-09-27 03:15 | 2015-09-27 | 7 | 3 | 105 | 58 | 1
2015-09-27 03:30 | 2015-09-27 | 7 | 3 | 105 | 58 | 1
2015-09-27 03:45 | 2015-09-27 | 7 | 3 | 107 | 58 | 1
2015-09-27 04:00 | 2015-09-27 | 7 | 4 | 104 | 57.9333 | 1
2015-09-27 04:15 | 2015-09-27 | 7 | 4 | 110 | 57.6833 | 1
2015-09-27 04:30 | 2015-09-27 | 7 | 4 | 119 | 57.4333 | 1
2015-09-27 04:45 | 2015-09-27 | 7 | 4 | 106 | 57.1833 | 1
2015-09-27 05:00 | 2015-09-27 | 7 | 5 | 111 | 57 | 1
2015-09-27 05:15 | 2015-09-27 | 7 | 5 | 111 | 57 | 1
2015-09-27 05:30 | 2015-09-27 | 7 | 5 | 105 | 57 | 1
2015-09-27 05:45 | 2015-09-27 | 7 | 5 | 105 | 57 | 1
2015-09-27 06:00 | 2015-09-27 | 7 | 6 | 107 | 57.0667 | 1
2015-09-27 06:15 | 2015-09-27 | 7 | 6 | 108 | 57.3167 | 1
2015-09-27 06:30 | 2015-09-27 | 7 | 6 | 107 | 57.5667 | 1
2015-09-27 06:45 | 2015-09-27 | 7 | 6 | 109 | 57.8167 | 1
2015-09-27 07:00 | 2015-09-27 | 7 | 7 | 116 | 58.2667 | 1
2015-09-27 07:15 | 2015-09-27 | 7 | 7 | 117 | 59.2667 | 1
2015-09-27 07:30 | 2015-09-27 | 7 | 7 | 109 | 60.2667 | 1
2015-09-27 07:45 | 2015-09-27 | 7 | 7 | 119 | 61.2667 | 1
2015-09-27 08:00 | 2015-09-27 | 7 | 8 | 113 | 62.2 | 1
2015-09-27 08:15 | 2015-09-27 | 7 | 8 | 117 | 62.95 | 1
2015-09-27 08:30 | 2015-09-27 | 7 | 8 | 114 | 63.7 | 1
2015-09-27 08:45 | 2015-09-27 | 7 | 8 | 108 | 64.45 | 1
2015-09-27 09:00 | 2015-09-27 | 7 | 9 | 118 | 65.1333 | 2
2015-09-27 09:15 | 2015-09-27 | 7 | 9 | 109 | 65.6333 | 2
2015-09-27 09:30 | 2015-09-27 | 7 | 9 | 111 | 66.1333 | 2
2015-09-27 09:45 | 2015-09-27 | 7 | 9 | 108 | 66.6333 | 2
2015-09-27 10:00 | 2015-09-27 | 7 | 10 | 111 | 67 | 2
2015-09-27 10:15 | 2015-09-27 | 7 | 10 | 111 | 67 | 2
2015-09-27 10:30 | 2015-09-27 | 7 | 10 | 116 | 67 | 2
2015-09-27 10:45 | 2015-09-27 | 7 | 10 | 113 | 67 | 2
2015-09-27 11:00 | 2015-09-27 | 7 | 11 | 110 | 67.1333 | 2
2015-09-27 11:15 | 2015-09-27 | 7 | 11 | 114 | 67.6333 | 2
2015-09-27 11:30 | 2015-09-27 | 7 | 11 | 107 | 68.1333 | 2
2015-09-27 11:45 | 2015-09-27 | 7 | 11 | 115 | 68.6333 | 2
2015-09-27 12:00 | 2015-09-27 | 7 | 12 | 117 | 69 | 2
2015-09-27 12:15 | 2015-09-27 | 7 | 12 | 117 | 69 | 2
2015-09-27 12:30 | 2015-09-27 | 7 | 12 | 112 | 69 | 2
2015-09-27 12:45 | 2015-09-27 | 7 | 12 | 115 | 69 | 2
2015-09-27 13:00 | 2015-09-27 | 7 | 13 | 113 | 69 | 2
2015-09-27 13:15 | 2015-09-27 | 7 | 13 | 112 | 69 | 2
2015-09-27 13:30 | 2015-09-27 | 7 | 13 | 111 | 69 | 2
2015-09-27 13:45 | 2015-09-27 | 7 | 13 | 110 | 69 | 2
2015-09-27 14:00 | 2015-09-27 | 7 | 14 | 117 | 68.8667 | 2
2015-09-27 14:15 | 2015-09-27 | 7 | 14 | 116 | 68.3667 | 2
2015-09-27 14:30 | 2015-09-27 | 7 | 14 | 116 | 67.8667 | 2
2015-09-27 14:45 | 2015-09-27 | 7 | 14 | 114 | 67.3667 | 2
2015-09-27 15:00 | 2015-09-27 | 7 | 15 | 119 | 67.1333 | 2
2015-09-27 15:15 | 2015-09-27 | 7 | 15 | 119 | 67.6333 | 2
2015-09-27 15:30 | 2015-09-27 | 7 | 15 | 116 | 68.1333 | 2
2015-09-27 15:45 | 2015-09-27 | 7 | 15 | 115 | 68.6333 | 2
2015-09-27 16:00 | 2015-09-27 | 7 | 16 | 109 | 68.8667 | 2
2015-09-27 16:15 | 2015-09-27 | 7 | 16 | 114 | 68.3667 | 2
2015-09-27 16:30 | 2015-09-27 | 7 | 16 | 113 | 67.8667 | 2
2015-09-27 16:45 | 2015-09-27 | 7 | 16 | 111 | 67.3667 | 2
2015-09-27 17:00 | 2015-09-27 | 7 | 17 | 111 | 66.6667 | 2
2015-09-27 17:15 | 2015-09-27 | 7 | 17 | 113 | 65.4167 | 2
2015-09-27 17:30 | 2015-09-27 | 7 | 17 | 120 | 64.1667 | 1
2015-09-27 17:45 | 2015-09-27 | 7 | 17 | 115 | 62.9167 | 1
2015-09-27 18:00 | 2015-09-27 | 7 | 18 | 115 | 61.9333 | 1
2015-09-27 18:15 | 2015-09-27 | 7 | 18 | 117 | 61.6833 | 1
2015-09-27 18:30 | 2015-09-27 | 7 | 18 | 112 | 61.4333 | 1
2015-09-27 18:45 | 2015-09-27 | 7 | 18 | 121 | 61.1833 | 1
2015-09-27 19:00 | 2015-09-27 | 7 | 19 | 112 | 61 | 1
2015-09-27 19:15 | 2015-09-27 | 7 | 19 | 116 | 61 | 1
2015-09-27 19:30 | 2015-09-27 | 7 | 19 | 110 | 61 | 1
2015-09-27 19:45 | 2015-09-27 | 7 | 19 | 113 | 61 | 1
2015-09-27 20:00 | 2015-09-27 | 7 | 20 | 113 | 60.9333 | 1
2015-09-27 20:15 | 2015-09-27 | 7 | 20 | 113 | 60.6833 | 1
2015-09-27 20:30 | 2015-09-27 | 7 | 20 | 115 | 60.4333 | 1
2015-09-27 20:45 | 2015-09-27 | 7 | 20 | 114 | 60.1833 | 1
2015-09-27 21:00 | 2015-09-27 | 7 | 21 | 123 | 59.9333 | 1
2015-09-27 21:15 | 2015-09-27 | 7 | 21 | 107 | 59.6833 | 1
2015-09-27 21:30 | 2015-09-27 | 7 | 21 | 108 | 59.4333 | 1
2015-09-27 21:45 | 2015-09-27 | 7 | 21 | 103 | 59.1833 | 1
2015-09-27 22:00 | 2015-09-27 | 7 | 22 | 106 | 58.8667 | 1
2015-09-27 22:15 | 2015-09-27 | 7 | 22 | 104 | 58.3667 | 1
2015-09-27 22:30 | 2015-09-27 | 7 | 22 | 103 | 57.8667 | 1
2015-09-27 22:45 | 2015-09-27 | 7 | 22 | 103 | 57.3667 | 1
2015-09-27 23:00 | 2015-09-27 | 7 | 23 | 97 | 57 | 1
2015-09-27 23:15 | 2015-09-27 | 7 | 23 | 101 | 57 | 1
2015-09-27 23:30 | 2015-09-27 | 7 | 23 | 105 | 57 | 1
2015-09-27 23:45 | 2015-09-27 | 7 | 23 | 99 | 57 | 1
2015-09-28 | 2015-09-28 | 1 | 0 | 100 | 56.9333 | 1
2015-09-28 00:15 | 2015-09-28 | 1 | 0 | 101 | 56.6833 | 1
2015-09-28 00:30 | 2015-09-28 | 1 | 0 | 101 | 56.4333 | 1
2015-09-28 00:45 | 2015-09-28 | 1 | 0 | 101 | 56.1833 | 1
2015-09-28 01:00 | 2015-09-28 | 1 | 1 | 104 | 56 | 1
2015-09-28 01:15 | 2015-09-28 | 1 | 1 | 102 | 56 | 1
2015-09-28 01:30 | 2015-09-28 | 1 | 1 | 104 | 56 | 1
2015-09-28 01:45 | 2015-09-28 | 1 | 1 | 98 | 56 | 1
2015-09-28 02:00 | 2015-09-28 | 1 | 2 | 100 | 56 | 1
2015-09-28 02:15 | 2015-09-28 | 1 | 2 | 107 | 56 | 1
2015-09-28 02:30 | 2015-09-28 | 1 | 2 | 97 | 56 | 1
2015-09-28 02:45 | 2015-09-28 | 1 | 2 | 100 | 56 | 1
2015-09-28 03:00 | 2015-09-28 | 1 | 3 | 99 | 56 | 1
2015-09-28 03:15 | 2015-09-28 | 1 | 3 | 105 | 56 | 1
2015-09-28 03:30 | 2015-09-28 | 1 | 3 | 102 | 56 | 1
2015-09-28 03:45 | 2015-09-28 | 1 | 3 | 98 | 56 | 1
2015-09-28 04:00 | 2015-09-28 | 1 | 4 | 101 | 56 | 1
2015-09-28 04:15 | 2015-09-28 | 1 | 4 | 102 | 56 | 1
2015-09-28 04:30 | 2015-09-28 | 1 | 4 | 97 | 56 | 1
2015-09-28 04:45 | 2015-09-28 | 1 | 4 | 102 | 56 | 1
2015-09-28 05:00 | 2015-09-28 | 1 | 5 | 99 | 56 | 1
2015-09-28 05:15 | 2015-09-28 | 1 | 5 | 101 | 56 | 1
2015-09-28 05:30 | 2015-09-28 | 1 | 5 | 105 | 56 | 1
2015-09-28 05:45 | 2015-09-28 | 1 | 5 | 101 | 56 | 1
2015-09-28 06:00 | 2015-09-28 | 1 | 6 | 104 | 56.0667 | 1
2015-09-28 06:15 | 2015-09-28 | 1 | 6 | 99 | 56.3167 | 1
2015-09-28 06:30 | 2015-09-28 | 1 | 6 | 100 | 56.5667 | 1
2015-09-28 06:45 | 2015-09-28 | 1 | 6 | 106 | 56.8167 | 1
2015-09-28 07:00 | 2015-09-28 | 1 | 7 | 102 | 57.1333 | 1
2015-09-28 07:15 | 2015-09-28 | 1 | 7 | 234 | 57.6333 | 1
2015-09-28 07:30 | 2015-09-28 | 1 | 7 | 262 | 58.1333 | 1
2015-09-28 07:45 | 2015-09-28 | 1 | 7 | 241 | 58.6333 | 1
2015-09-28 08:00 | 2015-09-28 | 1 | 8 | 232 | 59.1333 | 1
2015-09-28 08:15 | 2015-09-28 | 1 | 8 | 222 | 59.6333 | 1
2015-09-28 08:30 | 2015-09-28 | 1 | 8 | 205 | 60.1333 | 1
2015-09-28 08:45 | 2015-09-28 | 1 | 8 | 219 | 60.6333 | 1
2015-09-28 09:00 | 2015-09-28 | 1 | 9 | 215 | 61.0667 | 1
2015-09-28 09:15 | 2015-09-28 | 1 | 9 | 215 | 61.3167 | 1
2015-09-28 09:30 | 2015-09-28 | 1 | 9 | 217 | 61.5667 | 1
2015-09-28 09:45 | 2015-09-28 | 1 | 9 | 221 | 61.8167 | 1
2015-09-28 10:00 | 2015-09-28 | 1 | 10 | 222 | 62.2 | 1
2015-09-28 10:15 | 2015-09-28 | 1 | 10 | 221 | 62.95 | 1
2015-09-28 10:30 | 2015-09-28 | 1 | 10 | 217 | 63.7 | 1
2015-09-28 10:45 | 2015-09-28 | 1 | 10 | 204 | 64.45 | 1
2015-09-28 11:00 | 2015-09-28 | 1 | 11 | 218 | 65.0667 | 2
2015-09-28 11:15 | 2015-09-28 | 1 | 11 | 224 | 65.3167 | 2
2015-09-28 11:30 | 2015-09-28 | 1 | 11 | 233 | 65.5667 | 2
2015-09-28 11:45 | 2015-09-28 | 1 | 11 | 220 | 65.8167 | 2
2015-09-28 12:00 | 2015-09-28 | 1 | 12 | 229 | 66.1333 | 2
2015-09-28 12:15 | 2015-09-28 | 1 | 12 | 224 | 66.6333 | 2
2015-09-28 12:30 | 2015-09-28 | 1 | 12 | 246 | 67.1333 | 2
2015-09-28 12:45 | 2015-09-28 | 1 | 12 | 235 | 67.6333 | 2
2015-09-28 13:00 | 2015-09-28 | 1 | 13 | 230 | 68.0667 | 2
2015-09-28 13:15 | 2015-09-28 | 1 | 13 | 236 | 68.3167 | 2
2015-09-28 13:30 | 2015-09-28 | 1 | 13 | 245 | 68.5667 | 2
2015-09-28 13:45 | 2015-09-28 | 1 | 13 | 248 | 68.8167 | 2
2015-09-28 14:00 | 2015-09-28 | 1 | 14 | 260 | 69 | 2
2015-09-28 14:15 | 2015-09-28 | 1 | 14 | 245 | 69 | 2
2015-09-28 14:30 | 2015-09-28 | 1 | 14 | 258 | 69 | 2
2015-09-28 14:45 | 2015-09-28 | 1 | 14 | 241 | 69 | 2
2015-09-28 15:00 | 2015-09-28 | 1 | 15 | 242 | 68.8667 | 2
2015-09-28 15:15 | 2015-09-28 | 1 | 15 | 232 | 68.3667 | 2
2015-09-28 15:30 | 2015-09-28 | 1 | 15 | 246 | 67.8667 | 2
2015-09-28 15:45 | 2015-09-28 | 1 | 15 | 243 | 67.3667 | 2
2015-09-28 16:00 | 2015-09-28 | 1 | 16 | 236 | 66.8 | 2
2015-09-28 16:15 | 2015-09-28 | 1 | 16 | 231 | 66.05 | 2
2015-09-28 16:30 | 2015-09-28 | 1 | 16 | 227 | 65.3 | 2
2015-09-28 16:45 | 2015-09-28 | 1 | 16 | 241 | 64.55 | 1
2015-09-28 17:00 | 2015-09-28 | 1 | 17 | 242 | 63.8667 | 1
2015-09-28 17:15 | 2015-09-28 | 1 | 17 | 234 | 63.3667 | 1
2015-09-28 17:30 | 2015-09-28 | 1 | 17 | 233 | 62.8667 | 1
2015-09-28 17:45 | 2015-09-28 | 1 | 17 | 233 | 62.3667 | 1
2015-09-28 18:00 | 2015-09-28 | 1 | 18 | 228 | 61.9333 | 1
2015-09-28 18:15 | 2015-09-28 | 1 | 18 | 230 | 61.6833 | 1
2015-09-28 18:30 | 2015-09-28 | 1 | 18 | 234 | 61.4333 | 1
2015-09-28 18:45 | 2015-09-28 | 1 | 18 | 214 | 61.1833 | 1
2015-09-28 19:00 | 2015-09-28 | 1 | 19 | 200 | 60.9333 | 1
2015-09-28 19:15 | 2015-09-28 | 1 | 19 | 122 | 60.6833 | 1
2015-09-28 19:30 | 2015-09-28 | 1 | 19 | 131 | 60.4333 | 1
2015-09-28 19:45 | 2015-09-28 | 1 | 19 | 133 | 60.1833 | 1
2015-09-28 20:00 | 2015-09-28 | 1 | 20 | 128 | 60 | 1
2015-09-28 20:15 | 2015-09-28 | 1 | 20 | 126 | 60 | 1
2015-09-28 20:30 | 2015-09-28 | 1 | 20 | 124 | 60 | 1
2015-09-28 20:45 | 2015-09-28 | 1 | 20 | 127 | 60 | 1
2015-09-28 21:00 | 2015-09-28 | 1 | 21 | 126 | 59.9333 | 1
2015-09-28 21:15 | 2015-09-28 | 1 | 21 | 115 | 59.6833 | 1
2015-09-28 21:30 | 2015-09-28 | 1 | 21 | 109 | 59.4333 | 1
2015-09-28 21:45 | 2015-09-28 | 1 | 21 | 117 | 59.1833 | 1
2015-09-28 22:00 | 2015-09-28 | 1 | 22 | 121 | 59.0667 | 1
2015-09-28 22:15 | 2015-09-28 | 1 | 22 | 111 | 59.3167 | 1
2015-09-28 22:30 | 2015-09-28 | 1 | 22 | 118 | 59.5667 | 1
2015-09-28 22:45 | 2015-09-28 | 1 | 22 | 119 | 59.8167 | 1
2015-09-28 23:00 | 2015-09-28 | 1 | 23 | 116 | 59.9333 | 1
2015-09-28 23:15 | 2015-09-28 | 1 | 23 | 128 | 59.6833 | 1
2015-09-28 23:30 | 2015-09-28 | 1 | 23 | 120 | 59.4333 | 1
2015-09-28 23:45 | 2015-09-28 | 1 | 23 | 119 | 59.1833 | 1
2015-09-29 | 2015-09-29 | 2 | 0 | 117 | 59 | 1
2015-09-29 00:15 | 2015-09-29 | 2 | 0 | 120 | 59 | 1
2015-09-29 00:30 | 2015-09-29 | 2 | 0 | 118 | 59 | 1
2015-09-29 00:45 | 2015-09-29 | 2 | 0 | 106 | 59 | 1
2015-09-29 01:00 | 2015-09-29 | 2 | 1 | 109 | 58.9333 | 1
2015-09-29 01:15 | 2015-09-29 | 2 | 1 | 109 | 58.6833 | 1
2015-09-29 01:30 | 2015-09-29 | 2 | 1 | 112 | 58.4333 | 1
2015-09-29 01:45 | 2015-09-29 | 2 | 1 | 111 | 58.1833 | 1
2015-09-29 02:00 | 2015-09-29 | 2 | 2 | 108 | 58 | 1
2015-09-29 02:15 | 2015-09-29 | 2 | 2 | 111 | 58 | 1
2015-09-29 02:30 | 2015-09-29 | 2 | 2 | 110 | 58 | 1
2015-09-29 02:45 | 2015-09-29 | 2 | 2 | 113 | 58 | 1
2015-09-29 03:00 | 2015-09-29 | 2 | 3 | 109 | 58 | 1
2015-09-29 03:15 | 2015-09-29 | 2 | 3 | 113 | 58 | 1
2015-09-29 03:30 | 2015-09-29 | 2 | 3 | 104 | 58 | 1
2015-09-29 03:45 | 2015-09-29 | 2 | 3 | 112 | 58 | 1
2015-09-29 04:00 | 2015-09-29 | 2 | 4 | 112 | 58 | 1
2015-09-29 04:15 | 2015-09-29 | 2 | 4 | 108 | 58 | 1
2015-09-29 04:30 | 2015-09-29 | 2 | 4 | 106 | 58 | 1
2015-09-29 04:45 | 2015-09-29 | 2 | 4 | 114 | 58 | 1
2015-09-29 05:00 | 2015-09-29 | 2 | 5 | 107 | 58.0667 | 1
2015-09-29 05:15 | 2015-09-29 | 2 | 5 | 111 | 58.3167 | 1
2015-09-29 05:30 | 2015-09-29 | 2 | 5 | 109 | 58.5667 | 1
2015-09-29 05:45 | 2015-09-29 | 2 | 5 | 104 | 58.8167 | 1
2015-09-29 06:00 | 2015-09-29 | 2 | 6 | 116 | 59 | 1
2015-09-29 06:15 | 2015-09-29 | 2 | 6 | 109 | 59 | 1
2015-09-29 06:30 | 2015-09-29 | 2 | 6 | 108 | 59 | 1
2015-09-29 06:45 | 2015-09-29 | 2 | 6 | 105 | 59 | 1
2015-09-29 07:00 | 2015-09-29 | 2 | 7 | 108 | 59.1379 | 1
2015-09-29 07:15 | 2015-09-29 | 2 | 7 | 243 | 59.6552 | 1
2015-09-29 07:30 | 2015-09-29 | 2 | 7 | 208 | 60.1724 | 1
2015-09-29 07:45 | 2015-09-29 | 2 | 7 | 172 | 60.6897 | 1
2015-09-29 08:00 | 2015-09-29 | 2 | 8 | 171 | 61.1379 | 1
2015-09-29 08:15 | 2015-09-29 | 2 | 8 | 166 | 61.6552 | 1
2015-09-29 08:30 | 2015-09-29 | 2 | 8 | 187 | 62.1724 | 1
2015-09-29 08:45 | 2015-09-29 | 2 | 8 | 188 | 62.6897 | 1
2015-09-29 09:00 | 2015-09-29 | 2 | 9 | 174 | 62 | 1
2015-09-29 09:15 | 2015-09-29 | 2 | 9 | 175 | 62 | 1
2015-09-29 09:30 | 2015-09-29 | 2 | 9 | 190 | 62 | 1
2015-09-29 09:45 | 2015-09-29 | 2 | 9 | 201 | 62 | 1
2015-09-29 10:00 | 2015-09-29 | 2 | 10 | 202 | 62.2667 | 1
2015-09-29 10:15 | 2015-09-29 | 2 | 10 | 201 | 63.2667 | 1
2015-09-29 10:30 | 2015-09-29 | 2 | 10 | 201 | 64.2667 | 1
2015-09-29 10:45 | 2015-09-29 | 2 | 10 | 202 | 65.2667 | 2
2015-09-29 11:00 | 2015-09-29 | 2 | 11 | 205 | 66.0667 | 2
2015-09-29 11:15 | 2015-09-29 | 2 | 11 | 218 | 66.3167 | 2
2015-09-29 11:30 | 2015-09-29 | 2 | 11 | 227 | 66.5667 | 2
2015-09-29 11:45 | 2015-09-29 | 2 | 11 | 221 | 66.8167 | 2
2015-09-29 12:00 | 2015-09-29 | 2 | 12 | 210 | 67 | 2
2015-09-29 12:15 | 2015-09-29 | 2 | 12 | 218 | 67 | 2
2015-09-29 12:30 | 2015-09-29 | 2 | 12 | 211 | 67 | 2
2015-09-29 12:45 | 2015-09-29 | 2 | 12 | 223 | 67 | 2
2015-09-29 13:00 | 2015-09-29 | 2 | 13 | 212 | 66.9333 | 2
2015-09-29 13:15 | 2015-09-29 | 2 | 13 | 208 | 66.6833 | 2
2015-09-29 13:30 | 2015-09-29 | 2 | 13 | 217 | 66.4333 | 2
2015-09-29 13:45 | 2015-09-29 | 2 | 13 | 219 | 66.1833 | 2
2015-09-29 14:00 | 2015-09-29 | 2 | 14 | 228 | 66 | 2
2015-09-29 14:15 | 2015-09-29 | 2 | 14 | 211 | 66 | 2
2015-09-29 14:30 | 2015-09-29 | 2 | 14 | 218 | 66 | 2
2015-09-29 14:45 | 2015-09-29 | 2 | 14 | 210 | 66 | 2
2015-09-29 15:00 | 2015-09-29 | 2 | 15 | 208 | 65.8667 | 2
2015-09-29 15:15 | 2015-09-29 | 2 | 15 | 220 | 65.3667 | 2
2015-09-29 15:30 | 2015-09-29 | 2 | 15 | 220 | 64.8667 | 1
2015-09-29 15:45 | 2015-09-29 | 2 | 15 | 212 | 64.3667 | 1
2015-09-29 16:00 | 2015-09-29 | 2 | 16 | 213 | 63.8667 | 1
2015-09-29 16:15 | 2015-09-29 | 2 | 16 | 223 | 63.3667 | 1
2015-09-29 16:30 | 2015-09-29 | 2 | 16 | 216 | 62.8667 | 1
2015-09-29 16:45 | 2015-09-29 | 2 | 16 | 221 | 62.3667 | 1
2015-09-29 17:00 | 2015-09-29 | 2 | 17 | 212 | 61.8667 | 1
2015-09-29 17:15 | 2015-09-29 | 2 | 17 | 212 | 61.3667 | 1
2015-09-29 17:30 | 2015-09-29 | 2 | 17 | 200 | 60.8667 | 1
2015-09-29 17:45 | 2015-09-29 | 2 | 17 | 204 | 60.3667 | 1
2015-09-29 18:00 | 2015-09-29 | 2 | 18 | 208 | 60 | 1
2015-09-29 18:15 | 2015-09-29 | 2 | 18 | 203 | 60 | 1
2015-09-29 18:30 | 2015-09-29 | 2 | 18 | 199 | 60 | 1
2015-09-29 18:45 | 2015-09-29 | 2 | 18 | 196 | 60 | 1
2015-09-29 19:00 | 2015-09-29 | 2 | 19 | 186 | 60 | 1
2015-09-29 19:15 | 2015-09-29 | 2 | 19 | 131 | 60 | 1
2015-09-29 19:30 | 2015-09-29 | 2 | 19 | 135 | 60 | 1
2015-09-29 19:45 | 2015-09-29 | 2 | 19 | 121 | 60 | 1
2015-09-29 20:00 | 2015-09-29 | 2 | 20 | 121 | 59.9333 | 1
2015-09-29 20:15 | 2015-09-29 | 2 | 20 | 122 | 59.6833 | 1
2015-09-29 20:30 | 2015-09-29 | 2 | 20 | 129 | 59.4333 | 1
2015-09-29 20:45 | 2015-09-29 | 2 | 20 | 122 | 59.1833 | 1
2015-09-29 21:00 | 2015-09-29 | 2 | 21 | 122 | 59 | 1
2015-09-29 21:15 | 2015-09-29 | 2 | 21 | 120 | 59 | 1
2015-09-29 21:30 | 2015-09-29 | 2 | 21 | 116 | 59 | 1
2015-09-29 21:45 | 2015-09-29 | 2 | 21 | 123 | 59 | 1
2015-09-29 22:00 | 2015-09-29 | 2 | 22 | 118 | 59 | 1
2015-09-29 22:15 | 2015-09-29 | 2 | 22 | 118 | 59 | 1
2015-09-29 22:30 | 2015-09-29 | 2 | 22 | 114 | 59 | 1
2015-09-29 22:45 | 2015-09-29 | 2 | 22 | 125 | 59 | 1
2015-09-29 23:00 | 2015-09-29 | 2 | 23 | 119 | 59 | 1
2015-09-29 23:15 | 2015-09-29 | 2 | 23 | 123 | 59 | 1
2015-09-29 23:30 | 2015-09-29 | 2 | 23 | 131 | 59 | 1
2015-09-29 23:45 | 2015-09-29 | 2 | 23 | 119 | 59 | 1
2015-09-30 | 2015-09-30 | 3 | 0 | 129 | 59 | 1
2015-09-30 00:15 | 2015-09-30 | 3 | 0 | 124 | 59 | 1
2015-09-30 00:30 | 2015-09-30 | 3 | 0 | 118 | 59 | 1
2015-09-30 00:45 | 2015-09-30 | 3 | 0 | 118 | 59 | 1
2015-09-30 01:00 | 2015-09-30 | 3 | 1 | 118 | 59 | 1
2015-09-30 01:15 | 2015-09-30 | 3 | 1 | 120 | 59 | 1
2015-09-30 01:30 | 2015-09-30 | 3 | 1 | 111 | 59 | 1
2015-09-30 01:45 | 2015-09-30 | 3 | 1 | 109 | 59 | 1
2015-09-30 02:00 | 2015-09-30 | 3 | 2 | 107 | 59 | 1
2015-09-30 02:15 | 2015-09-30 | 3 | 2 | 110 | 59 | 1
2015-09-30 02:30 | 2015-09-30 | 3 | 2 | 114 | 59 | 1
2015-09-30 02:45 | 2015-09-30 | 3 | 2 | 111 | 59 | 1
2015-09-30 03:00 | 2015-09-30 | 3 | 3 | 108 | 58.9333 | 1
2015-09-30 03:15 | 2015-09-30 | 3 | 3 | 103 | 58.6833 | 1
2015-09-30 03:30 | 2015-09-30 | 3 | 3 | 111 | 58.4333 | 1
2015-09-30 03:45 | 2015-09-30 | 3 | 3 | 105 | 58.1833 | 1
2015-09-30 04:00 | 2015-09-30 | 3 | 4 | 114 | 58.0667 | 1
2015-09-30 04:15 | 2015-09-30 | 3 | 4 | 110 | 58.3167 | 1
2015-09-30 04:30 | 2015-09-30 | 3 | 4 | 109 | 58.5667 | 1
2015-09-30 04:45 | 2015-09-30 | 3 | 4 | 107 | 58.8167 | 1
2015-09-30 05:00 | 2015-09-30 | 3 | 5 | 110 | 59 | 1
2015-09-30 05:15 | 2015-09-30 | 3 | 5 | 117 | 59 | 1
2015-09-30 05:30 | 2015-09-30 | 3 | 5 | 109 | 59 | 1
2015-09-30 05:45 | 2015-09-30 | 3 | 5 | 105 | 59 | 1
2015-09-30 06:00 | 2015-09-30 | 3 | 6 | 112 | 59 | 1
2015-09-30 06:15 | 2015-09-30 | 3 | 6 | 118 | 59 | 1
2015-09-30 06:30 | 2015-09-30 | 3 | 6 | 113 | 59 | 1
2015-09-30 06:45 | 2015-09-30 | 3 | 6 | 118 | 59 | 1
2015-09-30 07:00 | 2015-09-30 | 3 | 7 | 111 | 59 | 1
2015-09-30 07:15 | 2015-09-30 | 3 | 7 | 210 | 59 | 1
2015-09-30 07:30 | 2015-09-30 | 3 | 7 | 197 | 59 | 1
2015-09-30 07:45 | 2015-09-30 | 3 | 7 | 170 | 59 | 1
2015-09-30 08:00 | 2015-09-30 | 3 | 8 | 173 | 59.0667 | 1
2015-09-30 08:15 | 2015-09-30 | 3 | 8 | 179 | 59.3167 | 1
2015-09-30 08:30 | 2015-09-30 | 3 | 8 | 184 | 59.5667 | 1
2015-09-30 08:45 | 2015-09-30 | 3 | 8 | 174 | 59.8167 | 1
2015-09-30 09:00 | 2015-09-30 | 3 | 9 | 183 | 60.0667 | 1
2015-09-30 09:15 | 2015-09-30 | 3 | 9 | 184 | 60.3167 | 1
2015-09-30 09:30 | 2015-09-30 | 3 | 9 | 189 | 60.5667 | 1
2015-09-30 09:45 | 2015-09-30 | 3 | 9 | 194 | 60.8167 | 1
2015-09-30 10:00 | 2015-09-30 | 3 | 10 | 201 | 61 | 1
2015-09-30 10:15 | 2015-09-30 | 3 | 10 | 191 | 61 | 1
2015-09-30 10:30 | 2015-09-30 | 3 | 10 | 192 | 61 | 1
2015-09-30 10:45 | 2015-09-30 | 3 | 10 | 194 | 61 | 1
2015-09-30 11:00 | 2015-09-30 | 3 | 11 | 209 | 61 | 1
2015-09-30 11:15 | 2015-09-30 | 3 | 11 | 198 | 61 | 1
2015-09-30 11:30 | 2015-09-30 | 3 | 11 | 202 | 61 | 1
2015-09-30 11:45 | 2015-09-30 | 3 | 11 | 211 | 61 | 1
2015-09-30 12:00 | 2015-09-30 | 3 | 12 | 207 | 61.0667 | 1
2015-09-30 12:15 | 2015-09-30 | 3 | 12 | 192 | 61.3167 | 1
2015-09-30 12:30 | 2015-09-30 | 3 | 12 | 192 | 61.5667 | 1
2015-09-30 12:45 | 2015-09-30 | 3 | 12 | 193 | 61.8167 | 1
2015-09-30 13:00 | 2015-09-30 | 3 | 13 | 189 | 62.0667 | 1
2015-09-30 13:15 | 2015-09-30 | 3 | 13 | 186 | 62.3167 | 1
2015-09-30 13:30 | 2015-09-30 | 3 | 13 | 193 | 62.5667 | 1
2015-09-30 13:45 | 2015-09-30 | 3 | 13 | 204 | 62.8167 | 1
2015-09-30 14:00 | 2015-09-30 | 3 | 14 | 201 | 63.0667 | 1
2015-09-30 14:15 | 2015-09-30 | 3 | 14 | 193 | 63.3167 | 1
2015-09-30 14:30 | 2015-09-30 | 3 | 14 | 192 | 63.5667 | 1
2015-09-30 14:45 | 2015-09-30 | 3 | 14 | 197 | 63.8167 | 1
2015-09-30 15:00 | 2015-09-30 | 3 | 15 | 212 | 64 | 1
2015-09-30 15:15 | 2015-09-30 | 3 | 15 | 191 | 64 | 1
2015-09-30 15:30 | 2015-09-30 | 3 | 15 | 191 | 64 | 1
2015-09-30 15:45 | 2015-09-30 | 3 | 15 | 194 | 64 | 1
2015-09-30 16:00 | 2015-09-30 | 3 | 16 | 193 | 64.0667 | 1
2015-09-30 16:15 | 2015-09-30 | 3 | 16 | 211 | 64.3167 | 1
2015-09-30 16:30 | 2015-09-30 | 3 | 16 | 194 | 64.5667 | 1
2015-09-30 16:45 | 2015-09-30 | 3 | 16 | 191 | 64.8167 | 1
2015-09-30 17:00 | 2015-09-30 | 3 | 17 | 197 | 65 | 1
2015-09-30 17:15 | 2015-09-30 | 3 | 17 | 198 | 65 | 1
2015-09-30 17:30 | 2015-09-30 | 3 | 17 | 209 | 65 | 1
2015-09-30 17:45 | 2015-09-30 | 3 | 17 | 187 | 65 | 1
2015-09-30 18:00 | 2015-09-30 | 3 | 18 | 191 | 65 | 1
2015-09-30 18:15 | 2015-09-30 | 3 | 18 | 196 | 65 | 1
2015-09-30 18:30 | 2015-09-30 | 3 | 18 | 189 | 65 | 1
2015-09-30 18:45 | 2015-09-30 | 3 | 18 | 203 | 65 | 1
2015-09-30 19:00 | 2015-09-30 | 3 | 19 | 197 | 64.9333 | 1
2015-09-30 19:15 | 2015-09-30 | 3 | 19 | 125 | 64.6833 | 1
2015-09-30 19:30 | 2015-09-30 | 3 | 19 | 128 | 64.4333 | 1
2015-09-30 19:45 | 2015-09-30 | 3 | 19 | 126 | 64.1833 | 1
2015-09-30 20:00 | 2015-09-30 | 3 | 20 | 142 | 63.8667 | 1
2015-09-30 20:15 | 2015-09-30 | 3 | 20 | 130 | 63.3667 | 1
2015-09-30 20:30 | 2015-09-30 | 3 | 20 | 131 | 62.8667 | 1
2015-09-30 20:45 | 2015-09-30 | 3 | 20 | 128 | 62.3667 | 1
2015-09-30 21:00 | 2015-09-30 | 3 | 21 | 124 | 61.9333 | 1
2015-09-30 21:15 | 2015-09-30 | 3 | 21 | 134 | 61.6833 | 1
2015-09-30 21:30 | 2015-09-30 | 3 | 21 | 110 | 61.4333 | 1
2015-09-30 21:45 | 2015-09-30 | 3 | 21 | 115 | 61.1833 | 1
2015-09-30 22:00 | 2015-09-30 | 3 | 22 | 106 | 61 | 1
2015-09-30 22:15 | 2015-09-30 | 3 | 22 | 118 | 61 | 1
2015-09-30 22:30 | 2015-09-30 | 3 | 22 | 117 | 61 | 1
2015-09-30 22:45 | 2015-09-30 | 3 | 22 | 112 | 61 | 1
2015-09-30 23:00 | 2015-09-30 | 3 | 23 | 112 | 61 | 1
2015-09-30 23:15 | 2015-09-30 | 3 | 23 | 107 | 61 | 1
2015-09-30 23:30 | 2015-09-30 | 3 | 23 | 115 | 61 | 1
2015-09-30 23:45 | 2015-09-30 | 3 | 23 | 112 | 61 | 1
2015-10-01 | 2015-10-01 | 4 | 0 | 109 | 61 | 1
2015-10-01 00:15 | 2015-10-01 | 4 | 0 | 107 | 61 | 1
2015-10-01 00:30 | 2015-10-01 | 4 | 0 | 117 | 61 | 1
2015-10-01 00:45 | 2015-10-01 | 4 | 0 | 114 | 61 | 1
2015-10-01 01:00 | 2015-10-01 | 4 | 1 | 107 | 60.9333 | 1
2015-10-01 01:15 | 2015-10-01 | 4 | 1 | 114 | 60.6833 | 1
2015-10-01 01:30 | 2015-10-01 | 4 | 1 | 109 | 60.4333 | 1
2015-10-01 01:45 | 2015-10-01 | 4 | 1 | 110 | 60.1833 | 1
2015-10-01 02:00 | 2015-10-01 | 4 | 2 | 105 | 60 | 1
2015-10-01 02:15 | 2015-10-01 | 4 | 2 | 111 | 60 | 1
2015-10-01 02:30 | 2015-10-01 | 4 | 2 | 117 | 60 | 1
2015-10-01 02:45 | 2015-10-01 | 4 | 2 | 106 | 60 | 1
2015-10-01 03:00 | 2015-10-01 | 4 | 3 | 108 | 60.0667 | 1
2015-10-01 03:15 | 2015-10-01 | 4 | 3 | 108 | 60.3167 | 1
2015-10-01 03:30 | 2015-10-01 | 4 | 3 | 109 | 60.5667 | 1
2015-10-01 03:45 | 2015-10-01 | 4 | 3 | 116 | 60.8167 | 1
2015-10-01 04:00 | 2015-10-01 | 4 | 4 | 109 | 60.9333 | 1
2015-10-01 04:15 | 2015-10-01 | 4 | 4 | 108 | 60.6833 | 1
2015-10-01 04:30 | 2015-10-01 | 4 | 4 | 107 | 60.4333 | 1
2015-10-01 04:45 | 2015-10-01 | 4 | 4 | 109 | 60.1833 | 1
2015-10-01 05:00 | 2015-10-01 | 4 | 5 | 113 | 60.0667 | 1
2015-10-01 05:15 | 2015-10-01 | 4 | 5 | 110 | 60.3167 | 1
2015-10-01 05:30 | 2015-10-01 | 4 | 5 | 110 | 60.5667 | 1
2015-10-01 05:45 | 2015-10-01 | 4 | 5 | 110 | 60.8167 | 1
2015-10-01 06:00 | 2015-10-01 | 4 | 6 | 118 | 61.0667 | 1
2015-10-01 06:15 | 2015-10-01 | 4 | 6 | 113 | 61.3167 | 1
2015-10-01 06:30 | 2015-10-01 | 4 | 6 | 115 | 61.5667 | 1
2015-10-01 06:45 | 2015-10-01 | 4 | 6 | 112 | 61.8167 | 1
2015-10-01 07:00 | 2015-10-01 | 4 | 7 | 111 | 62.2 | 1
2015-10-01 07:15 | 2015-10-01 | 4 | 7 | 204 | 62.95 | 1
2015-10-01 07:30 | 2015-10-01 | 4 | 7 | 183 | 63.7 | 1
2015-10-01 07:45 | 2015-10-01 | 4 | 7 | 181 | 64.45 | 1
2015-10-01 08:00 | 2015-10-01 | 4 | 8 | 178 | 65 | 1
2015-10-01 08:15 | 2015-10-01 | 4 | 8 | 178 | 65 | 1
2015-10-01 08:30 | 2015-10-01 | 4 | 8 | 181 | 65 | 1
2015-10-01 08:45 | 2015-10-01 | 4 | 8 | 186 | 65 | 1
2015-10-01 09:00 | 2015-10-01 | 4 | 9 | 197 | 65.2 | 2
2015-10-01 09:15 | 2015-10-01 | 4 | 9 | 187 | 65.95 | 2
2015-10-01 09:30 | 2015-10-01 | 4 | 9 | 186 | 66.7 | 2
2015-10-01 09:45 | 2015-10-01 | 4 | 9 | 186 | 67.45 | 2
2015-10-01 10:00 | 2015-10-01 | 4 | 10 | 186 | 68 | 2
2015-10-01 10:15 | 2015-10-01 | 4 | 10 | 204 | 68 | 2
2015-10-01 10:30 | 2015-10-01 | 4 | 10 | 188 | 68 | 2
2015-10-01 10:45 | 2015-10-01 | 4 | 10 | 194 | 68 | 2
2015-10-01 11:00 | 2015-10-01 | 4 | 11 | 199 | 68.0667 | 2
2015-10-01 11:15 | 2015-10-01 | 4 | 11 | 197 | 68.3167 | 2
2015-10-01 11:30 | 2015-10-01 | 4 | 11 | 192 | 68.5667 | 2
2015-10-01 11:45 | 2015-10-01 | 4 | 11 | 205 | 68.8167 | 2
2015-10-01 12:00 | 2015-10-01 | 4 | 12 | 208 | 69.2667 | 2
2015-10-01 12:15 | 2015-10-01 | 4 | 12 | 192 | 70.2667 | 3
2015-10-01 12:30 | 2015-10-01 | 4 | 12 | 195 | 71.2667 | 3
2015-10-01 12:45 | 2015-10-01 | 4 | 12 | 200 | 72.2667 | 3
2015-10-01 13:00 | 2015-10-01 | 4 | 13 | 209 | 72.9333 | 3
2015-10-01 13:15 | 2015-10-01 | 4 | 13 | 207 | 72.6833 | 3
2015-10-01 13:30 | 2015-10-01 | 4 | 13 | 198 | 72.4333 | 3
2015-10-01 13:45 | 2015-10-01 | 4 | 13 | 207 | 72.1833 | 3
2015-10-01 14:00 | 2015-10-01 | 4 | 14 | 209 | 71.8 | 3
2015-10-01 14:15 | 2015-10-01 | 4 | 14 | 213 | 71.05 | 3
2015-10-01 14:30 | 2015-10-01 | 4 | 14 | 210 | 70.3 | 3
2015-10-01 14:45 | 2015-10-01 | 4 | 14 | 210 | 69.55 | 2
2015-10-01 15:00 | 2015-10-01 | 4 | 15 | 206 | 69 | 2
2015-10-01 15:15 | 2015-10-01 | 4 | 15 | 212 | 69 | 2
2015-10-01 15:30 | 2015-10-01 | 4 | 15 | 201 | 69 | 2
2015-10-01 15:45 | 2015-10-01 | 4 | 15 | 218 | 69 | 2
2015-10-01 16:00 | 2015-10-01 | 4 | 16 | 197 | 68.9333 | 2
2015-10-01 16:15 | 2015-10-01 | 4 | 16 | 203 | 68.6833 | 2
2015-10-01 16:30 | 2015-10-01 | 4 | 16 | 196 | 68.4333 | 2
2015-10-01 16:45 | 2015-10-01 | 4 | 16 | 203 | 68.1833 | 2
2015-10-01 17:00 | 2015-10-01 | 4 | 17 | 211 | 67.7333 | 2
2015-10-01 17:15 | 2015-10-01 | 4 | 17 | 217 | 66.7333 | 2
2015-10-01 17:30 | 2015-10-01 | 4 | 17 | 203 | 65.7333 | 2
2015-10-01 17:45 | 2015-10-01 | 4 | 17 | 218 | 64.7333 | 1
2015-10-01 18:00 | 2015-10-01 | 4 | 18 | 199 | 63.9333 | 1
2015-10-01 18:15 | 2015-10-01 | 4 | 18 | 210 | 63.6833 | 1
2015-10-01 18:30 | 2015-10-01 | 4 | 18 | 202 | 63.4333 | 1
2015-10-01 18:45 | 2015-10-01 | 4 | 18 | 213 | 63.1833 | 1
2015-10-01 19:00 | 2015-10-01 | 4 | 19 | 201 | 63 | 1
2015-10-01 19:15 | 2015-10-01 | 4 | 19 | 123 | 63 | 1
2015-10-01 19:30 | 2015-10-01 | 4 | 19 | 126 | 63 | 1
2015-10-01 19:45 | 2015-10-01 | 4 | 19 | 121 | 63 | 1
2015-10-01 20:00 | 2015-10-01 | 4 | 20 | 126 | 62.8667 | 1
2015-10-01 20:15 | 2015-10-01 | 4 | 20 | 133 | 62.3667 | 1
2015-10-01 20:30 | 2015-10-01 | 4 | 20 | 122 | 61.8667 | 1
2015-10-01 20:45 | 2015-10-01 | 4 | 20 | 124 | 61.3667 | 1
2015-10-01 21:00 | 2015-10-01 | 4 | 21 | 120 | 60.9333 | 1
2015-10-01 21:15 | 2015-10-01 | 4 | 21 | 127 | 60.6833 | 1
2015-10-01 21:30 | 2015-10-01 | 4 | 21 | 121 | 60.4333 | 1
2015-10-01 21:45 | 2015-10-01 | 4 | 21 | 117 | 60.1833 | 1
2015-10-01 22:00 | 2015-10-01 | 4 | 22 | 118 | 60 | 1
2015-10-01 22:15 | 2015-10-01 | 4 | 22 | 120 | 60 | 1
2015-10-01 22:30 | 2015-10-01 | 4 | 22 | 127 | 60 | 1
2015-10-01 22:45 | 2015-10-01 | 4 | 22 | 128 | 60 | 1
2015-10-01 23:00 | 2015-10-01 | 4 | 23 | 125 | 59.9333 | 1
2015-10-01 23:15 | 2015-10-01 | 4 | 23 | 123 | 59.6833 | 1
2015-10-01 23:30 | 2015-10-01 | 4 | 23 | 121 | 59.4333 | 1
2015-10-01 23:45 | 2015-10-01 | 4 | 23 | 130 | 59.1833 | 1
2015-10-02 | 2015-10-02 | 5 | 0 | 122 | 59 | 1
2015-10-02 00:15 | 2015-10-02 | 5 | 0 | 120 | 59 | 1
2015-10-02 00:30 | 2015-10-02 | 5 | 0 | 120 | 59 | 1
2015-10-02 00:45 | 2015-10-02 | 5 | 0 | 114 | 59 | 1
2015-10-02 01:00 | 2015-10-02 | 5 | 1 | 122 | 59 | 1
2015-10-02 01:15 | 2015-10-02 | 5 | 1 | 110 | 59 | 1
2015-10-02 01:30 | 2015-10-02 | 5 | 1 | 113 | 59 | 1
2015-10-02 01:45 | 2015-10-02 | 5 | 1 | 108 | 59 | 1
2015-10-02 02:00 | 2015-10-02 | 5 | 2 | 113 | 58.9333 | 1
2015-10-02 02:15 | 2015-10-02 | 5 | 2 | 116 | 58.6833 | 1
2015-10-02 02:30 | 2015-10-02 | 5 | 2 | 110 | 58.4333 | 1
2015-10-02 02:45 | 2015-10-02 | 5 | 2 | 111 | 58.1833 | 1
2015-10-02 03:00 | 2015-10-02 | 5 | 3 | 107 | 57.9333 | 1
2015-10-02 03:15 | 2015-10-02 | 5 | 3 | 110 | 57.6833 | 1
2015-10-02 03:30 | 2015-10-02 | 5 | 3 | 115 | 57.4333 | 1
2015-10-02 03:45 | 2015-10-02 | 5 | 3 | 109 | 57.1833 | 1
2015-10-02 04:00 | 2015-10-02 | 5 | 4 | 106 | 57 | 1
2015-10-02 04:15 | 2015-10-02 | 5 | 4 | 113 | 57 | 1
2015-10-02 04:30 | 2015-10-02 | 5 | 4 | 113 | 57 | 1
2015-10-02 04:45 | 2015-10-02 | 5 | 4 | 110 | 57 | 1
2015-10-02 05:00 | 2015-10-02 | 5 | 5 | 110 | 57 | 1
2015-10-02 05:15 | 2015-10-02 | 5 | 5 | 105 | 57 | 1
2015-10-02 05:30 | 2015-10-02 | 5 | 5 | 116 | 57 | 1
2015-10-02 05:45 | 2015-10-02 | 5 | 5 | 113 | 57 | 1
2015-10-02 06:00 | 2015-10-02 | 5 | 6 | 116 | 58.0667 | 1
2015-10-02 06:15 | 2015-10-02 | 5 | 6 | 117 | 58.3167 | 1
2015-10-02 06:30 | 2015-10-02 | 5 | 6 | 111 | 58.5667 | 1
2015-10-02 06:45 | 2015-10-02 | 5 | 6 | 123 | 58.8167 | 1
2015-10-02 07:00 | 2015-10-02 | 5 | 7 | 115 | 59.2 | 1
2015-10-02 07:15 | 2015-10-02 | 5 | 7 | 170 | 59.95 | 1
2015-10-02 07:30 | 2015-10-02 | 5 | 7 | 166 | 60.7 | 1
2015-10-02 07:45 | 2015-10-02 | 5 | 7 | 162 | 61.45 | 1
2015-10-02 08:00 | 2015-10-02 | 5 | 8 | 179 | 62.2667 | 1
2015-10-02 08:15 | 2015-10-02 | 5 | 8 | 167 | 63.2667 | 1
2015-10-02 08:30 | 2015-10-02 | 5 | 8 | 180 | 64.2667 | 1
2015-10-02 08:45 | 2015-10-02 | 5 | 8 | 186 | 65.2667 | 2
2015-10-02 09:00 | 2015-10-02 | 5 | 9 | 200 | 66 | 2
2015-10-02 09:15 | 2015-10-02 | 5 | 9 | 199 | 66 | 2
2015-10-02 09:30 | 2015-10-02 | 5 | 9 | 199 | 66 | 2
2015-10-02 09:45 | 2015-10-02 | 5 | 9 | 193 | 66 | 2
2015-10-02 10:00 | 2015-10-02 | 5 | 10 | 204 | 66.1333 | 2
2015-10-02 10:15 | 2015-10-02 | 5 | 10 | 212 | 66.6333 | 2
2015-10-02 10:30 | 2015-10-02 | 5 | 10 | 203 | 67.1333 | 2
2015-10-02 10:45 | 2015-10-02 | 5 | 10 | 198 | 67.6333 | 2
2015-10-02 11:00 | 2015-10-02 | 5 | 11 | 201 | 68.1333 | 2
2015-10-02 11:15 | 2015-10-02 | 5 | 11 | 213 | 68.6333 | 2
2015-10-02 11:30 | 2015-10-02 | 5 | 11 | 215 | 69.1333 | 2
2015-10-02 11:45 | 2015-10-02 | 5 | 11 | 209 | 69.6333 | 2
2015-10-02 12:00 | 2015-10-02 | 5 | 12 | 205 | 70.2 | 3
2015-10-02 12:15 | 2015-10-02 | 5 | 12 | 203 | 70.95 | 3
2015-10-02 12:30 | 2015-10-02 | 5 | 12 | 218 | 71.7 | 3
2015-10-02 12:45 | 2015-10-02 | 5 | 12 | 211 | 72.45 | 3
2015-10-02 13:00 | 2015-10-02 | 5 | 13 | 200 | 72.7333 | 3
2015-10-02 13:15 | 2015-10-02 | 5 | 13 | 203 | 71.7333 | 3
2015-10-02 13:30 | 2015-10-02 | 5 | 13 | 204 | 70.7333 | 3
2015-10-02 13:45 | 2015-10-02 | 5 | 13 | 212 | 69.7333 | 2
2015-10-02 14:00 | 2015-10-02 | 5 | 14 | 210 | 68.9333 | 2
2015-10-02 14:15 | 2015-10-02 | 5 | 14 | 218 | 68.6833 | 2
2015-10-02 14:30 | 2015-10-02 | 5 | 14 | 229 | 68.4333 | 2
2015-10-02 14:45 | 2015-10-02 | 5 | 14 | 224 | 68.1833 | 2
2015-10-02 15:00 | 2015-10-02 | 5 | 15 | 220 | 68.0667 | 2
2015-10-02 15:15 | 2015-10-02 | 5 | 15 | 219 | 68.3167 | 2
2015-10-02 15:30 | 2015-10-02 | 5 | 15 | 217 | 68.5667 | 2
2015-10-02 15:45 | 2015-10-02 | 5 | 15 | 238 | 68.8167 | 2
2015-10-02 16:00 | 2015-10-02 | 5 | 16 | 215 | 68.8667 | 2
2015-10-02 16:15 | 2015-10-02 | 5 | 16 | 230 | 68.3667 | 2
2015-10-02 16:30 | 2015-10-02 | 5 | 16 | 219 | 67.8667 | 2
2015-10-02 16:45 | 2015-10-02 | 5 | 16 | 217 | 67.3667 | 2
2015-10-02 17:00 | 2015-10-02 | 5 | 17 | 222 | 66.7333 | 2
2015-10-02 17:15 | 2015-10-02 | 5 | 17 | 231 | 65.7333 | 2
2015-10-02 17:30 | 2015-10-02 | 5 | 17 | 210 | 64.7333 | 1
2015-10-02 17:45 | 2015-10-02 | 5 | 17 | 216 | 63.7333 | 1
2015-10-02 18:00 | 2015-10-02 | 5 | 18 | 212 | 62.8667 | 1
2015-10-02 18:15 | 2015-10-02 | 5 | 18 | 221 | 62.3667 | 1
2015-10-02 18:30 | 2015-10-02 | 5 | 18 | 201 | 61.8667 | 1
2015-10-02 18:45 | 2015-10-02 | 5 | 18 | 207 | 61.3667 | 1
2015-10-02 19:00 | 2015-10-02 | 5 | 19 | 191 | 61 | 1
2015-10-02 19:15 | 2015-10-02 | 5 | 19 | 129 | 61 | 1
2015-10-02 19:30 | 2015-10-02 | 5 | 19 | 129 | 61 | 1
2015-10-02 19:45 | 2015-10-02 | 5 | 19 | 123 | 61 | 1
2015-10-02 20:00 | 2015-10-02 | 5 | 20 | 118 | 60.9333 | 1
2015-10-02 20:15 | 2015-10-02 | 5 | 20 | 129 | 60.6833 | 1
2015-10-02 20:30 | 2015-10-02 | 5 | 20 | 123 | 60.4333 | 1
2015-10-02 20:45 | 2015-10-02 | 5 | 20 | 119 | 60.1833 | 1
2015-10-02 21:00 | 2015-10-02 | 5 | 21 | 119 | 60 | 1
2015-10-02 21:15 | 2015-10-02 | 5 | 21 | 114 | 60 | 1
2015-10-02 21:30 | 2015-10-02 | 5 | 21 | 113 | 60 | 1
2015-10-02 21:45 | 2015-10-02 | 5 | 21 | 110 | 60 | 1
2015-10-02 22:00 | 2015-10-02 | 5 | 22 | 107 | 59.9333 | 1
2015-10-02 22:15 | 2015-10-02 | 5 | 22 | 112 | 59.6833 | 1
2015-10-02 22:30 | 2015-10-02 | 5 | 22 | 120 | 59.4333 | 1
2015-10-02 22:45 | 2015-10-02 | 5 | 22 | 108 | 59.1833 | 1
2015-10-02 23:00 | 2015-10-02 | 5 | 23 | 110 | 59 | 1
2015-10-02 23:15 | 2015-10-02 | 5 | 23 | 107 | 59 | 1
2015-10-02 23:30 | 2015-10-02 | 5 | 23 | 106 | 59 | 1
2015-10-02 23:45 | 2015-10-02 | 5 | 23 | 115 | 59 | 1
2015-10-03 | 2015-10-03 | 6 | 0 | 107 | 58.9333 | 1
2015-10-03 00:15 | 2015-10-03 | 6 | 0 | 100 | 58.6833 | 1
2015-10-03 00:30 | 2015-10-03 | 6 | 0 | 97 | 58.4333 | 1
2015-10-03 00:45 | 2015-10-03 | 6 | 0 | 102 | 58.1833 | 1
2015-10-03 01:00 | 2015-10-03 | 6 | 1 | 94 | 58 | 1
2015-10-03 01:15 | 2015-10-03 | 6 | 1 | 97 | 58 | 1
2015-10-03 01:30 | 2015-10-03 | 6 | 1 | 94 | 58 | 1
2015-10-03 01:45 | 2015-10-03 | 6 | 1 | 94 | 58 | 1
2015-10-03 02:00 | 2015-10-03 | 6 | 2 | 103 | 57.9333 | 1
2015-10-03 02:15 | 2015-10-03 | 6 | 2 | 95 | 57.6833 | 1
2015-10-03 02:30 | 2015-10-03 | 6 | 2 | 100 | 57.4333 | 1
2015-10-03 02:45 | 2015-10-03 | 6 | 2 | 95 | 57.1833 | 1
2015-10-03 03:00 | 2015-10-03 | 6 | 3 | 92 | 56.9333 | 1
2015-10-03 03:15 | 2015-10-03 | 6 | 3 | 102 | 56.6833 | 1
2015-10-03 03:30 | 2015-10-03 | 6 | 3 | 94 | 56.4333 | 1
2015-10-03 03:45 | 2015-10-03 | 6 | 3 | 95 | 56.1833 | 1
2015-10-03 04:00 | 2015-10-03 | 6 | 4 | 96 | 56 | 1
2015-10-03 04:15 | 2015-10-03 | 6 | 4 | 99 | 56 | 1
2015-10-03 04:30 | 2015-10-03 | 6 | 4 | 97 | 56 | 1
2015-10-03 04:45 | 2015-10-03 | 6 | 4 | 96 | 56 | 1
2015-10-03 05:00 | 2015-10-03 | 6 | 5 | 90 | 56.0667 | 1
2015-10-03 05:15 | 2015-10-03 | 6 | 5 | 97 | 56.3167 | 1
2015-10-03 05:30 | 2015-10-03 | 6 | 5 | 92 | 56.5667 | 1
2015-10-03 05:45 | 2015-10-03 | 6 | 5 | 100 | 56.8167 | 1
2015-10-03 06:00 | 2015-10-03 | 6 | 6 | 99 | 57 | 1
2015-10-03 06:15 | 2015-10-03 | 6 | 6 | 96 | 57 | 1
2015-10-03 06:30 | 2015-10-03 | 6 | 6 | 99 | 57 | 1
2015-10-03 06:45 | 2015-10-03 | 6 | 6 | 93 | 57 | 1
2015-10-03 07:00 | 2015-10-03 | 6 | 7 | 96 | 57.2 | 1
2015-10-03 07:15 | 2015-10-03 | 6 | 7 | 98 | 57.95 | 1
2015-10-03 07:30 | 2015-10-03 | 6 | 7 | 90 | 58.7 | 1
2015-10-03 07:45 | 2015-10-03 | 6 | 7 | 90 | 59.45 | 1
2015-10-03 08:00 | 2015-10-03 | 6 | 8 | 98 | 60.2 | 1
2015-10-03 08:15 | 2015-10-03 | 6 | 8 | 88 | 60.95 | 1
2015-10-03 08:30 | 2015-10-03 | 6 | 8 | 94 | 61.7 | 1
2015-10-03 08:45 | 2015-10-03 | 6 | 8 | 89 | 62.45 | 1
2015-10-03 09:00 | 2015-10-03 | 6 | 9 | 89 | 63.1333 | 1
2015-10-03 09:15 | 2015-10-03 | 6 | 9 | 95 | 63.6333 | 1
2015-10-03 09:30 | 2015-10-03 | 6 | 9 | 85 | 64.1333 | 1
2015-10-03 09:45 | 2015-10-03 | 6 | 9 | 97 | 64.6333 | 1
2015-10-03 10:00 | 2015-10-03 | 6 | 10 | 100 | 65.2667 | 2
2015-10-03 10:15 | 2015-10-03 | 6 | 10 | 88 | 66.2667 | 2
2015-10-03 10:30 | 2015-10-03 | 6 | 10 | 91 | 67.2667 | 2
2015-10-03 10:45 | 2015-10-03 | 6 | 10 | 93 | 68.2667 | 2
2015-10-03 11:00 | 2015-10-03 | 6 | 11 | 90 | 69.0667 | 2
2015-10-03 11:15 | 2015-10-03 | 6 | 11 | 97 | 69.3167 | 2
2015-10-03 11:30 | 2015-10-03 | 6 | 11 | 94 | 69.5667 | 2
2015-10-03 11:45 | 2015-10-03 | 6 | 11 | 91 | 69.8167 | 2
2015-10-03 12:00 | 2015-10-03 | 6 | 12 | 88 | 69.8 | 2
2015-10-03 12:15 | 2015-10-03 | 6 | 12 | 97 | 69.05 | 2
2015-10-03 12:30 | 2015-10-03 | 6 | 12 | 93 | 68.3 | 2
2015-10-03 12:45 | 2015-10-03 | 6 | 12 | 92 | 67.55 | 2
2015-10-03 13:00 | 2015-10-03 | 6 | 13 | 88 | 66.8667 | 2
2015-10-03 13:15 | 2015-10-03 | 6 | 13 | 100 | 66.3667 | 2
2015-10-03 13:30 | 2015-10-03 | 6 | 13 | 92 | 65.8667 | 2
2015-10-03 13:45 | 2015-10-03 | 6 | 13 | 94 | 65.3667 | 2
2015-10-03 14:00 | 2015-10-03 | 6 | 14 | 95 | 64.8667 | 1
2015-10-03 14:15 | 2015-10-03 | 6 | 14 | 93 | 64.3667 | 1
2015-10-03 14:30 | 2015-10-03 | 6 | 14 | 98 | 63.8667 | 1
2015-10-03 14:45 | 2015-10-03 | 6 | 14 | 94 | 63.3667 | 1
2015-10-03 15:00 | 2015-10-03 | 6 | 15 | 95 | 62.8 | 1
2015-10-03 15:15 | 2015-10-03 | 6 | 15 | 89 | 62.05 | 1
2015-10-03 15:30 | 2015-10-03 | 6 | 15 | 94 | 61.3 | 1
2015-10-03 15:45 | 2015-10-03 | 6 | 15 | 95 | 60.55 | 1
2015-10-03 16:00 | 2015-10-03 | 6 | 16 | 97 | 59.9333 | 1
2015-10-03 16:15 | 2015-10-03 | 6 | 16 | 95 | 59.6833 | 1
2015-10-03 16:30 | 2015-10-03 | 6 | 16 | 97 | 59.4333 | 1
2015-10-03 16:45 | 2015-10-03 | 6 | 16 | 96 | 59.1833 | 1
2015-10-03 17:00 | 2015-10-03 | 6 | 17 | 92 | 58.9333 | 1
2015-10-03 17:15 | 2015-10-03 | 6 | 17 | 103 | 58.6833 | 1
2015-10-03 17:30 | 2015-10-03 | 6 | 17 | 97 | 58.4333 | 1
2015-10-03 17:45 | 2015-10-03 | 6 | 17 | 101 | 58.1833 | 1
2015-10-03 18:00 | 2015-10-03 | 6 | 18 | 98 | 58 | 1
2015-10-03 18:15 | 2015-10-03 | 6 | 18 | 102 | 58 | 1
2015-10-03 18:30 | 2015-10-03 | 6 | 18 | 98 | 58 | 1
2015-10-03 18:45 | 2015-10-03 | 6 | 18 | 101 | 58 | 1
2015-10-03 19:00 | 2015-10-03 | 6 | 19 | 97 | 58 | 1
2015-10-03 19:15 | 2015-10-03 | 6 | 19 | 98 | 58 | 1
2015-10-03 19:30 | 2015-10-03 | 6 | 19 | 105 | 58 | 1
2015-10-03 19:45 | 2015-10-03 | 6 | 19 | 96 | 58 | 1
2015-10-03 20:00 | 2015-10-03 | 6 | 20 | 98 | 58 | 1
2015-10-03 20:15 | 2015-10-03 | 6 | 20 | 94 | 58 | 1
2015-10-03 20:30 | 2015-10-03 | 6 | 20 | 99 | 58 | 1
2015-10-03 20:45 | 2015-10-03 | 6 | 20 | 96 | 58 | 1
2015-10-03 21:00 | 2015-10-03 | 6 | 21 | 96 | 57.931 | 1
2015-10-03 21:15 | 2015-10-03 | 6 | 21 | 104 | 57.6724 | 1
2015-10-03 21:30 | 2015-10-03 | 6 | 21 | 99 | 57.4138 | 1
2015-10-03 21:45 | 2015-10-03 | 6 | 21 | 102 | 57.1552 | 1
2015-10-03 22:00 | 2015-10-03 | 6 | 22 | 104 | 58 | 1
2015-10-03 22:15 | 2015-10-03 | 6 | 22 | 101 | 58 | 1
2015-10-03 22:30 | 2015-10-03 | 6 | 22 | 98 | 58 | 1
2015-10-03 22:45 | 2015-10-03 | 6 | 22 | 104 | 58 | 1
2015-10-03 23:00 | 2015-10-03 | 6 | 23 | 96 | 57.8 | 1
2015-10-03 23:15 | 2015-10-03 | 6 | 23 | 102 | 57.05 | 1
2015-10-03 23:30 | 2015-10-03 | 6 | 23 | 97 | 56.3 | 1
2015-10-03 23:45 | 2015-10-03 | 6 | 23 | 97 | 55.55 | 1
2015-10-04 | 2015-10-04 | 7 | 0 | 96 | 55.0667 | 1
2015-10-04 00:15 | 2015-10-04 | 7 | 0 | 96 | 55.3167 | 1
2015-10-04 00:30 | 2015-10-04 | 7 | 0 | 100 | 55.5667 | 1
2015-10-04 00:45 | 2015-10-04 | 7 | 0 | 97 | 55.8167 | 1
2015-10-04 01:00 | 2015-10-04 | 7 | 1 | 96 | 56.0667 | 1
2015-10-04 01:15 | 2015-10-04 | 7 | 1 | 101 | 56.3167 | 1
2015-10-04 01:30 | 2015-10-04 | 7 | 1 | 96 | 56.5667 | 1
2015-10-04 01:45 | 2015-10-04 | 7 | 1 | 94 | 56.8167 | 1
2015-10-04 02:00 | 2015-10-04 | 7 | 2 | 96 | 56.8667 | 1
2015-10-04 02:15 | 2015-10-04 | 7 | 2 | 93 | 56.3667 | 1
2015-10-04 02:30 | 2015-10-04 | 7 | 2 | 98 | 55.8667 | 1
2015-10-04 02:45 | 2015-10-04 | 7 | 2 | 98 | 55.3667 | 1
2015-10-04 03:00 | 2015-10-04 | 7 | 3 | 98 | 54.9333 | 1
2015-10-04 03:15 | 2015-10-04 | 7 | 3 | 100 | 54.6833 | 1
2015-10-04 03:30 | 2015-10-04 | 7 | 3 | 95 | 54.4333 | 1
2015-10-04 03:45 | 2015-10-04 | 7 | 3 | 96 | 54.1833 | 1
2015-10-04 04:00 | 2015-10-04 | 7 | 4 | 94 | 54.0667 | 1
2015-10-04 04:15 | 2015-10-04 | 7 | 4 | 96 | 54.3167 | 1
2015-10-04 04:30 | 2015-10-04 | 7 | 4 | 97 | 54.5667 | 1
2015-10-04 04:45 | 2015-10-04 | 7 | 4 | 99 | 54.8167 | 1
2015-10-04 05:00 | 2015-10-04 | 7 | 5 | 99 | 55 | 1
2015-10-04 05:15 | 2015-10-04 | 7 | 5 | 95 | 55 | 1
2015-10-04 05:30 | 2015-10-04 | 7 | 5 | 97 | 55 | 1
2015-10-04 05:45 | 2015-10-04 | 7 | 5 | 99 | 55 | 1
2015-10-04 06:00 | 2015-10-04 | 7 | 6 | 103 | 55 | 1
2015-10-04 06:15 | 2015-10-04 | 7 | 6 | 97 | 55 | 1
2015-10-04 06:30 | 2015-10-04 | 7 | 6 | 98 | 55 | 1
2015-10-04 06:45 | 2015-10-04 | 7 | 6 | 100 | 55 | 1
2015-10-04 07:00 | 2015-10-04 | 7 | 7 | 102 | 55.2 | 1
2015-10-04 07:15 | 2015-10-04 | 7 | 7 | 98 | 55.95 | 1
2015-10-04 07:30 | 2015-10-04 | 7 | 7 | 96 | 56.7 | 1
2015-10-04 07:45 | 2015-10-04 | 7 | 7 | 94 | 57.45 | 1
2015-10-04 08:00 | 2015-10-04 | 7 | 8 | 101 | 58.2667 | 1
2015-10-04 08:15 | 2015-10-04 | 7 | 8 | 101 | 59.2667 | 1
2015-10-04 08:30 | 2015-10-04 | 7 | 8 | 99 | 60.2667 | 1
2015-10-04 08:45 | 2015-10-04 | 7 | 8 | 112 | 61.2667 | 1
2015-10-04 09:00 | 2015-10-04 | 7 | 9 | 103 | 62.2667 | 1
2015-10-04 09:15 | 2015-10-04 | 7 | 9 | 102 | 63.2667 | 1
2015-10-04 09:30 | 2015-10-04 | 7 | 9 | 103 | 64.2667 | 1
2015-10-04 09:45 | 2015-10-04 | 7 | 9 | 102 | 65.2667 | 2
2015-10-04 10:00 | 2015-10-04 | 7 | 10 | 105 | 66.2 | 2
2015-10-04 10:15 | 2015-10-04 | 7 | 10 | 103 | 66.95 | 2
2015-10-04 10:30 | 2015-10-04 | 7 | 10 | 100 | 67.7 | 2
2015-10-04 10:45 | 2015-10-04 | 7 | 10 | 105 | 68.45 | 2
2015-10-04 11:00 | 2015-10-04 | 7 | 11 | 100 | 69.2 | 2
2015-10-04 11:15 | 2015-10-04 | 7 | 11 | 104 | 69.95 | 2
2015-10-04 11:30 | 2015-10-04 | 7 | 11 | 102 | 70.7 | 3
2015-10-04 11:45 | 2015-10-04 | 7 | 11 | 103 | 71.45 | 3
2015-10-04 12:00 | 2015-10-04 | 7 | 12 | 99 | 72 | 3
2015-10-04 12:15 | 2015-10-04 | 7 | 12 | 107 | 72 | 3
2015-10-04 12:30 | 2015-10-04 | 7 | 12 | 106 | 72 | 3
2015-10-04 12:45 | 2015-10-04 | 7 | 12 | 106 | 71.6875 | 3
2015-10-04 13:00 | 2015-10-04 | 7 | 13 | 101 | 71.0667 | 3
2015-10-04 13:15 | 2015-10-04 | 7 | 13 | 104 | 71.3167 | 3
2015-10-04 13:30 | 2015-10-04 | 7 | 13 | 104 | 71.5667 | 3
2015-10-04 13:45 | 2015-10-04 | 7 | 13 | 100 | 71.8167 | 3
2015-10-04 14:00 | 2015-10-04 | 7 | 14 | 109 | 72 | 3
2015-10-04 14:15 | 2015-10-04 | 7 | 14 | 106 | 72 | 3
2015-10-04 14:30 | 2015-10-04 | 7 | 14 | 105 | 72 | 3
2015-10-04 14:45 | 2015-10-04 | 7 | 14 | 107 | 72 | 3
2015-10-04 15:00 | 2015-10-04 | 7 | 15 | 109 | 71.9333 | 3
2015-10-04 15:15 | 2015-10-04 | 7 | 15 | 108 | 71.6833 | 3
2015-10-04 15:30 | 2015-10-04 | 7 | 15 | 107 | 71.4333 | 3
2015-10-04 15:45 | 2015-10-04 | 7 | 15 | 101 | 71.1833 | 3
2015-10-04 16:00 | 2015-10-04 | 7 | 16 | 107 | 70.8667 | 3
2015-10-04 16:15 | 2015-10-04 | 7 | 16 | 102 | 70.3667 | 3
2015-10-04 16:30 | 2015-10-04 | 7 | 16 | 104 | 69.8667 | 2
2015-10-04 16:45 | 2015-10-04 | 7 | 16 | 102 | 69.3667 | 2
2015-10-04 17:00 | 2015-10-04 | 7 | 17 | 104 | 68.7333 | 2
2015-10-04 17:15 | 2015-10-04 | 7 | 17 | 104 | 67.7333 | 2
2015-10-04 17:30 | 2015-10-04 | 7 | 17 | 111 | 66.7333 | 2
2015-10-04 17:45 | 2015-10-04 | 7 | 17 | 109 | 65.7333 | 2
2015-10-04 18:00 | 2015-10-04 | 7 | 18 | 107 | 64.8667 | 1
2015-10-04 18:15 | 2015-10-04 | 7 | 18 | 109 | 64.3667 | 1
2015-10-04 18:30 | 2015-10-04 | 7 | 18 | 106 | 63.8667 | 1
2015-10-04 18:45 | 2015-10-04 | 7 | 18 | 112 | 63.3667 | 1
2015-10-04 19:00 | 2015-10-04 | 7 | 19 | 107 | 63 | 1
2015-10-04 19:15 | 2015-10-04 | 7 | 19 | 106 | 63 | 1
2015-10-04 19:30 | 2015-10-04 | 7 | 19 | 104 | 63 | 1
2015-10-04 19:45 | 2015-10-04 | 7 | 19 | 112 | 63 | 1
2015-10-04 20:00 | 2015-10-04 | 7 | 20 | 107 | 63 | 1
2015-10-04 20:15 | 2015-10-04 | 7 | 20 | 108 | 63 | 1
2015-10-04 20:30 | 2015-10-04 | 7 | 20 | 108 | 63 | 1
2015-10-04 20:45 | 2015-10-04 | 7 | 20 | 110 | 63 | 1
2015-10-04 21:00 | 2015-10-04 | 7 | 21 | 105 | 62.9333 | 1
2015-10-04 21:15 | 2015-10-04 | 7 | 21 | 107 | 62.6833 | 1
2015-10-04 21:30 | 2015-10-04 | 7 | 21 | 105 | 62.4333 | 1
2015-10-04 21:45 | 2015-10-04 | 7 | 21 | 99 | 62.1833 | 1
2015-10-04 22:00 | 2015-10-04 | 7 | 22 | 100 | 62 | 1
2015-10-04 22:15 | 2015-10-04 | 7 | 22 | 98 | 62 | 1
2015-10-04 22:30 | 2015-10-04 | 7 | 22 | 106 | 62 | 1
2015-10-04 22:45 | 2015-10-04 | 7 | 22 | 101 | 62 | 1
2015-10-04 23:00 | 2015-10-04 | 7 | 23 | 101 | 61.8667 | 1
2015-10-04 23:15 | 2015-10-04 | 7 | 23 | 101 | 61.3667 | 1
2015-10-04 23:30 | 2015-10-04 | 7 | 23 | 99 | 60.8667 | 1
2015-10-04 23:45 | 2015-10-04 | 7 | 23 | 105 | 60.3667 | 1
2015-10-05 | 2015-10-05 | 1 | 0 | 101 | 60.0667 | 1
2015-10-05 00:15 | 2015-10-05 | 1 | 0 | 98 | 60.3167 | 1
2015-10-05 00:30 | 2015-10-05 | 1 | 0 | 104 | 60.5667 | 1
2015-10-05 00:45 | 2015-10-05 | 1 | 0 | 100 | 60.8167 | 1
2015-10-05 01:00 | 2015-10-05 | 1 | 1 | 98 | 61.0667 | 1
2015-10-05 01:15 | 2015-10-05 | 1 | 1 | 108 | 61.3167 | 1
2015-10-05 01:30 | 2015-10-05 | 1 | 1 | 99 | 61.5667 | 1
2015-10-05 01:45 | 2015-10-05 | 1 | 1 | 103 | 61.8167 | 1
2015-10-05 02:00 | 2015-10-05 | 1 | 2 | 98 | 61.7333 | 1
2015-10-05 02:15 | 2015-10-05 | 1 | 2 | 100 | 60.7333 | 1
2015-10-05 02:30 | 2015-10-05 | 1 | 2 | 101 | 59.7333 | 1
2015-10-05 02:45 | 2015-10-05 | 1 | 2 | 97 | 58.7333 | 1
2015-10-05 03:00 | 2015-10-05 | 1 | 3 | 101 | 58 | 1
2015-10-05 03:15 | 2015-10-05 | 1 | 3 | 99 | 58 | 1
2015-10-05 03:30 | 2015-10-05 | 1 | 3 | 100 | 58 | 1
2015-10-05 03:45 | 2015-10-05 | 1 | 3 | 106 | 58 | 1
2015-10-05 04:00 | 2015-10-05 | 1 | 4 | 101 | 58.1333 | 1
2015-10-05 04:15 | 2015-10-05 | 1 | 4 | 98 | 58.6333 | 1
2015-10-05 04:30 | 2015-10-05 | 1 | 4 | 102 | 59.1333 | 1
2015-10-05 04:45 | 2015-10-05 | 1 | 4 | 101 | 59.6333 | 1
2015-10-05 05:00 | 2015-10-05 | 1 | 5 | 102 | 60.0667 | 1
2015-10-05 05:15 | 2015-10-05 | 1 | 5 | 102 | 60.3167 | 1
2015-10-05 05:30 | 2015-10-05 | 1 | 5 | 106 | 60.5667 | 1
2015-10-05 05:45 | 2015-10-05 | 1 | 5 | 106 | 60.8167 | 1
2015-10-05 06:00 | 2015-10-05 | 1 | 6 | 100 | 61.1333 | 1
2015-10-05 06:15 | 2015-10-05 | 1 | 6 | 111 | 61.6333 | 1
2015-10-05 06:30 | 2015-10-05 | 1 | 6 | 105 | 62.1333 | 1
2015-10-05 06:45 | 2015-10-05 | 1 | 6 | 104 | 62.6333 | 1
2015-10-05 07:00 | 2015-10-05 | 1 | 7 | 106 | 63.0667 | 1
2015-10-05 07:15 | 2015-10-05 | 1 | 7 | 184 | 63.3167 | 1
2015-10-05 07:30 | 2015-10-05 | 1 | 7 | 168 | 63.5667 | 1
2015-10-05 07:45 | 2015-10-05 | 1 | 7 | 159 | 63.8167 | 1
2015-10-05 08:00 | 2015-10-05 | 1 | 8 | 158 | 64.0667 | 1
2015-10-05 08:15 | 2015-10-05 | 1 | 8 | 166 | 64.3167 | 1
2015-10-05 08:30 | 2015-10-05 | 1 | 8 | 170 | 64.5667 | 1
2015-10-05 08:45 | 2015-10-05 | 1 | 8 | 179 | 64.8167 | 1
2015-10-05 09:00 | 2015-10-05 | 1 | 9 | 191 | 65.0667 | 2
2015-10-05 09:15 | 2015-10-05 | 1 | 9 | 200 | 65.3167 | 2
2015-10-05 09:30 | 2015-10-05 | 1 | 9 | 207 | 65.5667 | 2
2015-10-05 09:45 | 2015-10-05 | 1 | 9 | 216 | 65.8167 | 2
2015-10-05 10:00 | 2015-10-05 | 1 | 10 | 202 | 66.0667 | 2
2015-10-05 10:15 | 2015-10-05 | 1 | 10 | 208 | 66.3167 | 2
2015-10-05 10:30 | 2015-10-05 | 1 | 10 | 213 | 66.5667 | 2
2015-10-05 10:45 | 2015-10-05 | 1 | 10 | 224 | 66.8167 | 2
2015-10-05 11:00 | 2015-10-05 | 1 | 11 | 231 | 67.0667 | 2
2015-10-05 11:15 | 2015-10-05 | 1 | 11 | 216 | 67.3167 | 2
2015-10-05 11:30 | 2015-10-05 | 1 | 11 | 222 | 67.5667 | 2
2015-10-05 11:45 | 2015-10-05 | 1 | 11 | 214 | 67.8167 | 2
2015-10-05 12:00 | 2015-10-05 | 1 | 12 | 235 | 68.1333 | 2
2015-10-05 12:15 | 2015-10-05 | 1 | 12 | 223 | 68.6333 | 2
2015-10-05 12:30 | 2015-10-05 | 1 | 12 | 219 | 69.1333 | 2
2015-10-05 12:45 | 2015-10-05 | 1 | 12 | 215 | 69.6333 | 2
2015-10-05 13:00 | 2015-10-05 | 1 | 13 | 234 | 70.0667 | 3
2015-10-05 13:15 | 2015-10-05 | 1 | 13 | 231 | 70.3167 | 3
2015-10-05 13:30 | 2015-10-05 | 1 | 13 | 231 | 70.5667 | 3
2015-10-05 13:45 | 2015-10-05 | 1 | 13 | 234 | 70.8167 | 3
2015-10-05 14:00 | 2015-10-05 | 1 | 14 | 231 | 71.1333 | 3
2015-10-05 14:15 | 2015-10-05 | 1 | 14 | 251 | 71.6333 | 3
2015-10-05 14:30 | 2015-10-05 | 1 | 14 | 242 | 72.1333 | 3
2015-10-05 14:45 | 2015-10-05 | 1 | 14 | 244 | 72.6333 | 3
2015-10-05 15:00 | 2015-10-05 | 1 | 15 | 235 | 72.9333 | 3
2015-10-05 15:15 | 2015-10-05 | 1 | 15 | 241 | 72.6833 | 3
2015-10-05 15:30 | 2015-10-05 | 1 | 15 | 239 | 72.4333 | 3
2015-10-05 15:45 | 2015-10-05 | 1 | 15 | 226 | 72.1833 | 3
2015-10-05 16:00 | 2015-10-05 | 1 | 16 | 232 | 71.8 | 3
2015-10-05 16:15 | 2015-10-05 | 1 | 16 | 237 | 71.05 | 3
2015-10-05 16:30 | 2015-10-05 | 1 | 16 | 232 | 70.3 | 3
2015-10-05 16:45 | 2015-10-05 | 1 | 16 | 241 | 69.55 | 2
2015-10-05 17:00 | 2015-10-05 | 1 | 17 | 233 | 68.9333 | 2
2015-10-05 17:15 | 2015-10-05 | 1 | 17 | 231 | 68.6833 | 2
2015-10-05 17:30 | 2015-10-05 | 1 | 17 | 229 | 68.4333 | 2
2015-10-05 17:45 | 2015-10-05 | 1 | 17 | 222 | 68.1833 | 2
2015-10-05 18:00 | 2015-10-05 | 1 | 18 | 227 | 67.9333 | 2
2015-10-05 18:15 | 2015-10-05 | 1 | 18 | 227 | 67.6833 | 2
2015-10-05 18:30 | 2015-10-05 | 1 | 18 | 221 | 67.4333 | 2
2015-10-05 18:45 | 2015-10-05 | 1 | 18 | 218 | 67.1833 | 2
2015-10-05 19:00 | 2015-10-05 | 1 | 19 | 210 | 66.9333 | 2
2015-10-05 19:15 | 2015-10-05 | 1 | 19 | 126 | 66.6833 | 2
2015-10-05 19:30 | 2015-10-05 | 1 | 19 | 117 | 66.4333 | 2
2015-10-05 19:45 | 2015-10-05 | 1 | 19 | 118 | 66.1833 | 2
2015-10-05 20:00 | 2015-10-05 | 1 | 20 | 112 | 65.9333 | 2
2015-10-05 20:15 | 2015-10-05 | 1 | 20 | 119 | 65.6833 | 2
2015-10-05 20:30 | 2015-10-05 | 1 | 20 | 113 | 65.4333 | 2
2015-10-05 20:45 | 2015-10-05 | 1 | 20 | 110 | 65.1833 | 2
2015-10-05 21:00 | 2015-10-05 | 1 | 21 | 106 | 65 | 1
2015-10-05 21:15 | 2015-10-05 | 1 | 21 | 114 | 65 | 1
2015-10-05 21:30 | 2015-10-05 | 1 | 21 | 103 | 65 | 1
2015-10-05 21:45 | 2015-10-05 | 1 | 21 | 108 | 65 | 1
2015-10-05 22:00 | 2015-10-05 | 1 | 22 | 99 | 64.9333 | 1
2015-10-05 22:15 | 2015-10-05 | 1 | 22 | 110 | 64.6833 | 1
2015-10-05 22:30 | 2015-10-05 | 1 | 22 | 107 | 64.4333 | 1
2015-10-05 22:45 | 2015-10-05 | 1 | 22 | 105 | 64.1833 | 1
2015-10-05 23:00 | 2015-10-05 | 1 | 23 | 104 | 63.8667 | 1
2015-10-05 23:15 | 2015-10-05 | 1 | 23 | 102 | 63.3667 | 1
2015-10-05 23:30 | 2015-10-05 | 1 | 23 | 105 | 62.8667 | 1
2015-10-05 23:45 | 2015-10-05 | 1 | 23 | 107 | 62.3667 | 1
2015-10-06 | 2015-10-06 | 2 | 0 | 104 | 62.0667 | 1
2015-10-06 00:15 | 2015-10-06 | 2 | 0 | 99 | 62.3167 | 1
2015-10-06 00:30 | 2015-10-06 | 2 | 0 | 104 | 62.5667 | 1
2015-10-06 00:45 | 2015-10-06 | 2 | 0 | 110 | 62.8167 | 1
2015-10-06 01:00 | 2015-10-06 | 2 | 1 | 102 | 63 | 1
2015-10-06 01:15 | 2015-10-06 | 2 | 1 | 104 | 63 | 1
2015-10-06 01:30 | 2015-10-06 | 2 | 1 | 98 | 63 | 1
2015-10-06 01:45 | 2015-10-06 | 2 | 1 | 101 | 63 | 1
2015-10-06 02:00 | 2015-10-06 | 2 | 2 | 104 | 62.9333 | 1
2015-10-06 02:15 | 2015-10-06 | 2 | 2 | 98 | 62.6833 | 1
2015-10-06 02:30 | 2015-10-06 | 2 | 2 | 107 | 62.4333 | 1
2015-10-06 02:45 | 2015-10-06 | 2 | 2 | 101 | 62.1833 | 1
2015-10-06 03:00 | 2015-10-06 | 2 | 3 | 100 | 61.8667 | 1
2015-10-06 03:15 | 2015-10-06 | 2 | 3 | 100 | 61.3667 | 1
2015-10-06 03:30 | 2015-10-06 | 2 | 3 | 101 | 60.8667 | 1
2015-10-06 03:45 | 2015-10-06 | 2 | 3 | 100 | 60.3667 | 1
2015-10-06 04:00 | 2015-10-06 | 2 | 4 | 113 | 60.0667 | 1
2015-10-06 04:15 | 2015-10-06 | 2 | 4 | 103 | 60.3167 | 1
2015-10-06 04:30 | 2015-10-06 | 2 | 4 | 104 | 60.5667 | 1
2015-10-06 04:45 | 2015-10-06 | 2 | 4 | 101 | 60.8167 | 1
2015-10-06 05:00 | 2015-10-06 | 2 | 5 | 106 | 60.9333 | 1
2015-10-06 05:15 | 2015-10-06 | 2 | 5 | 107 | 60.6833 | 1
2015-10-06 05:30 | 2015-10-06 | 2 | 5 | 104 | 60.4333 | 1
2015-10-06 05:45 | 2015-10-06 | 2 | 5 | 98 | 60.1833 | 1
2015-10-06 06:00 | 2015-10-06 | 2 | 6 | 104 | 60.2069 | 1
2015-10-06 06:15 | 2015-10-06 | 2 | 6 | 104 | 60.9828 | 1
2015-10-06 06:30 | 2015-10-06 | 2 | 6 | 104 | 61.7586 | 1
2015-10-06 06:45 | 2015-10-06 | 2 | 6 | 107 | 62.5345 | 1
2015-10-06 07:00 | 2015-10-06 | 2 | 7 | 104 | 63.069 | 1
2015-10-06 07:15 | 2015-10-06 | 2 | 7 | 177 | 63.3276 | 1
2015-10-06 07:30 | 2015-10-06 | 2 | 7 | 155 | 63.5862 | 1
2015-10-06 07:45 | 2015-10-06 | 2 | 7 | 148 | 63.8448 | 1
2015-10-06 08:00 | 2015-10-06 | 2 | 8 | 157 | 65.1333 | 2
2015-10-06 08:15 | 2015-10-06 | 2 | 8 | 160 | 65.6333 | 2
2015-10-06 08:30 | 2015-10-06 | 2 | 8 | 165 | 66.1333 | 2
2015-10-06 08:45 | 2015-10-06 | 2 | 8 | 164 | 66.6333 | 2
2015-10-06 09:00 | 2015-10-06 | 2 | 9 | 183 | 67.0667 | 2
2015-10-06 09:15 | 2015-10-06 | 2 | 9 | 189 | 67.3167 | 2
2015-10-06 09:30 | 2015-10-06 | 2 | 9 | 183 | 67.5667 | 2
2015-10-06 09:45 | 2015-10-06 | 2 | 9 | 200 | 67.8167 | 2
2015-10-06 10:00 | 2015-10-06 | 2 | 10 | 196 | 68.0667 | 2
2015-10-06 10:15 | 2015-10-06 | 2 | 10 | 193 | 68.3167 | 2
2015-10-06 10:30 | 2015-10-06 | 2 | 10 | 209 | 68.5667 | 2
2015-10-06 10:45 | 2015-10-06 | 2 | 10 | 221 | 68.8167 | 2
2015-10-06 11:00 | 2015-10-06 | 2 | 11 | 214 | 69 | 2
2015-10-06 11:15 | 2015-10-06 | 2 | 11 | 213 | 69 | 2
2015-10-06 11:30 | 2015-10-06 | 2 | 11 | 211 | 69 | 2
2015-10-06 11:45 | 2015-10-06 | 2 | 11 | 219 | 69 | 2
2015-10-06 12:00 | 2015-10-06 | 2 | 12 | 234 | 69.1333 | 2
2015-10-06 12:15 | 2015-10-06 | 2 | 12 | 227 | 69.6333 | 2
2015-10-06 12:30 | 2015-10-06 | 2 | 12 | 222 | 70.1333 | 3
2015-10-06 12:45 | 2015-10-06 | 2 | 12 | 212 | 70.6333 | 3
2015-10-06 13:00 | 2015-10-06 | 2 | 13 | 221 | 71.1333 | 3
2015-10-06 13:15 | 2015-10-06 | 2 | 13 | 224 | 71.6333 | 3
2015-10-06 13:30 | 2015-10-06 | 2 | 13 | 224 | 72.1333 | 3
2015-10-06 13:45 | 2015-10-06 | 2 | 13 | 229 | 72.6333 | 3
2015-10-06 14:00 | 2015-10-06 | 2 | 14 | 237 | 73 | 3
2015-10-06 14:15 | 2015-10-06 | 2 | 14 | 245 | 73 | 3
2015-10-06 14:30 | 2015-10-06 | 2 | 14 | 244 | 72.4857 | 3
2015-10-06 14:45 | 2015-10-06 | 2 | 14 | 253 | 71.6286 | 3
2015-10-06 15:00 | 2015-10-06 | 2 | 15 | 238 | 70.9333 | 3
2015-10-06 15:15 | 2015-10-06 | 2 | 15 | 237 | 70.6833 | 3
2015-10-06 15:30 | 2015-10-06 | 2 | 15 | 255 | 70.4333 | 3
2015-10-06 15:45 | 2015-10-06 | 2 | 15 | 237 | 70.1833 | 3
2015-10-06 16:00 | 2015-10-06 | 2 | 16 | 232 | 69.8 | 2
2015-10-06 16:15 | 2015-10-06 | 2 | 16 | 234 | 69.05 | 2
2015-10-06 16:30 | 2015-10-06 | 2 | 16 | 226 | 68.3 | 2
2015-10-06 16:45 | 2015-10-06 | 2 | 16 | 230 | 67.55 | 2
2015-10-06 17:00 | 2015-10-06 | 2 | 17 | 233 | 66.8 | 2
2015-10-06 17:15 | 2015-10-06 | 2 | 17 | 225 | 66.05 | 2
2015-10-06 17:30 | 2015-10-06 | 2 | 17 | 224 | 65.3 | 2
2015-10-06 17:45 | 2015-10-06 | 2 | 17 | 227 | 64.55 | 1
2015-10-06 18:00 | 2015-10-06 | 2 | 18 | 230 | 63.9333 | 1
2015-10-06 18:15 | 2015-10-06 | 2 | 18 | 223 | 63.6833 | 1
2015-10-06 18:30 | 2015-10-06 | 2 | 18 | 224 | 63.4333 | 1
2015-10-06 18:45 | 2015-10-06 | 2 | 18 | 219 | 63.1833 | 1
2015-10-06 19:00 | 2015-10-06 | 2 | 19 | 204 | 62.9333 | 1
2015-10-06 19:15 | 2015-10-06 | 2 | 19 | 146 | 62.6833 | 1
2015-10-06 19:30 | 2015-10-06 | 2 | 19 | 133 | 62.4333 | 1
2015-10-06 19:45 | 2015-10-06 | 2 | 19 | 137 | 62.1833 | 1
2015-10-06 20:00 | 2015-10-06 | 2 | 20 | 130 | 62 | 1
2015-10-06 20:15 | 2015-10-06 | 2 | 20 | 130 | 62 | 1
2015-10-06 20:30 | 2015-10-06 | 2 | 20 | 128 | 62 | 1
2015-10-06 20:45 | 2015-10-06 | 2 | 20 | 130 | 62 | 1
2015-10-06 21:00 | 2015-10-06 | 2 | 21 | 130 | 61.9333 | 1
2015-10-06 21:15 | 2015-10-06 | 2 | 21 | 118 | 61.6833 | 1
2015-10-06 21:30 | 2015-10-06 | 2 | 21 | 122 | 61.4333 | 1
2015-10-06 21:45 | 2015-10-06 | 2 | 21 | 110 | 61.1833 | 1
2015-10-06 22:00 | 2015-10-06 | 2 | 22 | 111 | 61 | 1
2015-10-06 22:15 | 2015-10-06 | 2 | 22 | 111 | 61 | 1
2015-10-06 22:30 | 2015-10-06 | 2 | 22 | 114 | 61 | 1
2015-10-06 22:45 | 2015-10-06 | 2 | 22 | 117 | 61 | 1
2015-10-06 23:00 | 2015-10-06 | 2 | 23 | 113 | 61 | 1
2015-10-06 23:15 | 2015-10-06 | 2 | 23 | 111 | 61 | 1
2015-10-06 23:30 | 2015-10-06 | 2 | 23 | 110 | 61 | 1
2015-10-06 23:45 | 2015-10-06 | 2 | 23 | 115 | 61 | 1
2015-10-07 | 2015-10-07 | 3 | 0 | 112 | 60.9333 | 1
2015-10-07 00:15 | 2015-10-07 | 3 | 0 | 111 | 60.6833 | 1
2015-10-07 00:30 | 2015-10-07 | 3 | 0 | 110 | 60.4333 | 1
2015-10-07 00:45 | 2015-10-07 | 3 | 0 | 108 | 60.1833 | 1
2015-10-07 01:00 | 2015-10-07 | 3 | 1 | 117 | 60.1053 | 1
2015-10-07 01:15 | 2015-10-07 | 3 | 1 | 111 | 60.5 | 1
2015-10-07 01:30 | 2015-10-07 | 3 | 1 | 112 | 60.8947 | 1
2015-10-07 01:45 | 2015-10-07 | 3 | 1 | 110 | 60.5 | 1
2015-10-07 02:00 | 2015-10-07 | 3 | 2 | 111 | 60 | 1
2015-10-07 02:15 | 2015-10-07 | 3 | 2 | 118 | 60 | 1
2015-10-07 02:30 | 2015-10-07 | 3 | 2 | 110 | 60 | 1
2015-10-07 02:45 | 2015-10-07 | 3 | 2 | 108 | 60 | 1
2015-10-07 03:00 | 2015-10-07 | 3 | 3 | 109 | 60.08 | 1
2015-10-07 03:15 | 2015-10-07 | 3 | 3 | 110 | 60.38 | 1
2015-10-07 03:30 | 2015-10-07 | 3 | 3 | 117 | 60.68 | 1
2015-10-07 03:45 | 2015-10-07 | 3 | 3 | 110 | 60.98 | 1
2015-10-07 04:00 | 2015-10-07 | 3 | 4 | 110 | 61 | 1
2015-10-07 04:15 | 2015-10-07 | 3 | 4 | 107 | 61 | 1
2015-10-07 04:30 | 2015-10-07 | 3 | 4 | 116 | 61 | 1
2015-10-07 04:45 | 2015-10-07 | 3 | 4 | 111 | 61 | 1
2015-10-07 05:00 | 2015-10-07 | 3 | 5 | 113 | 61 | 1
2015-10-07 05:15 | 2015-10-07 | 3 | 5 | 106 | 61 | 1
2015-10-07 05:30 | 2015-10-07 | 3 | 5 | 109 | 61 | 1
2015-10-07 05:45 | 2015-10-07 | 3 | 5 | 112 | 61 | 1
2015-10-07 06:00 | 2015-10-07 | 3 | 6 | 116 | 61.0667 | 1
2015-10-07 06:15 | 2015-10-07 | 3 | 6 | 119 | 61.3167 | 1
2015-10-07 06:30 | 2015-10-07 | 3 | 6 | 118 | 61.5667 | 1
2015-10-07 06:45 | 2015-10-07 | 3 | 6 | 115 | 61.8167 | 1
2015-10-07 07:00 | 2015-10-07 | 3 | 7 | 114 | 62.0667 | 1
2015-10-07 07:15 | 2015-10-07 | 3 | 7 | 236 | 62.3167 | 1
2015-10-07 07:30 | 2015-10-07 | 3 | 7 | 200 | 62.5667 | 1
2015-10-07 07:45 | 2015-10-07 | 3 | 7 | 193 | 62.8167 | 1
2015-10-07 08:00 | 2015-10-07 | 3 | 8 | 178 | 63.069 | 1
2015-10-07 08:15 | 2015-10-07 | 3 | 8 | 184 | 63.3276 | 1
2015-10-07 08:30 | 2015-10-07 | 3 | 8 | 201 | 63.5862 | 1
2015-10-07 08:45 | 2015-10-07 | 3 | 8 | 184 | 63.8448 | 1
2015-10-07 09:00 | 2015-10-07 | 3 | 9 | 190 | 64.1333 | 1
2015-10-07 09:15 | 2015-10-07 | 3 | 9 | 198 | 64.6333 | 1
2015-10-07 09:30 | 2015-10-07 | 3 | 9 | 207 | 65.1333 | 2
2015-10-07 09:45 | 2015-10-07 | 3 | 9 | 194 | 65.6333 | 2
2015-10-07 10:00 | 2015-10-07 | 3 | 10 | 199 | 66.0667 | 2
2015-10-07 10:15 | 2015-10-07 | 3 | 10 | 211 | 66.3167 | 2
2015-10-07 10:30 | 2015-10-07 | 3 | 10 | 219 | 66.5667 | 2
2015-10-07 10:45 | 2015-10-07 | 3 | 10 | 236 | 66.8167 | 2
2015-10-07 11:00 | 2015-10-07 | 3 | 11 | 222 | 67.3333 | 2
2015-10-07 11:15 | 2015-10-07 | 3 | 11 | 212 | 68.5833 | 2
2015-10-07 11:30 | 2015-10-07 | 3 | 11 | 215 | 69.8333 | 2
2015-10-07 11:45 | 2015-10-07 | 3 | 11 | 222 | 71.0833 | 3
2015-10-07 12:00 | 2015-10-07 | 3 | 12 | 226 | 72.0667 | 3
2015-10-07 12:15 | 2015-10-07 | 3 | 12 | 219 | 72.3167 | 3
2015-10-07 12:30 | 2015-10-07 | 3 | 12 | 225 | 72.5667 | 3
2015-10-07 12:45 | 2015-10-07 | 3 | 12 | 230 | 72.8167 | 3
2015-10-07 13:00 | 2015-10-07 | 3 | 13 | 223 | 72.7333 | 3
2015-10-07 13:15 | 2015-10-07 | 3 | 13 | 239 | 71.7333 | 3
2015-10-07 13:30 | 2015-10-07 | 3 | 13 | 243 | 70.7333 | 3
2015-10-07 13:45 | 2015-10-07 | 3 | 13 | 236 | 69.7333 | 2
2015-10-07 14:00 | 2015-10-07 | 3 | 14 | 238 | 68.8667 | 2
2015-10-07 14:15 | 2015-10-07 | 3 | 14 | 230 | 68.3667 | 2
2015-10-07 14:30 | 2015-10-07 | 3 | 14 | 229 | 67.8667 | 2
2015-10-07 14:45 | 2015-10-07 | 3 | 14 | 254 | 67.3667 | 2
2015-10-07 15:00 | 2015-10-07 | 3 | 15 | 243 | 66.9333 | 2
2015-10-07 15:15 | 2015-10-07 | 3 | 15 | 246 | 66.6833 | 2
2015-10-07 15:30 | 2015-10-07 | 3 | 15 | 233 | 66.4333 | 2
2015-10-07 15:45 | 2015-10-07 | 3 | 15 | 245 | 66.1833 | 2
2015-10-07 16:00 | 2015-10-07 | 3 | 16 | 239 | 65.8667 | 2
2015-10-07 16:15 | 2015-10-07 | 3 | 16 | 243 | 65.3667 | 2
2015-10-07 16:30 | 2015-10-07 | 3 | 16 | 231 | 64.8667 | 1
2015-10-07 16:45 | 2015-10-07 | 3 | 16 | 231 | 64.3667 | 1
2015-10-07 17:00 | 2015-10-07 | 3 | 17 | 230 | 63.8667 | 1
2015-10-07 17:15 | 2015-10-07 | 3 | 17 | 225 | 63.3667 | 1
2015-10-07 17:30 | 2015-10-07 | 3 | 17 | 236 | 62.8667 | 1
2015-10-07 17:45 | 2015-10-07 | 3 | 17 | 228 | 62.3667 | 1
2015-10-07 18:00 | 2015-10-07 | 3 | 18 | 214 | 61.9333 | 1
2015-10-07 18:15 | 2015-10-07 | 3 | 18 | 227 | 61.6833 | 1
2015-10-07 18:30 | 2015-10-07 | 3 | 18 | 217 | 61.4333 | 1
2015-10-07 18:45 | 2015-10-07 | 3 | 18 | 227 | 61.1833 | 1
2015-10-07 19:00 | 2015-10-07 | 3 | 19 | 213 | 60.9333 | 1
2015-10-07 19:15 | 2015-10-07 | 3 | 19 | 142 | 60.6833 | 1
2015-10-07 19:30 | 2015-10-07 | 3 | 19 | 126 | 60.4333 | 1
2015-10-07 19:45 | 2015-10-07 | 3 | 19 | 127 | 60.1833 | 1
2015-10-07 20:00 | 2015-10-07 | 3 | 20 | 124 | 59.9333 | 1
2015-10-07 20:15 | 2015-10-07 | 3 | 20 | 123 | 59.6833 | 1
2015-10-07 20:30 | 2015-10-07 | 3 | 20 | 134 | 59.4333 | 1
2015-10-07 20:45 | 2015-10-07 | 3 | 20 | 126 | 59.1833 | 1
2015-10-07 21:00 | 2015-10-07 | 3 | 21 | 120 | 59 | 1
2015-10-07 21:15 | 2015-10-07 | 3 | 21 | 110 | 59 | 1
2015-10-07 21:30 | 2015-10-07 | 3 | 21 | 117 | 59 | 1
2015-10-07 21:45 | 2015-10-07 | 3 | 21 | 110 | 59 | 1
2015-10-07 22:00 | 2015-10-07 | 3 | 22 | 110 | 59.1333 | 1
2015-10-07 22:15 | 2015-10-07 | 3 | 22 | 109 | 59.6333 | 1
2015-10-07 22:30 | 2015-10-07 | 3 | 22 | 107 | 60.1333 | 1
2015-10-07 22:45 | 2015-10-07 | 3 | 22 | 118 | 60.6333 | 1
2015-10-07 23:00 | 2015-10-07 | 3 | 23 | 110 | 61.0667 | 1
2015-10-07 23:15 | 2015-10-07 | 3 | 23 | 107 | 61.3167 | 1
2015-10-07 23:30 | 2015-10-07 | 3 | 23 | 108 | 61.5667 | 1
2015-10-07 23:45 | 2015-10-07 | 3 | 23 | 110 | 61.8167 | 1
2015-10-08 | 2015-10-08 | 4 | 0 | 115 | 61.8667 | 1
2015-10-08 00:15 | 2015-10-08 | 4 | 0 | 107 | 61.3667 | 1
2015-10-08 00:30 | 2015-10-08 | 4 | 0 | 108 | 60.8667 | 1
2015-10-08 00:45 | 2015-10-08 | 4 | 0 | 106 | 60.3667 | 1
2015-10-08 01:00 | 2015-10-08 | 4 | 1 | 110 | 60 | 1
2015-10-08 01:15 | 2015-10-08 | 4 | 1 | 114 | 60 | 1
2015-10-08 01:30 | 2015-10-08 | 4 | 1 | 108 | 60 | 1
2015-10-08 01:45 | 2015-10-08 | 4 | 1 | 107 | 60 | 1
2015-10-08 02:00 | 2015-10-08 | 4 | 2 | 105 | 60 | 1
2015-10-08 02:15 | 2015-10-08 | 4 | 2 | 114 | 60 | 1
2015-10-08 02:30 | 2015-10-08 | 4 | 2 | 109 | 60 | 1
2015-10-08 02:45 | 2015-10-08 | 4 | 2 | 109 | 60 | 1
2015-10-08 03:00 | 2015-10-08 | 4 | 3 | 105 | 59.9333 | 1
2015-10-08 03:15 | 2015-10-08 | 4 | 3 | 106 | 59.6833 | 1
2015-10-08 03:30 | 2015-10-08 | 4 | 3 | 118 | 59.4333 | 1
2015-10-08 03:45 | 2015-10-08 | 4 | 3 | 104 | 59.1833 | 1
2015-10-08 04:00 | 2015-10-08 | 4 | 4 | 106 | 59 | 1
2015-10-08 04:15 | 2015-10-08 | 4 | 4 | 104 | 59 | 1
2015-10-08 04:30 | 2015-10-08 | 4 | 4 | 111 | 59 | 1
2015-10-08 04:45 | 2015-10-08 | 4 | 4 | 111 | 59 | 1
2015-10-08 05:00 | 2015-10-08 | 4 | 5 | 109 | 59.1333 | 1
2015-10-08 05:15 | 2015-10-08 | 4 | 5 | 107 | 59.6333 | 1
2015-10-08 05:30 | 2015-10-08 | 4 | 5 | 108 | 60.1333 | 1
2015-10-08 05:45 | 2015-10-08 | 4 | 5 | 112 | 60.6333 | 1
2015-10-08 06:00 | 2015-10-08 | 4 | 6 | 110 | 61 | 1
2015-10-08 06:15 | 2015-10-08 | 4 | 6 | 112 | 61 | 1
2015-10-08 06:30 | 2015-10-08 | 4 | 6 | 108 | 61 | 1
2015-10-08 06:45 | 2015-10-08 | 4 | 6 | 112 | 61 | 1
2015-10-08 07:00 | 2015-10-08 | 4 | 7 | 111 | 61.2 | 1
2015-10-08 07:15 | 2015-10-08 | 4 | 7 | 213 | 61.95 | 1
2015-10-08 07:30 | 2015-10-08 | 4 | 7 | 217 | 62.7 | 1
2015-10-08 07:45 | 2015-10-08 | 4 | 7 | 162 | 63.45 | 1
2015-10-08 08:00 | 2015-10-08 | 4 | 8 | 169 | 64.0667 | 1
2015-10-08 08:15 | 2015-10-08 | 4 | 8 | 175 | 64.3167 | 1
2015-10-08 08:30 | 2015-10-08 | 4 | 8 | 191 | 64.5667 | 1
2015-10-08 08:45 | 2015-10-08 | 4 | 8 | 198 | 64.8167 | 1
2015-10-08 09:00 | 2015-10-08 | 4 | 9 | 183 | 65.2 | 2
2015-10-08 09:15 | 2015-10-08 | 4 | 9 | 195 | 65.95 | 2
2015-10-08 09:30 | 2015-10-08 | 4 | 9 | 212 | 66.7 | 2
2015-10-08 09:45 | 2015-10-08 | 4 | 9 | 198 | 67.45 | 2
2015-10-08 10:00 | 2015-10-08 | 4 | 10 | 201 | 68.0667 | 2
2015-10-08 10:15 | 2015-10-08 | 4 | 10 | 202 | 68.3167 | 2
2015-10-08 10:30 | 2015-10-08 | 4 | 10 | 219 | 68.5667 | 2
2015-10-08 10:45 | 2015-10-08 | 4 | 10 | 216 | 68.8167 | 2
2015-10-08 11:00 | 2015-10-08 | 4 | 11 | 214 | 69.1333 | 2
2015-10-08 11:15 | 2015-10-08 | 4 | 11 | 207 | 69.6333 | 2
2015-10-08 11:30 | 2015-10-08 | 4 | 11 | 215 | 70.1333 | 3
2015-10-08 11:45 | 2015-10-08 | 4 | 11 | 229 | 70.6333 | 3
2015-10-08 12:00 | 2015-10-08 | 4 | 12 | 224 | 71.5333 | 3
2015-10-08 12:15 | 2015-10-08 | 4 | 12 | 222 | 73.5333 | 3
2015-10-08 12:30 | 2015-10-08 | 4 | 12 | 215 | 75.5333 | 4
2015-10-08 12:45 | 2015-10-08 | 4 | 12 | 222 | 77.5333 | 4
2015-10-08 13:00 | 2015-10-08 | 4 | 13 | 244 | 79 | 4
2015-10-08 13:15 | 2015-10-08 | 4 | 13 | 216 | 79 | 4
2015-10-08 13:30 | 2015-10-08 | 4 | 13 | 235 | 79 | 4
2015-10-08 13:45 | 2015-10-08 | 4 | 13 | 223 | 79 | 4
2015-10-08 14:00 | 2015-10-08 | 4 | 14 | 243 | 78.7333 | 4
2015-10-08 14:15 | 2015-10-08 | 4 | 14 | 240 | 77.7333 | 4
2015-10-08 14:30 | 2015-10-08 | 4 | 14 | 238 | 76.7333 | 4
2015-10-08 14:45 | 2015-10-08 | 4 | 14 | 238 | 75.7333 | 4
2015-10-08 15:00 | 2015-10-08 | 4 | 15 | 251 | 74.8 | 3
2015-10-08 15:15 | 2015-10-08 | 4 | 15 | 243 | 74.05 | 3
2015-10-08 15:30 | 2015-10-08 | 4 | 15 | 228 | 73.3 | 3
2015-10-08 15:45 | 2015-10-08 | 4 | 15 | 234 | 72.55 | 3
2015-10-08 16:00 | 2015-10-08 | 4 | 16 | 237 | 72 | 3
2015-10-08 16:15 | 2015-10-08 | 4 | 16 | 243 | 72 | 3
2015-10-08 16:30 | 2015-10-08 | 4 | 16 | 229 | 72 | 3
2015-10-08 16:45 | 2015-10-08 | 4 | 16 | 224 | 72 | 3
2015-10-08 17:00 | 2015-10-08 | 4 | 17 | 234 | 71.6667 | 3
2015-10-08 17:15 | 2015-10-08 | 4 | 17 | 219 | 70.4167 | 3
2015-10-08 17:30 | 2015-10-08 | 4 | 17 | 236 | 69.1667 | 2
2015-10-08 17:45 | 2015-10-08 | 4 | 17 | 226 | 67.9167 | 2
2015-10-08 18:00 | 2015-10-08 | 4 | 18 | 209 | 66.8 | 2
2015-10-08 18:15 | 2015-10-08 | 4 | 18 | 216 | 66.05 | 2
2015-10-08 18:30 | 2015-10-08 | 4 | 18 | 205 | 65.3 | 2
2015-10-08 18:45 | 2015-10-08 | 4 | 18 | 220 | 64.55 | 1
2015-10-08 19:00 | 2015-10-08 | 4 | 19 | 202 | 63.9333 | 1
2015-10-08 19:15 | 2015-10-08 | 4 | 19 | 125 | 63.6833 | 1
2015-10-08 19:30 | 2015-10-08 | 4 | 19 | 122 | 63.4333 | 1
2015-10-08 19:45 | 2015-10-08 | 4 | 19 | 126 | 63.1833 | 1
2015-10-08 20:00 | 2015-10-08 | 4 | 20 | 118 | 63 | 1
2015-10-08 20:15 | 2015-10-08 | 4 | 20 | 115 | 63 | 1
2015-10-08 20:30 | 2015-10-08 | 4 | 20 | 113 | 63 | 1
2015-10-08 20:45 | 2015-10-08 | 4 | 20 | 115 | 63 | 1
2015-10-08 21:00 | 2015-10-08 | 4 | 21 | 107 | 63 | 1
2015-10-08 21:15 | 2015-10-08 | 4 | 21 | 108 | 63 | 1
2015-10-08 21:30 | 2015-10-08 | 4 | 21 | 104 | 63 | 1
2015-10-08 21:45 | 2015-10-08 | 4 | 21 | 104 | 63 | 1
2015-10-08 22:00 | 2015-10-08 | 4 | 22 | 112 | 62.9333 | 1
2015-10-08 22:15 | 2015-10-08 | 4 | 22 | 103 | 62.6833 | 1
2015-10-08 22:30 | 2015-10-08 | 4 | 22 | 103 | 62.4333 | 1
2015-10-08 22:45 | 2015-10-08 | 4 | 22 | 103 | 62.1833 | 1
2015-10-08 23:00 | 2015-10-08 | 4 | 23 | 104 | 61.9333 | 1
2015-10-08 23:15 | 2015-10-08 | 4 | 23 | 101 | 61.6833 | 1
2015-10-08 23:30 | 2015-10-08 | 4 | 23 | 112 | 61.4333 | 1
2015-10-08 23:45 | 2015-10-08 | 4 | 23 | 103 | 61.1833 | 1
2015-10-09 | 2015-10-09 | 5 | 0 | 106 | 60.9333 | 1
2015-10-09 00:15 | 2015-10-09 | 5 | 0 | 101 | 60.6833 | 1
2015-10-09 00:30 | 2015-10-09 | 5 | 0 | 102 | 60.4333 | 1
2015-10-09 00:45 | 2015-10-09 | 5 | 0 | 107 | 60.1833 | 1
2015-10-09 01:00 | 2015-10-09 | 5 | 1 | 104 | 59.9333 | 1
2015-10-09 01:15 | 2015-10-09 | 5 | 1 | 103 | 59.6833 | 1
2015-10-09 01:30 | 2015-10-09 | 5 | 1 | 106 | 59.4333 | 1
2015-10-09 01:45 | 2015-10-09 | 5 | 1 | 113 | 59.1833 | 1
2015-10-09 02:00 | 2015-10-09 | 5 | 2 | 102 | 58.8667 | 1
2015-10-09 02:15 | 2015-10-09 | 5 | 2 | 106 | 58.3667 | 1
2015-10-09 02:30 | 2015-10-09 | 5 | 2 | 99 | 57.8667 | 1
2015-10-09 02:45 | 2015-10-09 | 5 | 2 | 103 | 57.3667 | 1
2015-10-09 03:00 | 2015-10-09 | 5 | 3 | 111 | 57.0667 | 1
2015-10-09 03:15 | 2015-10-09 | 5 | 3 | 102 | 57.3167 | 1
2015-10-09 03:30 | 2015-10-09 | 5 | 3 | 107 | 57.5667 | 1
2015-10-09 03:45 | 2015-10-09 | 5 | 3 | 104 | 57.8167 | 1
2015-10-09 04:00 | 2015-10-09 | 5 | 4 | 105 | 57.9333 | 1
2015-10-09 04:15 | 2015-10-09 | 5 | 4 | 107 | 57.6833 | 1
2015-10-09 04:30 | 2015-10-09 | 5 | 4 | 103 | 57.4333 | 1
2015-10-09 04:45 | 2015-10-09 | 5 | 4 | 100 | 57.1833 | 1
2015-10-09 05:00 | 2015-10-09 | 5 | 5 | 104 | 57 | 1
2015-10-09 05:15 | 2015-10-09 | 5 | 5 | 100 | 57 | 1
2015-10-09 05:30 | 2015-10-09 | 5 | 5 | 106 | 57 | 1
2015-10-09 05:45 | 2015-10-09 | 5 | 5 | 103 | 57 | 1
2015-10-09 06:00 | 2015-10-09 | 5 | 6 | 108 | 57.2667 | 1
2015-10-09 06:15 | 2015-10-09 | 5 | 6 | 107 | 58.2667 | 1
2015-10-09 06:30 | 2015-10-09 | 5 | 6 | 106 | 59.2667 | 1
2015-10-09 06:45 | 2015-10-09 | 5 | 6 | 115 | 60.2667 | 1
2015-10-09 07:00 | 2015-10-09 | 5 | 7 | 112 | 61.0667 | 1
2015-10-09 07:15 | 2015-10-09 | 5 | 7 | 187 | 61.3167 | 1
2015-10-09 07:30 | 2015-10-09 | 5 | 7 | 174 | 61.5667 | 1
2015-10-09 07:45 | 2015-10-09 | 5 | 7 | 164 | 61.8167 | 1
2015-10-09 08:00 | 2015-10-09 | 5 | 8 | 168 | 62.2667 | 1
2015-10-09 08:15 | 2015-10-09 | 5 | 8 | 156 | 63.2667 | 1
2015-10-09 08:30 | 2015-10-09 | 5 | 8 | 164 | 64.2667 | 1
2015-10-09 08:45 | 2015-10-09 | 5 | 8 | 177 | 65.2667 | 2
2015-10-09 09:00 | 2015-10-09 | 5 | 9 | 198 | 66.0667 | 2
2015-10-09 09:15 | 2015-10-09 | 5 | 9 | 180 | 66.3167 | 2
2015-10-09 09:30 | 2015-10-09 | 5 | 9 | 193 | 66.5667 | 2
2015-10-09 09:45 | 2015-10-09 | 5 | 9 | 189 | 66.8167 | 2
2015-10-09 10:00 | 2015-10-09 | 5 | 10 | 189 | 66.5 | 2
2015-10-09 10:15 | 2015-10-09 | 5 | 10 | 202 | 66 | 2
2015-10-09 10:30 | 2015-10-09 | 5 | 10 | 212 | 66 | 2
2015-10-09 10:45 | 2015-10-09 | 5 | 10 | 222 | 66 | 2
2015-10-09 11:00 | 2015-10-09 | 5 | 11 | 212 | 66.7333 | 2
2015-10-09 11:15 | 2015-10-09 | 5 | 11 | 215 | 69.4833 | 2
2015-10-09 11:30 | 2015-10-09 | 5 | 11 | 216 | 72.2333 | 3
2015-10-09 11:45 | 2015-10-09 | 5 | 11 | 223 | 74.9833 | 3
2015-10-09 12:00 | 2015-10-09 | 5 | 12 | 230 | 77 | 4
2015-10-09 12:15 | 2015-10-09 | 5 | 12 | 217 | 77 | 4
2015-10-09 12:30 | 2015-10-09 | 5 | 12 | 224 | 77 | 4
2015-10-09 12:45 | 2015-10-09 | 5 | 12 | 220 | 77 | 4
2015-10-09 13:00 | 2015-10-09 | 5 | 13 | 222 | 77 | 4
2015-10-09 13:15 | 2015-10-09 | 5 | 13 | 235 | 77 | 4
2015-10-09 13:30 | 2015-10-09 | 5 | 13 | 214 | 77 | 4
2015-10-09 13:45 | 2015-10-09 | 5 | 13 | 221 | 77 | 4
2015-10-09 14:00 | 2015-10-09 | 5 | 14 | 225 | 76.9333 | 4
2015-10-09 14:15 | 2015-10-09 | 5 | 14 | 236 | 76.6833 | 4
2015-10-09 14:30 | 2015-10-09 | 5 | 14 | 224 | 76.4333 | 4
2015-10-09 14:45 | 2015-10-09 | 5 | 14 | 227 | 76.1833 | 4
2015-10-09 15:00 | 2015-10-09 | 5 | 15 | 223 | 75.9333 | 4
2015-10-09 15:15 | 2015-10-09 | 5 | 15 | 222 | 75.6833 | 4
2015-10-09 15:30 | 2015-10-09 | 5 | 15 | 245 | 75.4333 | 4
2015-10-09 15:45 | 2015-10-09 | 5 | 15 | 223 | 75.1833 | 4
2015-10-09 16:00 | 2015-10-09 | 5 | 16 | 236 | 74.6 | 3
2015-10-09 16:15 | 2015-10-09 | 5 | 16 | 218 | 73.1 | 3
2015-10-09 16:30 | 2015-10-09 | 5 | 16 | 225 | 71.6 | 3
2015-10-09 16:45 | 2015-10-09 | 5 | 16 | 235 | 70.1 | 3
2015-10-09 17:00 | 2015-10-09 | 5 | 17 | 219 | 68.5122 | 2
2015-10-09 17:15 | 2015-10-09 | 5 | 17 | 232 | 66.6829 | 2
2015-10-09 17:30 | 2015-10-09 | 5 | 17 | 225 | 64.8537 | 1
2015-10-09 17:45 | 2015-10-09 | 5 | 17 | 218 | 64.4211 | 1
2015-10-09 18:00 | 2015-10-09 | 5 | 18 | 214 | 64.9333 | 1
2015-10-09 18:15 | 2015-10-09 | 5 | 18 | 210 | 64.6833 | 1
2015-10-09 18:30 | 2015-10-09 | 5 | 18 | 205 | 64.4333 | 1
2015-10-09 18:45 | 2015-10-09 | 5 | 18 | 212 | 64.1833 | 1
2015-10-09 19:00 | 2015-10-09 | 5 | 19 | 197 | 63.9333 | 1
2015-10-09 19:15 | 2015-10-09 | 5 | 19 | 122 | 63.6833 | 1
2015-10-09 19:30 | 2015-10-09 | 5 | 19 | 125 | 63.4333 | 1
2015-10-09 19:45 | 2015-10-09 | 5 | 19 | 133 | 63.1833 | 1
2015-10-09 20:00 | 2015-10-09 | 5 | 20 | 128 | 63 | 1
2015-10-09 20:15 | 2015-10-09 | 5 | 20 | 121 | 63 | 1
2015-10-09 20:30 | 2015-10-09 | 5 | 20 | 120 | 63 | 1
2015-10-09 20:45 | 2015-10-09 | 5 | 20 | 124 | 63 | 1
2015-10-09 21:00 | 2015-10-09 | 5 | 21 | 127 | 62.9333 | 1
2015-10-09 21:15 | 2015-10-09 | 5 | 21 | 115 | 62.6833 | 1
2015-10-09 21:30 | 2015-10-09 | 5 | 21 | 108 | 62.4333 | 1
2015-10-09 21:45 | 2015-10-09 | 5 | 21 | 116 | 62.1833 | 1
2015-10-09 22:00 | 2015-10-09 | 5 | 22 | 119 | 62.0816 | 1
2015-10-09 22:15 | 2015-10-09 | 5 | 22 | 108 | 62.3878 | 1
2015-10-09 22:30 | 2015-10-09 | 5 | 22 | 111 | 62.6939 | 1
2015-10-09 22:45 | 2015-10-09 | 5 | 22 | 106 | 63 | 1
2015-10-09 23:00 | 2015-10-09 | 5 | 23 | 111 | 61.9 | 1
2015-10-09 23:15 | 2015-10-09 | 5 | 23 | 115 | 61.525 | 1
2015-10-09 23:30 | 2015-10-09 | 5 | 23 | 110 | 61.15 | 1
2015-10-09 23:45 | 2015-10-09 | 5 | 23 | 109 | 61 | 1
2015-10-10 | 2015-10-10 | 6 | 0 | 110 | 61 | 1
2015-10-10 00:15 | 2015-10-10 | 6 | 0 | 109 | 61 | 1
2015-10-10 00:30 | 2015-10-10 | 6 | 0 | 114 | 61 | 1
2015-10-10 00:45 | 2015-10-10 | 6 | 0 | 110 | 61 | 1
2015-10-10 01:00 | 2015-10-10 | 6 | 1 | 108 | 61 | 1
2015-10-10 01:15 | 2015-10-10 | 6 | 1 | 112 | 61 | 1
2015-10-10 01:30 | 2015-10-10 | 6 | 1 | 108 | 61 | 1
2015-10-10 01:45 | 2015-10-10 | 6 | 1 | 111 | 61 | 1
2015-10-10 02:00 | 2015-10-10 | 6 | 2 | 117 | 61 | 1
2015-10-10 02:15 | 2015-10-10 | 6 | 2 | 108 | 61 | 1
2015-10-10 02:30 | 2015-10-10 | 6 | 2 | 101 | 61 | 1
2015-10-10 02:45 | 2015-10-10 | 6 | 2 | 100 | 61 | 1
2015-10-10 03:00 | 2015-10-10 | 6 | 3 | 98 | 61 | 1
2015-10-10 03:15 | 2015-10-10 | 6 | 3 | 99 | 61 | 1
2015-10-10 03:30 | 2015-10-10 | 6 | 3 | 100 | 61 | 1
2015-10-10 03:45 | 2015-10-10 | 6 | 3 | 99 | 61 | 1
2015-10-10 04:00 | 2015-10-10 | 6 | 4 | 101 | 60.1143 | 1
2015-10-10 04:15 | 2015-10-10 | 6 | 4 | 97 | 60.5429 | 1
2015-10-10 04:30 | 2015-10-10 | 6 | 4 | 98 | 60.9714 | 1
2015-10-10 04:45 | 2015-10-10 | 6 | 4 | 105 | 61 | 1
2015-10-10 05:00 | 2015-10-10 | 6 | 5 | 103 | 61 | 1
2015-10-10 05:15 | 2015-10-10 | 6 | 5 | 102 | 61 | 1
2015-10-10 05:30 | 2015-10-10 | 6 | 5 | 96 | 61 | 1
2015-10-10 05:45 | 2015-10-10 | 6 | 5 | 103 | 61 | 1
2015-10-10 06:00 | 2015-10-10 | 6 | 6 | 103 | 60.1379 | 1
2015-10-10 06:15 | 2015-10-10 | 6 | 6 | 95 | 60.6552 | 1
2015-10-10 06:30 | 2015-10-10 | 6 | 6 | 99 | 61 | 1
2015-10-10 06:45 | 2015-10-10 | 6 | 6 | 101 | 60.6875 | 1
2015-10-10 07:00 | 2015-10-10 | 6 | 7 | 101 | 60.2 | 1
2015-10-10 07:15 | 2015-10-10 | 6 | 7 | 103 | 60.95 | 1
2015-10-10 07:30 | 2015-10-10 | 6 | 7 | 97 | 61.7 | 1
2015-10-10 07:45 | 2015-10-10 | 6 | 7 | 93 | 62.45 | 1
2015-10-10 08:00 | 2015-10-10 | 6 | 8 | 97 | 63 | 1
2015-10-10 08:15 | 2015-10-10 | 6 | 8 | 94 | 63 | 1
2015-10-10 08:30 | 2015-10-10 | 6 | 8 | 95 | 63 | 1
2015-10-10 08:45 | 2015-10-10 | 6 | 8 | 98 | 63 | 1
2015-10-10 09:00 | 2015-10-10 | 6 | 9 | 100 | 63.375 | 1
2015-10-10 09:15 | 2015-10-10 | 6 | 9 | 99 | 64.7812 | 1
2015-10-10 09:30 | 2015-10-10 | 6 | 9 | 95 | 66.2667 | 2
2015-10-10 09:45 | 2015-10-10 | 6 | 9 | 94 | 68 | 2
2015-10-10 10:00 | 2015-10-10 | 6 | 10 | 94 | 67.9333 | 2
2015-10-10 10:15 | 2015-10-10 | 6 | 10 | 94 | 67.6833 | 2
2015-10-10 10:30 | 2015-10-10 | 6 | 10 | 99 | 67.4333 | 2
2015-10-10 10:45 | 2015-10-10 | 6 | 10 | 94 | 67.1833 | 2
2015-10-10 11:00 | 2015-10-10 | 6 | 11 | 97 | 67.1429 | 2
2015-10-10 11:15 | 2015-10-10 | 6 | 11 | 98 | 67.6786 | 2
2015-10-10 11:30 | 2015-10-10 | 6 | 11 | 96 | 68.375 | 2
2015-10-10 11:45 | 2015-10-10 | 6 | 11 | 92 | 69.3125 | 2
2015-10-10 12:00 | 2015-10-10 | 6 | 12 | 95 | 69.9333 | 2
2015-10-10 12:15 | 2015-10-10 | 6 | 12 | 96 | 69.6833 | 2
2015-10-10 12:30 | 2015-10-10 | 6 | 12 | 98 | 69.4333 | 2
2015-10-10 12:45 | 2015-10-10 | 6 | 12 | 100 | 69.1833 | 2
2015-10-10 13:00 | 2015-10-10 | 6 | 13 | 97 | 69.0667 | 2
2015-10-10 13:15 | 2015-10-10 | 6 | 13 | 100 | 69.3167 | 2
2015-10-10 13:30 | 2015-10-10 | 6 | 13 | 108 | 69.5667 | 2
2015-10-10 13:45 | 2015-10-10 | 6 | 13 | 97 | 69.8167 | 2
2015-10-10 14:00 | 2015-10-10 | 6 | 14 | 101 | 70.0667 | 3
2015-10-10 14:15 | 2015-10-10 | 6 | 14 | 96 | 70.3167 | 3
2015-10-10 14:30 | 2015-10-10 | 6 | 14 | 100 | 70.5667 | 3
2015-10-10 14:45 | 2015-10-10 | 6 | 14 | 95 | 70.8167 | 3
2015-10-10 15:00 | 2015-10-10 | 6 | 15 | 110 | 70.8667 | 3
2015-10-10 15:15 | 2015-10-10 | 6 | 15 | 99 | 70.3667 | 3
2015-10-10 15:30 | 2015-10-10 | 6 | 15 | 101 | 69.8667 | 2
2015-10-10 15:45 | 2015-10-10 | 6 | 15 | 101 | 69.3667 | 2
2015-10-10 16:00 | 2015-10-10 | 6 | 16 | 100 | 68.8667 | 2
2015-10-10 16:15 | 2015-10-10 | 6 | 16 | 104 | 68.3667 | 2
2015-10-10 16:30 | 2015-10-10 | 6 | 16 | 101 | 67.8667 | 2
2015-10-10 16:45 | 2015-10-10 | 6 | 16 | 100 | 67.3667 | 2
2015-10-10 17:00 | 2015-10-10 | 6 | 17 | 99 | 66.8667 | 2
2015-10-10 17:15 | 2015-10-10 | 6 | 17 | 109 | 66.3667 | 2
2015-10-10 17:30 | 2015-10-10 | 6 | 17 | 107 | 65.8667 | 2
2015-10-10 17:45 | 2015-10-10 | 6 | 17 | 105 | 65.3667 | 2
2015-10-10 18:00 | 2015-10-10 | 6 | 18 | 104 | 65 | 1
2015-10-10 18:15 | 2015-10-10 | 6 | 18 | 104 | 65 | 1
2015-10-10 18:30 | 2015-10-10 | 6 | 18 | 107 | 65 | 1
2015-10-10 18:45 | 2015-10-10 | 6 | 18 | 105 | 65 | 1
2015-10-10 19:00 | 2015-10-10 | 6 | 19 | 105 | 64.9333 | 1
2015-10-10 19:15 | 2015-10-10 | 6 | 19 | 102 | 64.6833 | 1
2015-10-10 19:30 | 2015-10-10 | 6 | 19 | 109 | 64.4333 | 1
2015-10-10 19:45 | 2015-10-10 | 6 | 19 | 106 | 64.1833 | 1
2015-10-10 20:00 | 2015-10-10 | 6 | 20 | 104 | 64 | 1
2015-10-10 20:15 | 2015-10-10 | 6 | 20 | 105 | 64 | 1
2015-10-10 20:30 | 2015-10-10 | 6 | 20 | 104 | 64 | 1
2015-10-10 20:45 | 2015-10-10 | 6 | 20 | 109 | 64 | 1
2015-10-10 21:00 | 2015-10-10 | 6 | 21 | 106 | 64 | 1
2015-10-10 21:15 | 2015-10-10 | 6 | 21 | 103 | 64 | 1
2015-10-10 21:30 | 2015-10-10 | 6 | 21 | 103 | 64 | 1
2015-10-10 21:45 | 2015-10-10 | 6 | 21 | 105 | 64 | 1
2015-10-10 22:00 | 2015-10-10 | 6 | 22 | 106 | 63.9333 | 1
2015-10-10 22:15 | 2015-10-10 | 6 | 22 | 103 | 63.6833 | 1
2015-10-10 22:30 | 2015-10-10 | 6 | 22 | 102 | 63.4333 | 1
2015-10-10 22:45 | 2015-10-10 | 6 | 22 | 100 | 63.1833 | 1
2015-10-10 23:00 | 2015-10-10 | 6 | 23 | 105 | 63 | 1
2015-10-10 23:15 | 2015-10-10 | 6 | 23 | 98 | 63 | 1
2015-10-10 23:30 | 2015-10-10 | 6 | 23 | 100 | 63 | 1
2015-10-10 23:45 | 2015-10-10 | 6 | 23 | 101 | 63 | 1
2015-10-11 | 2015-10-11 | 7 | 0 | 98 | 62.9333 | 1
2015-10-11 00:15 | 2015-10-11 | 7 | 0 | 100 | 62.6833 | 1
2015-10-11 00:30 | 2015-10-11 | 7 | 0 | 98 | 62.4333 | 1
2015-10-11 00:45 | 2015-10-11 | 7 | 0 | 95 | 62.1833 | 1
2015-10-11 01:00 | 2015-10-11 | 7 | 1 | 95 | 61.9333 | 1
2015-10-11 01:15 | 2015-10-11 | 7 | 1 | 94 | 61.6833 | 1
2015-10-11 01:30 | 2015-10-11 | 7 | 1 | 95 | 61.4333 | 1
2015-10-11 01:45 | 2015-10-11 | 7 | 1 | 96 | 61.1833 | 1
2015-10-11 02:00 | 2015-10-11 | 7 | 2 | 95 | 61 | 1
2015-10-11 02:15 | 2015-10-11 | 7 | 2 | 104 | 61 | 1
2015-10-11 02:30 | 2015-10-11 | 7 | 2 | 96 | 61 | 1
2015-10-11 02:45 | 2015-10-11 | 7 | 2 | 93 | 61 | 1
2015-10-11 03:00 | 2015-10-11 | 7 | 3 | 94 | 60.9333 | 1
2015-10-11 03:15 | 2015-10-11 | 7 | 3 | 94 | 60.6833 | 1
2015-10-11 03:30 | 2015-10-11 | 7 | 3 | 93 | 60.4333 | 1
2015-10-11 03:45 | 2015-10-11 | 7 | 3 | 103 | 60.1833 | 1
2015-10-11 04:00 | 2015-10-11 | 7 | 4 | 97 | 59.9333 | 1
2015-10-11 04:15 | 2015-10-11 | 7 | 4 | 97 | 59.6833 | 1
2015-10-11 04:30 | 2015-10-11 | 7 | 4 | 94 | 59.4333 | 1
2015-10-11 04:45 | 2015-10-11 | 7 | 4 | 96 | 59.1833 | 1
2015-10-11 05:00 | 2015-10-11 | 7 | 5 | 105 | 59.0667 | 1
2015-10-11 05:15 | 2015-10-11 | 7 | 5 | 96 | 59.3167 | 1
2015-10-11 05:30 | 2015-10-11 | 7 | 5 | 96 | 59.5667 | 1
2015-10-11 05:45 | 2015-10-11 | 7 | 5 | 96 | 59.8167 | 1
2015-10-11 06:00 | 2015-10-11 | 7 | 6 | 100 | 60.0667 | 1
2015-10-11 06:15 | 2015-10-11 | 7 | 6 | 99 | 60.3167 | 1
2015-10-11 06:30 | 2015-10-11 | 7 | 6 | 98 | 60.5667 | 1
2015-10-11 06:45 | 2015-10-11 | 7 | 6 | 104 | 60.8167 | 1
2015-10-11 07:00 | 2015-10-11 | 7 | 7 | 104 | 61.1333 | 1
2015-10-11 07:15 | 2015-10-11 | 7 | 7 | 105 | 61.6333 | 1
2015-10-11 07:30 | 2015-10-11 | 7 | 7 | 101 | 62.1333 | 1
2015-10-11 07:45 | 2015-10-11 | 7 | 7 | 98 | 62.6333 | 1
2015-10-11 08:00 | 2015-10-11 | 7 | 8 | 105 | 63.2 | 1
2015-10-11 08:15 | 2015-10-11 | 7 | 8 | 102 | 63.95 | 1
2015-10-11 08:30 | 2015-10-11 | 7 | 8 | 101 | 64.7 | 1
2015-10-11 08:45 | 2015-10-11 | 7 | 8 | 103 | 65.45 | 2
2015-10-11 09:00 | 2015-10-11 | 7 | 9 | 96 | 66.0667 | 2
2015-10-11 09:15 | 2015-10-11 | 7 | 9 | 104 | 66.3167 | 2
2015-10-11 09:30 | 2015-10-11 | 7 | 9 | 95 | 66.5667 | 2
2015-10-11 09:45 | 2015-10-11 | 7 | 9 | 93 | 66.8167 | 2
2015-10-11 10:00 | 2015-10-11 | 7 | 10 | 92 | 67.0667 | 2
2015-10-11 10:15 | 2015-10-11 | 7 | 10 | 97 | 67.3167 | 2
2015-10-11 10:30 | 2015-10-11 | 7 | 10 | 91 | 67.5667 | 2
2015-10-11 10:45 | 2015-10-11 | 7 | 10 | 100 | 67.8167 | 2
2015-10-11 11:00 | 2015-10-11 | 7 | 11 | 96 | 68.3333 | 2
2015-10-11 11:15 | 2015-10-11 | 7 | 11 | 93 | 69.5833 | 2
2015-10-11 11:30 | 2015-10-11 | 7 | 11 | 96 | 70.8333 | 3
2015-10-11 11:45 | 2015-10-11 | 7 | 11 | 94 | 72.0833 | 3
2015-10-11 12:00 | 2015-10-11 | 7 | 12 | 98 | 72.9474 | 3
2015-10-11 12:15 | 2015-10-11 | 7 | 12 | 96 | 72.1579 | 3
2015-10-11 12:30 | 2015-10-11 | 7 | 12 | 93 | 71.3684 | 3
2015-10-11 12:45 | 2015-10-11 | 7 | 12 | 96 | 70.5789 | 3
2015-10-11 13:00 | 2015-10-11 | 7 | 13 | 98 | 69.9333 | 2
2015-10-11 13:15 | 2015-10-11 | 7 | 13 | 99 | 69.6833 | 2
2015-10-11 13:30 | 2015-10-11 | 7 | 13 | 97 | 69.4333 | 2
2015-10-11 13:45 | 2015-10-11 | 7 | 13 | 94 | 69.1833 | 2
2015-10-11 14:00 | 2015-10-11 | 7 | 14 | 98 | 68.8 | 2
2015-10-11 14:15 | 2015-10-11 | 7 | 14 | 104 | 68.05 | 2
2015-10-11 14:30 | 2015-10-11 | 7 | 14 | 98 | 67.3 | 2
2015-10-11 14:45 | 2015-10-11 | 7 | 14 | 98 | 66.55 | 2
2015-10-11 15:00 | 2015-10-11 | 7 | 15 | 101 | 65.8 | 2
2015-10-11 15:15 | 2015-10-11 | 7 | 15 | 104 | 65.05 | 2
2015-10-11 15:30 | 2015-10-11 | 7 | 15 | 100 | 64.3 | 1
2015-10-11 15:45 | 2015-10-11 | 7 | 15 | 97 | 63.55 | 1
2015-10-11 16:00 | 2015-10-11 | 7 | 16 | 99 | 62.8667 | 1
2015-10-11 16:15 | 2015-10-11 | 7 | 16 | 98 | 62.3667 | 1
2015-10-11 16:30 | 2015-10-11 | 7 | 16 | 103 | 61.8667 | 1
2015-10-11 16:45 | 2015-10-11 | 7 | 16 | 99 | 61.3667 | 1
2015-10-11 17:00 | 2015-10-11 | 7 | 17 | 105 | 61 | 1
2015-10-11 17:15 | 2015-10-11 | 7 | 17 | 97 | 61 | 1
2015-10-11 17:30 | 2015-10-11 | 7 | 17 | 104 | 61 | 1
2015-10-11 17:45 | 2015-10-11 | 7 | 17 | 106 | 61 | 1
2015-10-11 18:00 | 2015-10-11 | 7 | 18 | 104 | 61 | 1
2015-10-11 18:15 | 2015-10-11 | 7 | 18 | 101 | 61 | 1
2015-10-11 18:30 | 2015-10-11 | 7 | 18 | 98 | 61 | 1
2015-10-11 18:45 | 2015-10-11 | 7 | 18 | 104 | 61 | 1
2015-10-11 19:00 | 2015-10-11 | 7 | 19 | 102 | 61 | 1
2015-10-11 19:15 | 2015-10-11 | 7 | 19 | 103 | 61 | 1
2015-10-11 19:30 | 2015-10-11 | 7 | 19 | 100 | 61 | 1
2015-10-11 19:45 | 2015-10-11 | 7 | 19 | 97 | 61 | 1
2015-10-11 20:00 | 2015-10-11 | 7 | 20 | 106 | 60.9333 | 1
2015-10-11 20:15 | 2015-10-11 | 7 | 20 | 100 | 60.6833 | 1
2015-10-11 20:30 | 2015-10-11 | 7 | 20 | 100 | 60.4333 | 1
2015-10-11 20:45 | 2015-10-11 | 7 | 20 | 102 | 60.1833 | 1
2015-10-11 21:00 | 2015-10-11 | 7 | 21 | 99 | 60 | 1
2015-10-11 21:15 | 2015-10-11 | 7 | 21 | 103 | 60 | 1
2015-10-11 21:30 | 2015-10-11 | 7 | 21 | 96 | 60 | 1
2015-10-11 21:45 | 2015-10-11 | 7 | 21 | 96 | 60 | 1
2015-10-11 22:00 | 2015-10-11 | 7 | 22 | 95 | 60 | 1
2015-10-11 22:15 | 2015-10-11 | 7 | 22 | 98 | 60 | 1
2015-10-11 22:30 | 2015-10-11 | 7 | 22 | 96 | 60 | 1
2015-10-11 22:45 | 2015-10-11 | 7 | 22 | 102 | 60 | 1
2015-10-11 23:00 | 2015-10-11 | 7 | 23 | 100 | 59.9333 | 1
2015-10-11 23:15 | 2015-10-11 | 7 | 23 | 97 | 59.6833 | 1
2015-10-11 23:30 | 2015-10-11 | 7 | 23 | 102 | 59.4333 | 1
2015-10-11 23:45 | 2015-10-11 | 7 | 23 | 93 | 59.1833 | 1
2015-10-12 | 2015-10-12 | 0 | 0 | 103 | 58.9333 | 1
2015-10-12 00:15 | 2015-10-12 | 0 | 0 | 100 | 58.6833 | 1
2015-10-12 00:30 | 2015-10-12 | 0 | 0 | 96 | 58.4333 | 1
2015-10-12 00:45 | 2015-10-12 | 0 | 0 | 98 | 58.1833 | 1
2015-10-12 01:00 | 2015-10-12 | 0 | 1 | 102 | 57.9333 | 1
2015-10-12 01:15 | 2015-10-12 | 0 | 1 | 100 | 57.6833 | 1
2015-10-12 01:30 | 2015-10-12 | 0 | 1 | 99 | 57.4333 | 1
2015-10-12 01:45 | 2015-10-12 | 0 | 1 | 101 | 57.1833 | 1
2015-10-12 02:00 | 2015-10-12 | 0 | 2 | 96 | 57 | 1
2015-10-12 02:15 | 2015-10-12 | 0 | 2 | 103 | 57 | 1
2015-10-12 02:30 | 2015-10-12 | 0 | 2 | 96 | 57 | 1
2015-10-12 02:45 | 2015-10-12 | 0 | 2 | 101 | 57 | 1
2015-10-12 03:00 | 2015-10-12 | 0 | 3 | 93 | 57 | 1
2015-10-12 03:15 | 2015-10-12 | 0 | 3 | 102 | 57 | 1
2015-10-12 03:30 | 2015-10-12 | 0 | 3 | 98 | 57 | 1
2015-10-12 03:45 | 2015-10-12 | 0 | 3 | 97 | 57 | 1
2015-10-12 04:00 | 2015-10-12 | 0 | 4 | 98 | 57 | 1
2015-10-12 04:15 | 2015-10-12 | 0 | 4 | 96 | 57 | 1
2015-10-12 04:30 | 2015-10-12 | 0 | 4 | 100 | 57 | 1
2015-10-12 04:45 | 2015-10-12 | 0 | 4 | 100 | 57 | 1
2015-10-12 05:00 | 2015-10-12 | 0 | 5 | 96 | 57 | 1
2015-10-12 05:15 | 2015-10-12 | 0 | 5 | 96 | 57 | 1
2015-10-12 05:30 | 2015-10-12 | 0 | 5 | 99 | 57 | 1
2015-10-12 05:45 | 2015-10-12 | 0 | 5 | 95 | 57 | 1
2015-10-12 06:00 | 2015-10-12 | 0 | 6 | 101 | 57.1333 | 1
2015-10-12 06:15 | 2015-10-12 | 0 | 6 | 103 | 57.6333 | 1
2015-10-12 06:30 | 2015-10-12 | 0 | 6 | 100 | 58.1333 | 1
2015-10-12 06:45 | 2015-10-12 | 0 | 6 | 98 | 58.6333 | 1
2015-10-12 07:00 | 2015-10-12 | 0 | 7 | 98 | 59.2667 | 1
2015-10-12 07:15 | 2015-10-12 | 0 | 7 | 204 | 60.2667 | 1
2015-10-12 07:30 | 2015-10-12 | 0 | 7 | 188 | 61.2667 | 1
2015-10-12 07:45 | 2015-10-12 | 0 | 7 | 163 | 62.2667 | 1
2015-10-12 08:00 | 2015-10-12 | 0 | 8 | 163 | 63.2 | 1
2015-10-12 08:15 | 2015-10-12 | 0 | 8 | 163 | 63.95 | 1
2015-10-12 08:30 | 2015-10-12 | 0 | 8 | 184 | 64.7 | 1
2015-10-12 08:45 | 2015-10-12 | 0 | 8 | 195 | 65.45 | 2
2015-10-12 09:00 | 2015-10-12 | 0 | 9 | 204 | 66.0667 | 2
2015-10-12 09:15 | 2015-10-12 | 0 | 9 | 205 | 66.3167 | 2
2015-10-12 09:30 | 2015-10-12 | 0 | 9 | 208 | 66.5667 | 2
2015-10-12 09:45 | 2015-10-12 | 0 | 9 | 220 | 66.8167 | 2
2015-10-12 10:00 | 2015-10-12 | 0 | 10 | 227 | 67.1333 | 2
2015-10-12 10:15 | 2015-10-12 | 0 | 10 | 222 | 67.6333 | 2
2015-10-12 10:30 | 2015-10-12 | 0 | 10 | 215 | 68.1333 | 2
2015-10-12 10:45 | 2015-10-12 | 0 | 10 | 217 | 68.6333 | 2
2015-10-12 11:00 | 2015-10-12 | 0 | 11 | 208 | 69.1333 | 2
2015-10-12 11:15 | 2015-10-12 | 0 | 11 | 221 | 69.6333 | 2
2015-10-12 11:30 | 2015-10-12 | 0 | 11 | 212 | 70.1333 | 3
2015-10-12 11:45 | 2015-10-12 | 0 | 11 | 216 | 70.6333 | 3
2015-10-12 12:00 | 2015-10-12 | 0 | 12 | 233 | 71.1333 | 3
2015-10-12 12:15 | 2015-10-12 | 0 | 12 | 238 | 71.6333 | 3
2015-10-12 12:30 | 2015-10-12 | 0 | 12 | 241 | 72.1333 | 3
2015-10-12 12:45 | 2015-10-12 | 0 | 12 | 224 | 72.6333 | 3
2015-10-12 13:00 | 2015-10-12 | 0 | 13 | 238 | 73.0667 | 3
2015-10-12 13:15 | 2015-10-12 | 0 | 13 | 253 | 73.3167 | 3
2015-10-12 13:30 | 2015-10-12 | 0 | 13 | 254 | 73.5667 | 3
2015-10-12 13:45 | 2015-10-12 | 0 | 13 | 245 | 73.8167 | 3
2015-10-12 14:00 | 2015-10-12 | 0 | 14 | 251 | 74.4667 | 3
2015-10-12 14:15 | 2015-10-12 | 0 | 14 | 245 | 76.2167 | 4
2015-10-12 14:30 | 2015-10-12 | 0 | 14 | 251 | 77.9667 | 4
2015-10-12 14:45 | 2015-10-12 | 0 | 14 | 243 | 79.7167 | 4
2015-10-12 15:00 | 2015-10-12 | 0 | 15 | 265 | 80.8667 | 5
2015-10-12 15:15 | 2015-10-12 | 0 | 15 | 254 | 80.3667 | 5
2015-10-12 15:30 | 2015-10-12 | 0 | 15 | 268 | 79.8667 | 4
2015-10-12 15:45 | 2015-10-12 | 0 | 15 | 254 | 79.3667 | 4
2015-10-12 16:00 | 2015-10-12 | 0 | 16 | 269 | 78.7333 | 4
2015-10-12 16:15 | 2015-10-12 | 0 | 16 | 256 | 77.7333 | 4
2015-10-12 16:30 | 2015-10-12 | 0 | 16 | 257 | 76.7333 | 4
2015-10-12 16:45 | 2015-10-12 | 0 | 16 | 253 | 75.7333 | 4
2015-10-12 17:00 | 2015-10-12 | 0 | 17 | 253 | 74.8 | 3
2015-10-12 17:15 | 2015-10-12 | 0 | 17 | 255 | 74.05 | 3
2015-10-12 17:30 | 2015-10-12 | 0 | 17 | 247 | 73.3 | 3
2015-10-12 17:45 | 2015-10-12 | 0 | 17 | 262 | 72.55 | 3
2015-10-12 18:00 | 2015-10-12 | 0 | 18 | 241 | 72.0667 | 3
2015-10-12 18:15 | 2015-10-12 | 0 | 18 | 244 | 72.3167 | 3
2015-10-12 18:30 | 2015-10-12 | 0 | 18 | 229 | 72.5667 | 3
2015-10-12 18:45 | 2015-10-12 | 0 | 18 | 222 | 72.8167 | 3
2015-10-12 19:00 | 2015-10-12 | 0 | 19 | 220 | 73 | 3
2015-10-12 19:15 | 2015-10-12 | 0 | 19 | 138 | 73 | 3
2015-10-12 19:30 | 2015-10-12 | 0 | 19 | 124 | 73 | 3
2015-10-12 19:45 | 2015-10-12 | 0 | 19 | 124 | 73 | 3
2015-10-12 20:00 | 2015-10-12 | 0 | 20 | 116 | 72.8667 | 3
2015-10-12 20:15 | 2015-10-12 | 0 | 20 | 110 | 72.3667 | 3
2015-10-12 20:30 | 2015-10-12 | 0 | 20 | 114 | 71.8667 | 3
2015-10-12 20:45 | 2015-10-12 | 0 | 20 | 111 | 71.3667 | 3
2015-10-12 21:00 | 2015-10-12 | 0 | 21 | 121 | 70.9333 | 3
2015-10-12 21:15 | 2015-10-12 | 0 | 21 | 107 | 70.6833 | 3
2015-10-12 21:30 | 2015-10-12 | 0 | 21 | 105 | 70.4333 | 3
2015-10-12 21:45 | 2015-10-12 | 0 | 21 | 101 | 70.1833 | 3
2015-10-12 22:00 | 2015-10-12 | 0 | 22 | 108 | 69.8667 | 2
2015-10-12 22:15 | 2015-10-12 | 0 | 22 | 108 | 69.3667 | 2
2015-10-12 22:30 | 2015-10-12 | 0 | 22 | 106 | 68.8667 | 2
2015-10-12 22:45 | 2015-10-12 | 0 | 22 | 102 | 68.3667 | 2
2015-10-12 23:00 | 2015-10-12 | 0 | 23 | 98 | 67.8 | 2
2015-10-12 23:15 | 2015-10-12 | 0 | 23 | 105 | 67.05 | 2
2015-10-12 23:30 | 2015-10-12 | 0 | 23 | 105 | 66.3 | 2
2015-10-12 23:45 | 2015-10-12 | 0 | 23 | 102 | 65.55 | 2
2015-10-13 | 2015-10-13 | 2 | 0 | 104 | 64.9333 | 1
2015-10-13 00:15 | 2015-10-13 | 2 | 0 | 98 | 64.6833 | 1
2015-10-13 00:30 | 2015-10-13 | 2 | 0 | 110 | 64.4333 | 1
2015-10-13 00:45 | 2015-10-13 | 2 | 0 | 102 | 64.1833 | 1
2015-10-13 01:00 | 2015-10-13 | 2 | 1 | 105 | 63.9333 | 1
2015-10-13 01:15 | 2015-10-13 | 2 | 1 | 102 | 63.6833 | 1
2015-10-13 01:30 | 2015-10-13 | 2 | 1 | 103 | 63.4333 | 1
2015-10-13 01:45 | 2015-10-13 | 2 | 1 | 103 | 63.1833 | 1
2015-10-13 02:00 | 2015-10-13 | 2 | 2 | 101 | 63 | 1
2015-10-13 02:15 | 2015-10-13 | 2 | 2 | 96 | 63 | 1
2015-10-13 02:30 | 2015-10-13 | 2 | 2 | 100 | 63 | 1
2015-10-13 02:45 | 2015-10-13 | 2 | 2 | 105 | 63 | 1
2015-10-13 03:00 | 2015-10-13 | 2 | 3 | 99 | 62.9333 | 1
2015-10-13 03:15 | 2015-10-13 | 2 | 3 | 99 | 62.6833 | 1
2015-10-13 03:30 | 2015-10-13 | 2 | 3 | 98 | 62.4333 | 1
2015-10-13 03:45 | 2015-10-13 | 2 | 3 | 103 | 62.1833 | 1
2015-10-13 04:00 | 2015-10-13 | 2 | 4 | 101 | 62.0667 | 1
2015-10-13 04:15 | 2015-10-13 | 2 | 4 | 99 | 62.3167 | 1
2015-10-13 04:30 | 2015-10-13 | 2 | 4 | 97 | 62.5667 | 1
2015-10-13 04:45 | 2015-10-13 | 2 | 4 | 100 | 62.8167 | 1
2015-10-13 05:00 | 2015-10-13 | 2 | 5 | 98 | 63.0667 | 1
2015-10-13 05:15 | 2015-10-13 | 2 | 5 | 102 | 63.3167 | 1
2015-10-13 05:30 | 2015-10-13 | 2 | 5 | 103 | 63.5667 | 1
2015-10-13 05:45 | 2015-10-13 | 2 | 5 | 101 | 63.8167 | 1
2015-10-13 06:00 | 2015-10-13 | 2 | 6 | 98 | 64 | 1
2015-10-13 06:15 | 2015-10-13 | 2 | 6 | 100 | 64 | 1
2015-10-13 06:30 | 2015-10-13 | 2 | 6 | 104 | 64 | 1
2015-10-13 06:45 | 2015-10-13 | 2 | 6 | 106 | 64 | 1
2015-10-13 07:00 | 2015-10-13 | 2 | 7 | 105 | 64.3333 | 1
2015-10-13 07:15 | 2015-10-13 | 2 | 7 | 220 | 65.5833 | 2
2015-10-13 07:30 | 2015-10-13 | 2 | 7 | 211 | 66.8333 | 2
2015-10-13 07:45 | 2015-10-13 | 2 | 7 | 172 | 68.0833 | 2
2015-10-13 08:00 | 2015-10-13 | 2 | 8 | 174 | 69.0667 | 2
2015-10-13 08:15 | 2015-10-13 | 2 | 8 | 172 | 69.3167 | 2
2015-10-13 08:30 | 2015-10-13 | 2 | 8 | 197 | 69.5667 | 2
2015-10-13 08:45 | 2015-10-13 | 2 | 8 | 215 | 69.8167 | 2
2015-10-13 09:00 | 2015-10-13 | 2 | 9 | 193 | 70.1333 | 3
2015-10-13 09:15 | 2015-10-13 | 2 | 9 | 192 | 70.6333 | 3
2015-10-13 09:30 | 2015-10-13 | 2 | 9 | 213 | 71.1333 | 3
2015-10-13 09:45 | 2015-10-13 | 2 | 9 | 217 | 71.6333 | 3
2015-10-13 10:00 | 2015-10-13 | 2 | 10 | 213 | 72.0667 | 3
2015-10-13 10:15 | 2015-10-13 | 2 | 10 | 219 | 72.3167 | 3
2015-10-13 10:30 | 2015-10-13 | 2 | 10 | 220 | 72.5667 | 3
2015-10-13 10:45 | 2015-10-13 | 2 | 10 | 224 | 72.8167 | 3
2015-10-13 11:00 | 2015-10-13 | 2 | 11 | 230 | 73.1333 | 3
2015-10-13 11:15 | 2015-10-13 | 2 | 11 | 247 | 73.6333 | 3
2015-10-13 11:30 | 2015-10-13 | 2 | 11 | 229 | 74.1333 | 3
2015-10-13 11:45 | 2015-10-13 | 2 | 11 | 243 | 74.6333 | 3
2015-10-13 12:00 | 2015-10-13 | 2 | 12 | 239 | 75 | 3
2015-10-13 12:15 | 2015-10-13 | 2 | 12 | 259 | 75 | 3
2015-10-13 12:30 | 2015-10-13 | 2 | 12 | 252 | 75 | 3
2015-10-13 12:45 | 2015-10-13 | 2 | 12 | 256 | 75 | 3
2015-10-13 13:00 | 2015-10-13 | 2 | 13 | 252 | 75.8 | 4
2015-10-13 13:15 | 2015-10-13 | 2 | 13 | 264 | 78.8 | 4
2015-10-13 13:30 | 2015-10-13 | 2 | 13 | 246 | 81.8 | 5
2015-10-13 13:45 | 2015-10-13 | 2 | 13 | 256 | 84.8 | 5
2015-10-13 14:00 | 2015-10-13 | 2 | 14 | 254 | 86.8667 | 6
2015-10-13 14:15 | 2015-10-13 | 2 | 14 | 265 | 86.3667 | 6
2015-10-13 14:30 | 2015-10-13 | 2 | 14 | 254 | 85.8667 | 6
2015-10-13 14:45 | 2015-10-13 | 2 | 14 | 250 | 85.3667 | 6
2015-10-13 15:00 | 2015-10-13 | 2 | 15 | 260 | 84.6667 | 5
2015-10-13 15:15 | 2015-10-13 | 2 | 15 | 257 | 83.4167 | 5
2015-10-13 15:30 | 2015-10-13 | 2 | 15 | 253 | 82.1667 | 5
2015-10-13 15:45 | 2015-10-13 | 2 | 15 | 240 | 80.9167 | 5
2015-10-13 16:00 | 2015-10-13 | 2 | 16 | 247 | 79.6 | 4
2015-10-13 16:15 | 2015-10-13 | 2 | 16 | 247 | 78.1 | 4
2015-10-13 16:30 | 2015-10-13 | 2 | 16 | 251 | 76.6 | 4
2015-10-13 16:45 | 2015-10-13 | 2 | 16 | 239 | 75.1 | 4
2015-10-13 17:00 | 2015-10-13 | 2 | 17 | 246 | 73.8 | 3
2015-10-13 17:15 | 2015-10-13 | 2 | 17 | 243 | 73.05 | 3
2015-10-13 17:30 | 2015-10-13 | 2 | 17 | 246 | 72.3 | 3
2015-10-13 17:45 | 2015-10-13 | 2 | 17 | 244 | 71.55 | 3
2015-10-13 18:00 | 2015-10-13 | 2 | 18 | 229 | 70.9333 | 3
2015-10-13 18:15 | 2015-10-13 | 2 | 18 | 229 | 70.6833 | 3
2015-10-13 18:30 | 2015-10-13 | 2 | 18 | 226 | 70.4333 | 3
2015-10-13 18:45 | 2015-10-13 | 2 | 18 | 216 | 70.1833 | 3
2015-10-13 19:00 | 2015-10-13 | 2 | 19 | 217 | 69.8667 | 2
2015-10-13 19:15 | 2015-10-13 | 2 | 19 | 130 | 69.3667 | 2
2015-10-13 19:30 | 2015-10-13 | 2 | 19 | 126 | 68.8667 | 2
2015-10-13 19:45 | 2015-10-13 | 2 | 19 | 118 | 68.3667 | 2
2015-10-13 20:00 | 2015-10-13 | 2 | 20 | 123 | 68 | 2
2015-10-13 20:15 | 2015-10-13 | 2 | 20 | 122 | 68 | 2
2015-10-13 20:30 | 2015-10-13 | 2 | 20 | 113 | 68 | 2
2015-10-13 20:45 | 2015-10-13 | 2 | 20 | 114 | 68 | 2
2015-10-13 21:00 | 2015-10-13 | 2 | 21 | 107 | 68 | 2
2015-10-13 21:15 | 2015-10-13 | 2 | 21 | 112 | 68 | 2
2015-10-13 21:30 | 2015-10-13 | 2 | 21 | 104 | 68 | 2
2015-10-13 21:45 | 2015-10-13 | 2 | 21 | 106 | 68 | 2
2015-10-13 22:00 | 2015-10-13 | 2 | 22 | 100 | 67.8667 | 2
2015-10-13 22:15 | 2015-10-13 | 2 | 22 | 103 | 67.3667 | 2
2015-10-13 22:30 | 2015-10-13 | 2 | 22 | 111 | 66.8667 | 2
2015-10-13 22:45 | 2015-10-13 | 2 | 22 | 100 | 66.3667 | 2
2015-10-13 23:00 | 2015-10-13 | 2 | 23 | 104 | 65.9333 | 2
2015-10-13 23:15 | 2015-10-13 | 2 | 23 | 102 | 65.6833 | 2
2015-10-13 23:30 | 2015-10-13 | 2 | 23 | 104 | 65.4333 | 2
2015-10-13 23:45 | 2015-10-13 | 2 | 23 | 103 | 65.1833 | 2
2015-10-14 | 2015-10-14 | 3 | 0 | 105 | 65 | 1
2015-10-14 00:15 | 2015-10-14 | 3 | 0 | 99 | 65 | 1
2015-10-14 00:30 | 2015-10-14 | 3 | 0 | 105 | 65 | 1
2015-10-14 00:45 | 2015-10-14 | 3 | 0 | 107 | 65 | 1
2015-10-14 01:00 | 2015-10-14 | 3 | 1 | 102 | 65 | 1
2015-10-14 01:15 | 2015-10-14 | 3 | 1 | 104 | 65 | 1
2015-10-14 01:30 | 2015-10-14 | 3 | 1 | 100 | 65 | 1
2015-10-14 01:45 | 2015-10-14 | 3 | 1 | 101 | 65 | 1
2015-10-14 02:00 | 2015-10-14 | 3 | 2 | 103 | 64.8667 | 1
2015-10-14 02:15 | 2015-10-14 | 3 | 2 | 109 | 64.3667 | 1
2015-10-14 02:30 | 2015-10-14 | 3 | 2 | 101 | 63.8667 | 1
2015-10-14 02:45 | 2015-10-14 | 3 | 2 | 107 | 63.3667 | 1
2015-10-14 03:00 | 2015-10-14 | 3 | 3 | 100 | 63.0667 | 1
2015-10-14 03:15 | 2015-10-14 | 3 | 3 | 107 | 63.3167 | 1
2015-10-14 03:30 | 2015-10-14 | 3 | 3 | 104 | 63.5667 | 1
2015-10-14 03:45 | 2015-10-14 | 3 | 3 | 101 | 63.8167 | 1
2015-10-14 04:00 | 2015-10-14 | 3 | 4 | 99 | 63.9333 | 1
2015-10-14 04:15 | 2015-10-14 | 3 | 4 | 109 | 63.6833 | 1
2015-10-14 04:30 | 2015-10-14 | 3 | 4 | 104 | 63.4333 | 1
2015-10-14 04:45 | 2015-10-14 | 3 | 4 | 103 | 63.1833 | 1
2015-10-14 05:00 | 2015-10-14 | 3 | 5 | 102 | 63 | 1
2015-10-14 05:15 | 2015-10-14 | 3 | 5 | 105 | 63 | 1
2015-10-14 05:30 | 2015-10-14 | 3 | 5 | 105 | 63 | 1
2015-10-14 05:45 | 2015-10-14 | 3 | 5 | 104 | 63 | 1
2015-10-14 06:00 | 2015-10-14 | 3 | 6 | 101 | 63.0667 | 1
2015-10-14 06:15 | 2015-10-14 | 3 | 6 | 104 | 63.3167 | 1
2015-10-14 06:30 | 2015-10-14 | 3 | 6 | 101 | 63.5667 | 1
2015-10-14 06:45 | 2015-10-14 | 3 | 6 | 107 | 63.8167 | 1
2015-10-14 07:00 | 2015-10-14 | 3 | 7 | 114 | 64.1333 | 1
2015-10-14 07:15 | 2015-10-14 | 3 | 7 | 234 | 64.6333 | 1
2015-10-14 07:30 | 2015-10-14 | 3 | 7 | 207 | 65.1333 | 2
2015-10-14 07:45 | 2015-10-14 | 3 | 7 | 190 | 65.6333 | 2
2015-10-14 08:00 | 2015-10-14 | 3 | 8 | 175 | 66.2667 | 2
2015-10-14 08:15 | 2015-10-14 | 3 | 8 | 194 | 67.2667 | 2
2015-10-14 08:30 | 2015-10-14 | 3 | 8 | 185 | 68.2667 | 2
2015-10-14 08:45 | 2015-10-14 | 3 | 8 | 186 | 69.2667 | 2
2015-10-14 09:00 | 2015-10-14 | 3 | 9 | 209 | 70.0667 | 3
2015-10-14 09:15 | 2015-10-14 | 3 | 9 | 215 | 70.3167 | 3
2015-10-14 09:30 | 2015-10-14 | 3 | 9 | 213 | 70.5667 | 3
2015-10-14 09:45 | 2015-10-14 | 3 | 9 | 215 | 70.8167 | 3
2015-10-14 10:00 | 2015-10-14 | 3 | 10 | 212 | 71.1333 | 3
2015-10-14 10:15 | 2015-10-14 | 3 | 10 | 220 | 71.6333 | 3
2015-10-14 10:30 | 2015-10-14 | 3 | 10 | 216 | 72.1333 | 3
2015-10-14 10:45 | 2015-10-14 | 3 | 10 | 237 | 72.6333 | 3
2015-10-14 11:00 | 2015-10-14 | 3 | 11 | 222 | 73 | 3
2015-10-14 11:15 | 2015-10-14 | 3 | 11 | 222 | 73 | 3
2015-10-14 11:30 | 2015-10-14 | 3 | 11 | 236 | 73 | 3
2015-10-14 11:45 | 2015-10-14 | 3 | 11 | 234 | 73 | 3
2015-10-14 12:00 | 2015-10-14 | 3 | 12 | 244 | 73.1333 | 3
2015-10-14 12:15 | 2015-10-14 | 3 | 12 | 230 | 73.6333 | 3
2015-10-14 12:30 | 2015-10-14 | 3 | 12 | 235 | 74.1333 | 3
2015-10-14 12:45 | 2015-10-14 | 3 | 12 | 236 | 74.6333 | 3
2015-10-14 13:00 | 2015-10-14 | 3 | 13 | 231 | 74.814 | 3
2015-10-14 13:15 | 2015-10-14 | 3 | 13 | 228 | 74.1163 | 3
2015-10-14 13:30 | 2015-10-14 | 3 | 13 | 235 | 73.4186 | 3
2015-10-14 13:45 | 2015-10-14 | 3 | 13 | 238 | 73.7059 | 3
2015-10-14 14:00 | 2015-10-14 | 3 | 14 | 237 | 75.1333 | 4
2015-10-14 14:15 | 2015-10-14 | 3 | 14 | 233 | 75.6333 | 4
2015-10-14 14:30 | 2015-10-14 | 3 | 14 | 233 | 76.1333 | 4
2015-10-14 14:45 | 2015-10-14 | 3 | 14 | 234 | 76.6333 | 4
2015-10-14 15:00 | 2015-10-14 | 3 | 15 | 255 | 77 | 4
2015-10-14 15:15 | 2015-10-14 | 3 | 15 | 239 | 77 | 4
2015-10-14 15:30 | 2015-10-14 | 3 | 15 | 239 | 77 | 4
2015-10-14 15:45 | 2015-10-14 | 3 | 15 | 234 | 77 | 4
2015-10-14 16:00 | 2015-10-14 | 3 | 16 | 238 | 76.9333 | 4
2015-10-14 16:15 | 2015-10-14 | 3 | 16 | 250 | 76.6833 | 4
2015-10-14 16:30 | 2015-10-14 | 3 | 16 | 242 | 76.4333 | 4
2015-10-14 16:45 | 2015-10-14 | 3 | 16 | 236 | 76.1833 | 4
2015-10-14 17:00 | 2015-10-14 | 3 | 17 | 233 | 76.3636 | 4
2015-10-14 17:15 | 2015-10-14 | 3 | 17 | 225 | 77.7273 | 4
2015-10-14 17:30 | 2015-10-14 | 3 | 17 | 225 | 78.7037 | 4
2015-10-14 17:45 | 2015-10-14 | 3 | 17 | 227 | 74.2593 | 3
2015-10-14 18:00 | 2015-10-14 | 3 | 18 | 227 | 70.4667 | 3
2015-10-14 18:15 | 2015-10-14 | 3 | 18 | 218 | 68.4667 | 2
2015-10-14 18:30 | 2015-10-14 | 3 | 18 | 216 | 66.4667 | 2
2015-10-14 18:45 | 2015-10-14 | 3 | 18 | 214 | 64.4667 | 1
2015-10-14 19:00 | 2015-10-14 | 3 | 19 | 209 | 62.9333 | 1
2015-10-14 19:15 | 2015-10-14 | 3 | 19 | 125 | 62.6833 | 1
2015-10-14 19:30 | 2015-10-14 | 3 | 19 | 126 | 62.4333 | 1
2015-10-14 19:45 | 2015-10-14 | 3 | 19 | 122 | 62.1833 | 1
2015-10-14 20:00 | 2015-10-14 | 3 | 20 | 129 | 61.9333 | 1
2015-10-14 20:15 | 2015-10-14 | 3 | 20 | 126 | 61.6833 | 1
2015-10-14 20:30 | 2015-10-14 | 3 | 20 | 123 | 61.4333 | 1
2015-10-14 20:45 | 2015-10-14 | 3 | 20 | 118 | 61.1833 | 1
2015-10-14 21:00 | 2015-10-14 | 3 | 21 | 110 | 61.0667 | 1
2015-10-14 21:15 | 2015-10-14 | 3 | 21 | 110 | 61.3167 | 1
2015-10-14 21:30 | 2015-10-14 | 3 | 21 | 106 | 61.5667 | 1
2015-10-14 21:45 | 2015-10-14 | 3 | 21 | 103 | 61.8167 | 1
2015-10-14 22:00 | 2015-10-14 | 3 | 22 | 101 | 62 | 1
2015-10-14 22:15 | 2015-10-14 | 3 | 22 | 103 | 62 | 1
2015-10-14 22:30 | 2015-10-14 | 3 | 22 | 107 | 62 | 1
2015-10-14 22:45 | 2015-10-14 | 3 | 22 | 102 | 62 | 1
2015-10-14 23:00 | 2015-10-14 | 3 | 23 | 105 | 62 | 1
2015-10-14 23:15 | 2015-10-14 | 3 | 23 | 98 | 62 | 1
2015-10-14 23:30 | 2015-10-14 | 3 | 23 | 107 | 62 | 1
2015-10-14 23:45 | 2015-10-14 | 3 | 23 | 103 | 62 | 1
2015-10-15 | 2015-10-15 | 4 | 0 | 102 | 62 | 1
2015-10-15 00:15 | 2015-10-15 | 4 | 0 | 98 | 62 | 1
2015-10-15 00:30 | 2015-10-15 | 4 | 0 | 100 | 62 | 1
2015-10-15 00:45 | 2015-10-15 | 4 | 0 | 101 | 62 | 1
2015-10-15 01:00 | 2015-10-15 | 4 | 1 | 110 | 62 | 1
2015-10-15 01:15 | 2015-10-15 | 4 | 1 | 99 | 62 | 1
2015-10-15 01:30 | 2015-10-15 | 4 | 1 | 101 | 62 | 1
2015-10-15 01:45 | 2015-10-15 | 4 | 1 | 97 | 62 | 1
2015-10-15 02:00 | 2015-10-15 | 4 | 2 | 104 | 62 | 1
2015-10-15 02:15 | 2015-10-15 | 4 | 2 | 102 | 62 | 1
2015-10-15 02:30 | 2015-10-15 | 4 | 2 | 99 | 62 | 1
2015-10-15 02:45 | 2015-10-15 | 4 | 2 | 96 | 62 | 1
2015-10-15 03:00 | 2015-10-15 | 4 | 3 | 105 | 62 | 1
2015-10-15 03:15 | 2015-10-15 | 4 | 3 | 103 | 62 | 1
2015-10-15 03:30 | 2015-10-15 | 4 | 3 | 99 | 62 | 1
2015-10-15 03:45 | 2015-10-15 | 4 | 3 | 104 | 62 | 1
2015-10-15 04:00 | 2015-10-15 | 4 | 4 | 94 | 62 | 1
2015-10-15 04:15 | 2015-10-15 | 4 | 4 | 100 | 62 | 1
2015-10-15 04:30 | 2015-10-15 | 4 | 4 | 105 | 62 | 1
2015-10-15 04:45 | 2015-10-15 | 4 | 4 | 100 | 62 | 1
2015-10-15 05:00 | 2015-10-15 | 4 | 5 | 99 | 62 | 1
2015-10-15 05:15 | 2015-10-15 | 4 | 5 | 100 | 62 | 1
2015-10-15 05:30 | 2015-10-15 | 4 | 5 | 100 | 62 | 1
2015-10-15 05:45 | 2015-10-15 | 4 | 5 | 103 | 62 | 1
2015-10-15 06:00 | 2015-10-15 | 4 | 6 | 108 | 62.069 | 1
2015-10-15 06:15 | 2015-10-15 | 4 | 6 | 99 | 62.3276 | 1
2015-10-15 06:30 | 2015-10-15 | 4 | 6 | 107 | 62.5862 | 1
2015-10-15 06:45 | 2015-10-15 | 4 | 6 | 97 | 62.8448 | 1
2015-10-15 07:00 | 2015-10-15 | 4 | 7 | 102 | 62 | 1
2015-10-15 07:15 | 2015-10-15 | 4 | 7 | 243 | 62 | 1
2015-10-15 07:30 | 2015-10-15 | 4 | 7 | 229 | 62 | 1
2015-10-15 07:45 | 2015-10-15 | 4 | 7 | 215 | 62 | 1
2015-10-15 08:00 | 2015-10-15 | 4 | 8 | 218 | 62.1333 | 1
2015-10-15 08:15 | 2015-10-15 | 4 | 8 | 216 | 62.6333 | 1
2015-10-15 08:30 | 2015-10-15 | 4 | 8 | 212 | 63.1333 | 1
2015-10-15 08:45 | 2015-10-15 | 4 | 8 | 202 | 63.6333 | 1
2015-10-15 09:00 | 2015-10-15 | 4 | 9 | 193 | 64.0667 | 1
2015-10-15 09:15 | 2015-10-15 | 4 | 9 | 192 | 64.3167 | 1
2015-10-15 09:30 | 2015-10-15 | 4 | 9 | 213 | 64.5667 | 1
2015-10-15 09:45 | 2015-10-15 | 4 | 9 | 213 | 64.8167 | 1
2015-10-15 10:00 | 2015-10-15 | 4 | 10 | 199 | 65.1333 | 2
2015-10-15 10:15 | 2015-10-15 | 4 | 10 | 203 | 65.6333 | 2
2015-10-15 10:30 | 2015-10-15 | 4 | 10 | 222 | 66.1333 | 2
2015-10-15 10:45 | 2015-10-15 | 4 | 10 | 216 | 66.6333 | 2
2015-10-15 11:00 | 2015-10-15 | 4 | 11 | 207 | 67.1333 | 2
2015-10-15 11:15 | 2015-10-15 | 4 | 11 | 211 | 67.6333 | 2
2015-10-15 11:30 | 2015-10-15 | 4 | 11 | 232 | 68.1333 | 2
2015-10-15 11:45 | 2015-10-15 | 4 | 11 | 220 | 68.6333 | 2
2015-10-15 12:00 | 2015-10-15 | 4 | 12 | 209 | 69 | 2
2015-10-15 12:15 | 2015-10-15 | 4 | 12 | 210 | 69 | 2
2015-10-15 12:30 | 2015-10-15 | 4 | 12 | 211 | 69 | 2
2015-10-15 12:45 | 2015-10-15 | 4 | 12 | 216 | 69 | 2
2015-10-15 13:00 | 2015-10-15 | 4 | 13 | 230 | 69.48 | 2
2015-10-15 13:15 | 2015-10-15 | 4 | 13 | 203 | 71.28 | 3
2015-10-15 13:30 | 2015-10-15 | 4 | 13 | 210 | 70.7143 | 3
2015-10-15 13:45 | 2015-10-15 | 4 | 13 | 203 | 68.5714 | 2
2015-10-15 14:00 | 2015-10-15 | 4 | 14 | 211 | 66.9333 | 2
2015-10-15 14:15 | 2015-10-15 | 4 | 14 | 218 | 66.6833 | 2
2015-10-15 14:30 | 2015-10-15 | 4 | 14 | 223 | 66.4333 | 2
2015-10-15 14:45 | 2015-10-15 | 4 | 14 | 213 | 66.1833 | 2
2015-10-15 15:00 | 2015-10-15 | 4 | 15 | 221 | 65.9333 | 2
2015-10-15 15:15 | 2015-10-15 | 4 | 15 | 212 | 65.6833 | 2
2015-10-15 15:30 | 2015-10-15 | 4 | 15 | 209 | 65.4333 | 2
2015-10-15 15:45 | 2015-10-15 | 4 | 15 | 211 | 65.1833 | 2
2015-10-15 16:00 | 2015-10-15 | 4 | 16 | 200 | 64.8667 | 1
2015-10-15 16:15 | 2015-10-15 | 4 | 16 | 208 | 64.3667 | 1
2015-10-15 16:30 | 2015-10-15 | 4 | 16 | 208 | 63.8667 | 1
2015-10-15 16:45 | 2015-10-15 | 4 | 16 | 203 | 63.3667 | 1
2015-10-15 17:00 | 2015-10-15 | 4 | 17 | 203 | 63 | 1
2015-10-15 17:15 | 2015-10-15 | 4 | 17 | 199 | 63 | 1
2015-10-15 17:30 | 2015-10-15 | 4 | 17 | 219 | 63 | 1
2015-10-15 17:45 | 2015-10-15 | 4 | 17 | 230 | 63 | 1
2015-10-15 18:00 | 2015-10-15 | 4 | 18 | 211 | 63 | 1
2015-10-15 18:15 | 2015-10-15 | 4 | 18 | 222 | 63 | 1
2015-10-15 18:30 | 2015-10-15 | 4 | 18 | 211 | 63 | 1
2015-10-15 18:45 | 2015-10-15 | 4 | 18 | 212 | 63 | 1
2015-10-15 19:00 | 2015-10-15 | 4 | 19 | 202 | 62.9333 | 1
2015-10-15 19:15 | 2015-10-15 | 4 | 19 | 131 | 62.6833 | 1
2015-10-15 19:30 | 2015-10-15 | 4 | 19 | 134 | 62.4333 | 1
2015-10-15 19:45 | 2015-10-15 | 4 | 19 | 128 | 62.1833 | 1
2015-10-15 20:00 | 2015-10-15 | 4 | 20 | 129 | 62 | 1
2015-10-15 20:15 | 2015-10-15 | 4 | 20 | 124 | 62 | 1
2015-10-15 20:30 | 2015-10-15 | 4 | 20 | 126 | 62 | 1
2015-10-15 20:45 | 2015-10-15 | 4 | 20 | 131 | 62 | 1
2015-10-15 21:00 | 2015-10-15 | 4 | 21 | 124 | 61.9333 | 1
2015-10-15 21:15 | 2015-10-15 | 4 | 21 | 115 | 61.6833 | 1
2015-10-15 21:30 | 2015-10-15 | 4 | 21 | 107 | 61.4333 | 1
2015-10-15 21:45 | 2015-10-15 | 4 | 21 | 112 | 61.1833 | 1
2015-10-15 22:00 | 2015-10-15 | 4 | 22 | 120 | 61 | 1
2015-10-15 22:15 | 2015-10-15 | 4 | 22 | 115 | 61 | 1
2015-10-15 22:30 | 2015-10-15 | 4 | 22 | 115 | 61 | 1
2015-10-15 22:45 | 2015-10-15 | 4 | 22 | 115 | 61 | 1
2015-10-15 23:00 | 2015-10-15 | 4 | 23 | 111 | 61 | 1
2015-10-15 23:15 | 2015-10-15 | 4 | 23 | 126 | 61 | 1
2015-10-15 23:30 | 2015-10-15 | 4 | 23 | 112 | 61 | 1
2015-10-15 23:45 | 2015-10-15 | 4 | 23 | 113 | 61 | 1
2015-10-16 | 2015-10-16 | 5 | 0 | 107 | 61 | 1
2015-10-16 00:15 | 2015-10-16 | 5 | 0 | 113 | 61 | 1
2015-10-16 00:30 | 2015-10-16 | 5 | 0 | 111 | 61 | 1
2015-10-16 00:45 | 2015-10-16 | 5 | 0 | 104 | 61 | 1
2015-10-16 01:00 | 2015-10-16 | 5 | 1 | 97 | 61 | 1
2015-10-16 01:15 | 2015-10-16 | 5 | 1 | 94 | 61 | 1
2015-10-16 01:30 | 2015-10-16 | 5 | 1 | 99 | 61 | 1
2015-10-16 01:45 | 2015-10-16 | 5 | 1 | 97 | 61 | 1
2015-10-16 02:00 | 2015-10-16 | 5 | 2 | 98 | 61 | 1
2015-10-16 02:15 | 2015-10-16 | 5 | 2 | 90 | 61 | 1
2015-10-16 02:30 | 2015-10-16 | 5 | 2 | 103 | 61 | 1
2015-10-16 02:45 | 2015-10-16 | 5 | 2 | 100 | 61 | 1
2015-10-16 03:00 | 2015-10-16 | 5 | 3 | 96 | 61 | 1
2015-10-16 03:15 | 2015-10-16 | 5 | 3 | 96 | 61 | 1
2015-10-16 03:30 | 2015-10-16 | 5 | 3 | 92 | 61 | 1
2015-10-16 03:45 | 2015-10-16 | 5 | 3 | 97 | 61 | 1
2015-10-16 04:00 | 2015-10-16 | 5 | 4 | 101 | 61 | 1
2015-10-16 04:15 | 2015-10-16 | 5 | 4 | 93 | 61 | 1
2015-10-16 04:30 | 2015-10-16 | 5 | 4 | 94 | 61 | 1
2015-10-16 04:45 | 2015-10-16 | 5 | 4 | 97 | 61 | 1
2015-10-16 05:00 | 2015-10-16 | 5 | 5 | 101 | 60.9333 | 1
2015-10-16 05:15 | 2015-10-16 | 5 | 5 | 95 | 60.6833 | 1
2015-10-16 05:30 | 2015-10-16 | 5 | 5 | 97 | 60.4333 | 1
2015-10-16 05:45 | 2015-10-16 | 5 | 5 | 90 | 60.1833 | 1
2015-10-16 06:00 | 2015-10-16 | 5 | 6 | 103 | 60 | 1
2015-10-16 06:15 | 2015-10-16 | 5 | 6 | 98 | 60 | 1
2015-10-16 06:30 | 2015-10-16 | 5 | 6 | 98 | 60 | 1
2015-10-16 06:45 | 2015-10-16 | 5 | 6 | 101 | 60 | 1
2015-10-16 07:00 | 2015-10-16 | 5 | 7 | 98 | 60.0667 | 1
2015-10-16 07:15 | 2015-10-16 | 5 | 7 | 209 | 60.3167 | 1
2015-10-16 07:30 | 2015-10-16 | 5 | 7 | 201 | 60.5667 | 1
2015-10-16 07:45 | 2015-10-16 | 5 | 7 | 193 | 60.8167 | 1
2015-10-16 08:00 | 2015-10-16 | 5 | 8 | 181 | 61.0667 | 1
2015-10-16 08:15 | 2015-10-16 | 5 | 8 | 173 | 61.3167 | 1
2015-10-16 08:30 | 2015-10-16 | 5 | 8 | 172 | 61.5667 | 1
2015-10-16 08:45 | 2015-10-16 | 5 | 8 | 179 | 61.8167 | 1
2015-10-16 09:00 | 2015-10-16 | 5 | 9 | 186 | 62.1905 | 1
2015-10-16 09:15 | 2015-10-16 | 5 | 9 | 175 | 62.9048 | 1
2015-10-16 09:30 | 2015-10-16 | 5 | 9 | 188 | 63.619 | 1
2015-10-16 09:45 | 2015-10-16 | 5 | 9 | 184 | 64.7778 | 1
2015-10-16 10:00 | 2015-10-16 | 5 | 10 | 186 | 66 | 2
2015-10-16 10:15 | 2015-10-16 | 5 | 10 | 197 | 66 | 2
2015-10-16 10:30 | 2015-10-16 | 5 | 10 | 210 | 66 | 2
2015-10-16 10:45 | 2015-10-16 | 5 | 10 | 195 | 66 | 2
2015-10-16 11:00 | 2015-10-16 | 5 | 11 | 202 | 66.1333 | 2
2015-10-16 11:15 | 2015-10-16 | 5 | 11 | 206 | 66.6333 | 2
2015-10-16 11:30 | 2015-10-16 | 5 | 11 | 195 | 67.1333 | 2
2015-10-16 11:45 | 2015-10-16 | 5 | 11 | 205 | 67.6333 | 2
2015-10-16 12:00 | 2015-10-16 | 5 | 12 | 201 | 68.2759 | 2
2015-10-16 12:15 | 2015-10-16 | 5 | 12 | 198 | 69.3103 | 2
2015-10-16 12:30 | 2015-10-16 | 5 | 12 | 191 | 69.8387 | 2
2015-10-16 12:45 | 2015-10-16 | 5 | 12 | 207 | 69.3548 | 2
2015-10-16 13:00 | 2015-10-16 | 5 | 13 | 190 | 69.1333 | 2
2015-10-16 13:15 | 2015-10-16 | 5 | 13 | 190 | 69.6333 | 2
2015-10-16 13:30 | 2015-10-16 | 5 | 13 | 194 | 70.1333 | 3
2015-10-16 13:45 | 2015-10-16 | 5 | 13 | 211 | 70.6333 | 3
2015-10-16 14:00 | 2015-10-16 | 5 | 14 | 200 | 70.8947 | 3
2015-10-16 14:15 | 2015-10-16 | 5 | 14 | 200 | 70.5 | 3
2015-10-16 14:30 | 2015-10-16 | 5 | 14 | 204 | 70.1053 | 3
2015-10-16 14:45 | 2015-10-16 | 5 | 14 | 206 | 68.5 | 2
2015-10-16 15:00 | 2015-10-16 | 5 | 15 | 210 | 66.9333 | 2
2015-10-16 15:15 | 2015-10-16 | 5 | 15 | 226 | 66.6833 | 2
2015-10-16 15:30 | 2015-10-16 | 5 | 15 | 209 | 66.4333 | 2
2015-10-16 15:45 | 2015-10-16 | 5 | 15 | 210 | 66.1833 | 2
2015-10-16 16:00 | 2015-10-16 | 5 | 16 | 209 | 65.8 | 2
2015-10-16 16:15 | 2015-10-16 | 5 | 16 | 211 | 65.05 | 2
2015-10-16 16:30 | 2015-10-16 | 5 | 16 | 224 | 64.3 | 1
2015-10-16 16:45 | 2015-10-16 | 5 | 16 | 203 | 63.55 | 1
2015-10-16 17:00 | 2015-10-16 | 5 | 17 | 211 | 62.9333 | 1
2015-10-16 17:15 | 2015-10-16 | 5 | 17 | 209 | 62.6833 | 1
2015-10-16 17:30 | 2015-10-16 | 5 | 17 | 216 | 62.4333 | 1
2015-10-16 17:45 | 2015-10-16 | 5 | 17 | 219 | 62.1833 | 1
2015-10-16 18:00 | 2015-10-16 | 5 | 18 | 198 | 62 | 1
2015-10-16 18:15 | 2015-10-16 | 5 | 18 | 213 | 62 | 1
2015-10-16 18:30 | 2015-10-16 | 5 | 18 | 206 | 62 | 1
2015-10-16 18:45 | 2015-10-16 | 5 | 18 | 221 | 62 | 1
2015-10-16 19:00 | 2015-10-16 | 5 | 19 | 215 | 62 | 1
2015-10-16 19:15 | 2015-10-16 | 5 | 19 | 118 | 62 | 1
2015-10-16 19:30 | 2015-10-16 | 5 | 19 | 122 | 62 | 1
2015-10-16 19:45 | 2015-10-16 | 5 | 19 | 119 | 62 | 1
2015-10-16 20:00 | 2015-10-16 | 5 | 20 | 115 | 61.9333 | 1
2015-10-16 20:15 | 2015-10-16 | 5 | 20 | 135 | 61.6833 | 1
2015-10-16 20:30 | 2015-10-16 | 5 | 20 | 117 | 61.4333 | 1
2015-10-16 20:45 | 2015-10-16 | 5 | 20 | 116 | 61.1833 | 1
2015-10-16 21:00 | 2015-10-16 | 5 | 21 | 121 | 61 | 1
2015-10-16 21:15 | 2015-10-16 | 5 | 21 | 112 | 61 | 1
2015-10-16 21:30 | 2015-10-16 | 5 | 21 | 102 | 61 | 1
2015-10-16 21:45 | 2015-10-16 | 5 | 21 | 102 | 61 | 1
2015-10-16 22:00 | 2015-10-16 | 5 | 22 | 102 | 61 | 1
2015-10-16 22:15 | 2015-10-16 | 5 | 22 | 105 | 61 | 1
2015-10-16 22:30 | 2015-10-16 | 5 | 22 | 111 | 61 | 1
2015-10-16 22:45 | 2015-10-16 | 5 | 22 | 99 | 61 | 1
2015-10-16 23:00 | 2015-10-16 | 5 | 23 | 102 | 61 | 1
2015-10-16 23:15 | 2015-10-16 | 5 | 23 | 97 | 61 | 1
2015-10-16 23:30 | 2015-10-16 | 5 | 23 | 104 | 61 | 1
2015-10-16 23:45 | 2015-10-16 | 5 | 23 | 108 | 61 | 1
2015-10-17 | 2015-10-17 | 6 | 0 | 98 | 61 | 1
2015-10-17 00:15 | 2015-10-17 | 6 | 0 | 109 | 61 | 1
2015-10-17 00:30 | 2015-10-17 | 6 | 0 | 99 | 61 | 1
2015-10-17 00:45 | 2015-10-17 | 6 | 0 | 101 | 61 | 1
2015-10-17 01:00 | 2015-10-17 | 6 | 1 | 99 | 61 | 1
2015-10-17 01:15 | 2015-10-17 | 6 | 1 | 107 | 61 | 1
2015-10-17 01:30 | 2015-10-17 | 6 | 1 | 101 | 61 | 1
2015-10-17 01:45 | 2015-10-17 | 6 | 1 | 100 | 61 | 1
2015-10-17 02:00 | 2015-10-17 | 6 | 2 | 100 | 61 | 1
2015-10-17 02:15 | 2015-10-17 | 6 | 2 | 102 | 61 | 1
2015-10-17 02:30 | 2015-10-17 | 6 | 2 | 109 | 61 | 1
2015-10-17 02:45 | 2015-10-17 | 6 | 2 | 99 | 61 | 1
2015-10-17 03:00 | 2015-10-17 | 6 | 3 | 101 | 61 | 1
2015-10-17 03:15 | 2015-10-17 | 6 | 3 | 97 | 61 | 1
2015-10-17 03:30 | 2015-10-17 | 6 | 3 | 109 | 61 | 1
2015-10-17 03:45 | 2015-10-17 | 6 | 3 | 100 | 61 | 1
2015-10-17 04:00 | 2015-10-17 | 6 | 4 | 99 | 61.0667 | 1
2015-10-17 04:15 | 2015-10-17 | 6 | 4 | 100 | 61.3167 | 1
2015-10-17 04:30 | 2015-10-17 | 6 | 4 | 101 | 61.5667 | 1
2015-10-17 04:45 | 2015-10-17 | 6 | 4 | 106 | 61.8167 | 1
2015-10-17 05:00 | 2015-10-17 | 6 | 5 | 100 | 62 | 1
2015-10-17 05:15 | 2015-10-17 | 6 | 5 | 99 | 62 | 1
2015-10-17 05:30 | 2015-10-17 | 6 | 5 | 97 | 62 | 1
2015-10-17 05:45 | 2015-10-17 | 6 | 5 | 101 | 62 | 1
2015-10-17 06:00 | 2015-10-17 | 6 | 6 | 107 | 62 | 1
2015-10-17 06:15 | 2015-10-17 | 6 | 6 | 103 | 62 | 1
2015-10-17 06:30 | 2015-10-17 | 6 | 6 | 110 | 62 | 1
2015-10-17 06:45 | 2015-10-17 | 6 | 6 | 99 | 62 | 1
2015-10-17 07:00 | 2015-10-17 | 6 | 7 | 105 | 62.0667 | 1
2015-10-17 07:15 | 2015-10-17 | 6 | 7 | 110 | 62.3167 | 1
2015-10-17 07:30 | 2015-10-17 | 6 | 7 | 101 | 62.5667 | 1
2015-10-17 07:45 | 2015-10-17 | 6 | 7 | 96 | 62.8167 | 1
2015-10-17 08:00 | 2015-10-17 | 6 | 8 | 98 | 63.1333 | 1
2015-10-17 08:15 | 2015-10-17 | 6 | 8 | 103 | 63.6333 | 1
2015-10-17 08:30 | 2015-10-17 | 6 | 8 | 99 | 64.1333 | 1
2015-10-17 08:45 | 2015-10-17 | 6 | 8 | 115 | 64.6333 | 1
2015-10-17 09:00 | 2015-10-17 | 6 | 9 | 105 | 65.0667 | 2
2015-10-17 09:15 | 2015-10-17 | 6 | 9 | 101 | 65.3167 | 2
2015-10-17 09:30 | 2015-10-17 | 6 | 9 | 103 | 65.5667 | 2
2015-10-17 09:45 | 2015-10-17 | 6 | 9 | 102 | 65.8167 | 2
2015-10-17 10:00 | 2015-10-17 | 6 | 10 | 100 | 66 | 2
2015-10-17 10:15 | 2015-10-17 | 6 | 10 | 103 | 66 | 2
2015-10-17 10:30 | 2015-10-17 | 6 | 10 | 112 | 66 | 2
2015-10-17 10:45 | 2015-10-17 | 6 | 10 | 106 | 66 | 2
2015-10-17 11:00 | 2015-10-17 | 6 | 11 | 106 | 66.0667 | 2
2015-10-17 11:15 | 2015-10-17 | 6 | 11 | 101 | 66.3167 | 2
2015-10-17 11:30 | 2015-10-17 | 6 | 11 | 111 | 66.5667 | 2
2015-10-17 11:45 | 2015-10-17 | 6 | 11 | 112 | 66.8167 | 2
2015-10-17 12:00 | 2015-10-17 | 6 | 12 | 104 | 67 | 2
2015-10-17 12:15 | 2015-10-17 | 6 | 12 | 105 | 67 | 2
2015-10-17 12:30 | 2015-10-17 | 6 | 12 | 101 | 67 | 2
2015-10-17 12:45 | 2015-10-17 | 6 | 12 | 101 | 67 | 2
2015-10-17 13:00 | 2015-10-17 | 6 | 13 | 110 | 67.1333 | 2
2015-10-17 13:15 | 2015-10-17 | 6 | 13 | 99 | 67.6333 | 2
2015-10-17 13:30 | 2015-10-17 | 6 | 13 | 103 | 68.1333 | 2
2015-10-17 13:45 | 2015-10-17 | 6 | 13 | 101 | 68.6333 | 2
2015-10-17 14:00 | 2015-10-17 | 6 | 14 | 110 | 68.8667 | 2
2015-10-17 14:15 | 2015-10-17 | 6 | 14 | 105 | 68.3667 | 2
2015-10-17 14:30 | 2015-10-17 | 6 | 14 | 102 | 67.8667 | 2
2015-10-17 14:45 | 2015-10-17 | 6 | 14 | 100 | 67.3667 | 2
2015-10-17 15:00 | 2015-10-17 | 6 | 15 | 103 | 66.8974 | 2
2015-10-17 15:15 | 2015-10-17 | 6 | 15 | 110 | 66.5128 | 2
2015-10-17 15:30 | 2015-10-17 | 6 | 15 | 100 | 66.1282 | 2
2015-10-17 15:45 | 2015-10-17 | 6 | 15 | 104 | 66 | 2
2015-10-17 16:00 | 2015-10-17 | 6 | 16 | 99 | 65.8667 | 2
2015-10-17 16:15 | 2015-10-17 | 6 | 16 | 112 | 65.3667 | 2
2015-10-17 16:30 | 2015-10-17 | 6 | 16 | 102 | 64.8667 | 1
2015-10-17 16:45 | 2015-10-17 | 6 | 16 | 103 | 64.3667 | 1
2015-10-17 17:00 | 2015-10-17 | 6 | 17 | 103 | 63.9333 | 1
2015-10-17 17:15 | 2015-10-17 | 6 | 17 | 111 | 63.6833 | 1
2015-10-17 17:30 | 2015-10-17 | 6 | 17 | 116 | 63.4333 | 1
2015-10-17 17:45 | 2015-10-17 | 6 | 17 | 107 | 63.1833 | 1
2015-10-17 18:00 | 2015-10-17 | 6 | 18 | 107 | 63 | 1
2015-10-17 18:15 | 2015-10-17 | 6 | 18 | 107 | 63 | 1
2015-10-17 18:30 | 2015-10-17 | 6 | 18 | 114 | 63 | 1
2015-10-17 18:45 | 2015-10-17 | 6 | 18 | 108 | 63 | 1
2015-10-17 19:00 | 2015-10-17 | 6 | 19 | 110 | 63 | 1
2015-10-17 19:15 | 2015-10-17 | 6 | 19 | 104 | 63 | 1
2015-10-17 19:30 | 2015-10-17 | 6 | 19 | 113 | 63 | 1
2015-10-17 19:45 | 2015-10-17 | 6 | 19 | 109 | 63 | 1
2015-10-17 20:00 | 2015-10-17 | 6 | 20 | 109 | 63 | 1
2015-10-17 20:15 | 2015-10-17 | 6 | 20 | 106 | 63 | 1
2015-10-17 20:30 | 2015-10-17 | 6 | 20 | 108 | 63 | 1
2015-10-17 20:45 | 2015-10-17 | 6 | 20 | 113 | 63 | 1
2015-10-17 21:00 | 2015-10-17 | 6 | 21 | 107 | 63 | 1
2015-10-17 21:15 | 2015-10-17 | 6 | 21 | 106 | 63 | 1
2015-10-17 21:30 | 2015-10-17 | 6 | 21 | 99 | 63 | 1
2015-10-17 21:45 | 2015-10-17 | 6 | 21 | 104 | 63 | 1
2015-10-17 22:00 | 2015-10-17 | 6 | 22 | 104 | 62.08 | 1
2015-10-17 22:15 | 2015-10-17 | 6 | 22 | 102 | 62.38 | 1
2015-10-17 22:30 | 2015-10-17 | 6 | 22 | 96 | 62.68 | 1
2015-10-17 22:45 | 2015-10-17 | 6 | 22 | 101 | 62.98 | 1
2015-10-17 23:00 | 2015-10-17 | 6 | 23 | 96 | 62.1176 | 1
2015-10-17 23:15 | 2015-10-17 | 6 | 23 | 105 | 62.5588 | 1
2015-10-17 23:30 | 2015-10-17 | 6 | 23 | 104 | 63 | 1
2015-10-17 23:45 | 2015-10-17 | 6 | 23 | 101 | 61.8462 | 1
2015-10-18 | 2015-10-18 | 7 | 0 | 101 | 61 | 1
2015-10-18 00:15 | 2015-10-18 | 7 | 0 | 99 | 61 | 1
2015-10-18 00:30 | 2015-10-18 | 7 | 0 | 104 | 61 | 1
2015-10-18 00:45 | 2015-10-18 | 7 | 0 | 96 | 61 | 1
2015-10-18 01:00 | 2015-10-18 | 7 | 1 | 92 | 61 | 1
2015-10-18 01:15 | 2015-10-18 | 7 | 1 | 91 | 61 | 1
2015-10-18 01:30 | 2015-10-18 | 7 | 1 | 101 | 61 | 1
2015-10-18 01:45 | 2015-10-18 | 7 | 1 | 91 | 61 | 1
2015-10-18 02:00 | 2015-10-18 | 7 | 2 | 96 | 61 | 1
2015-10-18 02:15 | 2015-10-18 | 7 | 2 | 89 | 61 | 1
2015-10-18 02:30 | 2015-10-18 | 7 | 2 | 101 | 61 | 1
2015-10-18 02:45 | 2015-10-18 | 7 | 2 | 96 | 61 | 1
2015-10-18 03:00 | 2015-10-18 | 7 | 3 | 93 | 61 | 1
2015-10-18 03:15 | 2015-10-18 | 7 | 3 | 90 | 61 | 1
2015-10-18 03:30 | 2015-10-18 | 7 | 3 | 95 | 61 | 1
2015-10-18 03:45 | 2015-10-18 | 7 | 3 | 96 | 61 | 1
2015-10-18 04:00 | 2015-10-18 | 7 | 4 | 96 | 61 | 1
2015-10-18 04:15 | 2015-10-18 | 7 | 4 | 92 | 61 | 1
2015-10-18 04:30 | 2015-10-18 | 7 | 4 | 89 | 61 | 1
2015-10-18 04:45 | 2015-10-18 | 7 | 4 | 94 | 61 | 1
2015-10-18 05:00 | 2015-10-18 | 7 | 5 | 97 | 61.1951 | 1
2015-10-18 05:15 | 2015-10-18 | 7 | 5 | 95 | 61.9268 | 1
2015-10-18 05:30 | 2015-10-18 | 7 | 5 | 91 | 62.6585 | 1
2015-10-18 05:45 | 2015-10-18 | 7 | 5 | 101 | 62.5789 | 1
2015-10-18 06:00 | 2015-10-18 | 7 | 6 | 98 | 62 | 1
2015-10-18 06:15 | 2015-10-18 | 7 | 6 | 107 | 62 | 1
2015-10-18 06:30 | 2015-10-18 | 7 | 6 | 110 | 62 | 1
2015-10-18 06:45 | 2015-10-18 | 7 | 6 | 108 | 62 | 1
2015-10-18 07:00 | 2015-10-18 | 7 | 7 | 111 | 62.4 | 1
2015-10-18 07:15 | 2015-10-18 | 7 | 7 | 104 | 63.18 | 1
2015-10-18 07:30 | 2015-10-18 | 7 | 7 | 101 | 63.48 | 1
2015-10-18 07:45 | 2015-10-18 | 7 | 7 | 102 | 63.78 | 1
2015-10-18 08:00 | 2015-10-18 | 7 | 8 | 97 | 64 | 1
2015-10-18 08:15 | 2015-10-18 | 7 | 8 | 108 | 64 | 1
2015-10-18 08:30 | 2015-10-18 | 7 | 8 | 98 | 64 | 1
2015-10-18 08:45 | 2015-10-18 | 7 | 8 | 99 | 64 | 1
2015-10-18 09:00 | 2015-10-18 | 7 | 9 | 99 | 64.0667 | 1
2015-10-18 09:15 | 2015-10-18 | 7 | 9 | 104 | 64.3167 | 1
2015-10-18 09:30 | 2015-10-18 | 7 | 9 | 97 | 64.5667 | 1
2015-10-18 09:45 | 2015-10-18 | 7 | 9 | 101 | 64.8167 | 1
2015-10-18 10:00 | 2015-10-18 | 7 | 10 | 94 | 65.0667 | 2
2015-10-18 10:15 | 2015-10-18 | 7 | 10 | 105 | 65.3167 | 2
2015-10-18 10:30 | 2015-10-18 | 7 | 10 | 99 | 65.5667 | 2
2015-10-18 10:45 | 2015-10-18 | 7 | 10 | 99 | 65.8167 | 2
2015-10-18 11:00 | 2015-10-18 | 7 | 11 | 97 | 66.1333 | 2
2015-10-18 11:15 | 2015-10-18 | 7 | 11 | 96 | 66.6333 | 2
2015-10-18 11:30 | 2015-10-18 | 7 | 11 | 95 | 67.1333 | 2
2015-10-18 11:45 | 2015-10-18 | 7 | 11 | 106 | 67.6333 | 2
2015-10-18 12:00 | 2015-10-18 | 7 | 12 | 101 | 68 | 2
2015-10-18 12:15 | 2015-10-18 | 7 | 12 | 96 | 68 | 2
2015-10-18 12:30 | 2015-10-18 | 7 | 12 | 96 | 68 | 2
2015-10-18 12:45 | 2015-10-18 | 7 | 12 | 101 | 68 | 2
2015-10-18 13:00 | 2015-10-18 | 7 | 13 | 100 | 68 | 2
2015-10-18 13:15 | 2015-10-18 | 7 | 13 | 99 | 68 | 2
2015-10-18 13:30 | 2015-10-18 | 7 | 13 | 96 | 68 | 2
2015-10-18 13:45 | 2015-10-18 | 7 | 13 | 102 | 68 | 2
2015-10-18 14:00 | 2015-10-18 | 7 | 14 | 101 | 67.9333 | 2
2015-10-18 14:15 | 2015-10-18 | 7 | 14 | 98 | 67.6833 | 2
2015-10-18 14:30 | 2015-10-18 | 7 | 14 | 100 | 67.4333 | 2
2015-10-18 14:45 | 2015-10-18 | 7 | 14 | 101 | 67.1833 | 2
2015-10-18 15:00 | 2015-10-18 | 7 | 15 | 108 | 66.9333 | 2
2015-10-18 15:15 | 2015-10-18 | 7 | 15 | 100 | 66.6833 | 2
2015-10-18 15:30 | 2015-10-18 | 7 | 15 | 100 | 66.4333 | 2
2015-10-18 15:45 | 2015-10-18 | 7 | 15 | 94 | 66.1833 | 2
2015-10-18 16:00 | 2015-10-18 | 7 | 16 | 101 | 65.8667 | 2
2015-10-18 16:15 | 2015-10-18 | 7 | 16 | 95 | 65.3667 | 2
2015-10-18 16:30 | 2015-10-18 | 7 | 16 | 101 | 64.8667 | 1
2015-10-18 16:45 | 2015-10-18 | 7 | 16 | 101 | 64.3667 | 1
2015-10-18 17:00 | 2015-10-18 | 7 | 17 | 103 | 63.9048 | 1
2015-10-18 17:15 | 2015-10-18 | 7 | 17 | 101 | 63.5476 | 1
2015-10-18 17:30 | 2015-10-18 | 7 | 17 | 102 | 63.1905 | 1
2015-10-18 17:45 | 2015-10-18 | 7 | 17 | 111 | 63 | 1
2015-10-18 18:00 | 2015-10-18 | 7 | 18 | 110 | 63 | 1
2015-10-18 18:15 | 2015-10-18 | 7 | 18 | 113 | 63 | 1
2015-10-18 18:30 | 2015-10-18 | 7 | 18 | 107 | 63 | 1
2015-10-18 18:45 | 2015-10-18 | 7 | 18 | 117 | 62.6111 | 1
2015-10-18 19:00 | 2015-10-18 | 7 | 19 | 111 | 62.0889 | 1
2015-10-18 19:15 | 2015-10-18 | 7 | 19 | 111 | 62.4222 | 1
2015-10-18 19:30 | 2015-10-18 | 7 | 19 | 108 | 62.7556 | 1
2015-10-18 19:45 | 2015-10-18 | 7 | 19 | 103 | 62.7333 | 1
2015-10-18 20:00 | 2015-10-18 | 7 | 20 | 105 | 62 | 1
2015-10-18 20:15 | 2015-10-18 | 7 | 20 | 107 | 62 | 1
2015-10-18 20:30 | 2015-10-18 | 7 | 20 | 104 | 62 | 1
2015-10-18 20:45 | 2015-10-18 | 7 | 20 | 104 | 62 | 1
2015-10-18 21:00 | 2015-10-18 | 7 | 21 | 111 | 62.0851 | 1
2015-10-18 21:15 | 2015-10-18 | 7 | 21 | 104 | 62.4043 | 1
2015-10-18 21:30 | 2015-10-18 | 7 | 21 | 98 | 62.7234 | 1
2015-10-18 21:45 | 2015-10-18 | 7 | 21 | 95 | 62.8462 | 1
2015-10-18 22:00 | 2015-10-18 | 7 | 22 | 92 | 62 | 1
2015-10-18 22:15 | 2015-10-18 | 7 | 22 | 99 | 62 | 1
2015-10-18 22:30 | 2015-10-18 | 7 | 22 | 98 | 62 | 1
2015-10-18 22:45 | 2015-10-18 | 7 | 22 | 95 | 62 | 1
2015-10-18 23:00 | 2015-10-18 | 7 | 23 | 95 | 62 | 1
2015-10-18 23:15 | 2015-10-18 | 7 | 23 | 95 | 62 | 1
2015-10-18 23:30 | 2015-10-18 | 7 | 23 | 95 | 62 | 1
2015-10-18 23:45 | 2015-10-18 | 7 | 23 | 97 | 62 | 1
2015-10-19 | 2015-10-19 | 1 | 0 | 101 | 62.1667 | 1
2015-10-19 00:15 | 2015-10-19 | 1 | 0 | 98 | 62.7917 | 1
2015-10-19 00:30 | 2015-10-19 | 1 | 0 | 96 | 62.4444 | 1
2015-10-19 00:45 | 2015-10-19 | 1 | 0 | 91 | 61.6111 | 1
2015-10-19 01:00 | 2015-10-19 | 1 | 1 | 97 | 61 | 1
2015-10-19 01:15 | 2015-10-19 | 1 | 1 | 102 | 61 | 1
2015-10-19 01:30 | 2015-10-19 | 1 | 1 | 94 | 61 | 1
2015-10-19 01:45 | 2015-10-19 | 1 | 1 | 95 | 61 | 1
2015-10-19 02:00 | 2015-10-19 | 1 | 2 | 97 | 61 | 1
2015-10-19 02:15 | 2015-10-19 | 1 | 2 | 105 | 61 | 1
2015-10-19 02:30 | 2015-10-19 | 1 | 2 | 99 | 61 | 1
2015-10-19 02:45 | 2015-10-19 | 1 | 2 | 94 | 61 | 1
2015-10-19 03:00 | 2015-10-19 | 1 | 3 | 98 | 61 | 1
2015-10-19 03:15 | 2015-10-19 | 1 | 3 | 98 | 61 | 1
2015-10-19 03:30 | 2015-10-19 | 1 | 3 | 97 | 61 | 1
2015-10-19 03:45 | 2015-10-19 | 1 | 3 | 97 | 60.7333 | 1
2015-10-19 04:00 | 2015-10-19 | 1 | 4 | 105 | 60.1053 | 1
2015-10-19 04:15 | 2015-10-19 | 1 | 4 | 96 | 60.5 | 1
2015-10-19 04:30 | 2015-10-19 | 1 | 4 | 98 | 60.8947 | 1
2015-10-19 04:45 | 2015-10-19 | 1 | 4 | 91 | 61 | 1
2015-10-19 05:00 | 2015-10-19 | 1 | 5 | 98 | 61 | 1
2015-10-19 05:15 | 2015-10-19 | 1 | 5 | 97 | 61 | 1
2015-10-19 05:30 | 2015-10-19 | 1 | 5 | 97 | 61 | 1
2015-10-19 05:45 | 2015-10-19 | 1 | 5 | 95 | 61 | 1
2015-10-19 06:00 | 2015-10-19 | 1 | 6 | 98 | 60 | 1
2015-10-19 06:15 | 2015-10-19 | 1 | 6 | 100 | 60 | 1
2015-10-19 06:30 | 2015-10-19 | 1 | 6 | 98 | 60 | 1
2015-10-19 06:45 | 2015-10-19 | 1 | 6 | 95 | 60 | 1
2015-10-19 07:00 | 2015-10-19 | 1 | 7 | 100 | 60.1333 | 1
2015-10-19 07:15 | 2015-10-19 | 1 | 7 | 214 | 60.6333 | 1
2015-10-19 07:30 | 2015-10-19 | 1 | 7 | 196 | 61.1333 | 1
2015-10-19 07:45 | 2015-10-19 | 1 | 7 | 189 | 61.6333 | 1
2015-10-19 08:00 | 2015-10-19 | 1 | 8 | 187 | 62.0667 | 1
2015-10-19 08:15 | 2015-10-19 | 1 | 8 | 181 | 62.3167 | 1
2015-10-19 08:30 | 2015-10-19 | 1 | 8 | 177 | 62.5667 | 1
2015-10-19 08:45 | 2015-10-19 | 1 | 8 | 177 | 62.8167 | 1
2015-10-19 09:00 | 2015-10-19 | 1 | 9 | 173 | 63.0667 | 1
2015-10-19 09:15 | 2015-10-19 | 1 | 9 | 176 | 63.3167 | 1
2015-10-19 09:30 | 2015-10-19 | 1 | 9 | 183 | 63.5667 | 1
2015-10-19 09:45 | 2015-10-19 | 1 | 9 | 178 | 63.8167 | 1
2015-10-19 10:00 | 2015-10-19 | 1 | 10 | 179 | 64 | 1
2015-10-19 10:15 | 2015-10-19 | 1 | 10 | 177 | 64 | 1
2015-10-19 10:30 | 2015-10-19 | 1 | 10 | 178 | 64 | 1
2015-10-19 10:45 | 2015-10-19 | 1 | 10 | 184 | 64 | 1
2015-10-19 11:00 | 2015-10-19 | 1 | 11 | 171 | 65.0667 | 2
2015-10-19 11:15 | 2015-10-19 | 1 | 11 | 180 | 65.3167 | 2
2015-10-19 11:30 | 2015-10-19 | 1 | 11 | 178 | 65.5667 | 2
2015-10-19 11:45 | 2015-10-19 | 1 | 11 | 188 | 65.8167 | 2
2015-10-19 12:00 | 2015-10-19 | 1 | 12 | 176 | 66.0667 | 2
2015-10-19 12:15 | 2015-10-19 | 1 | 12 | 181 | 66.3167 | 2
2015-10-19 12:30 | 2015-10-19 | 1 | 12 | 176 | 66.5667 | 2
2015-10-19 12:45 | 2015-10-19 | 1 | 12 | 179 | 66.8167 | 2
2015-10-19 13:00 | 2015-10-19 | 1 | 13 | 193 | 67 | 2
2015-10-19 13:15 | 2015-10-19 | 1 | 13 | 193 | 67 | 2
2015-10-19 13:30 | 2015-10-19 | 1 | 13 | 190 | 67 | 2
2015-10-19 13:45 | 2015-10-19 | 1 | 13 | 186 | 67 | 2
2015-10-19 14:00 | 2015-10-19 | 1 | 14 | 194 | 67 | 2
2015-10-19 14:15 | 2015-10-19 | 1 | 14 | 202 | 67 | 2
2015-10-19 14:30 | 2015-10-19 | 1 | 14 | 193 | 67 | 2
2015-10-19 14:45 | 2015-10-19 | 1 | 14 | 200 | 67 | 2
2015-10-19 15:00 | 2015-10-19 | 1 | 15 | 203 | 66.9333 | 2
2015-10-19 15:15 | 2015-10-19 | 1 | 15 | 208 | 66.6833 | 2
2015-10-19 15:30 | 2015-10-19 | 1 | 15 | 199 | 66.4333 | 2
2015-10-19 15:45 | 2015-10-19 | 1 | 15 | 223 | 66.1833 | 2
2015-10-19 16:00 | 2015-10-19 | 1 | 16 | 210 | 65.9333 | 2
2015-10-19 16:15 | 2015-10-19 | 1 | 16 | 209 | 65.6833 | 2
2015-10-19 16:30 | 2015-10-19 | 1 | 16 | 208 | 65.4333 | 2
2015-10-19 16:45 | 2015-10-19 | 1 | 16 | 204 | 65.1833 | 2
2015-10-19 17:00 | 2015-10-19 | 1 | 17 | 190 | 64.8667 | 1
2015-10-19 17:15 | 2015-10-19 | 1 | 17 | 203 | 64.3667 | 1
2015-10-19 17:30 | 2015-10-19 | 1 | 17 | 189 | 63.8667 | 1
2015-10-19 17:45 | 2015-10-19 | 1 | 17 | 191 | 63.3667 | 1
2015-10-19 18:00 | 2015-10-19 | 1 | 18 | 183 | 63 | 1
2015-10-19 18:15 | 2015-10-19 | 1 | 18 | 190 | 63 | 1
2015-10-19 18:30 | 2015-10-19 | 1 | 18 | 196 | 63 | 1
2015-10-19 18:45 | 2015-10-19 | 1 | 18 | 182 | 63 | 1
2015-10-19 19:00 | 2015-10-19 | 1 | 19 | 178 | 62.9333 | 1
2015-10-19 19:15 | 2015-10-19 | 1 | 19 | 118 | 62.6833 | 1
2015-10-19 19:30 | 2015-10-19 | 1 | 19 | 127 | 62.4333 | 1
2015-10-19 19:45 | 2015-10-19 | 1 | 19 | 132 | 62.1833 | 1
2015-10-19 20:00 | 2015-10-19 | 1 | 20 | 125 | 62 | 1
2015-10-19 20:15 | 2015-10-19 | 1 | 20 | 119 | 62 | 1
2015-10-19 20:30 | 2015-10-19 | 1 | 20 | 120 | 62 | 1
2015-10-19 20:45 | 2015-10-19 | 1 | 20 | 132 | 62 | 1
2015-10-19 21:00 | 2015-10-19 | 1 | 21 | 122 | 61.9333 | 1
2015-10-19 21:15 | 2015-10-19 | 1 | 21 | 116 | 61.6833 | 1
2015-10-19 21:30 | 2015-10-19 | 1 | 21 | 108 | 61.4333 | 1
2015-10-19 21:45 | 2015-10-19 | 1 | 21 | 111 | 61.1833 | 1
2015-10-19 22:00 | 2015-10-19 | 1 | 22 | 122 | 61 | 1
2015-10-19 22:15 | 2015-10-19 | 1 | 22 | 108 | 61 | 1
2015-10-19 22:30 | 2015-10-19 | 1 | 22 | 109 | 61 | 1
2015-10-19 22:45 | 2015-10-19 | 1 | 22 | 109 | 61 | 1
2015-10-19 23:00 | 2015-10-19 | 1 | 23 | 121 | 60.9333 | 1
2015-10-19 23:15 | 2015-10-19 | 1 | 23 | 113 | 60.6833 | 1
2015-10-19 23:30 | 2015-10-19 | 1 | 23 | 110 | 60.4333 | 1
2015-10-19 23:45 | 2015-10-19 | 1 | 23 | 107 | 60.1833 | 1
2015-10-20 | 2015-10-20 | 2 | 0 | 105 | 59.9333 | 1
2015-10-20 00:15 | 2015-10-20 | 2 | 0 | 108 | 59.6833 | 1
2015-10-20 00:30 | 2015-10-20 | 2 | 0 | 105 | 59.4333 | 1
2015-10-20 00:45 | 2015-10-20 | 2 | 0 | 107 | 59.1833 | 1
2015-10-20 01:00 | 2015-10-20 | 2 | 1 | 103 | 58.9333 | 1
2015-10-20 01:15 | 2015-10-20 | 2 | 1 | 102 | 58.6833 | 1
2015-10-20 01:30 | 2015-10-20 | 2 | 1 | 111 | 58.4333 | 1
2015-10-20 01:45 | 2015-10-20 | 2 | 1 | 104 | 58.1833 | 1
2015-10-20 02:00 | 2015-10-20 | 2 | 2 | 110 | 57.9333 | 1
2015-10-20 02:15 | 2015-10-20 | 2 | 2 | 107 | 57.6833 | 1
2015-10-20 02:30 | 2015-10-20 | 2 | 2 | 108 | 57.4333 | 1
2015-10-20 02:45 | 2015-10-20 | 2 | 2 | 107 | 57.1833 | 1
2015-10-20 03:00 | 2015-10-20 | 2 | 3 | 104 | 57 | 1
2015-10-20 03:15 | 2015-10-20 | 2 | 3 | 102 | 57 | 1
2015-10-20 03:30 | 2015-10-20 | 2 | 3 | 99 | 57 | 1
2015-10-20 03:45 | 2015-10-20 | 2 | 3 | 105 | 57 | 1
2015-10-20 04:00 | 2015-10-20 | 2 | 4 | 108 | 57 | 1
2015-10-20 04:15 | 2015-10-20 | 2 | 4 | 102 | 57 | 1
2015-10-20 04:30 | 2015-10-20 | 2 | 4 | 104 | 57 | 1
2015-10-20 04:45 | 2015-10-20 | 2 | 4 | 103 | 57.0833 | 1
2015-10-20 05:00 | 2015-10-20 | 2 | 5 | 107 | 58 | 1
2015-10-20 05:15 | 2015-10-20 | 2 | 5 | 105 | 58 | 1
2015-10-20 05:30 | 2015-10-20 | 2 | 5 | 101 | 58 | 1
2015-10-20 05:45 | 2015-10-20 | 2 | 5 | 105 | 58 | 1
2015-10-20 06:00 | 2015-10-20 | 2 | 6 | 103 | 57.9333 | 1
2015-10-20 06:15 | 2015-10-20 | 2 | 6 | 112 | 57.6833 | 1
2015-10-20 06:30 | 2015-10-20 | 2 | 6 | 103 | 57.4333 | 1
2015-10-20 06:45 | 2015-10-20 | 2 | 6 | 104 | 57.1833 | 1
2015-10-20 07:00 | 2015-10-20 | 2 | 7 | 107 | 57.2667 | 1
2015-10-20 07:15 | 2015-10-20 | 2 | 7 | 151 | 58.2667 | 1
2015-10-20 07:30 | 2015-10-20 | 2 | 7 | 140 | 59.2667 | 1
2015-10-20 07:45 | 2015-10-20 | 2 | 7 | 144 | 60.2667 | 1
2015-10-20 08:00 | 2015-10-20 | 2 | 8 | 150 | 61.2 | 1
2015-10-20 08:15 | 2015-10-20 | 2 | 8 | 164 | 61.95 | 1
2015-10-20 08:30 | 2015-10-20 | 2 | 8 | 147 | 62.7 | 1
2015-10-20 08:45 | 2015-10-20 | 2 | 8 | 152 | 63.45 | 1
2015-10-20 09:00 | 2015-10-20 | 2 | 9 | 159 | 64.0667 | 1
2015-10-20 09:15 | 2015-10-20 | 2 | 9 | 172 | 64.3167 | 1
2015-10-20 09:30 | 2015-10-20 | 2 | 9 | 175 | 64.5667 | 1
2015-10-20 09:45 | 2015-10-20 | 2 | 9 | 175 | 64.8167 | 1
2015-10-20 10:00 | 2015-10-20 | 2 | 10 | 188 | 65.2 | 2
2015-10-20 10:15 | 2015-10-20 | 2 | 10 | 173 | 65.95 | 2
2015-10-20 10:30 | 2015-10-20 | 2 | 10 | 166 | 66.7 | 2
2015-10-20 10:45 | 2015-10-20 | 2 | 10 | 181 | 67.45 | 2
2015-10-20 11:00 | 2015-10-20 | 2 | 11 | 194 | 68.2667 | 2
2015-10-20 11:15 | 2015-10-20 | 2 | 11 | 175 | 69.2667 | 2
2015-10-20 11:30 | 2015-10-20 | 2 | 11 | 185 | 70.2667 | 3
2015-10-20 11:45 | 2015-10-20 | 2 | 11 | 181 | 71.2667 | 3
2015-10-20 12:00 | 2015-10-20 | 2 | 12 | 192 | 72.2667 | 3
2015-10-20 12:15 | 2015-10-20 | 2 | 12 | 189 | 73.2667 | 3
2015-10-20 12:30 | 2015-10-20 | 2 | 12 | 184 | 74.2667 | 3
2015-10-20 12:45 | 2015-10-20 | 2 | 12 | 181 | 75.2667 | 4
2015-10-20 13:00 | 2015-10-20 | 2 | 13 | 189 | 76.0667 | 4
2015-10-20 13:15 | 2015-10-20 | 2 | 13 | 208 | 76.3167 | 4
2015-10-20 13:30 | 2015-10-20 | 2 | 13 | 184 | 76.5667 | 4
2015-10-20 13:45 | 2015-10-20 | 2 | 13 | 190 | 76.8167 | 4
2015-10-20 14:00 | 2015-10-20 | 2 | 14 | 186 | 76.9333 | 4
2015-10-20 14:15 | 2015-10-20 | 2 | 14 | 188 | 76.6833 | 4
2015-10-20 14:30 | 2015-10-20 | 2 | 14 | 208 | 76.4333 | 4
2015-10-20 14:45 | 2015-10-20 | 2 | 14 | 186 | 76.1833 | 4
2015-10-20 15:00 | 2015-10-20 | 2 | 15 | 194 | 75.6667 | 4
2015-10-20 15:15 | 2015-10-20 | 2 | 15 | 202 | 74.4167 | 3
2015-10-20 15:30 | 2015-10-20 | 2 | 15 | 213 | 73.1667 | 3
2015-10-20 15:45 | 2015-10-20 | 2 | 15 | 206 | 71.9167 | 3
2015-10-20 16:00 | 2015-10-20 | 2 | 16 | 202 | 70.8 | 3
2015-10-20 16:15 | 2015-10-20 | 2 | 16 | 199 | 70.05 | 3
2015-10-20 16:30 | 2015-10-20 | 2 | 16 | 192 | 69.3 | 2
2015-10-20 16:45 | 2015-10-20 | 2 | 16 | 209 | 68.55 | 2
2015-10-20 17:00 | 2015-10-20 | 2 | 17 | 193 | 67.8667 | 2
2015-10-20 17:15 | 2015-10-20 | 2 | 17 | 198 | 67.3667 | 2
2015-10-20 17:30 | 2015-10-20 | 2 | 17 | 196 | 66.8667 | 2
2015-10-20 17:45 | 2015-10-20 | 2 | 17 | 200 | 66.3667 | 2
2015-10-20 18:00 | 2015-10-20 | 2 | 18 | 193 | 65.8 | 2
2015-10-20 18:15 | 2015-10-20 | 2 | 18 | 188 | 65.05 | 2
2015-10-20 18:30 | 2015-10-20 | 2 | 18 | 191 | 64.3 | 1
2015-10-20 18:45 | 2015-10-20 | 2 | 18 | 184 | 63.55 | 1
2015-10-20 19:00 | 2015-10-20 | 2 | 19 | 193 | 62.9333 | 1
2015-10-20 19:15 | 2015-10-20 | 2 | 19 | 118 | 62.6833 | 1
2015-10-20 19:30 | 2015-10-20 | 2 | 19 | 118 | 62.4333 | 1
2015-10-20 19:45 | 2015-10-20 | 2 | 19 | 119 | 62.1833 | 1
2015-10-20 20:00 | 2015-10-20 | 2 | 20 | 125 | 62 | 1
2015-10-20 20:15 | 2015-10-20 | 2 | 20 | 126 | 62 | 1
2015-10-20 20:30 | 2015-10-20 | 2 | 20 | 122 | 62 | 1
2015-10-20 20:45 | 2015-10-20 | 2 | 20 | 113 | 62 | 1
2015-10-20 21:00 | 2015-10-20 | 2 | 21 | 116 | 61.9333 | 1
2015-10-20 21:15 | 2015-10-20 | 2 | 21 | 113 | 61.6833 | 1
2015-10-20 21:30 | 2015-10-20 | 2 | 21 | 103 | 61.4333 | 1
2015-10-20 21:45 | 2015-10-20 | 2 | 21 | 107 | 61.1833 | 1
2015-10-20 22:00 | 2015-10-20 | 2 | 22 | 119 | 61 | 1
2015-10-20 22:15 | 2015-10-20 | 2 | 22 | 112 | 61 | 1
2015-10-20 22:30 | 2015-10-20 | 2 | 22 | 111 | 61 | 1
2015-10-20 22:45 | 2015-10-20 | 2 | 22 | 109 | 61 | 1
2015-10-20 23:00 | 2015-10-20 | 2 | 23 | 114 | 60.8667 | 1
2015-10-20 23:15 | 2015-10-20 | 2 | 23 | 114 | 60.3667 | 1
2015-10-20 23:30 | 2015-10-20 | 2 | 23 | 111 | 59.8667 | 1
2015-10-20 23:45 | 2015-10-20 | 2 | 23 | 109 | 59.3667 | 1
2015-10-21 | 2015-10-21 | 3 | 0 | 113 | 59 | 1
2015-10-21 00:15 | 2015-10-21 | 3 | 0 | 114 | 59 | 1
2015-10-21 00:30 | 2015-10-21 | 3 | 0 | 105 | 59 | 1
2015-10-21 00:45 | 2015-10-21 | 3 | 0 | 101 | 59 | 1
2015-10-21 01:00 | 2015-10-21 | 3 | 1 | 100 | 58.8667 | 1
2015-10-21 01:15 | 2015-10-21 | 3 | 1 | 104 | 58.3667 | 1
2015-10-21 01:30 | 2015-10-21 | 3 | 1 | 102 | 57.8667 | 1
2015-10-21 01:45 | 2015-10-21 | 3 | 1 | 109 | 57.3667 | 1
2015-10-21 02:00 | 2015-10-21 | 3 | 2 | 103 | 57 | 1
2015-10-21 02:15 | 2015-10-21 | 3 | 2 | 103 | 57 | 1
2015-10-21 02:30 | 2015-10-21 | 3 | 2 | 103 | 57 | 1
2015-10-21 02:45 | 2015-10-21 | 3 | 2 | 104 | 57 | 1
2015-10-21 03:00 | 2015-10-21 | 3 | 3 | 108 | 56.9333 | 1
2015-10-21 03:15 | 2015-10-21 | 3 | 3 | 102 | 56.6833 | 1
2015-10-21 03:30 | 2015-10-21 | 3 | 3 | 101 | 56.4333 | 1
2015-10-21 03:45 | 2015-10-21 | 3 | 3 | 108 | 56.1833 | 1
2015-10-21 04:00 | 2015-10-21 | 3 | 4 | 104 | 55.9333 | 1
2015-10-21 04:15 | 2015-10-21 | 3 | 4 | 103 | 55.6833 | 1
2015-10-21 04:30 | 2015-10-21 | 3 | 4 | 101 | 55.4333 | 1
2015-10-21 04:45 | 2015-10-21 | 3 | 4 | 105 | 55.1833 | 1
2015-10-21 05:00 | 2015-10-21 | 3 | 5 | 102 | 55.1333 | 1
2015-10-21 05:15 | 2015-10-21 | 3 | 5 | 111 | 55.6333 | 1
2015-10-21 05:30 | 2015-10-21 | 3 | 5 | 105 | 56.1333 | 1
2015-10-21 05:45 | 2015-10-21 | 3 | 5 | 102 | 56.6333 | 1
2015-10-21 06:00 | 2015-10-21 | 3 | 6 | 99 | 57.1333 | 1
2015-10-21 06:15 | 2015-10-21 | 3 | 6 | 105 | 57.6333 | 1
2015-10-21 06:30 | 2015-10-21 | 3 | 6 | 102 | 58.1333 | 1
2015-10-21 06:45 | 2015-10-21 | 3 | 6 | 113 | 58.6333 | 1
2015-10-21 07:00 | 2015-10-21 | 3 | 7 | 109 | 59.2667 | 1
2015-10-21 07:15 | 2015-10-21 | 3 | 7 | 150 | 60.2667 | 1
2015-10-21 07:30 | 2015-10-21 | 3 | 7 | 129 | 61.2667 | 1
2015-10-21 07:45 | 2015-10-21 | 3 | 7 | 141 | 62.2667 | 1
2015-10-21 08:00 | 2015-10-21 | 3 | 8 | 151 | 63.1333 | 1
2015-10-21 08:15 | 2015-10-21 | 3 | 8 | 148 | 63.6333 | 1
2015-10-21 08:30 | 2015-10-21 | 3 | 8 | 144 | 64.1333 | 1
2015-10-21 08:45 | 2015-10-21 | 3 | 8 | 170 | 64.6333 | 1
2015-10-21 09:00 | 2015-10-21 | 3 | 9 | 151 | 65.2 | 2
2015-10-21 09:15 | 2015-10-21 | 3 | 9 | 166 | 65.95 | 2
2015-10-21 09:30 | 2015-10-21 | 3 | 9 | 159 | 66.7 | 2
2015-10-21 09:45 | 2015-10-21 | 3 | 9 | 177 | 67.45 | 2
2015-10-21 10:00 | 2015-10-21 | 3 | 10 | 174 | 68.0667 | 2
2015-10-21 10:15 | 2015-10-21 | 3 | 10 | 175 | 68.3167 | 2
2015-10-21 10:30 | 2015-10-21 | 3 | 10 | 192 | 68.5667 | 2
2015-10-21 10:45 | 2015-10-21 | 3 | 10 | 178 | 68.8167 | 2
2015-10-21 11:00 | 2015-10-21 | 3 | 11 | 183 | 69.3333 | 2
2015-10-21 11:15 | 2015-10-21 | 3 | 11 | 176 | 70.5833 | 3
2015-10-21 11:30 | 2015-10-21 | 3 | 11 | 179 | 71.8333 | 3
2015-10-21 11:45 | 2015-10-21 | 3 | 11 | 187 | 73.0833 | 3
2015-10-21 12:00 | 2015-10-21 | 3 | 12 | 175 | 73.9333 | 3
2015-10-21 12:15 | 2015-10-21 | 3 | 12 | 188 | 73.6833 | 3
2015-10-21 12:30 | 2015-10-21 | 3 | 12 | 180 | 73.4333 | 3
2015-10-21 12:45 | 2015-10-21 | 3 | 12 | 173 | 73.1833 | 3
2015-10-21 13:00 | 2015-10-21 | 3 | 13 | 190 | 73 | 3
2015-10-21 13:15 | 2015-10-21 | 3 | 13 | 178 | 73 | 3
2015-10-21 13:30 | 2015-10-21 | 3 | 13 | 175 | 73 | 3
2015-10-21 13:45 | 2015-10-21 | 3 | 13 | 187 | 73 | 3
2015-10-21 14:00 | 2015-10-21 | 3 | 14 | 186 | 73 | 3
2015-10-21 14:15 | 2015-10-21 | 3 | 14 | 189 | 73 | 3
2015-10-21 14:30 | 2015-10-21 | 3 | 14 | 207 | 73 | 3
2015-10-21 14:45 | 2015-10-21 | 3 | 14 | 194 | 73 | 3
2015-10-21 15:00 | 2015-10-21 | 3 | 15 | 208 | 72.4667 | 3
2015-10-21 15:15 | 2015-10-21 | 3 | 15 | 203 | 70.4667 | 3
2015-10-21 15:30 | 2015-10-21 | 3 | 15 | 202 | 68.4667 | 2
2015-10-21 15:45 | 2015-10-21 | 3 | 15 | 216 | 66.4667 | 2
2015-10-21 16:00 | 2015-10-21 | 3 | 16 | 202 | 64.7333 | 1
2015-10-21 16:15 | 2015-10-21 | 3 | 16 | 201 | 63.7333 | 1
2015-10-21 16:30 | 2015-10-21 | 3 | 16 | 210 | 62.7333 | 1
2015-10-21 16:45 | 2015-10-21 | 3 | 16 | 217 | 61.7333 | 1
2015-10-21 17:00 | 2015-10-21 | 3 | 17 | 196 | 61 | 1
2015-10-21 17:15 | 2015-10-21 | 3 | 17 | 206 | 61 | 1
2015-10-21 17:30 | 2015-10-21 | 3 | 17 | 197 | 61 | 1
2015-10-21 17:45 | 2015-10-21 | 3 | 17 | 189 | 61 | 1
2015-10-21 18:00 | 2015-10-21 | 3 | 18 | 203 | 60.9333 | 1
2015-10-21 18:15 | 2015-10-21 | 3 | 18 | 184 | 60.6833 | 1
2015-10-21 18:30 | 2015-10-21 | 3 | 18 | 191 | 60.4333 | 1
2015-10-21 18:45 | 2015-10-21 | 3 | 18 | 187 | 60.1833 | 1
2015-10-21 19:00 | 2015-10-21 | 3 | 19 | 195 | 60 | 1
2015-10-21 19:15 | 2015-10-21 | 3 | 19 | 121 | 60 | 1
2015-10-21 19:30 | 2015-10-21 | 3 | 19 | 121 | 60 | 1
2015-10-21 19:45 | 2015-10-21 | 3 | 19 | 120 | 60 | 1
2015-10-21 20:00 | 2015-10-21 | 3 | 20 | 118 | 59.9333 | 1
2015-10-21 20:15 | 2015-10-21 | 3 | 20 | 130 | 59.6833 | 1
2015-10-21 20:30 | 2015-10-21 | 3 | 20 | 116 | 59.4333 | 1
2015-10-21 20:45 | 2015-10-21 | 3 | 20 | 119 | 59.1833 | 1
2015-10-21 21:00 | 2015-10-21 | 3 | 21 | 112 | 59 | 1
2015-10-21 21:15 | 2015-10-21 | 3 | 21 | 119 | 59 | 1
2015-10-21 21:30 | 2015-10-21 | 3 | 21 | 106 | 59 | 1
2015-10-21 21:45 | 2015-10-21 | 3 | 21 | 106 | 59 | 1
2015-10-21 22:00 | 2015-10-21 | 3 | 22 | 101 | 58.9333 | 1
2015-10-21 22:15 | 2015-10-21 | 3 | 22 | 106 | 58.6833 | 1
2015-10-21 22:30 | 2015-10-21 | 3 | 22 | 110 | 58.4333 | 1
2015-10-21 22:45 | 2015-10-21 | 3 | 22 | 102 | 58.1833 | 1
2015-10-21 23:00 | 2015-10-21 | 3 | 23 | 105 | 58 | 1
2015-10-21 23:15 | 2015-10-21 | 3 | 23 | 100 | 58 | 1
2015-10-21 23:30 | 2015-10-21 | 3 | 23 | 104 | 58 | 1
2015-10-21 23:45 | 2015-10-21 | 3 | 23 | 105 | 58 | 1
2015-10-22 | 2015-10-22 | 4 | 0 | 101 | 58 | 1
2015-10-22 00:15 | 2015-10-22 | 4 | 0 | 102 | 58 | 1
2015-10-22 00:30 | 2015-10-22 | 4 | 0 | 99 | 58 | 1
2015-10-22 00:45 | 2015-10-22 | 4 | 0 | 104 | 58 | 1
2015-10-22 01:00 | 2015-10-22 | 4 | 1 | 108 | 57.9333 | 1
2015-10-22 01:15 | 2015-10-22 | 4 | 1 | 105 | 57.6833 | 1
2015-10-22 01:30 | 2015-10-22 | 4 | 1 | 99 | 57.4333 | 1
2015-10-22 01:45 | 2015-10-22 | 4 | 1 | 100 | 57.1833 | 1
2015-10-22 02:00 | 2015-10-22 | 4 | 2 | 99 | 56.9333 | 1
2015-10-22 02:15 | 2015-10-22 | 4 | 2 | 109 | 56.6833 | 1
2015-10-22 02:30 | 2015-10-22 | 4 | 2 | 103 | 56.4333 | 1
2015-10-22 02:45 | 2015-10-22 | 4 | 2 | 102 | 56.1833 | 1
2015-10-22 03:00 | 2015-10-22 | 4 | 3 | 100 | 55.8667 | 1
2015-10-22 03:15 | 2015-10-22 | 4 | 3 | 102 | 55.3667 | 1
2015-10-22 03:30 | 2015-10-22 | 4 | 3 | 103 | 54.8667 | 1
2015-10-22 03:45 | 2015-10-22 | 4 | 3 | 98 | 54.3667 | 1
2015-10-22 04:00 | 2015-10-22 | 4 | 4 | 106 | 54.0667 | 1
2015-10-22 04:15 | 2015-10-22 | 4 | 4 | 105 | 54.3167 | 1
2015-10-22 04:30 | 2015-10-22 | 4 | 4 | 101 | 54.5667 | 1
2015-10-22 04:45 | 2015-10-22 | 4 | 4 | 101 | 54.8167 | 1
2015-10-22 05:00 | 2015-10-22 | 4 | 5 | 111 | 55.0667 | 1
2015-10-22 05:15 | 2015-10-22 | 4 | 5 | 104 | 55.3167 | 1
2015-10-22 05:30 | 2015-10-22 | 4 | 5 | 104 | 55.5667 | 1
2015-10-22 05:45 | 2015-10-22 | 4 | 5 | 98 | 55.8167 | 1
2015-10-22 06:00 | 2015-10-22 | 4 | 6 | 109 | 56.0667 | 1
2015-10-22 06:15 | 2015-10-22 | 4 | 6 | 106 | 56.3167 | 1
2015-10-22 06:30 | 2015-10-22 | 4 | 6 | 103 | 56.5667 | 1
2015-10-22 06:45 | 2015-10-22 | 4 | 6 | 105 | 56.8167 | 1
2015-10-22 07:00 | 2015-10-22 | 4 | 7 | 106 | 57.1333 | 1
2015-10-22 07:15 | 2015-10-22 | 4 | 7 | 153 | 57.6333 | 1
2015-10-22 07:30 | 2015-10-22 | 4 | 7 | 156 | 58.1333 | 1
2015-10-22 07:45 | 2015-10-22 | 4 | 7 | 148 | 58.6333 | 1
2015-10-22 08:00 | 2015-10-22 | 4 | 8 | 158 | 59.2667 | 1
2015-10-22 08:15 | 2015-10-22 | 4 | 8 | 151 | 60.2667 | 1
2015-10-22 08:30 | 2015-10-22 | 4 | 8 | 164 | 61.2667 | 1
2015-10-22 08:45 | 2015-10-22 | 4 | 8 | 158 | 62.2667 | 1
2015-10-22 09:00 | 2015-10-22 | 4 | 9 | 154 | 63.0667 | 1
2015-10-22 09:15 | 2015-10-22 | 4 | 9 | 163 | 63.3167 | 1
2015-10-22 09:30 | 2015-10-22 | 4 | 9 | 171 | 63.5667 | 1
2015-10-22 09:45 | 2015-10-22 | 4 | 9 | 171 | 63.8167 | 1
2015-10-22 10:00 | 2015-10-22 | 4 | 10 | 166 | 64.0667 | 1
2015-10-22 10:15 | 2015-10-22 | 4 | 10 | 176 | 64.3167 | 1
2015-10-22 10:30 | 2015-10-22 | 4 | 10 | 174 | 64.5667 | 1
2015-10-22 10:45 | 2015-10-22 | 4 | 10 | 179 | 64.8167 | 1
2015-10-22 11:00 | 2015-10-22 | 4 | 11 | 193 | 65.1333 | 2
2015-10-22 11:15 | 2015-10-22 | 4 | 11 | 187 | 65.6333 | 2
2015-10-22 11:30 | 2015-10-22 | 4 | 11 | 175 | 66.1333 | 2
2015-10-22 11:45 | 2015-10-22 | 4 | 11 | 179 | 66.6333 | 2
2015-10-22 12:00 | 2015-10-22 | 4 | 12 | 186 | 67.4 | 2
2015-10-22 12:15 | 2015-10-22 | 4 | 12 | 191 | 68.9 | 2
2015-10-22 12:30 | 2015-10-22 | 4 | 12 | 186 | 70.4 | 3
2015-10-22 12:45 | 2015-10-22 | 4 | 12 | 179 | 71.9 | 3
2015-10-22 13:00 | 2015-10-22 | 4 | 13 | 192 | 72.8667 | 3
2015-10-22 13:15 | 2015-10-22 | 4 | 13 | 192 | 72.3667 | 3
2015-10-22 13:30 | 2015-10-22 | 4 | 13 | 190 | 71.8667 | 3
2015-10-22 13:45 | 2015-10-22 | 4 | 13 | 194 | 71.3667 | 3
2015-10-22 14:00 | 2015-10-22 | 4 | 14 | 188 | 70.9333 | 3
2015-10-22 14:15 | 2015-10-22 | 4 | 14 | 205 | 70.6833 | 3
2015-10-22 14:30 | 2015-10-22 | 4 | 14 | 195 | 70.4333 | 3
2015-10-22 14:45 | 2015-10-22 | 4 | 14 | 203 | 70.1833 | 3
2015-10-22 15:00 | 2015-10-22 | 4 | 15 | 198 | 69.9333 | 2
2015-10-22 15:15 | 2015-10-22 | 4 | 15 | 204 | 69.6833 | 2
2015-10-22 15:30 | 2015-10-22 | 4 | 15 | 211 | 69.4333 | 2
2015-10-22 15:45 | 2015-10-22 | 4 | 15 | 197 | 69.1833 | 2
2015-10-22 16:00 | 2015-10-22 | 4 | 16 | 199 | 69 | 2
2015-10-22 16:15 | 2015-10-22 | 4 | 16 | 198 | 69 | 2
2015-10-22 16:30 | 2015-10-22 | 4 | 16 | 208 | 69 | 2
2015-10-22 16:45 | 2015-10-22 | 4 | 16 | 201 | 69 | 2
2015-10-22 17:00 | 2015-10-22 | 4 | 17 | 199 | 68.6 | 2
2015-10-22 17:15 | 2015-10-22 | 4 | 17 | 204 | 67.1 | 2
2015-10-22 17:30 | 2015-10-22 | 4 | 17 | 192 | 65.6 | 2
2015-10-22 17:45 | 2015-10-22 | 4 | 17 | 185 | 64.1 | 1
2015-10-22 18:00 | 2015-10-22 | 4 | 18 | 203 | 63.0667 | 1
2015-10-22 18:15 | 2015-10-22 | 4 | 18 | 196 | 63.3167 | 1
2015-10-22 18:30 | 2015-10-22 | 4 | 18 | 187 | 63.5667 | 1
2015-10-22 18:45 | 2015-10-22 | 4 | 18 | 178 | 63.8167 | 1
2015-10-22 19:00 | 2015-10-22 | 4 | 19 | 185 | 64.1333 | 1
2015-10-22 19:15 | 2015-10-22 | 4 | 19 | 132 | 64.6333 | 1
2015-10-22 19:30 | 2015-10-22 | 4 | 19 | 120 | 65.1333 | 2
2015-10-22 19:45 | 2015-10-22 | 4 | 19 | 117 | 65.6333 | 2
2015-10-22 20:00 | 2015-10-22 | 4 | 20 | 115 | 65.8 | 2
2015-10-22 20:15 | 2015-10-22 | 4 | 20 | 122 | 65.05 | 2
2015-10-22 20:30 | 2015-10-22 | 4 | 20 | 118 | 64.3 | 1
2015-10-22 20:45 | 2015-10-22 | 4 | 20 | 117 | 63.55 | 1
2015-10-22 21:00 | 2015-10-22 | 4 | 21 | 114 | 62.9333 | 1
2015-10-22 21:15 | 2015-10-22 | 4 | 21 | 117 | 62.6833 | 1
2015-10-22 21:30 | 2015-10-22 | 4 | 21 | 110 | 62.4333 | 1
2015-10-22 21:45 | 2015-10-22 | 4 | 21 | 105 | 62.1833 | 1
2015-10-22 22:00 | 2015-10-22 | 4 | 22 | 105 | 61.9333 | 1
2015-10-22 22:15 | 2015-10-22 | 4 | 22 | 105 | 61.6833 | 1
2015-10-22 22:30 | 2015-10-22 | 4 | 22 | 112 | 61.4333 | 1
2015-10-22 22:45 | 2015-10-22 | 4 | 22 | 106 | 61.1833 | 1
2015-10-22 23:00 | 2015-10-22 | 4 | 23 | 103 | 60.9333 | 1
2015-10-22 23:15 | 2015-10-22 | 4 | 23 | 100 | 60.6833 | 1
2015-10-22 23:30 | 2015-10-22 | 4 | 23 | 105 | 60.4333 | 1
2015-10-22 23:45 | 2015-10-22 | 4 | 23 | 108 | 60.1833 | 1
2015-10-23 | 2015-10-23 | 5 | 0 | 103 | 59.9333 | 1
2015-10-23 00:15 | 2015-10-23 | 5 | 0 | 102 | 59.6833 | 1
2015-10-23 00:30 | 2015-10-23 | 5 | 0 | 100 | 59.4333 | 1
2015-10-23 00:45 | 2015-10-23 | 5 | 0 | 109 | 59.1833 | 1
2015-10-23 01:00 | 2015-10-23 | 5 | 1 | 104 | 58.9333 | 1
2015-10-23 01:15 | 2015-10-23 | 5 | 1 | 108 | 58.6833 | 1
2015-10-23 01:30 | 2015-10-23 | 5 | 1 | 102 | 58.4333 | 1
2015-10-23 01:45 | 2015-10-23 | 5 | 1 | 98 | 58.1833 | 1
2015-10-23 02:00 | 2015-10-23 | 5 | 2 | 109 | 57.8667 | 1
2015-10-23 02:15 | 2015-10-23 | 5 | 2 | 99 | 57.3667 | 1
2015-10-23 02:30 | 2015-10-23 | 5 | 2 | 102 | 56.8667 | 1
2015-10-23 02:45 | 2015-10-23 | 5 | 2 | 98 | 56.3667 | 1
2015-10-23 03:00 | 2015-10-23 | 5 | 3 | 103 | 56 | 1
2015-10-23 03:15 | 2015-10-23 | 5 | 3 | 103 | 56 | 1
2015-10-23 03:30 | 2015-10-23 | 5 | 3 | 99 | 56 | 1
2015-10-23 03:45 | 2015-10-23 | 5 | 3 | 96 | 56 | 1
2015-10-23 04:00 | 2015-10-23 | 5 | 4 | 97 | 56 | 1
2015-10-23 04:15 | 2015-10-23 | 5 | 4 | 100 | 56 | 1
2015-10-23 04:30 | 2015-10-23 | 5 | 4 | 100 | 56 | 1
2015-10-23 04:45 | 2015-10-23 | 5 | 4 | 105 | 56 | 1
2015-10-23 05:00 | 2015-10-23 | 5 | 5 | 100 | 56.0667 | 1
2015-10-23 05:15 | 2015-10-23 | 5 | 5 | 102 | 56.3167 | 1
2015-10-23 05:30 | 2015-10-23 | 5 | 5 | 99 | 56.5667 | 1
2015-10-23 05:45 | 2015-10-23 | 5 | 5 | 105 | 56.8167 | 1
2015-10-23 06:00 | 2015-10-23 | 5 | 6 | 102 | 57 | 1
2015-10-23 06:15 | 2015-10-23 | 5 | 6 | 105 | 57 | 1
2015-10-23 06:30 | 2015-10-23 | 5 | 6 | 103 | 57 | 1
2015-10-23 06:45 | 2015-10-23 | 5 | 6 | 113 | 57 | 1
2015-10-23 07:00 | 2015-10-23 | 5 | 7 | 107 | 58.0667 | 1
2015-10-23 07:15 | 2015-10-23 | 5 | 7 | 149 | 58.3167 | 1
2015-10-23 07:30 | 2015-10-23 | 5 | 7 | 139 | 58.5667 | 1
2015-10-23 07:45 | 2015-10-23 | 5 | 7 | 147 | 58.8167 | 1
2015-10-23 08:00 | 2015-10-23 | 5 | 8 | 150 | 59.0667 | 1
2015-10-23 08:15 | 2015-10-23 | 5 | 8 | 146 | 59.3167 | 1
2015-10-23 08:30 | 2015-10-23 | 5 | 8 | 150 | 59.5667 | 1
2015-10-23 08:45 | 2015-10-23 | 5 | 8 | 151 | 59.8167 | 1
2015-10-23 09:00 | 2015-10-23 | 5 | 9 | 165 | 60.2667 | 1
2015-10-23 09:15 | 2015-10-23 | 5 | 9 | 161 | 61.2667 | 1
2015-10-23 09:30 | 2015-10-23 | 5 | 9 | 170 | 62.2667 | 1
2015-10-23 09:45 | 2015-10-23 | 5 | 9 | 169 | 63.2667 | 1
2015-10-23 10:00 | 2015-10-23 | 5 | 10 | 170 | 64.2 | 1
2015-10-23 10:15 | 2015-10-23 | 5 | 10 | 184 | 64.95 | 1
2015-10-23 10:30 | 2015-10-23 | 5 | 10 | 166 | 65.7 | 2
2015-10-23 10:45 | 2015-10-23 | 5 | 10 | 176 | 66.45 | 2
2015-10-23 11:00 | 2015-10-23 | 5 | 11 | 180 | 67 | 2
2015-10-23 11:15 | 2015-10-23 | 5 | 11 | 187 | 67 | 2
2015-10-23 11:30 | 2015-10-23 | 5 | 11 | 186 | 67 | 2
2015-10-23 11:45 | 2015-10-23 | 5 | 11 | 185 | 67 | 2
2015-10-23 12:00 | 2015-10-23 | 5 | 12 | 173 | 67.0667 | 2
2015-10-23 12:15 | 2015-10-23 | 5 | 12 | 178 | 67.3167 | 2
2015-10-23 12:30 | 2015-10-23 | 5 | 12 | 181 | 67.5667 | 2
2015-10-23 12:45 | 2015-10-23 | 5 | 12 | 176 | 67.8167 | 2
2015-10-23 13:00 | 2015-10-23 | 5 | 13 | 188 | 68 | 2
2015-10-23 13:15 | 2015-10-23 | 5 | 13 | 179 | 68 | 2
2015-10-23 13:30 | 2015-10-23 | 5 | 13 | 175 | 68 | 2
2015-10-23 13:45 | 2015-10-23 | 5 | 13 | 183 | 68 | 2
2015-10-23 14:00 | 2015-10-23 | 5 | 14 | 191 | 68 | 2
2015-10-23 14:15 | 2015-10-23 | 5 | 14 | 190 | 68 | 2
2015-10-23 14:30 | 2015-10-23 | 5 | 14 | 182 | 68 | 2
2015-10-23 14:45 | 2015-10-23 | 5 | 14 | 183 | 68 | 2
2015-10-23 15:00 | 2015-10-23 | 5 | 15 | 202 | 67.8667 | 2
2015-10-23 15:15 | 2015-10-23 | 5 | 15 | 192 | 67.3667 | 2
2015-10-23 15:30 | 2015-10-23 | 5 | 15 | 185 | 66.8667 | 2
2015-10-23 15:45 | 2015-10-23 | 5 | 15 | 176 | 66.3667 | 2
2015-10-23 16:00 | 2015-10-23 | 5 | 16 | 186 | 66.0667 | 2
2015-10-23 16:15 | 2015-10-23 | 5 | 16 | 191 | 66.3167 | 2
2015-10-23 16:30 | 2015-10-23 | 5 | 16 | 173 | 66.5667 | 2
2015-10-23 16:45 | 2015-10-23 | 5 | 16 | 186 | 66.8167 | 2
2015-10-23 17:00 | 2015-10-23 | 5 | 17 | 175 | 66.8 | 2
2015-10-23 17:15 | 2015-10-23 | 5 | 17 | 184 | 66.05 | 2
2015-10-23 17:30 | 2015-10-23 | 5 | 17 | 195 | 65.3 | 2
2015-10-23 17:45 | 2015-10-23 | 5 | 17 | 173 | 64.55 | 1
2015-10-23 18:00 | 2015-10-23 | 5 | 18 | 178 | 63.8 | 1
2015-10-23 18:15 | 2015-10-23 | 5 | 18 | 179 | 63.05 | 1
2015-10-23 18:30 | 2015-10-23 | 5 | 18 | 186 | 62.3 | 1
2015-10-23 18:45 | 2015-10-23 | 5 | 18 | 169 | 61.55 | 1
2015-10-23 19:00 | 2015-10-23 | 5 | 19 | 178 | 60.9333 | 1
2015-10-23 19:15 | 2015-10-23 | 5 | 19 | 114 | 60.6833 | 1
2015-10-23 19:30 | 2015-10-23 | 5 | 19 | 113 | 60.4333 | 1
2015-10-23 19:45 | 2015-10-23 | 5 | 19 | 127 | 60.1833 | 1
2015-10-23 20:00 | 2015-10-23 | 5 | 20 | 112 | 59.9333 | 1
2015-10-23 20:15 | 2015-10-23 | 5 | 20 | 114 | 59.6833 | 1
2015-10-23 20:30 | 2015-10-23 | 5 | 20 | 112 | 59.4333 | 1
2015-10-23 20:45 | 2015-10-23 | 5 | 20 | 118 | 59.1833 | 1
2015-10-23 21:00 | 2015-10-23 | 5 | 21 | 120 | 59 | 1
2015-10-23 21:15 | 2015-10-23 | 5 | 21 | 105 | 59 | 1
2015-10-23 21:30 | 2015-10-23 | 5 | 21 | 102 | 59 | 1
2015-10-23 21:45 | 2015-10-23 | 5 | 21 | 101 | 59 | 1
2015-10-23 22:00 | 2015-10-23 | 5 | 22 | 105 | 58.9333 | 1
2015-10-23 22:15 | 2015-10-23 | 5 | 22 | 103 | 58.6833 | 1
2015-10-23 22:30 | 2015-10-23 | 5 | 22 | 108 | 58.4333 | 1
2015-10-23 22:45 | 2015-10-23 | 5 | 22 | 96 | 58.1833 | 1
2015-10-23 23:00 | 2015-10-23 | 5 | 23 | 104 | 57.9333 | 1
2015-10-23 23:15 | 2015-10-23 | 5 | 23 | 103 | 57.6833 | 1
2015-10-23 23:30 | 2015-10-23 | 5 | 23 | 101 | 57.4333 | 1
2015-10-23 23:45 | 2015-10-23 | 5 | 23 | 102 | 57.1833 | 1
2015-10-24 | 2015-10-24 | 6 | 0 | 99 | 57 | 1
2015-10-24 00:15 | 2015-10-24 | 6 | 0 | 97 | 57 | 1
2015-10-24 00:30 | 2015-10-24 | 6 | 0 | 106 | 57 | 1
2015-10-24 00:45 | 2015-10-24 | 6 | 0 | 95 | 57 | 1
2015-10-24 01:00 | 2015-10-24 | 6 | 1 | 93 | 56.9333 | 1
2015-10-24 01:15 | 2015-10-24 | 6 | 1 | 89 | 56.6833 | 1
2015-10-24 01:30 | 2015-10-24 | 6 | 1 | 88 | 56.4333 | 1
2015-10-24 01:45 | 2015-10-24 | 6 | 1 | 94 | 56.1833 | 1
2015-10-24 02:00 | 2015-10-24 | 6 | 2 | 92 | 55.9333 | 1
2015-10-24 02:15 | 2015-10-24 | 6 | 2 | 93 | 55.6833 | 1
2015-10-24 02:30 | 2015-10-24 | 6 | 2 | 87 | 55.4333 | 1
2015-10-24 02:45 | 2015-10-24 | 6 | 2 | 95 | 55.1833 | 1
2015-10-24 03:00 | 2015-10-24 | 6 | 3 | 94 | 54.8667 | 1
2015-10-24 03:15 | 2015-10-24 | 6 | 3 | 90 | 54.3667 | 1
2015-10-24 03:30 | 2015-10-24 | 6 | 3 | 89 | 53.8667 | 1
2015-10-24 03:45 | 2015-10-24 | 6 | 3 | 89 | 53.3667 | 1
2015-10-24 04:00 | 2015-10-24 | 6 | 4 | 92 | 53.1333 | 1
2015-10-24 04:15 | 2015-10-24 | 6 | 4 | 92 | 53.6333 | 1
2015-10-24 04:30 | 2015-10-24 | 6 | 4 | 89 | 54.1333 | 1
2015-10-24 04:45 | 2015-10-24 | 6 | 4 | 91 | 54.6333 | 1
2015-10-24 05:00 | 2015-10-24 | 6 | 5 | 92 | 55.1333 | 1
2015-10-24 05:15 | 2015-10-24 | 6 | 5 | 88 | 55.6333 | 1
2015-10-24 05:30 | 2015-10-24 | 6 | 5 | 103 | 56.1333 | 1
2015-10-24 05:45 | 2015-10-24 | 6 | 5 | 89 | 56.6333 | 1
2015-10-24 06:00 | 2015-10-24 | 6 | 6 | 95 | 57.0667 | 1
2015-10-24 06:15 | 2015-10-24 | 6 | 6 | 89 | 57.3167 | 1
2015-10-24 06:30 | 2015-10-24 | 6 | 6 | 87 | 57.5667 | 1
2015-10-24 06:45 | 2015-10-24 | 6 | 6 | 96 | 57.8167 | 1
2015-10-24 07:00 | 2015-10-24 | 6 | 7 | 91 | 58.0667 | 1
2015-10-24 07:15 | 2015-10-24 | 6 | 7 | 92 | 58.3167 | 1
2015-10-24 07:30 | 2015-10-24 | 6 | 7 | 91 | 58.5667 | 1
2015-10-24 07:45 | 2015-10-24 | 6 | 7 | 82 | 58.8167 | 1
2015-10-24 08:00 | 2015-10-24 | 6 | 8 | 89 | 59.1333 | 1
2015-10-24 08:15 | 2015-10-24 | 6 | 8 | 88 | 59.6333 | 1
2015-10-24 08:30 | 2015-10-24 | 6 | 8 | 84 | 60.1333 | 1
2015-10-24 08:45 | 2015-10-24 | 6 | 8 | 87 | 60.6333 | 1
2015-10-24 09:00 | 2015-10-24 | 6 | 9 | 86 | 61.2 | 1
2015-10-24 09:15 | 2015-10-24 | 6 | 9 | 94 | 61.95 | 1
2015-10-24 09:30 | 2015-10-24 | 6 | 9 | 90 | 62.7 | 1
2015-10-24 09:45 | 2015-10-24 | 6 | 9 | 91 | 63.45 | 1
2015-10-24 10:00 | 2015-10-24 | 6 | 10 | 91 | 64.1333 | 1
2015-10-24 10:15 | 2015-10-24 | 6 | 10 | 86 | 64.6333 | 1
2015-10-24 10:30 | 2015-10-24 | 6 | 10 | 85 | 65.1333 | 2
2015-10-24 10:45 | 2015-10-24 | 6 | 10 | 89 | 65.6333 | 2
2015-10-24 11:00 | 2015-10-24 | 6 | 11 | 84 | 66.0667 | 2
2015-10-24 11:15 | 2015-10-24 | 6 | 11 | 95 | 66.3167 | 2
2015-10-24 11:30 | 2015-10-24 | 6 | 11 | 89 | 66.5667 | 2
2015-10-24 11:45 | 2015-10-24 | 6 | 11 | 87 | 66.8167 | 2
2015-10-24 12:00 | 2015-10-24 | 6 | 12 | 85 | 67.0667 | 2
2015-10-24 12:15 | 2015-10-24 | 6 | 12 | 87 | 67.3167 | 2
2015-10-24 12:30 | 2015-10-24 | 6 | 12 | 92 | 67.5667 | 2
2015-10-24 12:45 | 2015-10-24 | 6 | 12 | 86 | 67.8167 | 2
2015-10-24 13:00 | 2015-10-24 | 6 | 13 | 93 | 67.8182 | 2
2015-10-24 13:15 | 2015-10-24 | 6 | 13 | 84 | 67.1364 | 2
2015-10-24 13:30 | 2015-10-24 | 6 | 13 | 99 | 66.4545 | 2
2015-10-24 13:45 | 2015-10-24 | 6 | 13 | 90 | 65.6875 | 2
2015-10-24 14:00 | 2015-10-24 | 6 | 14 | 88 | 65.0667 | 2
2015-10-24 14:15 | 2015-10-24 | 6 | 14 | 84 | 65.3167 | 2
2015-10-24 14:30 | 2015-10-24 | 6 | 14 | 89 | 65.5667 | 2
2015-10-24 14:45 | 2015-10-24 | 6 | 14 | 86 | 65.8167 | 2
2015-10-24 15:00 | 2015-10-24 | 6 | 15 | 94 | 66.0667 | 2
2015-10-24 15:15 | 2015-10-24 | 6 | 15 | 90 | 66.3167 | 2
2015-10-24 15:30 | 2015-10-24 | 6 | 15 | 89 | 66.5667 | 2
2015-10-24 15:45 | 2015-10-24 | 6 | 15 | 91 | 66.8167 | 2
2015-10-24 16:00 | 2015-10-24 | 6 | 16 | 87 | 66.7333 | 2
2015-10-24 16:15 | 2015-10-24 | 6 | 16 | 95 | 65.7333 | 2
2015-10-24 16:30 | 2015-10-24 | 6 | 16 | 88 | 64.7333 | 1
2015-10-24 16:45 | 2015-10-24 | 6 | 16 | 88 | 63.7333 | 1
2015-10-24 17:00 | 2015-10-24 | 6 | 17 | 95 | 62.8667 | 1
2015-10-24 17:15 | 2015-10-24 | 6 | 17 | 102 | 62.3667 | 1
2015-10-24 17:30 | 2015-10-24 | 6 | 17 | 94 | 61.8667 | 1
2015-10-24 17:45 | 2015-10-24 | 6 | 17 | 94 | 61.3667 | 1
2015-10-24 18:00 | 2015-10-24 | 6 | 18 | 90 | 60.9333 | 1
2015-10-24 18:15 | 2015-10-24 | 6 | 18 | 90 | 60.6833 | 1
2015-10-24 18:30 | 2015-10-24 | 6 | 18 | 97 | 60.4333 | 1
2015-10-24 18:45 | 2015-10-24 | 6 | 18 | 91 | 60.1833 | 1
2015-10-24 19:00 | 2015-10-24 | 6 | 19 | 92 | 60 | 1
2015-10-24 19:15 | 2015-10-24 | 6 | 19 | 93 | 60 | 1
2015-10-24 19:30 | 2015-10-24 | 6 | 19 | 92 | 60 | 1
2015-10-24 19:45 | 2015-10-24 | 6 | 19 | 93 | 60 | 1
2015-10-24 20:00 | 2015-10-24 | 6 | 20 | 99 | 60 | 1
2015-10-24 20:15 | 2015-10-24 | 6 | 20 | 92 | 60 | 1
2015-10-24 20:30 | 2015-10-24 | 6 | 20 | 93 | 60 | 1
2015-10-24 20:45 | 2015-10-24 | 6 | 20 | 90 | 60 | 1
2015-10-24 21:00 | 2015-10-24 | 6 | 21 | 92 | 59.9333 | 1
2015-10-24 21:15 | 2015-10-24 | 6 | 21 | 94 | 59.6833 | 1
2015-10-24 21:30 | 2015-10-24 | 6 | 21 | 87 | 59.4333 | 1
2015-10-24 21:45 | 2015-10-24 | 6 | 21 | 97 | 59.1833 | 1
2015-10-24 22:00 | 2015-10-24 | 6 | 22 | 98 | 58.9333 | 1
2015-10-24 22:15 | 2015-10-24 | 6 | 22 | 94 | 58.6833 | 1
2015-10-24 22:30 | 2015-10-24 | 6 | 22 | 88 | 58.4333 | 1
2015-10-24 22:45 | 2015-10-24 | 6 | 22 | 98 | 58.1833 | 1
2015-10-24 23:00 | 2015-10-24 | 6 | 23 | 91 | 58 | 1
2015-10-24 23:15 | 2015-10-24 | 6 | 23 | 93 | 58 | 1
2015-10-24 23:30 | 2015-10-24 | 6 | 23 | 87 | 58 | 1
2015-10-24 23:45 | 2015-10-24 | 6 | 23 | 94 | 58 | 1
2015-10-25 | 2015-10-25 | 7 | 0 | 94 | 58 | 1
2015-10-25 00:15 | 2015-10-25 | 7 | 0 | 92 | 58 | 1
2015-10-25 00:30 | 2015-10-25 | 7 | 0 | 95 | 58 | 1
2015-10-25 00:45 | 2015-10-25 | 7 | 0 | 89 | 58 | 1
2015-10-25 01:00 | 2015-10-25 | 7 | 1 | 93 | 58 | 1
2015-10-25 01:15 | 2015-10-25 | 7 | 1 | 89 | 58 | 1
2015-10-25 01:30 | 2015-10-25 | 7 | 1 | 91 | 58 | 1
2015-10-25 01:45 | 2015-10-25 | 7 | 1 | 91 | 58 | 1
2015-10-25 02:00 | 2015-10-25 | 7 | 2 | 89 | 58.0667 | 1
2015-10-25 02:15 | 2015-10-25 | 7 | 2 | 95 | 58.3167 | 1
2015-10-25 02:30 | 2015-10-25 | 7 | 2 | 89 | 58.5667 | 1
2015-10-25 02:45 | 2015-10-25 | 7 | 2 | 98 | 58.8167 | 1
2015-10-25 03:00 | 2015-10-25 | 7 | 3 | 92 | 59 | 1
2015-10-25 03:15 | 2015-10-25 | 7 | 3 | 91 | 59 | 1
2015-10-25 03:30 | 2015-10-25 | 7 | 3 | 93 | 59 | 1
2015-10-25 03:45 | 2015-10-25 | 7 | 3 | 96 | 59 | 1
2015-10-25 04:00 | 2015-10-25 | 7 | 4 | 91 | 58.9333 | 1
2015-10-25 04:15 | 2015-10-25 | 7 | 4 | 90 | 58.6833 | 1
2015-10-25 04:30 | 2015-10-25 | 7 | 4 | 91 | 58.4333 | 1
2015-10-25 04:45 | 2015-10-25 | 7 | 4 | 102 | 58.1833 | 1
2015-10-25 05:00 | 2015-10-25 | 7 | 5 | 89 | 58.0667 | 1
2015-10-25 05:15 | 2015-10-25 | 7 | 5 | 93 | 58.3167 | 1
2015-10-25 05:30 | 2015-10-25 | 7 | 5 | 90 | 58.5667 | 1
2015-10-25 05:45 | 2015-10-25 | 7 | 5 | 95 | 58.8167 | 1
2015-10-25 06:00 | 2015-10-25 | 7 | 6 | 100 | 59 | 1
2015-10-25 06:15 | 2015-10-25 | 7 | 6 | 97 | 59 | 1
2015-10-25 06:30 | 2015-10-25 | 7 | 6 | 91 | 59 | 1
2015-10-25 06:45 | 2015-10-25 | 7 | 6 | 93 | 59 | 1
2015-10-25 07:00 | 2015-10-25 | 7 | 7 | 91 | 59.0667 | 1
2015-10-25 07:15 | 2015-10-25 | 7 | 7 | 100 | 59.3167 | 1
2015-10-25 07:30 | 2015-10-25 | 7 | 7 | 95 | 59.5667 | 1
2015-10-25 07:45 | 2015-10-25 | 7 | 7 | 97 | 59.8167 | 1
2015-10-25 08:00 | 2015-10-25 | 7 | 8 | 97 | 60.1333 | 1
2015-10-25 08:15 | 2015-10-25 | 7 | 8 | 99 | 60.6333 | 1
2015-10-25 08:30 | 2015-10-25 | 7 | 8 | 105 | 61.1333 | 1
2015-10-25 08:45 | 2015-10-25 | 7 | 8 | 97 | 61.6333 | 1
2015-10-25 09:00 | 2015-10-25 | 7 | 9 | 106 | 62.2667 | 1
2015-10-25 09:15 | 2015-10-25 | 7 | 9 | 109 | 63.2667 | 1
2015-10-25 09:30 | 2015-10-25 | 7 | 9 | 98 | 64.2667 | 1
2015-10-25 09:45 | 2015-10-25 | 7 | 9 | 102 | 65.2667 | 2
2015-10-25 10:00 | 2015-10-25 | 7 | 10 | 100 | 66 | 2
2015-10-25 10:15 | 2015-10-25 | 7 | 10 | 106 | 66 | 2
2015-10-25 10:30 | 2015-10-25 | 7 | 10 | 101 | 66 | 2
2015-10-25 10:45 | 2015-10-25 | 7 | 10 | 100 | 66 | 2
2015-10-25 11:00 | 2015-10-25 | 7 | 11 | 97 | 66.1333 | 2
2015-10-25 11:15 | 2015-10-25 | 7 | 11 | 105 | 66.6333 | 2
2015-10-25 11:30 | 2015-10-25 | 7 | 11 | 102 | 67.1333 | 2
2015-10-25 11:45 | 2015-10-25 | 7 | 11 | 100 | 67.6333 | 2
2015-10-25 12:00 | 2015-10-25 | 7 | 12 | 98 | 68.0667 | 2
2015-10-25 12:15 | 2015-10-25 | 7 | 12 | 101 | 68.3167 | 2
2015-10-25 12:30 | 2015-10-25 | 7 | 12 | 99 | 68.5667 | 2
2015-10-25 12:45 | 2015-10-25 | 7 | 12 | 107 | 68.8167 | 2
2015-10-25 13:00 | 2015-10-25 | 7 | 13 | 100 | 68.8 | 2
2015-10-25 13:15 | 2015-10-25 | 7 | 13 | 101 | 68.05 | 2
2015-10-25 13:30 | 2015-10-25 | 7 | 13 | 107 | 67.3 | 2
2015-10-25 13:45 | 2015-10-25 | 7 | 13 | 107 | 66.55 | 2
2015-10-25 14:00 | 2015-10-25 | 7 | 14 | 106 | 66.1333 | 2
2015-10-25 14:15 | 2015-10-25 | 7 | 14 | 105 | 66.6333 | 2
2015-10-25 14:30 | 2015-10-25 | 7 | 14 | 101 | 67.1333 | 2
2015-10-25 14:45 | 2015-10-25 | 7 | 14 | 107 | 67.6333 | 2
2015-10-25 15:00 | 2015-10-25 | 7 | 15 | 109 | 67.9333 | 2
2015-10-25 15:15 | 2015-10-25 | 7 | 15 | 103 | 67.6833 | 2
2015-10-25 15:30 | 2015-10-25 | 7 | 15 | 109 | 67.4333 | 2
2015-10-25 15:45 | 2015-10-25 | 7 | 15 | 104 | 67.1833 | 2
2015-10-25 16:00 | 2015-10-25 | 7 | 16 | 112 | 66.9333 | 2
2015-10-25 16:15 | 2015-10-25 | 7 | 16 | 107 | 66.6833 | 2
2015-10-25 16:30 | 2015-10-25 | 7 | 16 | 110 | 66.4333 | 2
2015-10-25 16:45 | 2015-10-25 | 7 | 16 | 107 | 66.1833 | 2
2015-10-25 17:00 | 2015-10-25 | 7 | 17 | 116 | 65.8 | 2
2015-10-25 17:15 | 2015-10-25 | 7 | 17 | 116 | 65.05 | 2
2015-10-25 17:30 | 2015-10-25 | 7 | 17 | 119 | 64.3 | 1
2015-10-25 17:45 | 2015-10-25 | 7 | 17 | 118 | 63.55 | 1
2015-10-25 18:00 | 2015-10-25 | 7 | 18 | 118 | 63 | 1
2015-10-25 18:15 | 2015-10-25 | 7 | 18 | 116 | 63 | 1
2015-10-25 18:30 | 2015-10-25 | 7 | 18 | 111 | 63 | 1
2015-10-25 18:45 | 2015-10-25 | 7 | 18 | 114 | 63 | 1
2015-10-25 19:00 | 2015-10-25 | 7 | 19 | 108 | 62.9333 | 1
2015-10-25 19:15 | 2015-10-25 | 7 | 19 | 112 | 62.6833 | 1
2015-10-25 19:30 | 2015-10-25 | 7 | 19 | 110 | 62.4333 | 1
2015-10-25 19:45 | 2015-10-25 | 7 | 19 | 116 | 62.1833 | 1
2015-10-25 20:00 | 2015-10-25 | 7 | 20 | 108 | 62.0851 | 1
2015-10-25 20:15 | 2015-10-25 | 7 | 20 | 102 | 62.4043 | 1
2015-10-25 20:30 | 2015-10-25 | 7 | 20 | 98 | 62.7234 | 1
2015-10-25 20:45 | 2015-10-25 | 7 | 20 | 97 | 62.8462 | 1
2015-10-25 21:00 | 2015-10-25 | 7 | 21 | 105 | 62.129 | 1
2015-10-25 21:15 | 2015-10-25 | 7 | 21 | 98 | 62.6129 | 1
2015-10-25 21:30 | 2015-10-25 | 7 | 21 | 101 | 63 | 1
2015-10-25 21:45 | 2015-10-25 | 7 | 21 | 95 | 63 | 1
2015-10-25 22:00 | 2015-10-25 | 7 | 22 | 99 | 61.8571 | 1
2015-10-25 22:15 | 2015-10-25 | 7 | 22 | 106 | 61.3214 | 1
2015-10-25 22:30 | 2015-10-25 | 7 | 22 | 102 | 61 | 1
2015-10-25 22:45 | 2015-10-25 | 7 | 22 | 101 | 61 | 1
2015-10-25 23:00 | 2015-10-25 | 7 | 23 | 98 | 61 | 1
2015-10-25 23:15 | 2015-10-25 | 7 | 23 | 99 | 61 | 1
2015-10-25 23:30 | 2015-10-25 | 7 | 23 | 99 | 61 | 1
2015-10-25 23:45 | 2015-10-25 | 7 | 23 | 104 | 61 | 1
2015-10-26 | 2015-10-26 | 1 | 0 | 104 | 60.9333 | 1
2015-10-26 00:15 | 2015-10-26 | 1 | 0 | 100 | 60.6833 | 1
2015-10-26 00:30 | 2015-10-26 | 1 | 0 | 98 | 60.4333 | 1
2015-10-26 00:45 | 2015-10-26 | 1 | 0 | 103 | 60.1833 | 1
2015-10-26 01:00 | 2015-10-26 | 1 | 1 | 97 | 59.9333 | 1
2015-10-26 01:15 | 2015-10-26 | 1 | 1 | 95 | 59.6833 | 1
2015-10-26 01:30 | 2015-10-26 | 1 | 1 | 106 | 59.4333 | 1
2015-10-26 01:45 | 2015-10-26 | 1 | 1 | 99 | 59.1833 | 1
2015-10-26 02:00 | 2015-10-26 | 1 | 2 | 98 | 59 | 1
2015-10-26 02:15 | 2015-10-26 | 1 | 2 | 94 | 59 | 1
2015-10-26 02:30 | 2015-10-26 | 1 | 2 | 101 | 59 | 1
2015-10-26 02:45 | 2015-10-26 | 1 | 2 | 101 | 59 | 1
2015-10-26 03:00 | 2015-10-26 | 1 | 3 | 96 | 58.8095 | 1
2015-10-26 03:15 | 2015-10-26 | 1 | 3 | 97 | 58.0952 | 1
2015-10-26 03:30 | 2015-10-26 | 1 | 3 | 104 | 57.381 | 1
2015-10-26 03:45 | 2015-10-26 | 1 | 3 | 98 | 57 | 1
2015-10-26 04:00 | 2015-10-26 | 1 | 4 | 99 | 57 | 1
2015-10-26 04:15 | 2015-10-26 | 1 | 4 | 94 | 57 | 1
2015-10-26 04:30 | 2015-10-26 | 1 | 4 | 103 | 55.9 | 1
2015-10-26 04:45 | 2015-10-26 | 1 | 4 | 99 | 55.8 | 1
2015-10-26 05:00 | 2015-10-26 | 1 | 5 | 100 | 56.8298 | 1
2015-10-26 05:15 | 2015-10-26 | 1 | 5 | 99 | 56.1915 | 1
2015-10-26 05:30 | 2015-10-26 | 1 | 5 | 98 | 55.5532 | 1
2015-10-26 05:45 | 2015-10-26 | 1 | 5 | 100 | 55.1538 | 1
2015-10-26 06:00 | 2015-10-26 | 1 | 6 | 103 | 56.1379 | 1
2015-10-26 06:15 | 2015-10-26 | 1 | 6 | 152 | 56.6552 | 1
2015-10-26 06:30 | 2015-10-26 | 1 | 6 | 134 | 57 | 1
2015-10-26 06:45 | 2015-10-26 | 1 | 6 | 128 | 57 | 1
2015-10-26 07:00 | 2015-10-26 | 1 | 7 | 128 | 57.8519 | 1
2015-10-26 07:15 | 2015-10-26 | 1 | 7 | 124 | 57.2963 | 1
2015-10-26 07:30 | 2015-10-26 | 1 | 7 | 127 | 57 | 1
2015-10-26 07:45 | 2015-10-26 | 1 | 7 | 140 | 57 | 1
2015-10-26 08:00 | 2015-10-26 | 1 | 8 | 158 | 57.0667 | 1
2015-10-26 08:15 | 2015-10-26 | 1 | 8 | 148 | 57.3167 | 1
2015-10-26 08:30 | 2015-10-26 | 1 | 8 | 147 | 57.5667 | 1
2015-10-26 08:45 | 2015-10-26 | 1 | 8 | 152 | 57.8167 | 1
2015-10-26 09:00 | 2015-10-26 | 1 | 9 | 157 | 58.0976 | 1
2015-10-26 09:15 | 2015-10-26 | 1 | 9 | 166 | 58.4634 | 1
2015-10-26 09:30 | 2015-10-26 | 1 | 9 | 162 | 58.8293 | 1
2015-10-26 09:45 | 2015-10-26 | 1 | 9 | 171 | 59 | 1
2015-10-26 10:00 | 2015-10-26 | 1 | 10 | 170 | 59.2759 | 1
2015-10-26 10:15 | 2015-10-26 | 1 | 10 | 176 | 60.3103 | 1
2015-10-26 10:30 | 2015-10-26 | 1 | 10 | 172 | 61.3448 | 1
2015-10-26 10:45 | 2015-10-26 | 1 | 10 | 174 | 62.3793 | 1
2015-10-26 11:00 | 2015-10-26 | 1 | 11 | 176 | 62.2353 | 1
2015-10-26 11:15 | 2015-10-26 | 1 | 11 | 189 | 63 | 1
2015-10-26 11:30 | 2015-10-26 | 1 | 11 | 192 | 63 | 1
2015-10-26 11:45 | 2015-10-26 | 1 | 11 | 184 | 63 | 1
2015-10-26 12:00 | 2015-10-26 | 1 | 12 | 175 | 63.2 | 1
2015-10-26 12:15 | 2015-10-26 | 1 | 12 | 182 | 63.95 | 1
2015-10-26 12:30 | 2015-10-26 | 1 | 12 | 184 | 64.7 | 1
2015-10-26 12:45 | 2015-10-26 | 1 | 12 | 195 | 65.45 | 2
2015-10-26 13:00 | 2015-10-26 | 1 | 13 | 188 | 66.0667 | 2
2015-10-26 13:15 | 2015-10-26 | 1 | 13 | 187 | 66.3167 | 2
2015-10-26 13:30 | 2015-10-26 | 1 | 13 | 191 | 66.5667 | 2
2015-10-26 13:45 | 2015-10-26 | 1 | 13 | 209 | 66.8167 | 2
2015-10-26 14:00 | 2015-10-26 | 1 | 14 | 205 | 67.1333 | 2
2015-10-26 14:15 | 2015-10-26 | 1 | 14 | 202 | 67.6333 | 2
2015-10-26 14:30 | 2015-10-26 | 1 | 14 | 213 | 68.1333 | 2
2015-10-26 14:45 | 2015-10-26 | 1 | 14 | 194 | 68.6333 | 2
2015-10-26 15:00 | 2015-10-26 | 1 | 15 | 197 | 69.2667 | 2
2015-10-26 15:15 | 2015-10-26 | 1 | 15 | 192 | 70.2667 | 3
2015-10-26 15:30 | 2015-10-26 | 1 | 15 | 184 | 71.2667 | 3
2015-10-26 15:45 | 2015-10-26 | 1 | 15 | 191 | 72.2667 | 3
2015-10-26 16:00 | 2015-10-26 | 1 | 16 | 193 | 72.4667 | 3
2015-10-26 16:15 | 2015-10-26 | 1 | 16 | 191 | 70.4667 | 3
2015-10-26 16:30 | 2015-10-26 | 1 | 16 | 191 | 68.4667 | 2
2015-10-26 16:45 | 2015-10-26 | 1 | 16 | 170 | 66.4667 | 2
2015-10-26 17:00 | 2015-10-26 | 1 | 17 | 183 | 64.8667 | 1
2015-10-26 17:15 | 2015-10-26 | 1 | 17 | 192 | 64.3667 | 1
2015-10-26 17:30 | 2015-10-26 | 1 | 17 | 176 | 63.8667 | 1
2015-10-26 17:45 | 2015-10-26 | 1 | 17 | 181 | 63.3667 | 1
2015-10-26 18:00 | 2015-10-26 | 1 | 18 | 178 | 62.9333 | 1
2015-10-26 18:15 | 2015-10-26 | 1 | 18 | 129 | 62.6833 | 1
2015-10-26 18:30 | 2015-10-26 | 1 | 18 | 117 | 62.4333 | 1
2015-10-26 18:45 | 2015-10-26 | 1 | 18 | 114 | 62.1833 | 1
2015-10-26 19:00 | 2015-10-26 | 1 | 19 | 118 | 61.9333 | 1
2015-10-26 19:15 | 2015-10-26 | 1 | 19 | 110 | 61.6833 | 1
2015-10-26 19:30 | 2015-10-26 | 1 | 19 | 122 | 61.4333 | 1
2015-10-26 19:45 | 2015-10-26 | 1 | 19 | 116 | 61.1833 | 1
2015-10-26 20:00 | 2015-10-26 | 1 | 20 | 118 | 60.9333 | 1
2015-10-26 20:15 | 2015-10-26 | 1 | 20 | 112 | 60.6833 | 1
2015-10-26 20:30 | 2015-10-26 | 1 | 20 | 108 | 60.4333 | 1
2015-10-26 20:45 | 2015-10-26 | 1 | 20 | 106 | 60.1833 | 1
2015-10-26 21:00 | 2015-10-26 | 1 | 21 | 105 | 59.9333 | 1
2015-10-26 21:15 | 2015-10-26 | 1 | 21 | 111 | 59.6833 | 1
2015-10-26 21:30 | 2015-10-26 | 1 | 21 | 101 | 59.4333 | 1
2015-10-26 21:45 | 2015-10-26 | 1 | 21 | 103 | 59.1833 | 1
2015-10-26 22:00 | 2015-10-26 | 1 | 22 | 96 | 59 | 1
2015-10-26 22:15 | 2015-10-26 | 1 | 22 | 101 | 59 | 1
2015-10-26 22:30 | 2015-10-26 | 1 | 22 | 103 | 59 | 1
2015-10-26 22:45 | 2015-10-26 | 1 | 22 | 96 | 59 | 1
2015-10-26 23:00 | 2015-10-26 | 1 | 23 | 94 | 59.0667 | 1
2015-10-26 23:15 | 2015-10-26 | 1 | 23 | 95 | 59.3167 | 1
2015-10-26 23:30 | 2015-10-26 | 1 | 23 | 96 | 59.5667 | 1
2015-10-26 23:45 | 2015-10-26 | 1 | 23 | 93 | 59.8167 | 1
2015-10-27 | 2015-10-27 | 2 | 0 | 106 | 59.9333 | 1
2015-10-27 00:15 | 2015-10-27 | 2 | 0 | 97 | 59.6833 | 1
2015-10-27 00:30 | 2015-10-27 | 2 | 0 | 99 | 59.4333 | 1
2015-10-27 00:45 | 2015-10-27 | 2 | 0 | 95 | 59.1833 | 1
2015-10-27 01:00 | 2015-10-27 | 2 | 1 | 95 | 59 | 1
2015-10-27 01:15 | 2015-10-27 | 2 | 1 | 105 | 59 | 1
2015-10-27 01:30 | 2015-10-27 | 2 | 1 | 96 | 59 | 1
2015-10-27 01:45 | 2015-10-27 | 2 | 1 | 97 | 59 | 1
2015-10-27 02:00 | 2015-10-27 | 2 | 2 | 98 | 59 | 1
2015-10-27 02:15 | 2015-10-27 | 2 | 2 | 102 | 59 | 1
2015-10-27 02:30 | 2015-10-27 | 2 | 2 | 98 | 59 | 1
2015-10-27 02:45 | 2015-10-27 | 2 | 2 | 97 | 59 | 1
2015-10-27 03:00 | 2015-10-27 | 2 | 3 | 95 | 59.0667 | 1
2015-10-27 03:15 | 2015-10-27 | 2 | 3 | 100 | 59.3167 | 1
2015-10-27 03:30 | 2015-10-27 | 2 | 3 | 101 | 59.5667 | 1
2015-10-27 03:45 | 2015-10-27 | 2 | 3 | 98 | 59.8167 | 1
2015-10-27 04:00 | 2015-10-27 | 2 | 4 | 98 | 60 | 1
2015-10-27 04:15 | 2015-10-27 | 2 | 4 | 98 | 60 | 1
2015-10-27 04:30 | 2015-10-27 | 2 | 4 | 102 | 60 | 1
2015-10-27 04:45 | 2015-10-27 | 2 | 4 | 99 | 60 | 1
2015-10-27 05:00 | 2015-10-27 | 2 | 5 | 100 | 60 | 1
2015-10-27 05:15 | 2015-10-27 | 2 | 5 | 99 | 60 | 1
2015-10-27 05:30 | 2015-10-27 | 2 | 5 | 102 | 60 | 1
2015-10-27 05:45 | 2015-10-27 | 2 | 5 | 102 | 60 | 1
2015-10-27 06:00 | 2015-10-27 | 2 | 6 | 109 | 60 | 1
2015-10-27 06:15 | 2015-10-27 | 2 | 6 | 161 | 60 | 1
2015-10-27 06:30 | 2015-10-27 | 2 | 6 | 149 | 60 | 1
2015-10-27 06:45 | 2015-10-27 | 2 | 6 | 142 | 60 | 1
2015-10-27 07:00 | 2015-10-27 | 2 | 7 | 142 | 60.1333 | 1
2015-10-27 07:15 | 2015-10-27 | 2 | 7 | 142 | 60.6333 | 1
2015-10-27 07:30 | 2015-10-27 | 2 | 7 | 146 | 61.1333 | 1
2015-10-27 07:45 | 2015-10-27 | 2 | 7 | 146 | 61.6333 | 1
2015-10-27 08:00 | 2015-10-27 | 2 | 8 | 144 | 62.0667 | 1
2015-10-27 08:15 | 2015-10-27 | 2 | 8 | 142 | 62.3167 | 1
2015-10-27 08:30 | 2015-10-27 | 2 | 8 | 159 | 62.5667 | 1
2015-10-27 08:45 | 2015-10-27 | 2 | 8 | 167 | 62.8167 | 1
2015-10-27 09:00 | 2015-10-27 | 2 | 9 | 161 | 63.0667 | 1
2015-10-27 09:15 | 2015-10-27 | 2 | 9 | 165 | 63.3167 | 1
2015-10-27 09:30 | 2015-10-27 | 2 | 9 | 155 | 63.5667 | 1
2015-10-27 09:45 | 2015-10-27 | 2 | 9 | 176 | 63.8167 | 1
2015-10-27 10:00 | 2015-10-27 | 2 | 10 | 176 | 64.1333 | 1
2015-10-27 10:15 | 2015-10-27 | 2 | 10 | 167 | 64.6333 | 1
2015-10-27 10:30 | 2015-10-27 | 2 | 10 | 179 | 65.1333 | 2
2015-10-27 10:45 | 2015-10-27 | 2 | 10 | 179 | 65.6333 | 2
2015-10-27 11:00 | 2015-10-27 | 2 | 11 | 173 | 66 | 2
2015-10-27 11:15 | 2015-10-27 | 2 | 11 | 194 | 66 | 2
2015-10-27 11:30 | 2015-10-27 | 2 | 11 | 180 | 66 | 2
2015-10-27 11:45 | 2015-10-27 | 2 | 11 | 182 | 66 | 2
2015-10-27 12:00 | 2015-10-27 | 2 | 12 | 169 | 65.9333 | 2
2015-10-27 12:15 | 2015-10-27 | 2 | 12 | 188 | 65.6833 | 2
2015-10-27 12:30 | 2015-10-27 | 2 | 12 | 196 | 65.4333 | 2
2015-10-27 12:45 | 2015-10-27 | 2 | 12 | 174 | 65.1833 | 2
2015-10-27 13:00 | 2015-10-27 | 2 | 13 | 188 | 65.1333 | 2
2015-10-27 13:15 | 2015-10-27 | 2 | 13 | 183 | 65.6333 | 2
2015-10-27 13:30 | 2015-10-27 | 2 | 13 | 172 | 66.1333 | 2
2015-10-27 13:45 | 2015-10-27 | 2 | 13 | 182 | 66.6333 | 2
2015-10-27 14:00 | 2015-10-27 | 2 | 14 | 181 | 66.9333 | 2
2015-10-27 14:15 | 2015-10-27 | 2 | 14 | 191 | 66.6833 | 2
2015-10-27 14:30 | 2015-10-27 | 2 | 14 | 175 | 66.4333 | 2
2015-10-27 14:45 | 2015-10-27 | 2 | 14 | 178 | 66.1833 | 2
2015-10-27 15:00 | 2015-10-27 | 2 | 15 | 181 | 66.0667 | 2
2015-10-27 15:15 | 2015-10-27 | 2 | 15 | 172 | 66.3167 | 2
2015-10-27 15:30 | 2015-10-27 | 2 | 15 | 179 | 66.5667 | 2
2015-10-27 15:45 | 2015-10-27 | 2 | 15 | 197 | 66.8167 | 2
2015-10-27 16:00 | 2015-10-27 | 2 | 16 | 177 | 67.0667 | 2
2015-10-27 16:15 | 2015-10-27 | 2 | 16 | 177 | 67.3167 | 2
2015-10-27 16:30 | 2015-10-27 | 2 | 16 | 183 | 67.5667 | 2
2015-10-27 16:45 | 2015-10-27 | 2 | 16 | 181 | 67.8167 | 2
2015-10-27 17:00 | 2015-10-27 | 2 | 17 | 189 | 67.9333 | 2
2015-10-27 17:15 | 2015-10-27 | 2 | 17 | 188 | 67.6833 | 2
2015-10-27 17:30 | 2015-10-27 | 2 | 17 | 181 | 67.4333 | 2
2015-10-27 17:45 | 2015-10-27 | 2 | 17 | 182 | 67.1833 | 2
2015-10-27 18:00 | 2015-10-27 | 2 | 18 | 181 | 66.8 | 2
2015-10-27 18:15 | 2015-10-27 | 2 | 18 | 135 | 66.05 | 2
2015-10-27 18:30 | 2015-10-27 | 2 | 18 | 128 | 65.3 | 2
2015-10-27 18:45 | 2015-10-27 | 2 | 18 | 120 | 64.55 | 1
2015-10-27 19:00 | 2015-10-27 | 2 | 19 | 119 | 64 | 1
2015-10-27 19:15 | 2015-10-27 | 2 | 19 | 134 | 64 | 1
2015-10-27 19:30 | 2015-10-27 | 2 | 19 | 125 | 64 | 1
2015-10-27 19:45 | 2015-10-27 | 2 | 19 | 123 | 64 | 1
2015-10-27 20:00 | 2015-10-27 | 2 | 20 | 119 | 63.9333 | 1
2015-10-27 20:15 | 2015-10-27 | 2 | 20 | 110 | 63.6833 | 1
2015-10-27 20:30 | 2015-10-27 | 2 | 20 | 106 | 63.4333 | 1
2015-10-27 20:45 | 2015-10-27 | 2 | 20 | 117 | 63.1833 | 1
2015-10-27 21:00 | 2015-10-27 | 2 | 21 | 106 | 63 | 1
2015-10-27 21:15 | 2015-10-27 | 2 | 21 | 107 | 63 | 1
2015-10-27 21:30 | 2015-10-27 | 2 | 21 | 108 | 63 | 1
2015-10-27 21:45 | 2015-10-27 | 2 | 21 | 111 | 63 | 1
2015-10-27 22:00 | 2015-10-27 | 2 | 22 | 118 | 63.9333 | 1
2015-10-27 22:15 | 2015-10-27 | 2 | 22 | 113 | 63.6833 | 1
2015-10-27 22:30 | 2015-10-27 | 2 | 22 | 116 | 63.4333 | 1
2015-10-27 22:45 | 2015-10-27 | 2 | 22 | 104 | 63.1833 | 1
2015-10-27 23:00 | 2015-10-27 | 2 | 23 | 108 | 62.9333 | 1
2015-10-27 23:15 | 2015-10-27 | 2 | 23 | 107 | 62.6833 | 1
2015-10-27 23:30 | 2015-10-27 | 2 | 23 | 112 | 62.4333 | 1
2015-10-27 23:45 | 2015-10-27 | 2 | 23 | 106 | 62.1833 | 1
2015-10-28 | 2015-10-28 | 3 | 0 | 103 | 62 | 1
2015-10-28 00:15 | 2015-10-28 | 3 | 0 | 101 | 62 | 1
2015-10-28 00:30 | 2015-10-28 | 3 | 0 | 100 | 62 | 1
2015-10-28 00:45 | 2015-10-28 | 3 | 0 | 111 | 62 | 1
2015-10-28 01:00 | 2015-10-28 | 3 | 1 | 101 | 62 | 1
2015-10-28 01:15 | 2015-10-28 | 3 | 1 | 99 | 62 | 1
2015-10-28 01:30 | 2015-10-28 | 3 | 1 | 99 | 62 | 1
2015-10-28 01:45 | 2015-10-28 | 3 | 1 | 107 | 62 | 1
2015-10-28 02:00 | 2015-10-28 | 3 | 2 | 100 | 61.9333 | 1
2015-10-28 02:15 | 2015-10-28 | 3 | 2 | 102 | 61.6833 | 1
2015-10-28 02:30 | 2015-10-28 | 3 | 2 | 99 | 61.4333 | 1
2015-10-28 02:45 | 2015-10-28 | 3 | 2 | 96 | 61.1833 | 1
2015-10-28 03:00 | 2015-10-28 | 3 | 3 | 111 | 60.8667 | 1
2015-10-28 03:15 | 2015-10-28 | 3 | 3 | 102 | 60.3667 | 1
2015-10-28 03:30 | 2015-10-28 | 3 | 3 | 102 | 59.8667 | 1
2015-10-28 03:45 | 2015-10-28 | 3 | 3 | 99 | 59.3667 | 1
2015-10-28 04:00 | 2015-10-28 | 3 | 4 | 104 | 59.0667 | 1
2015-10-28 04:15 | 2015-10-28 | 3 | 4 | 105 | 59.3167 | 1
2015-10-28 04:30 | 2015-10-28 | 3 | 4 | 101 | 59.5667 | 1
2015-10-28 04:45 | 2015-10-28 | 3 | 4 | 101 | 59.8167 | 1
2015-10-28 05:00 | 2015-10-28 | 3 | 5 | 100 | 60 | 1
2015-10-28 05:15 | 2015-10-28 | 3 | 5 | 106 | 60 | 1
2015-10-28 05:30 | 2015-10-28 | 3 | 5 | 109 | 60 | 1
2015-10-28 05:45 | 2015-10-28 | 3 | 5 | 103 | 60 | 1
2015-10-28 06:00 | 2015-10-28 | 3 | 6 | 110 | 60 | 1
2015-10-28 06:15 | 2015-10-28 | 3 | 6 | 155 | 60 | 1
2015-10-28 06:30 | 2015-10-28 | 3 | 6 | 150 | 60 | 1
2015-10-28 06:45 | 2015-10-28 | 3 | 6 | 162 | 60 | 1
2015-10-28 07:00 | 2015-10-28 | 3 | 7 | 143 | 60.1333 | 1
2015-10-28 07:15 | 2015-10-28 | 3 | 7 | 159 | 60.6333 | 1
2015-10-28 07:30 | 2015-10-28 | 3 | 7 | 151 | 61.1333 | 1
2015-10-28 07:45 | 2015-10-28 | 3 | 7 | 163 | 61.6333 | 1
2015-10-28 08:00 | 2015-10-28 | 3 | 8 | 175 | 62.1333 | 1
2015-10-28 08:15 | 2015-10-28 | 3 | 8 | 166 | 62.6333 | 1
2015-10-28 08:30 | 2015-10-28 | 3 | 8 | 174 | 63.1333 | 1
2015-10-28 08:45 | 2015-10-28 | 3 | 8 | 179 | 63.6333 | 1
2015-10-28 09:00 | 2015-10-28 | 3 | 9 | 182 | 64 | 1
2015-10-28 09:15 | 2015-10-28 | 3 | 9 | 196 | 64 | 1
2015-10-28 09:30 | 2015-10-28 | 3 | 9 | 190 | 64 | 1
2015-10-28 09:45 | 2015-10-28 | 3 | 9 | 178 | 64 | 1
2015-10-28 10:00 | 2015-10-28 | 3 | 10 | 186 | 64 | 1
2015-10-28 10:15 | 2015-10-28 | 3 | 10 | 188 | 64 | 1
2015-10-28 10:30 | 2015-10-28 | 3 | 10 | 188 | 64.6286 | 1
2015-10-28 10:45 | 2015-10-28 | 3 | 10 | 194 | 65.4857 | 2
2015-10-28 11:00 | 2015-10-28 | 3 | 11 | 186 | 66 | 2
2015-10-28 11:15 | 2015-10-28 | 3 | 11 | 179 | 66 | 2
2015-10-28 11:30 | 2015-10-28 | 3 | 11 | 187 | 66 | 2
2015-10-28 11:45 | 2015-10-28 | 3 | 11 | 188 | 66 | 2
2015-10-28 12:00 | 2015-10-28 | 3 | 12 | 185 | 66 | 2
2015-10-28 12:15 | 2015-10-28 | 3 | 12 | 188 | 66 | 2
2015-10-28 12:30 | 2015-10-28 | 3 | 12 | 182 | 66 | 2
2015-10-28 12:45 | 2015-10-28 | 3 | 12 | 181 | 66 | 2
2015-10-28 13:00 | 2015-10-28 | 3 | 13 | 190 | 66.2 | 2
2015-10-28 13:15 | 2015-10-28 | 3 | 13 | 198 | 66.95 | 2
2015-10-28 13:30 | 2015-10-28 | 3 | 13 | 195 | 67.7 | 2
2015-10-28 13:45 | 2015-10-28 | 3 | 13 | 195 | 68.45 | 2
2015-10-28 14:00 | 2015-10-28 | 3 | 14 | 196 | 69.2667 | 2
2015-10-28 14:15 | 2015-10-28 | 3 | 14 | 191 | 69.7333 | 2
2015-10-28 14:30 | 2015-10-28 | 3 | 14 | 196 | 68.7333 | 2
2015-10-28 14:45 | 2015-10-28 | 3 | 14 | 195 | 67.7333 | 2
2015-10-28 15:00 | 2015-10-28 | 3 | 15 | 197 | 66.6129 | 2
2015-10-28 15:15 | 2015-10-28 | 3 | 15 | 196 | 65.1613 | 2
2015-10-28 15:30 | 2015-10-28 | 3 | 15 | 190 | 63.8966 | 1
2015-10-28 15:45 | 2015-10-28 | 3 | 15 | 199 | 63.3793 | 1
2015-10-28 16:00 | 2015-10-28 | 3 | 16 | 195 | 63 | 1
2015-10-28 16:15 | 2015-10-28 | 3 | 16 | 203 | 63 | 1
2015-10-28 16:30 | 2015-10-28 | 3 | 16 | 202 | 63 | 1
2015-10-28 16:45 | 2015-10-28 | 3 | 16 | 186 | 63 | 1
2015-10-28 17:00 | 2015-10-28 | 3 | 17 | 185 | 62.9333 | 1
2015-10-28 17:15 | 2015-10-28 | 3 | 17 | 194 | 62.6833 | 1
2015-10-28 17:30 | 2015-10-28 | 3 | 17 | 185 | 62.4333 | 1
2015-10-28 17:45 | 2015-10-28 | 3 | 17 | 179 | 62.1833 | 1
2015-10-28 18:00 | 2015-10-28 | 3 | 18 | 182 | 61.9333 | 1
2015-10-28 18:15 | 2015-10-28 | 3 | 18 | 131 | 61.6833 | 1
2015-10-28 18:30 | 2015-10-28 | 3 | 18 | 123 | 61.4333 | 1
2015-10-28 18:45 | 2015-10-28 | 3 | 18 | 122 | 61.1833 | 1
2015-10-28 19:00 | 2015-10-28 | 3 | 19 | 124 | 61 | 1
2015-10-28 19:15 | 2015-10-28 | 3 | 19 | 123 | 61 | 1
2015-10-28 19:30 | 2015-10-28 | 3 | 19 | 131 | 61 | 1
2015-10-28 19:45 | 2015-10-28 | 3 | 19 | 128 | 61 | 1
2015-10-28 20:00 | 2015-10-28 | 3 | 20 | 124 | 61 | 1
2015-10-28 20:15 | 2015-10-28 | 3 | 20 | 119 | 61 | 1
2015-10-28 20:30 | 2015-10-28 | 3 | 20 | 110 | 61 | 1
2015-10-28 20:45 | 2015-10-28 | 3 | 20 | 115 | 61 | 1
2015-10-28 21:00 | 2015-10-28 | 3 | 21 | 111 | 60.9333 | 1
2015-10-28 21:15 | 2015-10-28 | 3 | 21 | 115 | 60.6833 | 1
2015-10-28 21:30 | 2015-10-28 | 3 | 21 | 107 | 60.4333 | 1
2015-10-28 21:45 | 2015-10-28 | 3 | 21 | 121 | 60.1833 | 1
2015-10-28 22:00 | 2015-10-28 | 3 | 22 | 122 | 60 | 1
2015-10-28 22:15 | 2015-10-28 | 3 | 22 | 129 | 60 | 1
2015-10-28 22:30 | 2015-10-28 | 3 | 22 | 131 | 60 | 1
2015-10-28 22:45 | 2015-10-28 | 3 | 22 | 119 | 60 | 1
2015-10-28 23:00 | 2015-10-28 | 3 | 23 | 122 | 59.9333 | 1
2015-10-28 23:15 | 2015-10-28 | 3 | 23 | 118 | 59.6833 | 1
2015-10-28 23:30 | 2015-10-28 | 3 | 23 | 120 | 59.4333 | 1
2015-10-28 23:45 | 2015-10-28 | 3 | 23 | 118 | 59.1833 | 1
2015-10-29 | 2015-10-29 | 4 | 0 | 105 | 59 | 1
2015-10-29 00:15 | 2015-10-29 | 4 | 0 | 106 | 59 | 1
2015-10-29 00:30 | 2015-10-29 | 4 | 0 | 107 | 59 | 1
2015-10-29 00:45 | 2015-10-29 | 4 | 0 | 110 | 59 | 1
2015-10-29 01:00 | 2015-10-29 | 4 | 1 | 100 | 59 | 1
2015-10-29 01:15 | 2015-10-29 | 4 | 1 | 103 | 59 | 1
2015-10-29 01:30 | 2015-10-29 | 4 | 1 | 98 | 59 | 1
2015-10-29 01:45 | 2015-10-29 | 4 | 1 | 104 | 59 | 1
2015-10-29 02:00 | 2015-10-29 | 4 | 2 | 110 | 58.9333 | 1
2015-10-29 02:15 | 2015-10-29 | 4 | 2 | 100 | 58.6833 | 1
2015-10-29 02:30 | 2015-10-29 | 4 | 2 | 102 | 58.4333 | 1
2015-10-29 02:45 | 2015-10-29 | 4 | 2 | 97 | 58.1833 | 1
2015-10-29 03:00 | 2015-10-29 | 4 | 3 | 107 | 58 | 1
2015-10-29 03:15 | 2015-10-29 | 4 | 3 | 108 | 58 | 1
2015-10-29 03:30 | 2015-10-29 | 4 | 3 | 101 | 58 | 1
2015-10-29 03:45 | 2015-10-29 | 4 | 3 | 101 | 58 | 1
2015-10-29 04:00 | 2015-10-29 | 4 | 4 | 113 | 57.9333 | 1
2015-10-29 04:15 | 2015-10-29 | 4 | 4 | 103 | 57.6833 | 1
2015-10-29 04:30 | 2015-10-29 | 4 | 4 | 103 | 57.4333 | 1
2015-10-29 04:45 | 2015-10-29 | 4 | 4 | 100 | 57.1833 | 1
2015-10-29 05:00 | 2015-10-29 | 4 | 5 | 109 | 57.0667 | 1
2015-10-29 05:15 | 2015-10-29 | 4 | 5 | 109 | 57.3167 | 1
2015-10-29 05:30 | 2015-10-29 | 4 | 5 | 108 | 57.5667 | 1
2015-10-29 05:45 | 2015-10-29 | 4 | 5 | 105 | 57.8167 | 1
2015-10-29 06:00 | 2015-10-29 | 4 | 6 | 111 | 57.9333 | 1
2015-10-29 06:15 | 2015-10-29 | 4 | 6 | 136 | 57.6833 | 1
2015-10-29 06:30 | 2015-10-29 | 4 | 6 | 133 | 57.4333 | 1
2015-10-29 06:45 | 2015-10-29 | 4 | 6 | 141 | 57.1833 | 1
2015-10-29 07:00 | 2015-10-29 | 4 | 7 | 143 | 57.2667 | 1
2015-10-29 07:15 | 2015-10-29 | 4 | 7 | 159 | 58.2667 | 1
2015-10-29 07:30 | 2015-10-29 | 4 | 7 | 149 | 59.2667 | 1
2015-10-29 07:45 | 2015-10-29 | 4 | 7 | 159 | 60.2667 | 1
2015-10-29 08:00 | 2015-10-29 | 4 | 8 | 169 | 61.2 | 1
2015-10-29 08:15 | 2015-10-29 | 4 | 8 | 172 | 61.95 | 1
2015-10-29 08:30 | 2015-10-29 | 4 | 8 | 172 | 62.7 | 1
2015-10-29 08:45 | 2015-10-29 | 4 | 8 | 180 | 63.45 | 1
2015-10-29 09:00 | 2015-10-29 | 4 | 9 | 168 | 64.1333 | 1
2015-10-29 09:15 | 2015-10-29 | 4 | 9 | 174 | 64.6333 | 1
2015-10-29 09:30 | 2015-10-29 | 4 | 9 | 175 | 65.1333 | 2
2015-10-29 09:45 | 2015-10-29 | 4 | 9 | 183 | 65.6333 | 2
2015-10-29 10:00 | 2015-10-29 | 4 | 10 | 187 | 66.1333 | 2
2015-10-29 10:15 | 2015-10-29 | 4 | 10 | 186 | 66.6333 | 2
2015-10-29 10:30 | 2015-10-29 | 4 | 10 | 180 | 67.1333 | 2
2015-10-29 10:45 | 2015-10-29 | 4 | 10 | 189 | 67.6333 | 2
2015-10-29 11:00 | 2015-10-29 | 4 | 11 | 191 | 68.0667 | 2
2015-10-29 11:15 | 2015-10-29 | 4 | 11 | 176 | 68.3167 | 2
2015-10-29 11:30 | 2015-10-29 | 4 | 11 | 175 | 68.5667 | 2
2015-10-29 11:45 | 2015-10-29 | 4 | 11 | 183 | 68.8167 | 2
2015-10-29 12:00 | 2015-10-29 | 4 | 12 | 185 | 69.1333 | 2
2015-10-29 12:15 | 2015-10-29 | 4 | 12 | 186 | 69.6333 | 2
2015-10-29 12:30 | 2015-10-29 | 4 | 12 | 189 | 70.1333 | 3
2015-10-29 12:45 | 2015-10-29 | 4 | 12 | 185 | 70.6333 | 3
2015-10-29 13:00 | 2015-10-29 | 4 | 13 | 185 | 70.9333 | 3
2015-10-29 13:15 | 2015-10-29 | 4 | 13 | 206 | 70.6833 | 3
2015-10-29 13:30 | 2015-10-29 | 4 | 13 | 186 | 70.4333 | 3
2015-10-29 13:45 | 2015-10-29 | 4 | 13 | 187 | 70.1833 | 3
2015-10-29 14:00 | 2015-10-29 | 4 | 14 | 187 | 69.9333 | 2
2015-10-29 14:15 | 2015-10-29 | 4 | 14 | 188 | 69.6833 | 2
2015-10-29 14:30 | 2015-10-29 | 4 | 14 | 215 | 69.4333 | 2
2015-10-29 14:45 | 2015-10-29 | 4 | 14 | 186 | 69.1833 | 2
2015-10-29 15:00 | 2015-10-29 | 4 | 15 | 189 | 68.8667 | 2
2015-10-29 15:15 | 2015-10-29 | 4 | 15 | 199 | 68.3667 | 2
2015-10-29 15:30 | 2015-10-29 | 4 | 15 | 181 | 67.8667 | 2
2015-10-29 15:45 | 2015-10-29 | 4 | 15 | 202 | 67.3667 | 2
2015-10-29 16:00 | 2015-10-29 | 4 | 16 | 195 | 66.8 | 2
2015-10-29 16:15 | 2015-10-29 | 4 | 16 | 180 | 66.05 | 2
2015-10-29 16:30 | 2015-10-29 | 4 | 16 | 183 | 65.3 | 2
2015-10-29 16:45 | 2015-10-29 | 4 | 16 | 185 | 64.55 | 1
2015-10-29 17:00 | 2015-10-29 | 4 | 17 | 189 | 63.9333 | 1
2015-10-29 17:15 | 2015-10-29 | 4 | 17 | 190 | 63.6833 | 1
2015-10-29 17:30 | 2015-10-29 | 4 | 17 | 187 | 63.4333 | 1
2015-10-29 17:45 | 2015-10-29 | 4 | 17 | 175 | 63.1833 | 1
2015-10-29 18:00 | 2015-10-29 | 4 | 18 | 180 | 62.9333 | 1
2015-10-29 18:15 | 2015-10-29 | 4 | 18 | 140 | 62.6833 | 1
2015-10-29 18:30 | 2015-10-29 | 4 | 18 | 121 | 62.4333 | 1
2015-10-29 18:45 | 2015-10-29 | 4 | 18 | 123 | 62.1833 | 1
2015-10-29 19:00 | 2015-10-29 | 4 | 19 | 121 | 61.9333 | 1
2015-10-29 19:15 | 2015-10-29 | 4 | 19 | 127 | 61.6833 | 1
2015-10-29 19:30 | 2015-10-29 | 4 | 19 | 131 | 61.4333 | 1
2015-10-29 19:45 | 2015-10-29 | 4 | 19 | 125 | 61.1833 | 1
2015-10-29 20:00 | 2015-10-29 | 4 | 20 | 121 | 61 | 1
2015-10-29 20:15 | 2015-10-29 | 4 | 20 | 106 | 61 | 1
2015-10-29 20:30 | 2015-10-29 | 4 | 20 | 109 | 61 | 1
2015-10-29 20:45 | 2015-10-29 | 4 | 20 | 114 | 61 | 1
2015-10-29 21:00 | 2015-10-29 | 4 | 21 | 110 | 60.9333 | 1
2015-10-29 21:15 | 2015-10-29 | 4 | 21 | 110 | 60.6833 | 1
2015-10-29 21:30 | 2015-10-29 | 4 | 21 | 107 | 60.4333 | 1
2015-10-29 21:45 | 2015-10-29 | 4 | 21 | 120 | 60.1833 | 1
2015-10-29 22:00 | 2015-10-29 | 4 | 22 | 119 | 59.9333 | 1
2015-10-29 22:15 | 2015-10-29 | 4 | 22 | 112 | 59.6833 | 1
2015-10-29 22:30 | 2015-10-29 | 4 | 22 | 119 | 59.4333 | 1
2015-10-29 22:45 | 2015-10-29 | 4 | 22 | 113 | 59.1833 | 1
2015-10-29 23:00 | 2015-10-29 | 4 | 23 | 119 | 58.8 | 1
2015-10-29 23:15 | 2015-10-29 | 4 | 23 | 125 | 58.05 | 1
2015-10-29 23:30 | 2015-10-29 | 4 | 23 | 116 | 57.3 | 1
2015-10-29 23:45 | 2015-10-29 | 4 | 23 | 111 | 56.55 | 1
2015-10-30 | 2015-10-30 | 5 | 0 | 114 | 56.2667 | 1
2015-10-30 00:15 | 2015-10-30 | 5 | 0 | 112 | 57.2667 | 1
2015-10-30 00:30 | 2015-10-30 | 5 | 0 | 111 | 58.2667 | 1
2015-10-30 00:45 | 2015-10-30 | 5 | 0 | 111 | 59.2667 | 1
2015-10-30 01:00 | 2015-10-30 | 5 | 1 | 104 | 59.6667 | 1
2015-10-30 01:15 | 2015-10-30 | 5 | 1 | 103 | 58.4167 | 1
2015-10-30 01:30 | 2015-10-30 | 5 | 1 | 106 | 57.1667 | 1
2015-10-30 01:45 | 2015-10-30 | 5 | 1 | 102 | 55.9167 | 1
2015-10-30 02:00 | 2015-10-30 | 5 | 2 | 103 | 55.0667 | 1
2015-10-30 02:15 | 2015-10-30 | 5 | 2 | 105 | 55.3167 | 1
2015-10-30 02:30 | 2015-10-30 | 5 | 2 | 108 | 55.5667 | 1
2015-10-30 02:45 | 2015-10-30 | 5 | 2 | 104 | 55.8167 | 1
2015-10-30 03:00 | 2015-10-30 | 5 | 3 | 100 | 55.8 | 1
2015-10-30 03:15 | 2015-10-30 | 5 | 3 | 110 | 55.05 | 1
2015-10-30 03:30 | 2015-10-30 | 5 | 3 | 104 | 54.3 | 1
2015-10-30 03:45 | 2015-10-30 | 5 | 3 | 105 | 53.55 | 1
2015-10-30 04:00 | 2015-10-30 | 5 | 4 | 104 | 53.1333 | 1
2015-10-30 04:15 | 2015-10-30 | 5 | 4 | 108 | 53.6333 | 1
2015-10-30 04:30 | 2015-10-30 | 5 | 4 | 107 | 54.1333 | 1
2015-10-30 04:45 | 2015-10-30 | 5 | 4 | 102 | 54.6333 | 1
2015-10-30 05:00 | 2015-10-30 | 5 | 5 | 103 | 55 | 1
2015-10-30 05:15 | 2015-10-30 | 5 | 5 | 106 | 55 | 1
2015-10-30 05:30 | 2015-10-30 | 5 | 5 | 108 | 55 | 1
2015-10-30 05:45 | 2015-10-30 | 5 | 5 | 119 | 55 | 1
2015-10-30 06:00 | 2015-10-30 | 5 | 6 | 112 | 55.0667 | 1
2015-10-30 06:15 | 2015-10-30 | 5 | 6 | 131 | 55.3167 | 1
2015-10-30 06:30 | 2015-10-30 | 5 | 6 | 131 | 55.5667 | 1
2015-10-30 06:45 | 2015-10-30 | 5 | 6 | 135 | 55.8167 | 1
2015-10-30 07:00 | 2015-10-30 | 5 | 7 | 136 | 56.3333 | 1
2015-10-30 07:15 | 2015-10-30 | 5 | 7 | 135 | 57.5833 | 1
2015-10-30 07:30 | 2015-10-30 | 5 | 7 | 149 | 58.8333 | 1
2015-10-30 07:45 | 2015-10-30 | 5 | 7 | 149 | 60.0833 | 1
2015-10-30 08:00 | 2015-10-30 | 5 | 8 | 161 | 61.2667 | 1
2015-10-30 08:15 | 2015-10-30 | 5 | 8 | 159 | 62.2667 | 1
2015-10-30 08:30 | 2015-10-30 | 5 | 8 | 169 | 63.2667 | 1
2015-10-30 08:45 | 2015-10-30 | 5 | 8 | 159 | 64.2667 | 1
2015-10-30 09:00 | 2015-10-30 | 5 | 9 | 162 | 65.1333 | 2
2015-10-30 09:15 | 2015-10-30 | 5 | 9 | 162 | 65.6333 | 2
2015-10-30 09:30 | 2015-10-30 | 5 | 9 | 159 | 66.1333 | 2
2015-10-30 09:45 | 2015-10-30 | 5 | 9 | 145 | 66.6333 | 2
2015-10-30 10:00 | 2015-10-30 | 5 | 10 | 144 | 67.0667 | 2
2015-10-30 10:15 | 2015-10-30 | 5 | 10 | 143 | 67.3167 | 2
2015-10-30 10:30 | 2015-10-30 | 5 | 10 | 159 | 67.5667 | 2
2015-10-30 10:45 | 2015-10-30 | 5 | 10 | 172 | 67.8167 | 2
2015-10-30 11:00 | 2015-10-30 | 5 | 11 | 167 | 68.1333 | 2
2015-10-30 11:15 | 2015-10-30 | 5 | 11 | 166 | 68.6333 | 2
2015-10-30 11:30 | 2015-10-30 | 5 | 11 | 164 | 69.1333 | 2
2015-10-30 11:45 | 2015-10-30 | 5 | 11 | 158 | 69.6333 | 2
2015-10-30 12:00 | 2015-10-30 | 5 | 12 | 158 | 70 | 2
2015-10-30 12:15 | 2015-10-30 | 5 | 12 | 159 | 70 | 2
2015-10-30 12:30 | 2015-10-30 | 5 | 12 | 160 | 70 | 2
2015-10-30 12:45 | 2015-10-30 | 5 | 12 | 163 | 70 | 2
2015-10-30 13:00 | 2015-10-30 | 5 | 13 | 162 | 70.4 | 3
2015-10-30 13:15 | 2015-10-30 | 5 | 13 | 163 | 71.9 | 3
2015-10-30 13:30 | 2015-10-30 | 5 | 13 | 163 | 73.4 | 3
2015-10-30 13:45 | 2015-10-30 | 5 | 13 | 167 | 74.9 | 3
2015-10-30 14:00 | 2015-10-30 | 5 | 14 | 174 | 75.9333 | 4
2015-10-30 14:15 | 2015-10-30 | 5 | 14 | 167 | 75.6833 | 4
2015-10-30 14:30 | 2015-10-30 | 5 | 14 | 175 | 75.4333 | 4
2015-10-30 14:45 | 2015-10-30 | 5 | 14 | 179 | 75.1833 | 4
2015-10-30 15:00 | 2015-10-30 | 5 | 15 | 174 | 74.7333 | 3
2015-10-30 15:15 | 2015-10-30 | 5 | 15 | 167 | 73.7333 | 3
2015-10-30 15:30 | 2015-10-30 | 5 | 15 | 170 | 72.7333 | 3
2015-10-30 15:45 | 2015-10-30 | 5 | 15 | 158 | 71.7333 | 3
2015-10-30 16:00 | 2015-10-30 | 5 | 16 | 163 | 70.8667 | 3
2015-10-30 16:15 | 2015-10-30 | 5 | 16 | 163 | 70.3667 | 3
2015-10-30 16:30 | 2015-10-30 | 5 | 16 | 160 | 69.8667 | 2
2015-10-30 16:45 | 2015-10-30 | 5 | 16 | 161 | 69.3667 | 2
2015-10-30 17:00 | 2015-10-30 | 5 | 17 | 164 | 68.7333 | 2
2015-10-30 17:15 | 2015-10-30 | 5 | 17 | 164 | 67.7333 | 2
2015-10-30 17:30 | 2015-10-30 | 5 | 17 | 161 | 66.7333 | 2
2015-10-30 17:45 | 2015-10-30 | 5 | 17 | 171 | 65.7333 | 2
2015-10-30 18:00 | 2015-10-30 | 5 | 18 | 164 | 64.9333 | 1
2015-10-30 18:15 | 2015-10-30 | 5 | 18 | 125 | 64.6833 | 1
2015-10-30 18:30 | 2015-10-30 | 5 | 18 | 124 | 64.4333 | 1
2015-10-30 18:45 | 2015-10-30 | 5 | 18 | 115 | 64.1833 | 1
2015-10-30 19:00 | 2015-10-30 | 5 | 19 | 121 | 63.9333 | 1
2015-10-30 19:15 | 2015-10-30 | 5 | 19 | 124 | 63.6833 | 1
2015-10-30 19:30 | 2015-10-30 | 5 | 19 | 118 | 63.4333 | 1
2015-10-30 19:45 | 2015-10-30 | 5 | 19 | 120 | 63.1833 | 1
2015-10-30 20:00 | 2015-10-30 | 5 | 20 | 121 | 62.9333 | 1
2015-10-30 20:15 | 2015-10-30 | 5 | 20 | 114 | 62.6833 | 1
2015-10-30 20:30 | 2015-10-30 | 5 | 20 | 114 | 62.4333 | 1
2015-10-30 20:45 | 2015-10-30 | 5 | 20 | 117 | 62.1833 | 1
2015-10-30 21:00 | 2015-10-30 | 5 | 21 | 114 | 61.9333 | 1
2015-10-30 21:15 | 2015-10-30 | 5 | 21 | 121 | 61.6833 | 1
2015-10-30 21:30 | 2015-10-30 | 5 | 21 | 112 | 61.4333 | 1
2015-10-30 21:45 | 2015-10-30 | 5 | 21 | 118 | 61.1833 | 1
2015-10-30 22:00 | 2015-10-30 | 5 | 22 | 114 | 61 | 1
2015-10-30 22:15 | 2015-10-30 | 5 | 22 | 112 | 61 | 1
2015-10-30 22:30 | 2015-10-30 | 5 | 22 | 119 | 61 | 1
2015-10-30 22:45 | 2015-10-30 | 5 | 22 | 116 | 61 | 1
2015-10-30 23:00 | 2015-10-30 | 5 | 23 | 115 | 60.9333 | 1
2015-10-30 23:15 | 2015-10-30 | 5 | 23 | 110 | 60.6833 | 1
2015-10-30 23:30 | 2015-10-30 | 5 | 23 | 115 | 60.4333 | 1
2015-10-30 23:45 | 2015-10-30 | 5 | 23 | 111 | 60.1833 | 1
2015-10-31 | 2015-10-31 | 6 | 0 | 120 | 59.9333 | 1
2015-10-31 00:15 | 2015-10-31 | 6 | 0 | 117 | 59.6833 | 1
2015-10-31 00:30 | 2015-10-31 | 6 | 0 | 107 | 59.4333 | 1
2015-10-31 00:45 | 2015-10-31 | 6 | 0 | 106 | 59.1833 | 1
2015-10-31 01:00 | 2015-10-31 | 6 | 1 | 107 | 58.9333 | 1
2015-10-31 01:15 | 2015-10-31 | 6 | 1 | 104 | 58.6833 | 1
2015-10-31 01:30 | 2015-10-31 | 6 | 1 | 111 | 58.4333 | 1
2015-10-31 01:45 | 2015-10-31 | 6 | 1 | 107 | 58.1833 | 1
2015-10-31 02:00 | 2015-10-31 | 6 | 2 | 109 | 58 | 1
2015-10-31 02:15 | 2015-10-31 | 6 | 2 | 103 | 58 | 1
2015-10-31 02:30 | 2015-10-31 | 6 | 2 | 108 | 58 | 1
2015-10-31 02:45 | 2015-10-31 | 6 | 2 | 111 | 58 | 1
2015-10-31 03:00 | 2015-10-31 | 6 | 3 | 101 | 57.9333 | 1
2015-10-31 03:15 | 2015-10-31 | 6 | 3 | 104 | 57.6833 | 1
2015-10-31 03:30 | 2015-10-31 | 6 | 3 | 107 | 57.4333 | 1
2015-10-31 03:45 | 2015-10-31 | 6 | 3 | 106 | 57.1833 | 1
2015-10-31 04:00 | 2015-10-31 | 6 | 4 | 107 | 57 | 1
2015-10-31 04:15 | 2015-10-31 | 6 | 4 | 105 | 57 | 1
2015-10-31 04:30 | 2015-10-31 | 6 | 4 | 105 | 57 | 1
2015-10-31 04:45 | 2015-10-31 | 6 | 4 | 112 | 57 | 1
2015-10-31 05:00 | 2015-10-31 | 6 | 5 | 102 | 57.0667 | 1
2015-10-31 05:15 | 2015-10-31 | 6 | 5 | 104 | 57.3167 | 1
2015-10-31 05:30 | 2015-10-31 | 6 | 5 | 103 | 57.5667 | 1
2015-10-31 05:45 | 2015-10-31 | 6 | 5 | 105 | 57.8167 | 1
2015-10-31 06:00 | 2015-10-31 | 6 | 6 | 104 | 57.9333 | 1
2015-10-31 06:15 | 2015-10-31 | 6 | 6 | 110 | 57.6833 | 1
2015-10-31 06:30 | 2015-10-31 | 6 | 6 | 104 | 57.4333 | 1
2015-10-31 06:45 | 2015-10-31 | 6 | 6 | 99 | 57.1833 | 1
2015-10-31 07:00 | 2015-10-31 | 6 | 7 | 98 | 57.3333 | 1
2015-10-31 07:15 | 2015-10-31 | 6 | 7 | 100 | 58.5833 | 1
2015-10-31 07:30 | 2015-10-31 | 6 | 7 | 98 | 59.8333 | 1
2015-10-31 07:45 | 2015-10-31 | 6 | 7 | 101 | 61.0833 | 1
2015-10-31 08:00 | 2015-10-31 | 6 | 8 | 102 | 62.2 | 1
2015-10-31 08:15 | 2015-10-31 | 6 | 8 | 97 | 62.95 | 1
2015-10-31 08:30 | 2015-10-31 | 6 | 8 | 96 | 63.7 | 1
2015-10-31 08:45 | 2015-10-31 | 6 | 8 | 100 | 64.45 | 1
2015-10-31 09:00 | 2015-10-31 | 6 | 9 | 99 | 65.0667 | 2
2015-10-31 09:15 | 2015-10-31 | 6 | 9 | 101 | 65.3167 | 2
2015-10-31 09:30 | 2015-10-31 | 6 | 9 | 101 | 65.5667 | 2
2015-10-31 09:45 | 2015-10-31 | 6 | 9 | 101 | 65.8167 | 2
2015-10-31 10:00 | 2015-10-31 | 6 | 10 | 108 | 66.1333 | 2
2015-10-31 10:15 | 2015-10-31 | 6 | 10 | 98 | 66.6333 | 2
2015-10-31 10:30 | 2015-10-31 | 6 | 10 | 98 | 67.1333 | 2
2015-10-31 10:45 | 2015-10-31 | 6 | 10 | 99 | 67.6333 | 2
2015-10-31 11:00 | 2015-10-31 | 6 | 11 | 98 | 68.3333 | 2
2015-10-31 11:15 | 2015-10-31 | 6 | 11 | 96 | 69.5833 | 2
2015-10-31 11:30 | 2015-10-31 | 6 | 11 | 105 | 70.8333 | 3
2015-10-31 11:45 | 2015-10-31 | 6 | 11 | 102 | 72.0833 | 3
2015-10-31 12:00 | 2015-10-31 | 6 | 12 | 100 | 72.8 | 3
2015-10-31 12:15 | 2015-10-31 | 6 | 12 | 97 | 72.05 | 3
2015-10-31 12:30 | 2015-10-31 | 6 | 12 | 105 | 71.3 | 3
2015-10-31 12:45 | 2015-10-31 | 6 | 12 | 103 | 70.55 | 3
2015-10-31 13:00 | 2015-10-31 | 6 | 13 | 100 | 69.9333 | 2
2015-10-31 13:15 | 2015-10-31 | 6 | 13 | 99 | 69.6833 | 2
2015-10-31 13:30 | 2015-10-31 | 6 | 13 | 101 | 69.4333 | 2
2015-10-31 13:45 | 2015-10-31 | 6 | 13 | 100 | 69.1833 | 2
2015-10-31 14:00 | 2015-10-31 | 6 | 14 | 105 | 69.0667 | 2
2015-10-31 14:15 | 2015-10-31 | 6 | 14 | 100 | 69.3167 | 2
2015-10-31 14:30 | 2015-10-31 | 6 | 14 | 102 | 69.5667 | 2
2015-10-31 14:45 | 2015-10-31 | 6 | 14 | 99 | 69.8167 | 2
2015-10-31 15:00 | 2015-10-31 | 6 | 15 | 104 | 69.6 | 2
2015-10-31 15:15 | 2015-10-31 | 6 | 15 | 100 | 68.1 | 2
2015-10-31 15:30 | 2015-10-31 | 6 | 15 | 104 | 66.6 | 2
2015-10-31 15:45 | 2015-10-31 | 6 | 15 | 103 | 65.1 | 2
2015-10-31 16:00 | 2015-10-31 | 6 | 16 | 106 | 63.8667 | 1
2015-10-31 16:15 | 2015-10-31 | 6 | 16 | 103 | 63.3667 | 1
2015-10-31 16:30 | 2015-10-31 | 6 | 16 | 110 | 62.8667 | 1
2015-10-31 16:45 | 2015-10-31 | 6 | 16 | 109 | 62.3667 | 1
2015-10-31 17:00 | 2015-10-31 | 6 | 17 | 106 | 61.9333 | 1
2015-10-31 17:15 | 2015-10-31 | 6 | 17 | 105 | 61.6833 | 1
2015-10-31 17:30 | 2015-10-31 | 6 | 17 | 106 | 61.4333 | 1
2015-10-31 17:45 | 2015-10-31 | 6 | 17 | 110 | 61.1833 | 1
2015-10-31 18:00 | 2015-10-31 | 6 | 18 | 104 | 60.9333 | 1
2015-10-31 18:15 | 2015-10-31 | 6 | 18 | 105 | 60.6833 | 1
2015-10-31 18:30 | 2015-10-31 | 6 | 18 | 103 | 60.4333 | 1
2015-10-31 18:45 | 2015-10-31 | 6 | 18 | 103 | 60.1833 | 1
2015-10-31 19:00 | 2015-10-31 | 6 | 19 | 105 | 60.1333 | 1
2015-10-31 19:15 | 2015-10-31 | 6 | 19 | 109 | 60.6333 | 1
2015-10-31 19:30 | 2015-10-31 | 6 | 19 | 109 | 61 | 1
2015-10-31 19:45 | 2015-10-31 | 6 | 19 | 104 | 61 | 1
2015-10-31 20:00 | 2015-10-31 | 6 | 20 | 102 | 60.9333 | 1
2015-10-31 20:15 | 2015-10-31 | 6 | 20 | 113 | 60.6833 | 1
2015-10-31 20:30 | 2015-10-31 | 6 | 20 | 104 | 60.4333 | 1
2015-10-31 20:45 | 2015-10-31 | 6 | 20 | 106 | 60.1833 | 1
2015-10-31 21:00 | 2015-10-31 | 6 | 21 | 103 | 60.0667 | 1
2015-10-31 21:15 | 2015-10-31 | 6 | 21 | 110 | 60.3167 | 1
2015-10-31 21:30 | 2015-10-31 | 6 | 21 | 105 | 60.5667 | 1
2015-10-31 21:45 | 2015-10-31 | 6 | 21 | 109 | 60.8167 | 1
2015-10-31 22:00 | 2015-10-31 | 6 | 22 | 100 | 61 | 1
2015-10-31 22:15 | 2015-10-31 | 6 | 22 | 106 | 61 | 1
2015-10-31 22:30 | 2015-10-31 | 6 | 22 | 101 | 61 | 1
2015-10-31 22:45 | 2015-10-31 | 6 | 22 | 105 | 61 | 1
2015-10-31 23:00 | 2015-10-31 | 6 | 23 | 107 | 61 | 1
2015-10-31 23:15 | 2015-10-31 | 6 | 23 | 104 | 61 | 1
2015-10-31 23:30 | 2015-10-31 | 6 | 23 | 94 | 61 | 1
2015-10-31 23:45 | 2015-10-31 | 6 | 23 | 92 | 61 | 1
Formulas:
Date = DATE(YEAR([Date]),MONTH([Date]),DAY([Date]))

## DR Calculation
MediumOffice | CZ03 |  |  |  |  | precool | temp reset
| TempRange | hour | power | oat | range | 0 | 4 | DR% | DR (kW)
| 1 | 1 | 224.6336 | 61.6926 | 1 | 0.19203 | -4.719 | 0.07128 | 16.0119
| 1 | 1 | 224.6336 | 61.6926 | 1 | 0.19203 | -4.719 | 0.07128 | 16.0119
| 1 | 1 | 224.6336 | 61.6926 | 1 | 0.19203 | -4.719 | 0.07128 | 16.0119
| 1 | 1 | 224.6336 | 61.6926 | 1 | 0.19203 | -4.719 | 0.07128 | 16.0119
| 1 | 2 | 224.6336 | 61.6926 | 1 | 0.021674 | 9.8639 | 0.11201 | 25.1613
| 1 | 2 | 224.6336 | 61.6926 | 1 | 0.021674 | 9.8639 | 0.11201 | 25.1613
| 1 | 2 | 224.6336 | 61.6926 | 1 | 0.021674 | 9.8639 | 0.11201 | 25.1613
| 1 | 2 | 224.6336 | 61.6926 | 1 | 0.021674 | 9.8639 | 0.11201 | 25.1613
| 1 | 3 | 224.6336 | 61.6926 | 1 | -0.011327 | 12.447 | 0.11748 | 26.3905
| 1 | 3 | 224.6336 | 61.6926 | 1 | -0.011327 | 12.447 | 0.11748 | 26.3905
| 1 | 3 | 224.6336 | 61.6926 | 1 | -0.011327 | 12.447 | 0.11748 | 26.3905
| 1 | 3 | 224.6336 | 61.6926 | 1 | -0.011327 | 12.447 | 0.11748 | 26.3905
| 1 | 4 | 224.6336 | 61.6926 | 1 | -0.040987 | 12.4854 | 0.099568 | 22.3663
| 1 | 4 | 224.6336 | 61.6926 | 1 | -0.040987 | 12.4854 | 0.099568 | 22.3663
| 1 | 4 | 224.6336 | 61.6926 | 1 | -0.040987 | 12.4854 | 0.099568 | 22.3663
| 1 | 4 | 224.6336 | 61.6926 | 1 | -0.040987 | 12.4854 | 0.099568 | 22.3663
| TempRange | hour | power | oat | range | 0 | 4 | DR% | DR (kW)
| 2 | 1 | 227.4739 | 67.6092 | 1 | 0.19203 | -4.719 | 0.082642 | 18.7989
| 2 | 1 | 227.4739 | 67.6092 | 1 | 0.19203 | -4.719 | 0.082642 | 18.7989
| 2 | 1 | 227.4739 | 67.6092 | 1 | 0.19203 | -4.719 | 0.082642 | 18.7989
| 2 | 1 | 227.4739 | 67.6092 | 1 | 0.19203 | -4.719 | 0.082642 | 18.7989
| 2 | 2 | 227.4739 | 67.6092 | 1 | 0.021674 | 9.8639 | 0.11329 | 25.7711
| 2 | 2 | 227.4739 | 67.6092 | 1 | 0.021674 | 9.8639 | 0.11329 | 25.7711
| 2 | 2 | 227.4739 | 67.6092 | 1 | 0.021674 | 9.8639 | 0.11329 | 25.7711
| 2 | 2 | 227.4739 | 67.6092 | 1 | 0.021674 | 9.8639 | 0.11329 | 25.7711
| 2 | 3 | 227.4739 | 67.6092 | 1 | -0.011327 | 12.447 | 0.11681 | 26.5717
| 2 | 3 | 227.4739 | 67.6092 | 1 | -0.011327 | 12.447 | 0.11681 | 26.5717
| 2 | 3 | 227.4739 | 67.6092 | 1 | -0.011327 | 12.447 | 0.11681 | 26.5717
| 2 | 3 | 227.4739 | 67.6092 | 1 | -0.011327 | 12.447 | 0.11681 | 26.5717
| 2 | 4 | 227.4739 | 67.6092 | 1 | -0.040987 | 12.4854 | 0.097143 | 22.0975
| 2 | 4 | 227.4739 | 67.6092 | 1 | -0.040987 | 12.4854 | 0.097143 | 22.0975
| 2 | 4 | 227.4739 | 67.6092 | 1 | -0.040987 | 12.4854 | 0.097143 | 22.0975
| 2 | 4 | 227.4739 | 67.6092 | 1 | -0.040987 | 12.4854 | 0.097143 | 22.0975
| TempRange | hour | power | oat | range | 0 | 4 | DR% | DR (kW)
| 3 | 1 | 234.9057 | 72.1396 | 1 | 0.19203 | -4.719 | 0.091342 | 21.4567
| 3 | 1 | 234.9057 | 72.1396 | 1 | 0.19203 | -4.719 | 0.091342 | 21.4567
| 3 | 1 | 234.9057 | 72.1396 | 1 | 0.19203 | -4.719 | 0.091342 | 21.4567
| 3 | 1 | 234.9057 | 72.1396 | 1 | 0.19203 | -4.719 | 0.091342 | 21.4567
| 3 | 2 | 234.9057 | 72.1396 | 1 | 0.021674 | 9.8639 | 0.11427 | 26.8438
| 3 | 2 | 234.9057 | 72.1396 | 1 | 0.021674 | 9.8639 | 0.11427 | 26.8438
| 3 | 2 | 234.9057 | 72.1396 | 1 | 0.021674 | 9.8639 | 0.11427 | 26.8438
| 3 | 2 | 234.9057 | 72.1396 | 1 | 0.021674 | 9.8639 | 0.11427 | 26.8438
| 3 | 3 | 234.9057 | 72.1396 | 1 | -0.011327 | 12.447 | 0.1163 | 27.3193
| 3 | 3 | 234.9057 | 72.1396 | 1 | -0.011327 | 12.447 | 0.1163 | 27.3193
| 3 | 3 | 234.9057 | 72.1396 | 1 | -0.011327 | 12.447 | 0.1163 | 27.3193
| 3 | 3 | 234.9057 | 72.1396 | 1 | -0.011327 | 12.447 | 0.1163 | 27.3193
| 3 | 4 | 234.9057 | 72.1396 | 1 | -0.040987 | 12.4854 | 0.095286 | 22.3832
| 3 | 4 | 234.9057 | 72.1396 | 1 | -0.040987 | 12.4854 | 0.095286 | 22.3832
| 3 | 4 | 234.9057 | 72.1396 | 1 | -0.040987 | 12.4854 | 0.095286 | 22.3832
| 3 | 4 | 234.9057 | 72.1396 | 1 | -0.040987 | 12.4854 | 0.095286 | 22.3832
| TempRange | hour | power | oat | range | 0 | 4 | DR% | DR (kW)
| 4 | 1 | 242.2877 | 76.9243 | 2 | 0.19203 | -4.719 | 0.10053 | 24.3572
| 4 | 1 | 242.2877 | 76.9243 | 2 | 0.19203 | -4.719 | 0.10053 | 24.3572
| 4 | 1 | 242.2877 | 76.9243 | 2 | 0.19203 | -4.719 | 0.10053 | 24.3572
| 4 | 1 | 242.2877 | 76.9243 | 2 | 0.19203 | -4.719 | 0.10053 | 24.3572
| 4 | 2 | 242.2877 | 76.9243 | 2 | 0.021674 | 9.8639 | 0.11531 | 27.9386
| 4 | 2 | 242.2877 | 76.9243 | 2 | 0.021674 | 9.8639 | 0.11531 | 27.9386
| 4 | 2 | 242.2877 | 76.9243 | 2 | 0.021674 | 9.8639 | 0.11531 | 27.9386
| 4 | 2 | 242.2877 | 76.9243 | 2 | 0.021674 | 9.8639 | 0.11531 | 27.9386
| 4 | 3 | 242.2877 | 76.9243 | 2 | -0.011327 | 12.447 | 0.11576 | 28.0465
| 4 | 3 | 242.2877 | 76.9243 | 2 | -0.011327 | 12.447 | 0.11576 | 28.0465
| 4 | 3 | 242.2877 | 76.9243 | 2 | -0.011327 | 12.447 | 0.11576 | 28.0465
| 4 | 3 | 242.2877 | 76.9243 | 2 | -0.011327 | 12.447 | 0.11576 | 28.0465
| 4 | 4 | 242.2877 | 76.9243 | 2 | -0.040987 | 12.4854 | 0.093325 | 22.6115
| 4 | 4 | 242.2877 | 76.9243 | 2 | -0.040987 | 12.4854 | 0.093325 | 22.6115
| 4 | 4 | 242.2877 | 76.9243 | 2 | -0.040987 | 12.4854 | 0.093325 | 22.6115
| 4 | 4 | 242.2877 | 76.9243 | 2 | -0.040987 | 12.4854 | 0.093325 | 22.6115
| TempRange | hour | power | oat | range | 0 | 4 | DR% | DR (kW)
| 5 | 1 | 265.0244 | 82.1462 | 2 | 0.19203 | -4.719 | 0.11056 | 29.3005
| 5 | 1 | 265.0244 | 82.1462 | 2 | 0.19203 | -4.719 | 0.11056 | 29.3005
| 5 | 1 | 265.0244 | 82.1462 | 2 | 0.19203 | -4.719 | 0.11056 | 29.3005
| 5 | 1 | 265.0244 | 82.1462 | 2 | 0.19203 | -4.719 | 0.11056 | 29.3005
| 5 | 2 | 265.0244 | 82.1462 | 2 | 0.021674 | 9.8639 | 0.11644 | 30.8604
| 5 | 2 | 265.0244 | 82.1462 | 2 | 0.021674 | 9.8639 | 0.11644 | 30.8604
| 5 | 2 | 265.0244 | 82.1462 | 2 | 0.021674 | 9.8639 | 0.11644 | 30.8604
| 5 | 2 | 265.0244 | 82.1462 | 2 | 0.021674 | 9.8639 | 0.11644 | 30.8604
| 5 | 3 | 265.0244 | 82.1462 | 2 | -0.011327 | 12.447 | 0.11517 | 30.5217
| 5 | 3 | 265.0244 | 82.1462 | 2 | -0.011327 | 12.447 | 0.11517 | 30.5217
| 5 | 3 | 265.0244 | 82.1462 | 2 | -0.011327 | 12.447 | 0.11517 | 30.5217
| 5 | 3 | 265.0244 | 82.1462 | 2 | -0.011327 | 12.447 | 0.11517 | 30.5217
| 5 | 4 | 265.0244 | 82.1462 | 2 | -0.040987 | 12.4854 | 0.091184 | 24.1661
| 5 | 4 | 265.0244 | 82.1462 | 2 | -0.040987 | 12.4854 | 0.091184 | 24.1661
| 5 | 4 | 265.0244 | 82.1462 | 2 | -0.040987 | 12.4854 | 0.091184 | 24.1661
| 5 | 4 | 265.0244 | 82.1462 | 2 | -0.040987 | 12.4854 | 0.091184 | 24.1661
| TempRange | hour | power | oat | range | 0 | 4 | DR% | DR (kW)
| 6 | 1 | 253.4255 | 87.5605 | 2 | 0.19203 | -4.719 | 0.12096 | 30.6531
| 6 | 1 | 253.4255 | 87.5605 | 2 | 0.19203 | -4.719 | 0.12096 | 30.6531
| 6 | 1 | 253.4255 | 87.5605 | 2 | 0.19203 | -4.719 | 0.12096 | 30.6531
| 6 | 1 | 253.4255 | 87.5605 | 2 | 0.19203 | -4.719 | 0.12096 | 30.6531
| 6 | 2 | 253.4255 | 87.5605 | 2 | 0.021674 | 9.8639 | 0.11762 | 29.8071
| 6 | 2 | 253.4255 | 87.5605 | 2 | 0.021674 | 9.8639 | 0.11762 | 29.8071
| 6 | 2 | 253.4255 | 87.5605 | 2 | 0.021674 | 9.8639 | 0.11762 | 29.8071
| 6 | 2 | 253.4255 | 87.5605 | 2 | 0.021674 | 9.8639 | 0.11762 | 29.8071
| 6 | 3 | 253.4255 | 87.5605 | 2 | -0.011327 | 12.447 | 0.11455 | 29.0305
| 6 | 3 | 253.4255 | 87.5605 | 2 | -0.011327 | 12.447 | 0.11455 | 29.0305
| 6 | 3 | 253.4255 | 87.5605 | 2 | -0.011327 | 12.447 | 0.11455 | 29.0305
| 6 | 3 | 253.4255 | 87.5605 | 2 | -0.011327 | 12.447 | 0.11455 | 29.0305
| 6 | 4 | 253.4255 | 87.5605 | 2 | -0.040987 | 12.4854 | 0.088965 | 22.5461
| 6 | 4 | 253.4255 | 87.5605 | 2 | -0.040987 | 12.4854 | 0.088965 | 22.5461
| 6 | 4 | 253.4255 | 87.5605 | 2 | -0.040987 | 12.4854 | 0.088965 | 22.5461
| 6 | 4 | 253.4255 | 87.5605 | 2 | -0.040987 | 12.4854 | 0.088965 | 22.5461
| TempRange | hour | power | oat | range | 0 | 4 | DR% | DR (kW)
| 7 | 1 | 248.6667 | 90.7944 | 2 | 0.19203 | -4.719 | 0.12717 | 31.6218
| 7 | 1 | 248.6667 | 90.7944 | 2 | 0.19203 | -4.719 | 0.12717 | 31.6218
| 7 | 1 | 248.6667 | 90.7944 | 2 | 0.19203 | -4.719 | 0.12717 | 31.6218
| 7 | 1 | 248.6667 | 90.7944 | 2 | 0.19203 | -4.719 | 0.12717 | 31.6218
| 7 | 2 | 248.6667 | 90.7944 | 2 | 0.021674 | 9.8639 | 0.11832 | 29.4217
| 7 | 2 | 248.6667 | 90.7944 | 2 | 0.021674 | 9.8639 | 0.11832 | 29.4217
| 7 | 2 | 248.6667 | 90.7944 | 2 | 0.021674 | 9.8639 | 0.11832 | 29.4217
| 7 | 2 | 248.6667 | 90.7944 | 2 | 0.021674 | 9.8639 | 0.11832 | 29.4217
| 7 | 3 | 248.6667 | 90.7944 | 2 | -0.011327 | 12.447 | 0.11419 | 28.3942
| 7 | 3 | 248.6667 | 90.7944 | 2 | -0.011327 | 12.447 | 0.11419 | 28.3942
| 7 | 3 | 248.6667 | 90.7944 | 2 | -0.011327 | 12.447 | 0.11419 | 28.3942
| 7 | 3 | 248.6667 | 90.7944 | 2 | -0.011327 | 12.447 | 0.11419 | 28.3942
| 7 | 4 | 248.6667 | 90.7944 | 2 | -0.040987 | 12.4854 | 0.08764 | 21.7931
| 7 | 4 | 248.6667 | 90.7944 | 2 | -0.040987 | 12.4854 | 0.08764 | 21.7931
| 7 | 4 | 248.6667 | 90.7944 | 2 | -0.040987 | 12.4854 | 0.08764 | 21.7931
| 7 | 4 | 248.6667 | 90.7944 | 2 | -0.040987 | 12.4854 | 0.08764 | 21.7931

## Outside Temp
Date | CZ03 | CZ04 | CZ12 | CZ13
2015-05-01 01:00 | 63.7333 | 63.7667 | 61.7667 | 69.7667
2015-05-01 01:15 | 62.7333 | 63.2667 | 61.2667 | 69.2667
2015-05-01 01:30 | 61.7333 | 62.7667 | 60.7667 | 68.7667
2015-05-01 01:45 | 60.7333 | 62.2667 | 60.2667 | 68.2667
2015-05-01 02:00 | 59.9333 | 62.1167 | 59.65 | 67.8833
2015-05-01 02:15 | 59.6833 | 62.3667 | 58.9 | 67.6333
2015-05-01 02:30 | 59.4333 | 62.6167 | 58.15 | 67.3833
2015-05-01 02:45 | 59.1833 | 62.8667 | 57.4 | 67.1333
2015-05-01 03:00 | 58.9333 | 62.8833 | 57 | 66.7667
2015-05-01 03:15 | 58.6833 | 62.6333 | 57 | 66.2667
2015-05-01 03:30 | 58.4333 | 62.3833 | 57 | 65.7667
2015-05-01 03:45 | 58.1833 | 62.1333 | 57 | 65.2667
2015-05-01 04:00 | 58 | 62.1167 | 56.8833 | 64.65
2015-05-01 04:15 | 58 | 62.3667 | 56.6333 | 63.9
2015-05-01 04:30 | 58 | 62.6167 | 56.3833 | 63.15
2015-05-01 04:45 | 58 | 62.8667 | 56.1333 | 62.4
2015-05-01 05:00 | 58.0667 | 63 | 55.8833 | 62.35
2015-05-01 05:15 | 58.3167 | 63 | 55.6333 | 63.1
2015-05-01 05:30 | 58.5667 | 63 | 55.3833 | 63.85
2015-05-01 05:45 | 58.8167 | 63 | 55.1333 | 64.6
2015-05-01 06:00 | 59.2667 | 63.4667 | 55 | 65.5833
2015-05-01 06:15 | 60.2667 | 64.4667 | 55 | 66.8333
2015-05-01 06:30 | 61.2667 | 65.4667 | 55 | 68.0833
2015-05-01 06:45 | 62.2667 | 66.4667 | 55 | 69.3333
2015-05-01 07:00 | 63.4 | 67.4667 | 55.9333 | 70.9333
2015-05-01 07:15 | 64.9 | 68.4667 | 57.9333 | 72.9333
2015-05-01 07:30 | 66.4 | 69.4667 | 59.9333 | 74.9333
2015-05-01 07:45 | 67.9 | 70.4667 | 61.9333 | 76.9333
2015-05-01 08:00 | 68.8 | 71.35 | 63.9333 | 78.1167
2015-05-01 08:15 | 68.05 | 72.1 | 65.9333 | 78.3667
2015-05-01 08:30 | 67.3 | 72.85 | 67.9333 | 78.6167
2015-05-01 08:45 | 66.55 | 73.6 | 69.9333 | 78.8667
2015-05-01 09:00 | 66.0667 | 74.4667 | 71.7 | 79.35
2015-05-01 09:15 | 66.3167 | 75.4667 | 73.2 | 80.1
2015-05-01 09:30 | 66.5667 | 76.4667 | 74.7 | 80.85
2015-05-01 09:45 | 66.8167 | 77.4667 | 76.2 | 81.6
2015-05-01 10:00 | 67.0667 | 78.35 | 77.4667 | 82.2333
2015-05-01 10:15 | 67.3167 | 79.1 | 78.4667 | 82.7333
2015-05-01 10:30 | 67.5667 | 79.85 | 79.4667 | 83.2333
2015-05-01 10:45 | 67.8167 | 80.6 | 80.4667 | 83.7333
2015-05-01 11:00 | 68.2667 | 81.2333 | 81.1167 | 84.5833
2015-05-01 11:15 | 69.2667 | 81.7333 | 81.3667 | 85.8333
2015-05-01 11:30 | 70.2667 | 82.2333 | 81.6167 | 87.0833
2015-05-01 11:45 | 71.2667 | 82.7333 | 81.8667 | 88.3333
2015-05-01 12:00 | 71.9333 | 82.7667 | 82.1167 | 89.1167
2015-05-01 12:15 | 71.6833 | 82.2667 | 82.3667 | 89.3667
2015-05-01 12:30 | 71.4333 | 81.7667 | 82.6167 | 89.6167
2015-05-01 12:45 | 71.1833 | 81.2667 | 82.8667 | 89.8667
2015-05-01 13:00 | 70.907 | 80.7667 | 83.1167 | 90.2333
2015-05-01 13:15 | 70.5581 | 80.2667 | 83.3667 | 90.7333
2015-05-01 13:30 | 70.2093 | 79.7667 | 83.6167 | 91.2333
2015-05-01 13:45 | 68.9412 | 79.2667 | 83.8667 | 91.7333
2015-05-01 14:00 | 66.9333 | 78.8833 | 84 | 92
2015-05-01 14:15 | 66.6833 | 78.6333 | 84 | 92
2015-05-01 14:30 | 66.4333 | 78.3833 | 84 | 92
2015-05-01 14:45 | 66.1833 | 78.1333 | 84 | 92
2015-05-01 15:00 | 65.9333 | 77.7667 | 84 | 91.8833
2015-05-01 15:15 | 65.6833 | 77.2667 | 84 | 91.6333
2015-05-01 15:30 | 65.4333 | 76.7667 | 84 | 91.3833
2015-05-01 15:45 | 65.1833 | 76.2667 | 84 | 91.1333
2015-05-01 16:00 | 64.8 | 75.8833 | 84 | 91.1167
2015-05-01 16:15 | 64.05 | 75.6333 | 84 | 91.3667
2015-05-01 16:30 | 63.3 | 75.3833 | 84 | 91.6167
2015-05-01 16:45 | 62.55 | 75.1333 | 84 | 91.8667
2015-05-01 17:00 | 61.8 | 74.5333 | 83.7667 | 91.8833
2015-05-01 17:15 | 61.05 | 73.5333 | 83.2667 | 91.6333
2015-05-01 17:30 | 60.3 | 72.5333 | 82.7667 | 91.3833
2015-05-01 17:45 | 59.55 | 71.5333 | 82.2667 | 91.1333
2015-05-01 18:00 | 58.8667 | 70.4167 | 81.65 | 90.5333
2015-05-01 18:15 | 58.3667 | 69.1667 | 80.9 | 89.5333
2015-05-01 18:30 | 57.8667 | 67.9167 | 80.15 | 88.5333
2015-05-01 18:45 | 57.3667 | 66.6667 | 79.4 | 87.5333
2015-05-01 19:00 | 57 | 65.7667 | 78.4167 | 86.5333
2015-05-01 19:15 | 57 | 65.2667 | 77.1667 | 85.5333
2015-05-01 19:30 | 57 | 64.7667 | 75.9167 | 84.5333
2015-05-01 19:45 | 57 | 64.2667 | 74.6667 | 83.5333
2015-05-01 20:00 | 56.9333 | 63.65 | 73.65 | 82.5333
2015-05-01 20:15 | 56.6833 | 62.9 | 72.9 | 81.5333
2015-05-01 20:30 | 56.4333 | 62.15 | 72.15 | 80.5333
2015-05-01 20:45 | 56.1833 | 61.4 | 71.4 | 79.5333
2015-05-01 21:00 | 56 | 60.8833 | 70.65 | 78.7667
2015-05-01 21:15 | 56 | 60.6333 | 69.9 | 78.2667
2015-05-01 21:30 | 56 | 60.3833 | 69.15 | 77.7667
2015-05-01 21:45 | 56 | 60.1333 | 68.4 | 77.2667
2015-05-01 22:00 | 55.9333 | 59.7667 | 67.8833 | 76.5333
2015-05-01 22:15 | 55.6833 | 59.2667 | 67.6333 | 75.5333
2015-05-01 22:30 | 55.4333 | 58.7667 | 67.3833 | 74.5333
2015-05-01 22:45 | 55.1833 | 58.2667 | 67.1333 | 73.5333
2015-05-01 23:00 | 54.9333 | 57.8833 | 66.7667 | 73
2015-05-01 23:15 | 54.6833 | 57.6333 | 66.2667 | 73
2015-05-01 23:30 | 54.4333 | 57.3833 | 65.7667 | 73
2015-05-01 23:45 | 54.1833 | 57.1333 | 65.2667 | 73
2015-05-02 | 54 | 57 | 64.8833 | 72.4167
2015-05-02 00:15 | 54 | 57 | 64.6333 | 71.1667
2015-05-02 00:30 | 54 | 57 | 64.3833 | 69.9167
2015-05-02 00:45 | 54 | 57 | 64.1333 | 68.6667
2015-05-02 01:00 | 53.9333 | 56.2222 | 63.8833 | 67.7667
2015-05-02 01:15 | 53.6833 | 55 | 63.6333 | 67.2667
2015-05-02 01:30 | 53.4333 | 55 | 63.3833 | 66.7667
2015-05-02 01:45 | 53.1833 | 55 | 63.1333 | 66.2667
2015-05-02 02:00 | 53.2105 | 54.7667 | 62.8833 | 65.8833
2015-05-02 02:15 | 54 | 54.2667 | 62.6333 | 65.6333
2015-05-02 02:30 | 54 | 53.7667 | 62.3833 | 65.3833
2015-05-02 02:45 | 54 | 53.2667 | 62.1333 | 65.1333
2015-05-02 03:00 | 54 | 53 | 61.8833 | 64.8833
2015-05-02 03:15 | 53.82 | 53 | 61.6333 | 64.6333
2015-05-02 03:30 | 53.52 | 53 | 61.3833 | 64.3833
2015-05-02 03:45 | 53.22 | 53 | 61.1333 | 64.1333
2015-05-02 04:00 | 53.0667 | 52.8833 | 60.7667 | 63.8833
2015-05-02 04:15 | 53.3167 | 52.6333 | 60.2667 | 63.6333
2015-05-02 04:30 | 53.5667 | 52.3833 | 59.7667 | 63.3833
2015-05-02 04:45 | 53.8167 | 52.1333 | 59.2667 | 63.1333
2015-05-02 05:00 | 53.9333 | 52.2745 | 58.7667 | 63.1167
2015-05-02 05:15 | 53.6833 | 52.8627 | 58.2667 | 63.3667
2015-05-02 05:30 | 53.4333 | 53.451 | 57.7667 | 63.6167
2015-05-02 05:45 | 53.1833 | 53.8889 | 57.2667 | 63.8667
2015-05-02 06:00 | 53.0667 | 53.3889 | 57 | 64.7
2015-05-02 06:15 | 53.3167 | 54.0952 | 57 | 66.2
2015-05-02 06:30 | 53.5667 | 54.4524 | 57 | 67.7
2015-05-02 06:45 | 53.8167 | 54.8095 | 57 | 69.2
2015-05-02 07:00 | 54.2 | 55.35 | 57.7 | 70.4667
2015-05-02 07:15 | 54.95 | 56.1 | 59.2 | 71.4667
2015-05-02 07:30 | 55.7 | 56.85 | 60.7 | 72.4667
2015-05-02 07:45 | 56.45 | 57.6 | 62.2 | 73.4667
2015-05-02 08:00 | 57.2 | 58.6364 | 63.5833 | 74.4667
2015-05-02 08:15 | 57.95 | 59.6735 | 64.8333 | 75.4667
2015-05-02 08:30 | 58.7 | 60.5918 | 66.0833 | 76.4667
2015-05-02 08:45 | 59.45 | 61.5102 | 67.3333 | 77.4667
2015-05-02 09:00 | 60.1333 | 62.4667 | 68.7 | 78.5833
2015-05-02 09:15 | 60.6333 | 63.4667 | 70.2 | 79.8333
2015-05-02 09:30 | 61.1333 | 64.4667 | 71.7 | 81.0833
2015-05-02 09:45 | 61.6333 | 65.4667 | 73.2 | 82.3333
2015-05-02 10:00 | 62 | 66.35 | 74.4667 | 83.2333
2015-05-02 10:15 | 62 | 67.1 | 75.4667 | 83.7333
2015-05-02 10:30 | 62 | 67.85 | 76.4667 | 84.2333
2015-05-02 10:45 | 62 | 68.6 | 77.4667 | 84.7333
2015-05-02 11:00 | 62.1333 | 69.35 | 78.35 | 85.1167
2015-05-02 11:15 | 62.6333 | 70.1 | 79.1 | 85.3667
2015-05-02 11:30 | 63.1333 | 70.85 | 79.85 | 85.6167
2015-05-02 11:45 | 63.6333 | 71.6 | 80.6 | 85.8667
2015-05-02 12:00 | 64.1333 | 72.1167 | 81.2333 | 86.4667
2015-05-02 12:15 | 64.6333 | 72.3667 | 81.7333 | 87.4667
2015-05-02 12:30 | 65.1333 | 72.6167 | 82.2333 | 88.4667
2015-05-02 12:45 | 65.6333 | 72.8667 | 82.7333 | 89.4667
2015-05-02 13:00 | 66 | 72.8833 | 83.1167 | 89.8833
2015-05-02 13:15 | 66 | 72.6333 | 83.3667 | 89.6333
2015-05-02 13:30 | 66 | 72.3833 | 83.6167 | 89.3833
2015-05-02 13:45 | 66 | 72.1333 | 83.8667 | 89.1333
2015-05-02 14:00 | 65.9333 | 72 | 84.1167 | 89.1167
2015-05-02 14:15 | 65.6833 | 72 | 84.3667 | 89.3667
2015-05-02 14:30 | 65.4333 | 72 | 84.6167 | 89.6167
2015-05-02 14:45 | 65.1833 | 72 | 84.8667 | 89.8667
2015-05-02 15:00 | 64.8667 | 71.7667 | 85.2333 | 89.8833
2015-05-02 15:15 | 64.3667 | 71.2667 | 85.7333 | 89.6333
2015-05-02 15:30 | 63.8667 | 70.7667 | 86.2333 | 89.3833
2015-05-02 15:45 | 63.3667 | 70.2667 | 86.7333 | 89.1333
2015-05-02 16:00 | 62.8667 | 69.7667 | 86.7667 | 89
2015-05-02 16:15 | 62.3667 | 69.2667 | 86.2667 | 89
2015-05-02 16:30 | 61.8667 | 68.7667 | 85.7667 | 89
2015-05-02 16:45 | 61.3667 | 68.2667 | 85.2667 | 89
2015-05-02 17:00 | 60.8667 | 67.65 | 84.7667 | 88.8833
2015-05-02 17:15 | 60.3667 | 66.9 | 84.2667 | 88.6333
2015-05-02 17:30 | 59.8667 | 66.15 | 83.7667 | 88.3833
2015-05-02 17:45 | 59.3667 | 65.4 | 83.2667 | 88.1333
2015-05-02 18:00 | 58.8667 | 64.65 | 82.5333 | 87.5333
2015-05-02 18:15 | 58.3667 | 63.9 | 81.5333 | 86.5333
2015-05-02 18:30 | 57.8667 | 63.15 | 80.5333 | 85.5333
2015-05-02 18:45 | 57.3667 | 62.4 | 79.5333 | 84.5333
2015-05-02 19:00 | 56.8667 | 61.7667 | 78.5333 | 83.4167
2015-05-02 19:15 | 56.3667 | 61.2667 | 77.5333 | 82.1667
2015-05-02 19:30 | 55.8667 | 60.7667 | 76.5333 | 80.9167
2015-05-02 19:45 | 55.3667 | 60.2667 | 75.5333 | 79.6667
2015-05-02 20:00 | 55 | 59.7667 | 74.65 | 78.5333
2015-05-02 20:15 | 55 | 59.2667 | 73.9 | 77.5333
2015-05-02 20:30 | 55 | 58.7667 | 73.15 | 76.5333
2015-05-02 20:45 | 55 | 58.2667 | 72.4 | 75.5333
2015-05-02 21:00 | 54.9333 | 57.7667 | 71.65 | 74.5333
2015-05-02 21:15 | 54.6833 | 57.2667 | 70.9 | 73.5333
2015-05-02 21:30 | 54.4333 | 56.7667 | 70.15 | 72.5333
2015-05-02 21:45 | 54.1833 | 56.2667 | 69.4 | 71.5333
2015-05-02 22:00 | 54 | 56 | 68.8833 | 70.5333
2015-05-02 22:15 | 54 | 56 | 68.6333 | 69.5333
2015-05-02 22:30 | 54 | 56 | 68.3833 | 68.5333
2015-05-02 22:45 | 54 | 56 | 68.1333 | 67.5333
2015-05-02 23:00 | 53.9333 | 55.8833 | 67.7667 | 66.8833
2015-05-02 23:15 | 53.6833 | 55.6333 | 67.2667 | 66.6333
2015-05-02 23:30 | 53.4333 | 55.3833 | 66.7667 | 66.3833
2015-05-02 23:45 | 53.1833 | 55.1333 | 66.2667 | 66.1333
2015-05-03 | 53 | 54.8833 | 65.8833 | 66
2015-05-03 00:15 | 53 | 54.6333 | 65.6333 | 66
2015-05-03 00:30 | 53 | 54.3833 | 65.3833 | 66
2015-05-03 00:45 | 53 | 54.1333 | 65.1333 | 66
2015-05-03 01:00 | 53.0667 | 53.8833 | 64.8833 | 65.5333
2015-05-03 01:15 | 53.3167 | 53.6333 | 64.6333 | 64.5333
2015-05-03 01:30 | 53.5667 | 53.3833 | 64.3833 | 63.5333
2015-05-03 01:45 | 53.8167 | 53.1333 | 64.1333 | 62.5333
2015-05-03 02:00 | 53.9333 | 53 | 63.8833 | 62.2333
2015-05-03 02:15 | 53.6833 | 53 | 63.6333 | 62.7333
2015-05-03 02:30 | 53.4333 | 53 | 63.3833 | 63.2333
2015-05-03 02:45 | 53.1833 | 53 | 63.1333 | 63.7333
2015-05-03 03:00 | 52.9333 | 52.8833 | 62.8833 | 63.4167
2015-05-03 03:15 | 52.6833 | 52.6333 | 62.6333 | 62.1667
2015-05-03 03:30 | 52.4333 | 52.3833 | 62.3833 | 60.9167
2015-05-03 03:45 | 52.1833 | 52.1333 | 62.1333 | 59.6667
2015-05-03 04:00 | 52 | 52 | 61.8833 | 58.5333
2015-05-03 04:15 | 52 | 52 | 61.6333 | 57.5333
2015-05-03 04:30 | 52 | 52 | 61.3833 | 56.5333
2015-05-03 04:45 | 52 | 52 | 61.1333 | 55.5333
2015-05-03 05:00 | 52 | 52 | 60.7667 | 55.1167
2015-05-03 05:15 | 52 | 52 | 60.2667 | 55.3667
2015-05-03 05:30 | 52.2778 | 52 | 59.7667 | 55.6167
2015-05-03 05:45 | 52.6944 | 52 | 59.2667 | 55.8667
2015-05-03 06:00 | 53.1333 | 52.2333 | 59.1167 | 56.7
2015-05-03 06:15 | 53.6333 | 52.7333 | 59.3667 | 58.2
2015-05-03 06:30 | 54 | 53.2333 | 59.6167 | 59.7
2015-05-03 06:45 | 54 | 53.7333 | 59.8667 | 61.2
2015-05-03 07:00 | 54.2 | 54.35 | 60.4667 | 62.7
2015-05-03 07:15 | 54.95 | 55.1 | 61.4667 | 64.2
2015-05-03 07:30 | 55.7 | 55.85 | 62.4667 | 65.7
2015-05-03 07:45 | 56.45 | 56.6 | 63.4667 | 67.2
2015-05-03 08:00 | 57.1333 | 57.35 | 64.8167 | 68.7
2015-05-03 08:15 | 57.6333 | 58.1 | 66.5667 | 70.2
2015-05-03 08:30 | 58.1333 | 58.85 | 68.3167 | 71.7
2015-05-03 08:45 | 58.6333 | 59.6 | 70.0667 | 73.2
2015-05-03 09:00 | 59.1333 | 60.35 | 71.4667 | 74.4667
2015-05-03 09:15 | 59.6333 | 61.1 | 72.4667 | 75.4667
2015-05-03 09:30 | 60.1333 | 61.85 | 73.4667 | 76.4667
2015-05-03 09:45 | 60.6333 | 62.6 | 74.4667 | 77.4667
2015-05-03 10:00 | 61.0667 | 63.4667 | 75.4667 | 78.35
2015-05-03 10:15 | 61.3167 | 64.4667 | 76.4667 | 79.1
2015-05-03 10:30 | 61.5667 | 65.4667 | 77.4667 | 79.85
2015-05-03 10:45 | 61.8167 | 66.4667 | 78.4667 | 80.6
2015-05-03 11:00 | 62.1333 | 67.2333 | 79.35 | 81.35
2015-05-03 11:15 | 62.6333 | 67.7333 | 80.1 | 82.1
2015-05-03 11:30 | 63.1333 | 68.2333 | 80.85 | 82.85
2015-05-03 11:45 | 63.6333 | 68.7333 | 81.6 | 83.6
2015-05-03 12:00 | 64.0667 | 69 | 82.2333 | 84
2015-05-03 12:15 | 64.3167 | 69 | 82.7333 | 84
2015-05-03 12:30 | 64.5667 | 69 | 83.2333 | 84
2015-05-03 12:45 | 64.8167 | 69 | 83.7333 | 84
2015-05-03 13:00 | 64.9333 | 68.8833 | 84 | 84.1167
2015-05-03 13:15 | 64.6833 | 68.6333 | 84 | 84.3667
2015-05-03 13:30 | 64.4333 | 68.3833 | 84 | 84.6167
2015-05-03 13:45 | 64.1833 | 68.1333 | 84 | 84.8667
2015-05-03 14:00 | 64 | 68 | 83.7667 | 85.2333
2015-05-03 14:15 | 64 | 68 | 83.2667 | 85.7333
2015-05-03 14:30 | 64 | 68 | 82.7667 | 86.2333
2015-05-03 14:45 | 64 | 68 | 82.2667 | 86.7333
2015-05-03 15:00 | 63.9333 | 67.8833 | 81.65 | 87
2015-05-03 15:15 | 63.6833 | 67.6333 | 80.9 | 87
2015-05-03 15:30 | 63.4333 | 67.3833 | 80.15 | 87
2015-05-03 15:45 | 63.1833 | 67.1333 | 79.4 | 87
2015-05-03 16:00 | 62.8667 | 66.7667 | 78.65 | 86.8833
2015-05-03 16:15 | 62.3667 | 66.2667 | 77.9 | 86.6333
2015-05-03 16:30 | 61.8667 | 65.7667 | 77.15 | 86.3833
2015-05-03 16:45 | 61.3667 | 65.2667 | 76.4 | 86.1333
2015-05-03 17:00 | 60.8 | 64.65 | 76.1167 | 85.8833
2015-05-03 17:15 | 60.05 | 63.9 | 76.3667 | 85.6333
2015-05-03 17:30 | 59.3 | 63.15 | 76.6167 | 85.3833
2015-05-03 17:45 | 58.55 | 62.4 | 76.8667 | 85.1333
2015-05-03 18:00 | 57.8667 | 61.65 | 76.65 | 84.65
2015-05-03 18:15 | 57.3667 | 60.9 | 75.9 | 83.9
2015-05-03 18:30 | 56.8667 | 60.15 | 75.15 | 83.15
2015-05-03 18:45 | 56.3667 | 59.4 | 74.4 | 82.4
2015-05-03 19:00 | 55.9333 | 58.7667 | 73.7667 | 81.1833
2015-05-03 19:15 | 55.6833 | 58.2667 | 73.2667 | 79.4333
2015-05-03 19:30 | 55.4333 | 57.7667 | 72.7667 | 77.6833
2015-05-03 19:45 | 55.1833 | 57.2667 | 72.2667 | 75.9333
2015-05-03 20:00 | 54.9333 | 56.8833 | 72 | 74.5333
2015-05-03 20:15 | 54.6833 | 56.6333 | 72 | 73.5333
2015-05-03 20:30 | 54.4333 | 56.3833 | 72 | 72.5333
2015-05-03 20:45 | 54.1833 | 56.1333 | 72 | 71.5333
2015-05-03 21:00 | 54 | 55.8833 | 71.8833 | 70.5333
2015-05-03 21:15 | 54 | 55.6333 | 71.6333 | 69.5333
2015-05-03 21:30 | 54 | 55.3833 | 71.3833 | 68.5333
2015-05-03 21:45 | 54 | 55.1333 | 71.1333 | 67.5333
2015-05-03 22:00 | 53.9333 | 55 | 70.8833 | 66.65
2015-05-03 22:15 | 53.6833 | 55 | 70.6333 | 65.9
2015-05-03 22:30 | 53.4333 | 55 | 70.3833 | 65.15
2015-05-03 22:45 | 53.1833 | 55 | 70.1333 | 64.4
2015-05-03 23:00 | 53 | 55 | 69.8833 | 63.65
2015-05-03 23:15 | 53 | 55 | 69.6333 | 62.9
2015-05-03 23:30 | 53 | 55 | 69.3833 | 62.15
2015-05-03 23:45 | 53 | 55 | 69.1333 | 61.4
2015-05-04 | 53 | 55.1167 | 69 | 60.8833
2015-05-04 00:15 | 53 | 55.3667 | 69 | 60.6333
2015-05-04 00:30 | 53 | 55.6167 | 68.8571 | 60.3833
2015-05-04 00:45 | 53 | 55.8667 | 66.6154 | 60.1333
2015-05-04 01:00 | 52.9333 | 55.8833 | 65.1167 | 59.8833
2015-05-04 01:15 | 52.6833 | 55.6333 | 65.3667 | 59.6333
2015-05-04 01:30 | 52.4333 | 55.3833 | 65.6167 | 59.3833
2015-05-04 01:45 | 52.1833 | 55.1333 | 65.8667 | 59.1333
2015-05-04 02:00 | 52 | 55 | 65.7667 | 58.7667
2015-05-04 02:15 | 52 | 55 | 65.2667 | 58.2667
2015-05-04 02:30 | 52 | 55 | 64.7667 | 57.7667
2015-05-04 02:45 | 52 | 55 | 64.2667 | 57.2667
2015-05-04 03:00 | 52 | 55 | 64 | 56.7667
2015-05-04 03:15 | 52 | 55 | 64 | 56.2667
2015-05-04 03:30 | 52 | 55 | 64 | 55.7667
2015-05-04 03:45 | 52 | 55 | 64 | 55.2667
2015-05-04 04:00 | 52 | 54.8833 | 64.2414 | 54.8833
2015-05-04 04:15 | 52 | 54.6333 | 64.7586 | 54.6333
2015-05-04 04:30 | 52 | 54.3833 | 64.4667 | 54.3833
2015-05-04 04:45 | 52 | 54.1333 | 64 | 54.1333
2015-05-04 05:00 | 52 | 54 | 64 | 54.1167
2015-05-04 05:15 | 52 | 54 | 64 | 54.3667
2015-05-04 05:30 | 52 | 54 | 64 | 54.6167
2015-05-04 05:45 | 52 | 54 | 64 | 54.8667
2015-05-04 06:00 | 52 | 54 | 64.1167 | 55.2333
2015-05-04 06:15 | 52 | 54 | 64.3667 | 55.7333
2015-05-04 06:30 | 52 | 54 | 64.6167 | 56.2333
2015-05-04 06:45 | 52 | 54 | 64.8667 | 56.7333
2015-05-04 07:00 | 52.0667 | 54 | 65.35 | 57.5833
2015-05-04 07:15 | 52.3167 | 54 | 66.1 | 58.8333
2015-05-04 07:30 | 52.5667 | 54 | 66.85 | 60.0833
2015-05-04 07:45 | 52.8167 | 54 | 67.6 | 61.3333
2015-05-04 08:00 | 53.069 | 54.35 | 68.35 | 62.35
2015-05-04 08:15 | 53.3276 | 55.1 | 69.1 | 63.1
2015-05-04 08:30 | 53.5862 | 55.85 | 69.85 | 63.85
2015-05-04 08:45 | 53.8448 | 56.6 | 70.6 | 64.6
2015-05-04 09:00 | 53 | 57 | 71.3684 | 65.5833
2015-05-04 09:15 | 53 | 57 | 72.0769 | 66.8333
2015-05-04 09:30 | 53 | 57 | 72.4615 | 68.0833
2015-05-04 09:45 | 53 | 57 | 72.8462 | 69.3333
2015-05-04 10:00 | 53.2424 | 57.5385 | 73.8571 | 70.4667
2015-05-04 10:15 | 54.1515 | 58.6923 | 73.551 | 71.4667
2015-05-04 10:30 | 55.037 | 59.8462 | 73.2449 | 72.4667
2015-05-04 10:45 | 55.5926 | 61 | 73 | 73.4667
2015-05-04 11:00 | 56.1333 | 61.35 | 73.6667 | 74.2333
2015-05-04 11:15 | 56.6333 | 62.1 | 75.0513 | 74.7333
2015-05-04 11:30 | 57.1333 | 62.85 | 75.8205 | 75.2333
2015-05-04 11:45 | 57.6333 | 63.6 | 76.5897 | 75.7333
2015-05-04 12:00 | 58.0667 | 64 | 77.1167 | 76.4667
2015-05-04 12:15 | 58.3167 | 64 | 77.3667 | 77.4667
2015-05-04 12:30 | 58.5667 | 64 | 77.6167 | 78.4667
2015-05-04 12:45 | 58.8167 | 64 | 77.8667 | 79.4667
2015-05-04 13:00 | 59.2963 | 64 | 78 | 80
2015-05-04 13:15 | 60.4074 | 64 | 78 | 80
2015-05-04 13:30 | 60.5758 | 64 | 78 | 80
2015-05-04 13:45 | 59.6667 | 64 | 78 | 80
2015-05-04 14:00 | 59 | 64 | 77.7667 | 80.2333
2015-05-04 14:15 | 59 | 64 | 77.2667 | 80.7333
2015-05-04 14:30 | 58.3 | 64 | 76.7667 | 81.2333
2015-05-04 14:45 | 57.55 | 64 | 76.2667 | 81.7333
2015-05-04 15:00 | 56.9333 | 63.8833 | 76 | 82.1167
2015-05-04 15:15 | 56.6833 | 63.6333 | 76 | 82.3667
2015-05-04 15:30 | 56.4333 | 63.3833 | 76 | 82.6167
2015-05-04 15:45 | 56.1833 | 63.1333 | 76 | 82.8667
2015-05-04 16:00 | 56 | 62.65 | 76 | 82.8833
2015-05-04 16:15 | 56 | 61.9 | 76 | 82.6333
2015-05-04 16:30 | 56 | 61.15 | 76 | 82.3833
2015-05-04 16:45 | 56 | 60.4 | 76 | 82.1333
2015-05-04 17:00 | 55.9333 | 59.7667 | 75.8727 | 81.7667
2015-05-04 17:15 | 55.6833 | 59.2667 | 75.6 | 81.2667
2015-05-04 17:30 | 55.4333 | 58.7667 | 75.3273 | 80.7667
2015-05-04 17:45 | 55.1833 | 58.2667 | 75.0545 | 80.2667
2015-05-04 18:00 | 54.9333 | 57.7667 | 74.3636 | 79.65
2015-05-04 18:15 | 54.6833 | 57.2667 | 71.9375 | 78.9
2015-05-04 18:30 | 54.4333 | 56.7667 | 70.3939 | 78.15
2015-05-04 18:45 | 54.1833 | 56.2667 | 69.4848 | 77.4
2015-05-04 19:00 | 54 | 55.7667 | 62.2143 | 76.7667
2015-05-04 19:15 | 54 | 55.2667 | 64.4 | 76.2667
2015-05-04 19:30 | 54 | 54.7667 | 62.3333 | 75.7667
2015-05-04 19:45 | 54 | 54.2667 | 62.5385 | 75.2667
2015-05-04 20:00 | 54 | 53.7667 | 63.3889 | 74.5333
2015-05-04 20:15 | 54 | 53.2667 | 64.2222 | 73.5333
2015-05-04 20:30 | 54 | 52.7667 | 65 | 72.5333
2015-05-04 20:45 | 54 | 52.2667 | 65 | 71.5333
2015-05-04 21:00 | 53.9333 | 52.1167 | 66 | 70.4167
2015-05-04 21:15 | 53.6833 | 52.3667 | 66 | 69.1667
2015-05-04 21:30 | 53.4333 | 52.6167 | 66.3429 | 67.9167
2015-05-04 21:45 | 53.1833 | 52.8667 | 66.7714 | 66.6667
2015-05-04 22:00 | 53.1429 | 53 | 67 | 65.65
2015-05-04 22:15 | 53.6786 | 53 | 67 | 64.9
2015-05-04 22:30 | 53.8125 | 53 | 66.6923 | 64.15
2015-05-04 22:45 | 53.3438 | 53 | 66.1154 | 63.4
2015-05-04 23:00 | 53 | 52.8833 | 67 | 62.7667
2015-05-04 23:15 | 53 | 52.6333 | 67 | 62.2667
2015-05-04 23:30 | 53 | 52.3833 | 67 | 61.7667
2015-05-04 23:45 | 53 | 52.1333 | 67 | 61.2667
2015-05-05 | 53 | 52 | 66.875 | 60.65
2015-05-05 00:15 | 53 | 52 | 66.6071 | 59.9
2015-05-05 00:30 | 53 | 52 | 66.3393 | 59.15
2015-05-05 00:45 | 53 | 52 | 66.0714 | 58.4
2015-05-05 01:00 | 52.9333 | 52 | 66 | 57.8833
2015-05-05 01:15 | 52.6833 | 52 | 66 | 57.6333
2015-05-05 01:30 | 52.4333 | 52 | 66 | 57.3833
2015-05-05 01:45 | 52.1833 | 52 | 66 | 57.1333
2015-05-05 02:00 | 52 | 51.8833 | 66 | 56.7667
2015-05-05 02:15 | 52 | 51.6333 | 66 | 56.2667
2015-05-05 02:30 | 52 | 51.3833 | 66 | 55.7667
2015-05-05 02:45 | 52 | 51.1333 | 66 | 55.2667
2015-05-05 03:00 | 52 | 51.1167 | 66 | 54.8833
2015-05-05 03:15 | 52 | 51.3667 | 66 | 54.6333
2015-05-05 03:30 | 52 | 51.6167 | 66 | 54.3833
2015-05-05 03:45 | 52 | 51.8667 | 66 | 54.1333
2015-05-05 04:00 | 52.0667 | 51.8833 | 66 | 53.8833
2015-05-05 04:15 | 52.3167 | 51.6333 | 66 | 53.6333
2015-05-05 04:30 | 52.5667 | 51.3833 | 66 | 53.3833
2015-05-05 04:45 | 52.8167 | 51.1333 | 66 | 53.1333
2015-05-05 05:00 | 53 | 51 | 64.7667 | 53.1167
2015-05-05 05:15 | 53 | 51 | 64.2667 | 53.3667
2015-05-05 05:30 | 53 | 51 | 63.7667 | 53.6167
2015-05-05 05:45 | 53 | 51 | 63.2667 | 53.8667
2015-05-05 06:00 | 53 | 51.35 | 63.1167 | 54.35
2015-05-05 06:15 | 53 | 52.1 | 63.3667 | 55.1
2015-05-05 06:30 | 53 | 52.85 | 63.6167 | 55.85
2015-05-05 06:45 | 53 | 53.6 | 63.8667 | 56.6
2015-05-05 07:00 | 53.1333 | 54.2333 | 64.4667 | 57.5833
2015-05-05 07:15 | 53.6333 | 54.7333 | 65.4667 | 58.8333
2015-05-05 07:30 | 54.1333 | 55.2333 | 66.4667 | 60.0833
2015-05-05 07:45 | 54.6333 | 55.7333 | 67.4667 | 61.3333
2015-05-05 08:00 | 55.1333 | 56.2333 | 68 | 62.35
2015-05-05 08:15 | 55.6333 | 56.7333 | 68 | 63.1
2015-05-05 08:30 | 56.1333 | 57.2333 | 68 | 63.85
2015-05-05 08:45 | 56.6333 | 57.7333 | 68 | 64.6
2015-05-05 09:00 | 57 | 58.4667 | 68.2333 | 65.4667
2015-05-05 09:15 | 57 | 59.4667 | 68.7333 | 66.4667
2015-05-05 09:30 | 57 | 60.4667 | 69.2333 | 67.4667
2015-05-05 09:45 | 57 | 61.4667 | 69.7333 | 68.4667
2015-05-05 10:00 | 57.2 | 62.4667 | 70.4667 | 69.35
2015-05-05 10:15 | 57.95 | 63.4667 | 71.4667 | 70.1
2015-05-05 10:30 | 58.7 | 64.4667 | 72.4667 | 70.85
2015-05-05 10:45 | 59.45 | 65.4667 | 73.4667 | 71.6
2015-05-05 11:00 | 60 | 66.35 | 74.35 | 72.5833
2015-05-05 11:15 | 60 | 67.1 | 75.1 | 73.8333
2015-05-05 11:30 | 60 | 67.85 | 75.85 | 75.0833
2015-05-05 11:45 | 60 | 68.6 | 76.6 | 76.3333
2015-05-05 12:00 | 60.0667 | 68.7667 | 77.2333 | 77.1167
2015-05-05 12:15 | 60.3167 | 68.2667 | 77.7333 | 77.3667
2015-05-05 12:30 | 60.5667 | 67.7667 | 78.2333 | 77.6167
2015-05-05 12:45 | 60.8167 | 67.2667 | 78.7333 | 77.8667
2015-05-05 13:00 | 61 | 67 | 79.1167 | 78.2333
2015-05-05 13:15 | 61 | 67 | 79.3667 | 78.7333
2015-05-05 13:30 | 61 | 67 | 79.6167 | 79.2333
2015-05-05 13:45 | 61 | 67 | 79.8667 | 79.7333
2015-05-05 14:00 | 60.9333 | 66.8833 | 80 | 80.1167
2015-05-05 14:15 | 60.6833 | 66.6333 | 80 | 80.3667
2015-05-05 14:30 | 60.4333 | 66.3833 | 80 | 80.6167
2015-05-05 14:45 | 60.1833 | 66.1333 | 80 | 80.8667
2015-05-05 15:00 | 59.9333 | 66 | 80.2333 | 80.8833
2015-05-05 15:15 | 59.6833 | 66 | 80.7333 | 80.6333
2015-05-05 15:30 | 59.4333 | 66 | 81.2333 | 80.3833
2015-05-05 15:45 | 59.1833 | 66 | 81.7333 | 80.1333
2015-05-05 16:00 | 58.8667 | 65.65 | 82.1167 | 80
2015-05-05 16:15 | 58.3667 | 64.9 | 82.3667 | 80
2015-05-05 16:30 | 57.8667 | 64.15 | 82.6167 | 80
2015-05-05 16:45 | 57.3667 | 63.4 | 82.8667 | 80
2015-05-05 17:00 | 56.9333 | 62.65 | 82.8833 | 79.7667
2015-05-05 17:15 | 56.6833 | 61.9 | 82.6333 | 79.2667
2015-05-05 17:30 | 56.4333 | 61.15 | 82.3833 | 78.7667
2015-05-05 17:45 | 56.1833 | 60.4 | 82.1333 | 78.2667
2015-05-05 18:00 | 55.9333 | 59.65 | 81.3 | 77.65
2015-05-05 18:15 | 55.6833 | 58.9 | 79.8 | 76.9
2015-05-05 18:30 | 55.4333 | 58.15 | 78.3 | 76.15
2015-05-05 18:45 | 55.1833 | 57.4 | 76.8 | 75.4
2015-05-05 19:00 | 54.9333 | 57 | 75.5333 | 74.5333
2015-05-05 19:15 | 54.6833 | 57 | 74.5333 | 73.5333
2015-05-05 19:30 | 54.4333 | 57 | 73.5333 | 72.5333
2015-05-05 19:45 | 54.1833 | 57 | 72.5333 | 71.5333
2015-05-05 20:00 | 54 | 57 | 71.7667 | 70.4167
2015-05-05 20:15 | 54 | 57 | 71.2667 | 69.1667
2015-05-05 20:30 | 54 | 57 | 70.7667 | 67.9167
2015-05-05 20:45 | 54 | 57 | 70.2667 | 66.6667
2015-05-05 21:00 | 53.9333 | 56.7667 | 69.7667 | 65.5333
2015-05-05 21:15 | 53.6833 | 56.2667 | 69.2667 | 64.5333
2015-05-05 21:30 | 53.4333 | 55.7667 | 68.7667 | 63.5333
2015-05-05 21:45 | 53.1833 | 55.2667 | 68.2667 | 62.5333
2015-05-05 22:00 | 53 | 54.7667 | 67.8833 | 61.7667
2015-05-05 22:15 | 53 | 54.2667 | 67.6333 | 61.2667
2015-05-05 22:30 | 53 | 53.7667 | 67.3833 | 60.7667
2015-05-05 22:45 | 53 | 53.2667 | 67.1333 | 60.2667
2015-05-05 23:00 | 52.9333 | 52.8833 | 66.8833 | 59.7667
2015-05-05 23:15 | 52.6833 | 52.6333 | 66.6333 | 59.2667
2015-05-05 23:30 | 52.4333 | 52.3833 | 66.3833 | 58.7667
2015-05-05 23:45 | 52.1833 | 52.1333 | 66.1333 | 58.2667
2015-05-06 | 52 | 51.8833 | 66 | 57.7667
2015-05-06 00:15 | 52 | 51.6333 | 66 | 57.2667
2015-05-06 00:30 | 52 | 51.3833 | 66 | 56.7667
2015-05-06 00:45 | 52 | 51.1333 | 66 | 56.2667
2015-05-06 01:00 | 52 | 50.8833 | 65.8833 | 55.7667
2015-05-06 01:15 | 52 | 50.6333 | 65.6333 | 55.2667
2015-05-06 01:30 | 52 | 50.3833 | 65.3833 | 54.7667
2015-05-06 01:45 | 52 | 50.1333 | 65.1333 | 54.2667
2015-05-06 02:00 | 51.9333 | 50 | 64.8833 | 53.8833
2015-05-06 02:15 | 51.6833 | 50 | 64.6333 | 53.6333
2015-05-06 02:30 | 51.4333 | 50 | 64.3833 | 53.3833
2015-05-06 02:45 | 51.1833 | 50 | 64.1333 | 53.1333
2015-05-06 03:00 | 51.2222 | 49.8833 | 63.8833 | 52.8833
2015-05-06 03:15 | 51.9762 | 49.6333 | 63.6333 | 52.6333
2015-05-06 03:30 | 51.619 | 49.3833 | 63.3833 | 52.3833
2015-05-06 03:45 | 51.2619 | 49.1333 | 63.1333 | 52.1333
2015-05-06 04:00 | 51.1818 | 49 | 63 | 51.8833
2015-05-06 04:15 | 51.8636 | 49 | 63 | 51.6333
2015-05-06 04:30 | 51.6842 | 49 | 63 | 51.3833
2015-05-06 04:45 | 51.2895 | 49 | 63 | 51.1333
2015-05-06 05:00 | 51.1026 | 48.8833 | 62.8833 | 51.1167
2015-05-06 05:15 | 51.4872 | 48.6333 | 62.6333 | 51.3667
2015-05-06 05:30 | 51.8718 | 48.3833 | 62.3833 | 51.6167
2015-05-06 05:45 | 51.5238 | 48.1333 | 62.1333 | 51.8667
2015-05-06 06:00 | 51.1333 | 48.4667 | 62.1167 | 52.35
2015-05-06 06:15 | 51.6333 | 49.4667 | 62.3667 | 53.1
2015-05-06 06:30 | 52.1333 | 50.4667 | 62.6167 | 53.85
2015-05-06 06:45 | 52.6333 | 51.4667 | 62.8667 | 54.6
2015-05-06 07:00 | 53.1333 | 52.2333 | 63.5833 | 55.35
2015-05-06 07:15 | 53.6333 | 52.7333 | 64.8333 | 56.1
2015-05-06 07:30 | 54.1333 | 53.2333 | 66.0833 | 56.85
2015-05-06 07:45 | 54.6333 | 53.7333 | 67.3333 | 57.6
2015-05-06 08:00 | 55.2 | 54.35 | 68.4667 | 58.35
2015-05-06 08:15 | 55.95 | 55.1 | 69.4667 | 59.1
2015-05-06 08:30 | 56.7 | 55.85 | 70.4667 | 59.85
2015-05-06 08:45 | 57.45 | 56.6 | 71.4667 | 60.6
2015-05-06 09:00 | 58 | 57.4667 | 72.7 | 61.2333
2015-05-06 09:15 | 58 | 58.4667 | 74.2 | 61.7333
2015-05-06 09:30 | 58 | 59.4667 | 75.7 | 62.2333
2015-05-06 09:45 | 58 | 60.4667 | 77.2 | 62.7333
2015-05-06 10:00 | 58.2 | 61.2333 | 78.1167 | 63.4667
2015-05-06 10:15 | 58.95 | 61.7333 | 78.3667 | 64.4667
2015-05-06 10:30 | 59.7 | 62.2333 | 78.6167 | 65.4667
2015-05-06 10:45 | 60.45 | 62.7333 | 78.8667 | 66.4667
2015-05-06 11:00 | 61.2927 | 63.35 | 79.2333 | 67.35
2015-05-06 11:15 | 62.3902 | 64.1 | 79.7333 | 68.1
2015-05-06 11:30 | 63.4878 | 64.85 | 80.2333 | 68.85
2015-05-06 11:45 | 64 | 65.6 | 80.7333 | 69.6
2015-05-06 12:00 | 63.9333 | 66.35 | 81 | 70.2333
2015-05-06 12:15 | 63.6833 | 67.1 | 81 | 70.7333
2015-05-06 12:30 | 63.4333 | 67.85 | 81 | 71.2333
2015-05-06 12:45 | 63.1833 | 68.6 | 81 | 71.7333
2015-05-06 13:00 | 63 | 69 | 81.4667 | 72.1167
2015-05-06 13:15 | 63 | 69 | 82.4667 | 72.3667
2015-05-06 13:30 | 63 | 69 | 83.4667 | 72.6167
2015-05-06 13:45 | 63 | 69 | 84.4667 | 72.8667
2015-05-06 14:00 | 63 | 69.1167 | 85 | 73.2333
2015-05-06 14:15 | 63 | 69.3667 | 85 | 73.7333
2015-05-06 14:30 | 63 | 69.6167 | 85 | 74.2333
2015-05-06 14:45 | 63 | 69.8667 | 85 | 74.7333
2015-05-06 15:00 | 62.8667 | 69.8833 | 85.1167 | 75
2015-05-06 15:15 | 62.3667 | 69.6333 | 85.3667 | 75
2015-05-06 15:30 | 61.8667 | 69.3833 | 85.6167 | 75
2015-05-06 15:45 | 61.3667 | 69.1333 | 85.8667 | 75
2015-05-06 16:00 | 60.9333 | 68.65 | 85.7667 | 75
2015-05-06 16:15 | 60.6833 | 67.9 | 85.2667 | 75
2015-05-06 16:30 | 60.4333 | 67.15 | 84.7667 | 75
2015-05-06 16:45 | 60.1833 | 66.4 | 84.2667 | 75
2015-05-06 17:00 | 59.8 | 65.7667 | 83.65 | 74.7667
2015-05-06 17:15 | 59.05 | 65.2667 | 82.9 | 74.2667
2015-05-06 17:30 | 58.3 | 64.7667 | 82.15 | 73.7667
2015-05-06 17:45 | 57.55 | 64.2667 | 81.4 | 73.2667
2015-05-06 18:00 | 56.8667 | 63.65 | 80.65 | 72.65
2015-05-06 18:15 | 56.3667 | 62.9 | 79.9 | 71.9
2015-05-06 18:30 | 55.8667 | 62.15 | 79.15 | 71.15
2015-05-06 18:45 | 55.3667 | 61.4 | 78.4 | 70.4
2015-05-06 19:00 | 54.8667 | 60.7667 | 77.5333 | 69.7667
2015-05-06 19:15 | 54.3667 | 60.2667 | 76.5333 | 69.2667
2015-05-06 19:30 | 53.8667 | 59.7667 | 75.5333 | 68.7667
2015-05-06 19:45 | 53.3667 | 59.2667 | 74.5333 | 68.2667
2015-05-06 20:00 | 53 | 58.7667 | 73.7667 | 67.7667
2015-05-06 20:15 | 53 | 58.2667 | 73.2667 | 67.2667
2015-05-06 20:30 | 53 | 57.7667 | 72.7667 | 66.7667
2015-05-06 20:45 | 53 | 57.2667 | 72.2667 | 66.2667
2015-05-06 21:00 | 53 | 56.8833 | 71.7667 | 65.7667
2015-05-06 21:15 | 53 | 56.6333 | 71.2667 | 65.2667
2015-05-06 21:30 | 53 | 56.3833 | 70.7667 | 64.7667
2015-05-06 21:45 | 53 | 56.1333 | 70.2667 | 64.2667
2015-05-06 22:00 | 52.9333 | 55.65 | 70 | 63.7667
2015-05-06 22:15 | 52.6833 | 54.9 | 70 | 63.2667
2015-05-06 22:30 | 52.4333 | 54.15 | 70 | 62.7667
2015-05-06 22:45 | 52.1833 | 53.4 | 70 | 62.2667
2015-05-06 23:00 | 52 | 52.8833 | 69.7667 | 61.65
2015-05-06 23:15 | 52 | 52.6333 | 69.2667 | 60.9
2015-05-06 23:30 | 52 | 52.3833 | 68.7667 | 60.15
2015-05-06 23:45 | 52 | 52.1333 | 68.2667 | 59.4
2015-05-07 | 52 | 51.8833 | 68 | 59
2015-05-07 00:15 | 52 | 51.6333 | 68 | 59
2015-05-07 00:30 | 52 | 51.3833 | 68 | 59
2015-05-07 00:45 | 52 | 51.1333 | 68 | 59
2015-05-07 01:00 | 51.9333 | 51 | 68 | 58.8833
2015-05-07 01:15 | 51.6833 | 51 | 68 | 58.6333
2015-05-07 01:30 | 51.4333 | 51 | 68 | 58.3833
2015-05-07 01:45 | 51.1833 | 51 | 68 | 58.1333
2015-05-07 02:00 | 51 | 50.8833 | 67.8833 | 57.8833
2015-05-07 02:15 | 51 | 50.6333 | 67.6333 | 57.6333
2015-05-07 02:30 | 51 | 50.3833 | 67.3833 | 57.3833
2015-05-07 02:45 | 51 | 50.1333 | 67.1333 | 57.1333
2015-05-07 03:00 | 50.9333 | 50 | 67 | 56.7667
2015-05-07 03:15 | 50.6833 | 50 | 67 | 56.2667
2015-05-07 03:30 | 50.4333 | 50 | 67 | 55.7667
2015-05-07 03:45 | 50.1833 | 50 | 67 | 55.2667
2015-05-07 04:00 | 50 | 49.8833 | 66.7667 | 54.8833
2015-05-07 04:15 | 50 | 49.6333 | 66.2667 | 54.6333
2015-05-07 04:30 | 50 | 49.3833 | 65.7667 | 54.3833
2015-05-07 04:45 | 50 | 49.1333 | 65.2667 | 54.1333
2015-05-07 05:00 | 50.0667 | 49.1167 | 64.7667 | 54
2015-05-07 05:15 | 50.3167 | 49.3667 | 64.2667 | 54
2015-05-07 05:30 | 50.5667 | 49.6167 | 63.7667 | 54
2015-05-07 05:45 | 50.8167 | 49.8667 | 63.2667 | 54
2015-05-07 06:00 | 51.1333 | 50.1167 | 63.2333 | 54.2333
2015-05-07 06:15 | 51.6333 | 50.3667 | 63.7333 | 54.7333
2015-05-07 06:30 | 52.1333 | 50.6167 | 64.2333 | 55.2333
2015-05-07 06:45 | 52.6333 | 50.8667 | 64.7333 | 55.7333
2015-05-07 07:00 | 53.1333 | 51.2333 | 65.5833 | 56
2015-05-07 07:15 | 53.6333 | 51.7333 | 66.8333 | 56
2015-05-07 07:30 | 54.1333 | 52.2333 | 68.0833 | 56
2015-05-07 07:45 | 54.6333 | 52.7333 | 69.3333 | 56
2015-05-07 08:00 | 55.1333 | 53.35 | 70.5833 | 56
2015-05-07 08:15 | 55.6333 | 54.1 | 71.8333 | 56
2015-05-07 08:30 | 56.1333 | 54.85 | 73.0833 | 56
2015-05-07 08:45 | 56.6333 | 55.6 | 74.3333 | 56
2015-05-07 09:00 | 57.2 | 56.1167 | 75.4667 | 55.8833
2015-05-07 09:15 | 57.95 | 56.3667 | 76.4667 | 55.6333
2015-05-07 09:30 | 58.7 | 56.6167 | 77.4667 | 55.3833
2015-05-07 09:45 | 59.45 | 56.8667 | 78.4667 | 55.1333
2015-05-07 10:00 | 60.0667 | 57 | 79.35 | 55.4667
2015-05-07 10:15 | 60.3167 | 57 | 80.1 | 56.4667
2015-05-07 10:30 | 60.5667 | 57 | 80.85 | 57.4667
2015-05-07 10:45 | 60.8167 | 57 | 81.6 | 58.4667
2015-05-07 11:00 | 61 | 56.8833 | 82.2333 | 59.4667
2015-05-07 11:15 | 60.8039 | 56.6333 | 82.7333 | 60.4667
2015-05-07 11:30 | 60.5098 | 56.3833 | 83.2333 | 61.4667
2015-05-07 11:45 | 60.2157 | 56.1333 | 83.7333 | 62.4667
2015-05-07 12:00 | 60.0667 | 56.1167 | 84.1167 | 62.7586
2015-05-07 12:15 | 60.3167 | 56.3667 | 84.3667 | 62.2414
2015-05-07 12:30 | 60.5667 | 56.6167 | 84.6167 | 61.7241
2015-05-07 12:45 | 60.8167 | 56.8667 | 84.8667 | 61.2069
2015-05-07 13:00 | 61.2 | 57 | 85.1167 | 59.4444
2015-05-07 13:15 | 61.95 | 57 | 85.3667 | 56.7778
2015-05-07 13:30 | 62.7 | 57 | 85.6167 | 56.2273
2015-05-07 13:45 | 63.45 | 57 | 85.8667 | 59.6364
2015-05-07 14:00 | 64.1333 | 57.2333 | 86.35 | 61.4667
2015-05-07 14:15 | 64.6333 | 57.7333 | 87.1 | 62.4667
2015-05-07 14:30 | 65.1333 | 58.2333 | 87.85 | 63.4667
2015-05-07 14:45 | 65.6333 | 58.7333 | 88.6 | 64.4667
2015-05-07 15:00 | 65.7333 | 58.8833 | 89 | 64.2821
2015-05-07 15:15 | 64.7333 | 58.6333 | 89 | 62.7436
2015-05-07 15:30 | 63.7333 | 58.3833 | 89 | 61.2051
2015-05-07 15:45 | 62.7333 | 58.1333 | 89 | 58.5238
2015-05-07 16:00 | 62 | 57.7667 | 89 | 56.4615
2015-05-07 16:15 | 62 | 57.2667 | 89 | 55.6
2015-05-07 16:30 | 62 | 56.7667 | 89 | 54.9333
2015-05-07 16:45 | 62 | 56.2667 | 89 | 54.2667
2015-05-07 17:00 | 62.0667 | 56.1167 | 88.8833 | 53.8833
2015-05-07 17:15 | 62.3167 | 56.3667 | 88.6333 | 53.6333
2015-05-07 17:30 | 62.5667 | 56.6167 | 88.3833 | 53.3833
2015-05-07 17:45 | 62.8167 | 56.8667 | 88.1333 | 53.1333
2015-05-07 18:00 | 62.8 | 56.8833 | 87.65 | 53.1167
2015-05-07 18:15 | 62.05 | 56.6333 | 86.9 | 53.3667
2015-05-07 18:30 | 61.3 | 56.3833 | 86.15 | 53.6167
2015-05-07 18:45 | 60.55 | 56.1333 | 85.4 | 53.8667
2015-05-07 19:00 | 59.7333 | 55.8833 | 83.8333 | 54
2015-05-07 19:15 | 58.7333 | 55.6333 | 81.3333 | 54
2015-05-07 19:30 | 57.7333 | 55.3833 | 78.8333 | 54
2015-05-07 19:45 | 56.7333 | 55.1333 | 76.3333 | 54
2015-05-07 20:00 | 55.8667 | 55 | 75.1167 | 53.65
2015-05-07 20:15 | 55.3667 | 55 | 75.3667 | 52.9
2015-05-07 20:30 | 54.8667 | 55 | 75.6167 | 52.15
2015-05-07 20:45 | 54.3667 | 55 | 75.8667 | 51.4
2015-05-07 21:00 | 54 | 54.8158 | 76 | 51
2015-05-07 21:15 | 54 | 54.4211 | 76 | 51
2015-05-07 21:30 | 54 | 54.0263 | 76 | 51
2015-05-07 21:45 | 54 | 54 | 76 | 51
2015-05-07 22:00 | 53.9333 | 54 | 75.8833 | 50.8833
2015-05-07 22:15 | 53.6833 | 54 | 75.6333 | 50.6333
2015-05-07 22:30 | 53.4333 | 54 | 75.3833 | 50.3833
2015-05-07 22:45 | 53.1833 | 54 | 75.1333 | 50.1333
2015-05-07 23:00 | 52.9333 | 53.8833 | 74.8833 | 50
2015-05-07 23:15 | 52.6833 | 53.6333 | 74.6333 | 50
2015-05-07 23:30 | 52.4333 | 53.3833 | 74.3833 | 50
2015-05-07 23:45 | 52.1833 | 53.1333 | 74.1333 | 50
2015-05-08 | 52 | 53 | 73.8833 | 50
2015-05-08 00:15 | 52 | 53 | 73.6333 | 50
2015-05-08 00:30 | 52 | 53 | 73.3833 | 50
2015-05-08 00:45 | 52 | 53 | 73.1333 | 50
2015-05-08 01:00 | 52.0667 | 53 | 72.7667 | 50
2015-05-08 01:15 | 52.3167 | 53 | 72.2667 | 50
2015-05-08 01:30 | 52.5667 | 53 | 71.7667 | 50
2015-05-08 01:45 | 52.8167 | 53 | 71.2667 | 50
2015-05-08 02:00 | 53 | 52.8833 | 70.8833 | 50.1167
2015-05-08 02:15 | 53 | 52.6333 | 70.6333 | 50.3667
2015-05-08 02:30 | 53 | 52.3833 | 70.3833 | 50.6167
2015-05-08 02:45 | 53 | 52.1333 | 70.1333 | 50.8667
2015-05-08 03:00 | 52.9333 | 52 | 69.8833 | 51
2015-05-08 03:15 | 52.6833 | 52 | 69.6333 | 51
2015-05-08 03:30 | 52.4333 | 52 | 69.3833 | 51
2015-05-08 03:45 | 52.1833 | 52 | 69.1333 | 51
2015-05-08 04:00 | 51.8667 | 51.8833 | 69 | 51
2015-05-08 04:15 | 51.3667 | 51.6333 | 69 | 51
2015-05-08 04:30 | 50.8667 | 51.3833 | 69 | 51
2015-05-08 04:45 | 50.3667 | 51.1333 | 69 | 51
2015-05-08 05:00 | 50.0667 | 51 | 68.65 | 51.1167
2015-05-08 05:15 | 50.3167 | 51 | 67.9 | 51.3667
2015-05-08 05:30 | 50.5667 | 51 | 67.15 | 51.6167
2015-05-08 05:45 | 50.8167 | 51 | 66.4 | 51.8667
2015-05-08 06:00 | 51.2 | 51.35 | 66.2333 | 52
2015-05-08 06:15 | 51.95 | 52.1 | 66.7333 | 52
2015-05-08 06:30 | 52.7 | 52.85 | 67.2333 | 52
2015-05-08 06:45 | 53.45 | 53.6 | 67.7333 | 52
2015-05-08 07:00 | 54.2667 | 54.35 | 68.35 | 52.2333
2015-05-08 07:15 | 55.2667 | 55.1 | 69.1 | 52.7333
2015-05-08 07:30 | 56.2667 | 55.85 | 69.85 | 53.2333
2015-05-08 07:45 | 57.2667 | 56.6 | 70.6 | 53.7333
2015-05-08 08:00 | 58.0667 | 57.2333 | 71.5833 | 54.35
2015-05-08 08:15 | 58.3167 | 57.7333 | 72.8333 | 55.1
2015-05-08 08:30 | 58.5667 | 58.2333 | 74.0833 | 55.85
2015-05-08 08:45 | 58.8167 | 58.7333 | 75.3333 | 56.6
2015-05-08 09:00 | 59.1333 | 59.35 | 76.2333 | 57.2333
2015-05-08 09:15 | 59.6333 | 60.1 | 76.7333 | 57.7333
2015-05-08 09:30 | 60.1333 | 60.85 | 77.2333 | 58.2333
2015-05-08 09:45 | 60.6333 | 61.6 | 77.7333 | 58.7333
2015-05-08 10:00 | 61.0667 | 62.2333 | 78.4667 | 59.2333
2015-05-08 10:15 | 61.3167 | 62.7333 | 79.4667 | 59.7333
2015-05-08 10:30 | 61.5667 | 63.2333 | 80.4667 | 60.2333
2015-05-08 10:45 | 61.8167 | 63.7333 | 81.4667 | 60.7333
2015-05-08 11:00 | 62.0667 | 64.35 | 82.2333 | 61.1167
2015-05-08 11:15 | 62.3167 | 65.1 | 82.7333 | 61.3667
2015-05-08 11:30 | 62.5667 | 65.85 | 83.2333 | 61.6167
2015-05-08 11:45 | 62.8167 | 66.6 | 83.7333 | 61.8667
2015-05-08 12:00 | 63.2667 | 67.4667 | 84.35 | 62.1167
2015-05-08 12:15 | 64.2667 | 68.4667 | 85.1 | 62.3667
2015-05-08 12:30 | 65.2667 | 69.4667 | 85.85 | 62.6167
2015-05-08 12:45 | 66.2667 | 70.4667 | 86.6 | 62.8667
2015-05-08 13:00 | 67.0667 | 71 | 87.2333 | 63.1167
2015-05-08 13:15 | 67.3167 | 71 | 87.7333 | 63.3667
2015-05-08 13:30 | 67.5667 | 71 | 88.2333 | 63.6167
2015-05-08 13:45 | 67.8167 | 71 | 88.7333 | 63.8667
2015-05-08 14:00 | 67.8 | 70.8833 | 89.2333 | 64
2015-05-08 14:15 | 67.05 | 70.6333 | 89.7333 | 64
2015-05-08 14:30 | 66.3 | 70.3833 | 90.2333 | 64
2015-05-08 14:45 | 65.55 | 70.1333 | 90.7333 | 64
2015-05-08 15:00 | 64.9333 | 69.7667 | 91.1167 | 64.1167
2015-05-08 15:15 | 64.6833 | 69.2667 | 91.3667 | 64.3667
2015-05-08 15:30 | 64.4333 | 68.7667 | 91.6167 | 64.6167
2015-05-08 15:45 | 64.1833 | 68.2667 | 91.8667 | 64.8667
2015-05-08 16:00 | 63.8 | 67.7667 | 91.8833 | 64.8833
2015-05-08 16:15 | 63.05 | 67.2667 | 91.6333 | 64.6333
2015-05-08 16:30 | 62.3 | 66.7667 | 91.3833 | 64.3833
2015-05-08 16:45 | 61.55 | 66.2667 | 91.1333 | 64.1333
2015-05-08 17:00 | 60.8667 | 65.7667 | 90.65 | 64
2015-05-08 17:15 | 60.3667 | 65.2667 | 89.9 | 64
2015-05-08 17:30 | 59.8667 | 64.7667 | 89.15 | 64
2015-05-08 17:45 | 59.3667 | 64.2667 | 88.4 | 64
2015-05-08 18:00 | 58.7333 | 63.65 | 87.65 | 63.8833
2015-05-08 18:15 | 57.7333 | 62.9 | 86.9 | 63.6333
2015-05-08 18:30 | 56.7333 | 62.15 | 86.15 | 63.3833
2015-05-08 18:45 | 55.7333 | 61.4 | 85.4 | 63.1333
2015-05-08 19:00 | 55 | 60.65 | 84.5333 | 62.7667
2015-05-08 19:15 | 55 | 59.9 | 83.5333 | 62.2667
2015-05-08 19:30 | 55 | 59.15 | 82.5333 | 61.7667
2015-05-08 19:45 | 55 | 58.4 | 81.5333 | 61.2667
2015-05-08 20:00 | 54.9333 | 57.65 | 80.5333 | 60.7667
2015-05-08 20:15 | 54.6833 | 56.9 | 79.5333 | 60.2667
2015-05-08 20:30 | 54.4333 | 56.15 | 78.5333 | 59.7667
2015-05-08 20:45 | 54.1833 | 55.4 | 77.5333 | 59.2667
2015-05-08 21:00 | 54 | 54.8833 | 76.65 | 58.8833
2015-05-08 21:15 | 54 | 54.6333 | 75.9 | 58.6333
2015-05-08 21:30 | 54 | 54.3833 | 75.15 | 58.3833
2015-05-08 21:45 | 54 | 54.1333 | 74.4 | 58.1333
2015-05-08 22:00 | 53.9333 | 54 | 74 | 58.1167
2015-05-08 22:15 | 53.6833 | 54 | 73.3636 | 58.3667
2015-05-08 22:30 | 53.4333 | 54 | 73 | 58.6167
2015-05-08 22:45 | 53.1833 | 54 | 73 | 58.8667
2015-05-08 23:00 | 53.4444 | 54 | 73 | 59
2015-05-08 23:15 | 54 | 54 | 73 | 59
2015-05-08 23:30 | 54 | 54.1786 | 73 | 59
2015-05-08 23:45 | 54 | 54.7143 | 73 | 59
2015-05-09 | 52.0667 | 55 | 72.8833 | 59
2015-05-09 00:15 | 52.3167 | 55 | 72.6333 | 59
2015-05-09 00:30 | 52.5667 | 55 | 72.3833 | 59
2015-05-09 00:45 | 52.8167 | 55 | 72.1333 | 59
2015-05-09 01:00 | 53 | 55 | 71.8833 | 59
2015-05-09 01:15 | 53 | 55 | 71.6333 | 59
2015-05-09 01:30 | 53 | 55 | 71.3833 | 59
2015-05-09 01:45 | 53 | 55 | 71.1333 | 59
2015-05-09 02:00 | 53 | 54.8833 | 70.7667 | 58.8833
2015-05-09 02:15 | 53 | 54.6333 | 70.2667 | 58.6333
2015-05-09 02:30 | 53 | 54.3833 | 69.7667 | 58.3833
2015-05-09 02:45 | 53 | 54.1333 | 69.2667 | 58.1333
2015-05-09 03:00 | 53 | 54 | 68.7667 | 58.1167
2015-05-09 03:15 | 53 | 54 | 68.2667 | 58.3667
2015-05-09 03:30 | 53 | 54 | 67.7667 | 58.6167
2015-05-09 03:45 | 53 | 54 | 67.2667 | 58.8667
2015-05-09 04:00 | 53 | 54 | 66.7667 | 59
2015-05-09 04:15 | 53 | 54 | 66.2667 | 59
2015-05-09 04:30 | 53 | 54 | 65.7667 | 59
2015-05-09 04:45 | 53 | 54 | 65.2667 | 59
2015-05-09 05:00 | 53 | 54 | 65 | 59.1167
2015-05-09 05:15 | 53 | 54 | 65 | 59.3667
2015-05-09 05:30 | 53 | 54 | 65 | 59.6167
2015-05-09 05:45 | 53 | 54 | 65 | 59.8667
2015-05-09 06:00 | 53.0667 | 54.1167 | 64.7667 | 60.1167
2015-05-09 06:15 | 53.3167 | 54.3667 | 64.2667 | 60.3667
2015-05-09 06:30 | 53.5667 | 54.6167 | 63.7667 | 60.6167
2015-05-09 06:45 | 53.8167 | 54.8667 | 63.2667 | 60.8667
2015-05-09 07:00 | 54 | 55.1167 | 63.7 | 61.4667
2015-05-09 07:15 | 54 | 55.3667 | 65.2 | 62.4667
2015-05-09 07:30 | 54 | 55.6167 | 66.7 | 63.4667
2015-05-09 07:45 | 54 | 55.8667 | 68.2 | 64.4667
2015-05-09 08:00 | 54.0909 | 56.1167 | 69.5833 | 65.35
2015-05-09 08:15 | 54.4318 | 56.3667 | 70.8333 | 66.1
2015-05-09 08:30 | 54.7727 | 56.6167 | 72.0833 | 66.85
2015-05-09 08:45 | 55 | 56.8667 | 73.3333 | 67.6
2015-05-09 09:00 | 55.0667 | 57.2333 | 74.35 | 68.1167
2015-05-09 09:15 | 55.3167 | 57.7333 | 75.1 | 68.3667
2015-05-09 09:30 | 55.5667 | 58.2333 | 75.85 | 68.6167
2015-05-09 09:45 | 55.8167 | 58.7333 | 76.6 | 68.8667
2015-05-09 10:00 | 56.0667 | 59.4667 | 77.2333 | 69.1167
2015-05-09 10:15 | 56.3167 | 60.4667 | 77.7333 | 69.3667
2015-05-09 10:30 | 56.5667 | 61.4667 | 78.2333 | 69.6167
2015-05-09 10:45 | 56.8167 | 62.4667 | 78.7333 | 69.8667
2015-05-09 11:00 | 57.2 | 63.1167 | 79.2333 | 70.1167
2015-05-09 11:15 | 57.95 | 63.3667 | 79.7333 | 70.3667
2015-05-09 11:30 | 58.7 | 63.6167 | 80.2333 | 70.6167
2015-05-09 11:45 | 59.45 | 63.8667 | 80.7333 | 70.8667
2015-05-09 12:00 | 60.0952 | 64.1167 | 81.1167 | 71.35
2015-05-09 12:15 | 60.4524 | 64.3667 | 81.3667 | 72.1
2015-05-09 12:30 | 60.8095 | 64.6167 | 81.6167 | 72.85
2015-05-09 12:45 | 61.3889 | 64.8667 | 81.8667 | 73.6
2015-05-09 13:00 | 62.1333 | 65.2333 | 82.2333 | 74.2333
2015-05-09 13:15 | 62.6333 | 65.7333 | 82.7333 | 74.7333
2015-05-09 13:30 | 63.1333 | 66.2333 | 83.2333 | 75.2333
2015-05-09 13:45 | 63.6333 | 66.7333 | 83.7333 | 75.7333
2015-05-09 14:00 | 63.9333 | 67 | 84.2333 | 76.1167
2015-05-09 14:15 | 63.6833 | 67 | 84.7333 | 76.3667
2015-05-09 14:30 | 63.4333 | 67 | 85.2333 | 76.6167
2015-05-09 14:45 | 63.1833 | 67 | 85.7333 | 76.8667
2015-05-09 15:00 | 62.8 | 66.8833 | 86.2333 | 77
2015-05-09 15:15 | 62.05 | 66.6333 | 86.7333 | 77
2015-05-09 15:30 | 61.3 | 66.3833 | 87.2333 | 77
2015-05-09 15:45 | 60.55 | 66.1333 | 87.7333 | 77
2015-05-09 16:00 | 59.7333 | 65.7667 | 88 | 76.8833
2015-05-09 16:15 | 58.7333 | 65.2667 | 88 | 76.6333
2015-05-09 16:30 | 57.7333 | 64.7667 | 88 | 76.3833
2015-05-09 16:45 | 56.7333 | 64.2667 | 88 | 76.1333
2015-05-09 17:00 | 55.7143 | 63.5333 | 88 | 75.8833
2015-05-09 17:15 | 55 | 62.5333 | 88 | 75.6333
2015-05-09 17:30 | 55 | 61.5333 | 88 | 75.3833
2015-05-09 17:45 | 55 | 60.5333 | 88 | 75.1333
2015-05-09 18:00 | 55 | 59.65 | 87.5333 | 74.7667
2015-05-09 18:15 | 55 | 58.9 | 86.5333 | 74.2667
2015-05-09 18:30 | 55 | 58.15 | 85.5333 | 73.7667
2015-05-09 18:45 | 55 | 57.4 | 84.5333 | 73.2667
2015-05-09 19:00 | 54.9333 | 56.7667 | 83.1833 | 72.7667
2015-05-09 19:15 | 54.6833 | 56.2667 | 81.4333 | 72.2667
2015-05-09 19:30 | 54.4333 | 55.7667 | 79.6833 | 71.7667
2015-05-09 19:45 | 54.1833 | 55.2667 | 77.9333 | 71.2667
2015-05-09 20:00 | 54 | 55 | 76.1833 | 70.7667
2015-05-09 20:15 | 54 | 55 | 74.4333 | 70.2667
2015-05-09 20:30 | 54 | 55 | 72.6833 | 69.7667
2015-05-09 20:45 | 54 | 55 | 70.9333 | 69.2667
2015-05-09 21:00 | 54 | 55 | 69.65 | 69
2015-05-09 21:15 | 54 | 55 | 68.9 | 69
2015-05-09 21:30 | 54 | 55 | 68.15 | 69
2015-05-09 21:45 | 54 | 55 | 67.4 | 69
2015-05-09 22:00 | 54 | 55 | 67 | 68.7667
2015-05-09 22:15 | 54 | 55 | 67 | 68.2667
2015-05-09 22:30 | 53.8667 | 55 | 67 | 67.7667
2015-05-09 22:45 | 53.3667 | 55 | 67 | 67.2667
2015-05-09 23:00 | 53 | 55 | 66.8833 | 66.7667
2015-05-09 23:15 | 53 | 55 | 66.6333 | 66.2667
2015-05-09 23:30 | 53 | 55 | 66.3833 | 65.7667
2015-05-09 23:45 | 53 | 55 | 66.1333 | 65.2667
2015-05-10 | 52.9333 | 55 | 65.3333 | 64.7667
2015-05-10 00:15 | 52.6833 | 55 | 64 | 64.2667
2015-05-10 00:30 | 52.4333 | 55 | 63.875 | 63.7667
2015-05-10 00:45 | 52.1833 | 55 | 62 | 63.2667
2015-05-10 01:00 | 52 | 55 | 60.7667 | 62.7667
2015-05-10 01:15 | 52 | 55 | 60.2667 | 62.2667
2015-05-10 01:30 | 52 | 55 | 59.7667 | 61.7667
2015-05-10 01:45 | 52 | 55 | 59.2667 | 61.2667
2015-05-10 02:00 | 52 | 55 | 59 | 60.7667
2015-05-10 02:15 | 52 | 55 | 59 | 60.2667
2015-05-10 02:30 | 52 | 55 | 59 | 59.7667
2015-05-10 02:45 | 52 | 55 | 59 | 59.2667
2015-05-10 03:00 | 52 | 54.8833 | 59.4667 | 59
2015-05-10 03:15 | 52 | 54.6333 | 60.4667 | 59
2015-05-10 03:30 | 52 | 54.3833 | 61.4667 | 59
2015-05-10 03:45 | 52 | 54.1333 | 62.4667 | 59
2015-05-10 04:00 | 52 | 54 | 62.5333 | 58.8833
2015-05-10 04:15 | 52 | 54 | 61.5333 | 58.6333
2015-05-10 04:30 | 52 | 54 | 60.5333 | 58.3833
2015-05-10 04:45 | 52 | 54 | 59.5333 | 58.1333
2015-05-10 05:00 | 52 | 54 | 58.8833 | 58.1167
2015-05-10 05:15 | 52 | 54 | 58.6333 | 58.3667
2015-05-10 05:30 | 52 | 54 | 58.3833 | 58.6167
2015-05-10 05:45 | 52 | 54 | 58.1333 | 58.8667
2015-05-10 06:00 | 52 | 54.1167 | 58.1167 | 59.4667
2015-05-10 06:15 | 52 | 54.3667 | 58.3667 | 60.4667
2015-05-10 06:30 | 52 | 54.6167 | 58.6167 | 61.4667
2015-05-10 06:45 | 52 | 54.8667 | 58.8667 | 62.4667
2015-05-10 07:00 | 52.0667 | 55 | 59.4667 | 63.35
2015-05-10 07:15 | 52.3167 | 55.2692 | 60.4667 | 64.1
2015-05-10 07:30 | 52.5667 | 55.5577 | 61.4667 | 64.85
2015-05-10 07:45 | 52.8167 | 55.8462 | 62.4667 | 65.6
2015-05-10 08:00 | 53.0667 | 56.2188 | 63.4667 | 66.4667
2015-05-10 08:15 | 53.3167 | 56.6875 | 64.4667 | 67.4667
2015-05-10 08:30 | 53.5667 | 57.3571 | 65.4667 | 68.4667
2015-05-10 08:45 | 53.8167 | 58.4286 | 66.4667 | 69.4667
2015-05-10 09:00 | 54.1333 | 59.4667 | 67.35 | 70.4667
2015-05-10 09:15 | 54.6333 | 60.4667 | 68.1 | 71.4667
2015-05-10 09:30 | 55.1333 | 61.4667 | 68.85 | 72.4667
2015-05-10 09:45 | 55.6333 | 62.4667 | 69.6 | 73.4667
2015-05-10 10:00 | 56.1333 | 63.35 | 70.2333 | 74.4667
2015-05-10 10:15 | 56.6333 | 64.1 | 70.7333 | 75.4667
2015-05-10 10:30 | 57.2667 | 64.85 | 71.2333 | 76.4667
2015-05-10 10:45 | 58.2667 | 65.6 | 71.7333 | 77.4667
2015-05-10 11:00 | 59 | 66 | 72.35 | 78
2015-05-10 11:15 | 59 | 66 | 73.1 | 78
2015-05-10 11:30 | 59.0714 | 66 | 73.85 | 78
2015-05-10 11:45 | 59.6071 | 66 | 74.6 | 78
2015-05-10 12:00 | 60.0667 | 66.1167 | 75.35 | 78.4667
2015-05-10 12:15 | 60.3167 | 66.3667 | 76.1 | 79.4667
2015-05-10 12:30 | 60.5667 | 66.6167 | 76.85 | 80.4667
2015-05-10 12:45 | 60.8167 | 66.8667 | 77.6 | 81.4667
2015-05-10 13:00 | 60.9333 | 66.8833 | 78.1167 | 82.1167
2015-05-10 13:15 | 60.6833 | 66.6333 | 78.3667 | 82.3667
2015-05-10 13:30 | 60.4333 | 66.3833 | 78.6167 | 82.6167
2015-05-10 13:45 | 60.1833 | 66.1333 | 78.8667 | 82.8667
2015-05-10 14:00 | 60 | 66 | 79.2333 | 83.1167
2015-05-10 14:15 | 60 | 66 | 79.7333 | 83.3667
2015-05-10 14:30 | 60 | 66 | 80.2333 | 83.6167
2015-05-10 14:45 | 60 | 66 | 80.7333 | 83.8667
2015-05-10 15:00 | 59.9333 | 65.8833 | 81.1167 | 84.1167
2015-05-10 15:15 | 59.6833 | 65.6333 | 81.3667 | 84.3667
2015-05-10 15:30 | 59.4333 | 65.3833 | 81.6167 | 84.6167
2015-05-10 15:45 | 59.1833 | 65.1333 | 81.8667 | 84.8667
2015-05-10 16:00 | 58.9333 | 64.7667 | 82.1167 | 85
2015-05-10 16:15 | 58.6833 | 64.2667 | 82.3667 | 85
2015-05-10 16:30 | 58.4333 | 63.7667 | 82.6167 | 85
2015-05-10 16:45 | 58.1833 | 63.2667 | 82.8667 | 85
2015-05-10 17:00 | 57.8667 | 62.7667 | 83 | 84.7667
2015-05-10 17:15 | 57.3667 | 62.2667 | 83 | 84.2667
2015-05-10 17:30 | 56.8667 | 61.7667 | 83 | 83.7667
2015-05-10 17:45 | 56.3667 | 61.2667 | 83 | 83.2667
2015-05-10 18:00 | 55.9333 | 60.65 | 82.65 | 82.5333
2015-05-10 18:15 | 55.6833 | 59.9 | 81.9 | 81.5333
2015-05-10 18:30 | 55.4333 | 59.15 | 81.15 | 80.5333
2015-05-10 18:45 | 55.1833 | 58.4 | 80.4 | 79.5333
2015-05-10 19:00 | 55 | 57.7667 | 79.1833 | 78.7667
2015-05-10 19:15 | 55 | 57.2667 | 77.4333 | 78.2667
2015-05-10 19:30 | 55 | 56.7667 | 75.6833 | 77.7667
2015-05-10 19:45 | 55 | 56.2667 | 73.9333 | 77.2667
2015-05-10 20:00 | 55 | 55.7667 | 72.8833 | 76.65
2015-05-10 20:15 | 55 | 55.2667 | 72.6333 | 75.9
2015-05-10 20:30 | 55 | 54.7667 | 72.3833 | 75.15
2015-05-10 20:45 | 55 | 54.2667 | 72.1333 | 74.4
2015-05-10 21:00 | 54.9333 | 54 | 71.4167 | 73.65
2015-05-10 21:15 | 54.6833 | 54 | 70.1667 | 72.9
2015-05-10 21:30 | 54.4333 | 54 | 68.9167 | 72.15
2015-05-10 21:45 | 54.1833 | 54 | 67.6667 | 71.4
2015-05-10 22:00 | 54 | 54.1167 | 66.8833 | 70.7667
2015-05-10 22:15 | 54 | 54.3667 | 66.6333 | 70.2667
2015-05-10 22:30 | 54 | 54.6167 | 66.3833 | 69.7667
2015-05-10 22:45 | 54 | 54.8667 | 66.1333 | 69.2667
2015-05-10 23:00 | 53.9333 | 55 | 65.65 | 68.5333
2015-05-10 23:15 | 53.6833 | 55 | 64.9 | 67.5333
2015-05-10 23:30 | 53.4333 | 55 | 64.15 | 66.5333
2015-05-10 23:45 | 53.1833 | 55 | 63.4 | 65.5333
2015-05-11 | 53 | 54.7667 | 63.2333 | 64.7667
2015-05-11 00:15 | 53 | 54.2667 | 63.7333 | 64.2667
2015-05-11 00:30 | 53 | 53.7667 | 64.2333 | 63.7667
2015-05-11 00:45 | 53 | 53.2667 | 64.7333 | 63.2667
2015-05-11 01:00 | 53 | 52.8833 | 64.7667 | 62.8833
2015-05-11 01:15 | 53 | 52.6333 | 64.2667 | 62.6333
2015-05-11 01:30 | 53 | 52.3833 | 63.7667 | 62.3833
2015-05-11 01:45 | 53 | 52.1333 | 63.2667 | 62.1333
2015-05-11 02:00 | 53 | 52 | 62.5333 | 61.8833
2015-05-11 02:15 | 53 | 52 | 61.5333 | 61.6333
2015-05-11 02:30 | 53 | 52 | 60.5333 | 61.3833
2015-05-11 02:45 | 53 | 52 | 59.5333 | 61.1333
2015-05-11 03:00 | 53.0851 | 51.8833 | 58.7667 | 60.8833
2015-05-11 03:15 | 53.4043 | 51.6333 | 58.2667 | 60.6333
2015-05-11 03:30 | 53.7234 | 51.3833 | 57.7667 | 60.3833
2015-05-11 03:45 | 53.6364 | 51.1333 | 57.2667 | 60.1333
2015-05-11 04:00 | 52 | 51 | 57.2333 | 60
2015-05-11 04:15 | 52 | 51 | 57.7333 | 60
2015-05-11 04:30 | 52 | 51 | 58.2333 | 60
2015-05-11 04:45 | 52 | 51 | 58.7333 | 60
2015-05-11 05:00 | 52 | 51 | 58.5333 | 60
2015-05-11 05:15 | 52 | 51 | 57.5333 | 60
2015-05-11 05:30 | 52 | 51 | 56.5333 | 60
2015-05-11 05:45 | 52 | 51 | 55.5333 | 60
2015-05-11 06:00 | 52.2857 | 51.35 | 55.2333 | 60.4667
2015-05-11 06:15 | 53.3571 | 52.1 | 55.7333 | 61.4667
2015-05-11 06:30 | 53.8125 | 52.85 | 56.2333 | 62.4667
2015-05-11 06:45 | 53.3438 | 53.6 | 56.7333 | 63.4667
2015-05-11 07:00 | 53.1333 | 54.35 | 57.5833 | 64.4667
2015-05-11 07:15 | 53.6333 | 55.1 | 58.8333 | 65.4667
2015-05-11 07:30 | 54.1333 | 55.85 | 60.0833 | 66.4667
2015-05-11 07:45 | 54.6333 | 56.6 | 61.3333 | 67.4667
2015-05-11 08:00 | 55.0667 | 57.4667 | 62.4667 | 68.35
2015-05-11 08:15 | 55.3167 | 58.4667 | 63.4667 | 69.1
2015-05-11 08:30 | 55.5667 | 59.4667 | 64.4667 | 69.85
2015-05-11 08:45 | 55.8167 | 60.4667 | 65.4667 | 70.6
2015-05-11 09:00 | 56.0755 | 61.2333 | 66.4375 | 71.4667
2015-05-11 09:15 | 56.3585 | 61.7333 | 67 | 72.4667
2015-05-11 09:30 | 56.6415 | 62.2333 | 66.08 | 73.4667
2015-05-11 09:45 | 56.9245 | 62.7333 | 66.68 | 74.4667
2015-05-11 10:00 | 58.0667 | 63.2333 | 67.1167 | 75.35
2015-05-11 10:15 | 58.3167 | 63.7333 | 67.3667 | 76.1
2015-05-11 10:30 | 58.5667 | 64.2333 | 67.6167 | 76.85
2015-05-11 10:45 | 58.8167 | 64.7333 | 67.8667 | 77.6
2015-05-11 11:00 | 59.0667 | 65 | 68.1167 | 78.35
2015-05-11 11:15 | 59.3167 | 65 | 68.3667 | 79.1
2015-05-11 11:30 | 59.5667 | 65 | 68.6167 | 79.85
2015-05-11 11:45 | 59.8167 | 65 | 68.8667 | 80.6
2015-05-11 12:00 | 60.6667 | 64.7667 | 69.1167 | 81.2333
2015-05-11 12:15 | 60.7593 | 64.2667 | 69.3667 | 81.7333
2015-05-11 12:30 | 60.4815 | 63.7667 | 69.6167 | 82.2333
2015-05-11 12:45 | 60.2037 | 63.2667 | 69.8667 | 82.7333
2015-05-11 13:00 | 60 | 63.2333 | 70.1167 | 83.1167
2015-05-11 13:15 | 60 | 63.7333 | 70.3667 | 83.3667
2015-05-11 13:30 | 60 | 64.2333 | 70.6167 | 83.6167
2015-05-11 13:45 | 60 | 64.7333 | 70.8667 | 83.8667
2015-05-11 14:00 | 59.9333 | 64.7667 | 71 | 84
2015-05-11 14:15 | 59.6833 | 64.2667 | 71 | 84
2015-05-11 14:30 | 59.4333 | 63.7667 | 71 | 84
2015-05-11 14:45 | 59.1833 | 63.2667 | 71 | 84
2015-05-11 15:00 | 59 | 63 | 71.7 | 84
2015-05-11 15:15 | 59 | 63 | 71.76 | 84
2015-05-11 15:30 | 59 | 63 | 71.46 | 84
2015-05-11 15:45 | 59 | 63 | 71.16 | 84
2015-05-11 16:00 | 58.8667 | 62.65 | 71.1167 | 83.65
2015-05-11 16:15 | 58.3667 | 61.9 | 71.3667 | 82.9
2015-05-11 16:30 | 57.8667 | 61.15 | 71.6167 | 82.15
2015-05-11 16:45 | 57.3667 | 60.4 | 71.8667 | 81.4
2015-05-11 17:00 | 56.9333 | 59.7667 | 72 | 80.65
2015-05-11 17:15 | 56.6833 | 59.2667 | 72 | 79.9
2015-05-11 17:30 | 56.4333 | 58.7667 | 72 | 79.15
2015-05-11 17:45 | 56.1833 | 58.2667 | 72 | 78.4
2015-05-11 18:00 | 55.8667 | 57.7667 | 71.7667 | 77.4167
2015-05-11 18:15 | 55.3667 | 57.2667 | 71.2667 | 76.1667
2015-05-11 18:30 | 54.8667 | 56.7667 | 70.7667 | 74.9167
2015-05-11 18:45 | 54.3667 | 56.2667 | 70.2667 | 73.6667
2015-05-11 19:00 | 53.9333 | 55.7667 | 69.7667 | 72.4167
2015-05-11 19:15 | 53.6833 | 55.2667 | 69.2667 | 71.1667
2015-05-11 19:30 | 53.4333 | 54.7667 | 68.7667 | 69.9167
2015-05-11 19:45 | 53.1833 | 54.2667 | 68.2667 | 68.6667
2015-05-11 20:00 | 53 | 54 | 67.7667 | 67.65
2015-05-11 20:15 | 53 | 54 | 67.2667 | 66.9
2015-05-11 20:30 | 53 | 54 | 66.7667 | 66.15
2015-05-11 20:45 | 53 | 54 | 66.2667 | 65.4
2015-05-11 21:00 | 52.9333 | 53.8833 | 65.8627 | 64.65
2015-05-11 21:15 | 52.6833 | 53.6333 | 65.5686 | 63.9
2015-05-11 21:30 | 52.4333 | 53.3833 | 65.2745 | 63.15
2015-05-11 21:45 | 52.1833 | 53.1333 | 65 | 62.4
2015-05-11 22:00 | 52 | 52.8833 | 64.8833 | 61.7667
2015-05-11 22:15 | 52 | 52.6333 | 64.6333 | 61.2667
2015-05-11 22:30 | 52 | 52.3833 | 64.3833 | 60.7667
2015-05-11 22:45 | 52 | 52.1333 | 64.1333 | 60.2667
2015-05-11 23:00 | 52 | 51.8833 | 63.7667 | 59.65
2015-05-11 23:15 | 52 | 51.6333 | 63.2667 | 58.9
2015-05-11 23:30 | 52 | 51.3833 | 62.7667 | 58.15
2015-05-11 23:45 | 52 | 51.1333 | 62.2667 | 57.4
2015-05-12 | 51.9333 | 50.8833 | 62 | 56.8833
2015-05-12 00:15 | 51.6833 | 50.6333 | 61.95 | 56.6333
2015-05-12 00:30 | 51.4333 | 50.3833 | 61.575 | 56.3833
2015-05-12 00:45 | 51.1833 | 50.1333 | 61.2 | 56.1333
2015-05-12 01:00 | 51 | 49.7667 | 61 | 55.7667
2015-05-12 01:15 | 51 | 49.2667 | 61 | 55.2667
2015-05-12 01:30 | 51 | 48.7667 | 61 | 54.7667
2015-05-12 01:45 | 51 | 48.2667 | 61 | 54.2667
2015-05-12 02:00 | 51 | 48.1167 | 60.8627 | 53.8833
2015-05-12 02:15 | 51 | 48.3667 | 60.5686 | 53.6333
2015-05-12 02:30 | 51 | 48.6167 | 60.2745 | 53.3833
2015-05-12 02:45 | 51 | 48.8667 | 59.8889 | 53.1333
2015-05-12 03:00 | 51 | 48.8833 | 59 | 52.8833
2015-05-12 03:15 | 51 | 48.6333 | 59 | 52.6333
2015-05-12 03:30 | 51 | 48.3833 | 59 | 52.3833
2015-05-12 03:45 | 51 | 48.1333 | 59 | 52.1333
2015-05-12 04:00 | 51 | 47.8833 | 59 | 52
2015-05-12 04:15 | 51 | 47.6333 | 58.7667 | 52
2015-05-12 04:30 | 51 | 47.3833 | 58.2667 | 52
2015-05-12 04:45 | 51 | 47.1333 | 57.5333 | 52
2015-05-12 05:00 | 51.0667 | 47.2333 | 56.8833 | 52
2015-05-12 05:15 | 51.3167 | 47.7333 | 56.6333 | 52
2015-05-12 05:30 | 51.5667 | 48.2333 | 56.3833 | 52
2015-05-12 05:45 | 51.8167 | 48.7333 | 56.1333 | 52
2015-05-12 06:00 | 52.0667 | 49.4667 | 56 | 52.2333
2015-05-12 06:15 | 52.3167 | 50.4667 | 56 | 52.7333
2015-05-12 06:30 | 52.5667 | 51.4667 | 56 | 53.2333
2015-05-12 06:45 | 52.8167 | 52.4667 | 56 | 53.7333
2015-05-12 07:00 | 53.1333 | 53.4667 | 56 | 54.4667
2015-05-12 07:15 | 53.6333 | 54.4667 | 56 | 55.4667
2015-05-12 07:30 | 54.1333 | 55.4667 | 56 | 56.4667
2015-05-12 07:45 | 54.6333 | 56.4667 | 56 | 57.4667
2015-05-12 08:00 | 55.1333 | 57.2333 | 56 | 58.35
2015-05-12 08:15 | 55.6333 | 57.7333 | 56 | 59.1
2015-05-12 08:30 | 56.1333 | 58.2333 | 56.2 | 59.85
2015-05-12 08:45 | 56.6333 | 58.7333 | 56.7 | 60.6
2015-05-12 09:00 | 57 | 59.1167 | 57.5714 | 61.35
2015-05-12 09:15 | 57 | 59.3667 | 59 | 62.1
2015-05-12 09:30 | 57 | 59.6167 | 59.75 | 62.85
2015-05-12 09:45 | 57 | 59.8667 | 60 | 63.6
2015-05-12 10:00 | 57.1333 | 60.2333 | 60.4375 | 64.4667
2015-05-12 10:15 | 57.6333 | 60.7333 | 61.1364 | 65.4667
2015-05-12 10:30 | 58.1333 | 61.2333 | 61.4773 | 66.4667
2015-05-12 10:45 | 58.6333 | 61.7333 | 61.8182 | 67.4667
2015-05-12 11:00 | 59.1333 | 62.1167 | 62.5 | 68.1167
2015-05-12 11:15 | 59.6333 | 62.3667 | 63.5714 | 68.3667
2015-05-12 11:30 | 60.1333 | 62.6167 | 64.6429 | 68.6167
2015-05-12 11:45 | 60.6333 | 62.8667 | 65.7143 | 68.8667
2015-05-12 12:00 | 61 | 63.4375 | 67.3818 | 69.1167
2015-05-12 12:15 | 61 | 63.8636 | 68.2 | 69.3667
2015-05-12 12:30 | 61 | 63.5227 | 69.0182 | 69.6167
2015-05-12 12:45 | 61 | 63.1818 | 69.8364 | 69.8667
2015-05-12 13:00 | 61.0667 | 63 | 70.35 | 70.35
2015-05-12 13:15 | 61.3167 | 63 | 71.1 | 71.1
2015-05-12 13:30 | 61.5667 | 63 | 71.85 | 71.85
2015-05-12 13:45 | 61.8167 | 63 | 72.6 | 72.6
2015-05-12 14:00 | 61.9333 | 63.1167 | 72.8833 | 73.2333
2015-05-12 14:15 | 61.6833 | 63.3667 | 72.6333 | 73.7333
2015-05-12 14:30 | 61.4333 | 63.6167 | 72.3833 | 74.2333
2015-05-12 14:45 | 61.1833 | 63.8667 | 72.1333 | 74.7333
2015-05-12 15:00 | 60.8 | 64.1167 | 72 | 75
2015-05-12 15:15 | 60.05 | 64.3667 | 72 | 75
2015-05-12 15:30 | 59.3 | 64.6167 | 72 | 75
2015-05-12 15:45 | 58.55 | 64.8667 | 72 | 75
2015-05-12 16:00 | 57.8667 | 64.4167 | 71.8833 | 74.8833
2015-05-12 16:15 | 57.3667 | 63.1667 | 71.6333 | 74.6333
2015-05-12 16:30 | 56.8667 | 61.9167 | 71.3833 | 74.3833
2015-05-12 16:45 | 56.3667 | 60.6667 | 71.1333 | 74.1333
2015-05-12 17:00 | 55.9333 | 59.65 | 70.8833 | 73.7667
2015-05-12 17:15 | 55.6833 | 58.9 | 70.6333 | 73.2667
2015-05-12 17:30 | 55.4333 | 58.15 | 70.3833 | 72.7667
2015-05-12 17:45 | 55.1833 | 57.4 | 70.1333 | 72.2667
2015-05-12 18:00 | 54.9333 | 56.8833 | 70 | 71.65
2015-05-12 18:15 | 54.6833 | 56.6333 | 70 | 70.9
2015-05-12 18:30 | 54.4333 | 56.3833 | 70 | 70.15
2015-05-12 18:45 | 54.1833 | 56.1333 | 70 | 69.4
2015-05-12 19:00 | 53.9333 | 55.7667 | 69.8833 | 68.7667
2015-05-12 19:15 | 53.6833 | 55.2667 | 69.6333 | 68.2667
2015-05-12 19:30 | 53.4333 | 54.7667 | 69.3833 | 67.7667
2015-05-12 19:45 | 53.1833 | 54.2667 | 69.1333 | 67.2667
2015-05-12 20:00 | 53 | 53.8833 | 68.8833 | 66.65
2015-05-12 20:15 | 53 | 53.6333 | 68.6333 | 65.9
2015-05-12 20:30 | 53 | 53.3833 | 68.3833 | 65.15
2015-05-12 20:45 | 53 | 53.1333 | 68.1333 | 64.4
2015-05-12 21:00 | 53 | 53 | 67.7544 | 63.65
2015-05-12 21:15 | 53 | 53 | 67.2281 | 62.9
2015-05-12 21:30 | 53 | 53 | 66.7018 | 62.15
2015-05-12 21:45 | 53 | 53 | 66.1754 | 61.4
2015-05-12 22:00 | 53 | 53 | 66.5 | 60.7667
2015-05-12 22:15 | 53 | 53 | 65.75 | 60.2667
2015-05-12 22:30 | 53 | 53 | 65.2812 | 59.7667
2015-05-12 22:45 | 53 | 53 | 64.5714 | 59.2667
2015-05-12 23:00 | 53 | 52.8833 | 63.8158 | 58.8833
2015-05-12 23:15 | 53 | 52.6333 | 63.4211 | 58.6333
2015-05-12 23:30 | 53 | 52.3833 | 63.0263 | 58.3833
2015-05-12 23:45 | 53 | 52.1333 | 63 | 58.1333
2015-05-13 | 53 | 52.1167 | 63 | 57.7667
2015-05-13 00:15 | 53 | 52.3667 | 63 | 57.2667
2015-05-13 00:30 | 53 | 52.6167 | 63 | 56.7667
2015-05-13 00:45 | 53 | 52.8667 | 63 | 56.2667
2015-05-13 01:00 | 52.9333 | 52.8833 | 63 | 55.8833
2015-05-13 01:15 | 52.6833 | 52.6333 | 63 | 55.6333
2015-05-13 01:30 | 52.4333 | 52.3833 | 63 | 55.3833
2015-05-13 01:45 | 52.1833 | 52.1333 | 63 | 55.1333
2015-05-13 02:00 | 52 | 51.7667 | 63 | 54.8833
2015-05-13 02:15 | 52 | 51.2667 | 63 | 54.6333
2015-05-13 02:30 | 52 | 50.7667 | 63 | 54.3833
2015-05-13 02:45 | 52 | 50.2667 | 63 | 54.1333
2015-05-13 03:00 | 52 | 50 | 63 | 53.7667
2015-05-13 03:15 | 52 | 50 | 63 | 53.2667
2015-05-13 03:30 | 52 | 50 | 63 | 52.7667
2015-05-13 03:45 | 52 | 50 | 63 | 52.2667
2015-05-13 04:00 | 52 | 49.7667 | 63.3889 | 51.8833
2015-05-13 04:15 | 52 | 49.2667 | 63.6667 | 51.6333
2015-05-13 04:30 | 52 | 48.7667 | 63 | 51.3833
2015-05-13 04:45 | 52 | 48.2667 | 63 | 51.1333
2015-05-13 05:00 | 52.0667 | 48.2333 | 63 | 51.1167
2015-05-13 05:15 | 52.3167 | 48.7333 | 63 | 51.3667
2015-05-13 05:30 | 52.5667 | 49.2333 | 63 | 51.6167
2015-05-13 05:45 | 52.8167 | 49.7333 | 63 | 51.8667
2015-05-13 06:00 | 53.1333 | 50.2333 | 62.8833 | 52.35
2015-05-13 06:15 | 53.6333 | 50.7333 | 62.6333 | 53.1
2015-05-13 06:30 | 54.1333 | 51.2333 | 62.3833 | 53.85
2015-05-13 06:45 | 54.6333 | 51.7333 | 62.1333 | 54.6
2015-05-13 07:00 | 55.0667 | 52.2333 | 62.1167 | 55.35
2015-05-13 07:15 | 55.3167 | 52.7333 | 62.3667 | 56.1
2015-05-13 07:30 | 55.5667 | 53.2333 | 62.6167 | 56.85
2015-05-13 07:45 | 55.8167 | 53.7333 | 62.8667 | 57.6
2015-05-13 08:00 | 56.1481 | 54.35 | 63.4667 | 58.35
2015-05-13 08:15 | 56.7037 | 55.1 | 64.4667 | 59.1
2015-05-13 08:30 | 57.4242 | 55.85 | 65.4667 | 59.85
2015-05-13 08:45 | 58.3333 | 56.6 | 66.4667 | 60.6
2015-05-13 09:00 | 58.8621 | 57.35 | 67.35 | 61.35
2015-05-13 09:15 | 58.3448 | 58.1 | 68.1 | 62.1
2015-05-13 09:30 | 57.8276 | 58.85 | 68.85 | 62.85
2015-05-13 09:45 | 57.3103 | 59.6 | 69.6 | 63.6
2015-05-13 10:00 | 59.0667 | 60.35 | 70.5833 | 64.2333
2015-05-13 10:15 | 59.3167 | 61.1 | 71.8333 | 64.7333
2015-05-13 10:30 | 59.5667 | 61.85 | 73.0833 | 65.2333
2015-05-13 10:45 | 59.8167 | 62.6 | 74.3333 | 65.7333
2015-05-13 11:00 | 60.2 | 63.1167 | 75 | 66.2333
2015-05-13 11:15 | 60.95 | 63.3667 | 75 | 66.7333
2015-05-13 11:30 | 61.7 | 63.6167 | 75 | 67.2333
2015-05-13 11:45 | 62.45 | 63.8667 | 75 | 67.7333
2015-05-13 12:00 | 63 | 64 | 75.2333 | 68.35
2015-05-13 12:15 | 63 | 64 | 75.7333 | 69.1
2015-05-13 12:30 | 63 | 64 | 76.2333 | 69.85
2015-05-13 12:45 | 63 | 64 | 76.7333 | 70.6
2015-05-13 13:00 | 63.0667 | 64.2333 | 77.35 | 71
2015-05-13 13:15 | 63.3167 | 64.7333 | 78.1 | 71
2015-05-13 13:30 | 63.5667 | 65.2333 | 78.85 | 71
2015-05-13 13:45 | 63.8167 | 65.7333 | 79.6 | 71
2015-05-13 14:00 | 64 | 66 | 80.35 | 71.2333
2015-05-13 14:15 | 64 | 66 | 81.1 | 71.7333
2015-05-13 14:30 | 64 | 66 | 81.85 | 72.2333
2015-05-13 14:45 | 64 | 66 | 82.6 | 72.7333
2015-05-13 15:00 | 63.8667 | 66 | 83 | 72.8833
2015-05-13 15:15 | 63.3667 | 66 | 83 | 72.6333
2015-05-13 15:30 | 62.8667 | 66 | 83 | 72.3833
2015-05-13 15:45 | 62.3667 | 66 | 83 | 72.1333
2015-05-13 16:00 | 61.9333 | 65.8833 | 82.8833 | 71.8833
2015-05-13 16:15 | 61.6833 | 65.6333 | 82.6333 | 71.6333
2015-05-13 16:30 | 61.4333 | 65.3833 | 82.3833 | 71.3833
2015-05-13 16:45 | 61.1833 | 65.1333 | 82.1333 | 71.1333
2015-05-13 17:00 | 60.8667 | 64.7667 | 81.8833 | 70.8833
2015-05-13 17:15 | 60.3667 | 64.2667 | 81.6333 | 70.6333
2015-05-13 17:30 | 59.8667 | 63.7667 | 81.3833 | 70.3833
2015-05-13 17:45 | 59.3667 | 63.2667 | 81.1333 | 70.1333
2015-05-13 18:00 | 58.8667 | 62.7667 | 80.65 | 69.8833
2015-05-13 18:15 | 58.3667 | 62.2667 | 79.9 | 69.6333
2015-05-13 18:30 | 57.8667 | 61.7667 | 79.15 | 69.3833
2015-05-13 18:45 | 57.3667 | 61.2667 | 78.4 | 69.1333
2015-05-13 19:00 | 57 | 60.65 | 77.4167 | 68.7667
2015-05-13 19:15 | 57 | 59.9 | 76.1667 | 68.2667
2015-05-13 19:30 | 57 | 59.15 | 74.9167 | 67.7667
2015-05-13 19:45 | 57 | 58.4 | 73.6667 | 67.2667
2015-05-13 20:00 | 56.9333 | 57.8833 | 72.65 | 66.8833
2015-05-13 20:15 | 56.6833 | 57.6333 | 71.9 | 66.6333
2015-05-13 20:30 | 56.4333 | 57.3833 | 71.15 | 66.3833
2015-05-13 20:45 | 56.1833 | 57.1333 | 70.4 | 66.1333
2015-05-13 21:00 | 56.069 | 56.8833 | 69.65 | 65.65
2015-05-13 21:15 | 56.3276 | 56.6333 | 68.9 | 64.9
2015-05-13 21:30 | 56.5862 | 56.3833 | 68.15 | 64.15
2015-05-13 21:45 | 56.8448 | 56.1333 | 67.4 | 63.4
2015-05-13 22:00 | 57 | 55.8833 | 66.7667 | 62.8833
2015-05-13 22:15 | 57 | 55.6333 | 66.2667 | 62.6333
2015-05-13 22:30 | 57 | 55.3833 | 65.7667 | 62.3833
2015-05-13 22:45 | 57 | 55.1333 | 65.2667 | 62.1333
2015-05-13 23:00 | 57 | 55 | 64.8833 | 61.7667
2015-05-13 23:15 | 57 | 55 | 64.6333 | 61.2667
2015-05-13 23:30 | 57 | 55 | 64.3833 | 60.7667
2015-05-13 23:45 | 57 | 55 | 64.1333 | 60.2667
2015-05-14 | 57 | 55 | 64 | 59.7667
2015-05-14 00:15 | 57 | 55 | 64 | 59.2667
2015-05-14 00:30 | 57 | 55 | 64 | 58.7667
2015-05-14 00:45 | 57 | 55 | 64 | 58.2667
2015-05-14 01:00 | 56.9333 | 55 | 64 | 58
2015-05-14 01:15 | 56.6833 | 55 | 64 | 58
2015-05-14 01:30 | 56.4333 | 55 | 64 | 58
2015-05-14 01:45 | 56.1833 | 55 | 64 | 58
2015-05-14 02:00 | 56.0667 | 55 | 64 | 57.7667
2015-05-14 02:15 | 56.3167 | 55 | 64 | 57.2667
2015-05-14 02:30 | 56.5667 | 55 | 64 | 56.7667
2015-05-14 02:45 | 56.8167 | 55 | 64 | 56.2667
2015-05-14 03:00 | 57 | 54.8833 | 63.8833 | 55.8833
2015-05-14 03:15 | 57 | 54.6333 | 63.6333 | 55.6333
2015-05-14 03:30 | 57 | 54.3833 | 63.3833 | 55.3833
2015-05-14 03:45 | 57 | 54.1333 | 63.1333 | 55.1333
2015-05-14 04:00 | 56.9333 | 54 | 62.8833 | 55
2015-05-14 04:15 | 56.6833 | 54 | 62.6333 | 55
2015-05-14 04:30 | 56.4333 | 54 | 62.3833 | 55
2015-05-14 04:45 | 56.1833 | 54 | 62.1333 | 55
2015-05-14 05:00 | 55.7895 | 54 | 61.8833 | 55
2015-05-14 05:15 | 55 | 54 | 61.6333 | 55
2015-05-14 05:30 | 55.7317 | 54 | 61.3833 | 55
2015-05-14 05:45 | 56.4634 | 54 | 61.1333 | 55
2015-05-14 06:00 | 57 | 54.2333 | 61.2333 | 55
2015-05-14 06:15 | 57 | 54.7333 | 61.7333 | 55
2015-05-14 06:30 | 57 | 55.2333 | 62.2333 | 55
2015-05-14 06:45 | 57 | 55.7333 | 62.7333 | 55
2015-05-14 07:00 | 57.1333 | 56.2333 | 63.35 | 55
2015-05-14 07:15 | 57.6333 | 56.7333 | 64.1 | 55
2015-05-14 07:30 | 58.1333 | 57.2333 | 64.85 | 55
2015-05-14 07:45 | 58.6333 | 57.7333 | 65.6 | 55
2015-05-14 08:00 | 59.1333 | 58.35 | 66.4667 | 55.2333
2015-05-14 08:15 | 59.6333 | 59.1 | 67.4667 | 55.7333
2015-05-14 08:30 | 60.1333 | 59.85 | 68.4667 | 56.2333
2015-05-14 08:45 | 60.6333 | 60.6 | 69.4667 | 56.7333
2015-05-14 09:00 | 60.9333 | 61.2333 | 70.35 | 57.1167
2015-05-14 09:15 | 60.6833 | 61.7333 | 71.1 | 57.3667
2015-05-14 09:30 | 60.4333 | 62.2333 | 71.85 | 57.6167
2015-05-14 09:45 | 60.1833 | 62.7333 | 72.6 | 57.8667
2015-05-14 10:00 | 60.2553 | 63.5833 | 73.4667 | 58.4667
2015-05-14 10:15 | 61.2128 | 64.8333 | 74.4667 | 59.4667
2015-05-14 10:30 | 62.1702 | 66.0833 | 75.4667 | 60.4667
2015-05-14 10:45 | 63 | 67.3333 | 76.4667 | 61.4667
2015-05-14 11:00 | 63 | 67.0667 | 77.2333 | 62
2015-05-14 11:15 | 62.82 | 65.0667 | 77.7333 | 62
2015-05-14 11:30 | 62.52 | 63.0667 | 78.2333 | 62
2015-05-14 11:45 | 62.22 | 61.0667 | 78.7333 | 62
2015-05-14 12:00 | 62 | 59.8833 | 79.2333 | 62.4667
2015-05-14 12:15 | 62 | 59.6333 | 79.7333 | 63.4667
2015-05-14 12:30 | 62 | 59.3833 | 80.2333 | 64.4667
2015-05-14 12:45 | 62 | 59.1333 | 80.7333 | 65.4667
2015-05-14 13:00 | 62.1333 | 58.7586 | 81.125 | 66.1167
2015-05-14 13:15 | 62.6333 | 58.2414 | 81.3929 | 66.3667
2015-05-14 13:30 | 63.1333 | 57.7241 | 81.6607 | 66.6167
2015-05-14 13:45 | 63.6333 | 57.2069 | 81.9286 | 66.8667
2015-05-14 14:00 | 64.0667 | 57.5962 | 83.8833 | 67
2015-05-14 14:15 | 64.3167 | 56.7308 | 83.6333 | 67
2015-05-14 14:30 | 64.5667 | 55.8654 | 83.3833 | 67
2015-05-14 14:45 | 64.8167 | 55 | 83.1333 | 67
2015-05-14 15:00 | 64.9333 | 55 | 82.8833 | 67.2333
2015-05-14 15:15 | 64.6833 | 55 | 82.6333 | 67.7333
2015-05-14 15:30 | 64.4333 | 55 | 82.3833 | 68.2333
2015-05-14 15:45 | 64.1833 | 55 | 82.1333 | 68.7333
2015-05-14 16:00 | 63.8667 | 55.2333 | 82 | 67.8333
2015-05-14 16:15 | 63.3667 | 55.7333 | 82 | 65.3333
2015-05-14 16:30 | 62.8667 | 56.2333 | 82 | 62.8333
2015-05-14 16:45 | 62.3667 | 56.7333 | 82 | 60.3333
2015-05-14 17:00 | 61.8667 | 57.1167 | 81.8833 | 57.9259
2015-05-14 17:15 | 61.3667 | 57.3667 | 81.6333 | 56.8148
2015-05-14 17:30 | 60.8667 | 57.6167 | 81.3833 | 55.7037
2015-05-14 17:45 | 60.3667 | 57.8667 | 81.1333 | 54.5926
2015-05-14 18:00 | 59.9333 | 57.8833 | 81 | 54
2015-05-14 18:15 | 59.6833 | 57.6333 | 80.8462 | 54
2015-05-14 18:30 | 59.4333 | 57.3833 | 78.8846 | 54
2015-05-14 18:45 | 59.1833 | 57.1333 | 78.3077 | 54
2015-05-14 19:00 | 58.8667 | 57 | 77.6111 | 54.1167
2015-05-14 19:15 | 58.3667 | 57 | 76.8095 | 54.3667
2015-05-14 19:30 | 57.8667 | 57 | 76.0952 | 54.6167
2015-05-14 19:45 | 57.3667 | 57 | 75.381 | 54.8667
2015-05-14 20:00 | 56.9333 | 57 | 73.3529 | 55.1167
2015-05-14 20:15 | 56.6833 | 57 | 63 | 55.3667
2015-05-14 20:30 | 56.4333 | 57 | 63.5714 | 55.6167
2015-05-14 20:45 | 56.1833 | 57 | 63.1111 | 55.8667
2015-05-14 21:00 | 56 | 56.7667 | 64.4118 | 56
2015-05-14 21:15 | 56 | 56.2667 | 65.2941 | 56
2015-05-14 21:30 | 56 | 55.7667 | 65.7692 | 56
2015-05-14 21:45 | 56 | 55.2667 | 64.6154 | 56
2015-05-14 22:00 | 56 | 55 | 64.2333 | 55.8833
2015-05-14 22:15 | 56 | 55 | 64.7333 | 55.6333
2015-05-14 22:30 | 56 | 55 | 65.2333 | 55.3833
2015-05-14 22:45 | 56 | 55 | 65.7333 | 55.1333
2015-05-14 23:00 | 55.9333 | 55 | 66.1167 | 54.8833
2015-05-14 23:15 | 55.6833 | 55 | 66.3667 | 54.6333
2015-05-14 23:30 | 55.4333 | 55 | 66.6167 | 54.3833
2015-05-14 23:45 | 55.1833 | 55 | 66.8667 | 54.1333
2015-05-15 | 54.9333 | 55 | 67.1167 | 54
2015-05-15 00:15 | 54.6833 | 55 | 67.3667 | 54
2015-05-15 00:30 | 54.4333 | 55 | 67.6167 | 54
2015-05-15 00:45 | 54.1833 | 55 | 67.8667 | 54
2015-05-15 01:00 | 54 | 54.6111 | 67.7667 | 54
2015-05-15 01:15 | 54 | 53.9048 | 67.2667 | 53.7917
2015-05-15 01:30 | 54 | 53.5476 | 66.7667 | 53.4792
2015-05-15 01:45 | 54 | 53.1905 | 66.2667 | 53.1667
2015-05-15 02:00 | 54 | 53.28 | 66.1167 | 52.8833
2015-05-15 02:15 | 54 | 53.88 | 66.3667 | 52.6333
2015-05-15 02:30 | 54 | 53.6571 | 66.6167 | 52.3833
2015-05-15 02:45 | 54 | 53.2286 | 66.8667 | 52.1333
2015-05-15 03:00 | 53.9333 | 53.1167 | 66.65 | 52.2414
2015-05-15 03:15 | 53.6833 | 53.3667 | 65.9 | 52.7586
2015-05-15 03:30 | 53.4333 | 53.6167 | 65.15 | 53.2759
2015-05-15 03:45 | 53.1833 | 53.8667 | 64.4 | 53.7931
2015-05-15 04:00 | 53 | 54 | 63.7667 | 53
2015-05-15 04:15 | 53 | 54 | 63.2667 | 53
2015-05-15 04:30 | 53 | 54 | 62.7667 | 53
2015-05-15 04:45 | 53 | 53.4444 | 62.2667 | 53
2015-05-15 05:00 | 53 | 53 | 61.8833 | 53.1167
2015-05-15 05:15 | 53 | 53 | 61.6333 | 53.3667
2015-05-15 05:30 | 53 | 53 | 61.3833 | 53.6167
2015-05-15 05:45 | 53 | 53 | 61.1333 | 53.8667
2015-05-15 06:00 | 53.1333 | 53.2333 | 61.35 | 54
2015-05-15 06:15 | 53.6333 | 53.7333 | 62.1 | 54
2015-05-15 06:30 | 54.1333 | 54.2333 | 62.85 | 54
2015-05-15 06:45 | 54.6333 | 54.7333 | 63.6 | 54
2015-05-15 07:00 | 55.0667 | 55.1167 | 64.35 | 54.1167
2015-05-15 07:15 | 55.3167 | 55.3667 | 65.1 | 54.3667
2015-05-15 07:30 | 55.5667 | 55.6167 | 65.85 | 54.6167
2015-05-15 07:45 | 55.8167 | 55.8667 | 66.6 | 54.8667
2015-05-15 08:00 | 56.0667 | 56.4667 | 67.7 | 55.2059
2015-05-15 08:15 | 56.3167 | 57.4667 | 69.2 | 55.6471
2015-05-15 08:30 | 56.5667 | 58.4667 | 70.7 | 56.2308
2015-05-15 08:45 | 56.8167 | 59.4667 | 72.2 | 57.3846
2015-05-15 09:00 | 57.0667 | 60.2333 | 73.4667 | 59.5556
2015-05-15 09:15 | 57.3167 | 60.7333 | 74.4667 | 60.2549
2015-05-15 09:30 | 57.5667 | 61.2333 | 75.4667 | 60.549
2015-05-15 09:45 | 57.8167 | 61.7333 | 76.4667 | 60.8431
2015-05-15 10:00 | 58 | 62.1167 | 77.35 | 60.8293
2015-05-15 10:15 | 58 | 62.3667 | 78.1 | 60.4634
2015-05-15 10:30 | 58 | 62.6167 | 78.85 | 60.0976
2015-05-15 10:45 | 58 | 62.8667 | 79.6 | 58.2632
2015-05-15 11:00 | 58.2 | 63 | 80.35 | 56
2015-05-15 11:15 | 58.95 | 63 | 81.1 | 57.6981
2015-05-15 11:30 | 59.7 | 63 | 81.85 | 59.3962
2015-05-15 11:45 | 60.45 | 63 | 82.6 | 61.0943
2015-05-15 12:00 | 61 | 63.2333 | 83.1167 | 62.5833
2015-05-15 12:15 | 61 | 63.7333 | 83.3667 | 63.8333
2015-05-15 12:30 | 61 | 64.2333 | 83.6167 | 65.0833
2015-05-15 12:45 | 61 | 64.7333 | 83.8667 | 66.3333
2015-05-15 13:00 | 60.9333 | 65 | 83.8833 | 67.2333
2015-05-15 13:15 | 60.6833 | 65 | 83.6333 | 67.7333
2015-05-15 13:30 | 60.4333 | 65 | 83.3833 | 68.2333
2015-05-15 13:45 | 60.1833 | 65 | 83.1333 | 68.7333
2015-05-15 14:00 | 60 | 65 | 83.1167 | 69.1167
2015-05-15 14:15 | 60 | 65 | 83.3667 | 69.3667
2015-05-15 14:30 | 60 | 65 | 83.6167 | 69.6167
2015-05-15 14:45 | 60 | 65 | 83.8667 | 69.8667
2015-05-15 15:00 | 59.9333 | 64.8833 | 84.1167 | 70
2015-05-15 15:15 | 59.6833 | 64.6333 | 84.3667 | 70
2015-05-15 15:30 | 59.4333 | 64.3833 | 84.6167 | 70
2015-05-15 15:45 | 59.1833 | 64.1333 | 84.8667 | 70
2015-05-15 16:00 | 58.9333 | 63.7667 | 85.2333 | 69.5333
2015-05-15 16:15 | 58.6833 | 63.2667 | 85.7333 | 68.5333
2015-05-15 16:30 | 58.4333 | 62.7667 | 86.2333 | 67.5333
2015-05-15 16:45 | 58.1833 | 62.2667 | 86.7333 | 66.5333
2015-05-15 17:00 | 58 | 61.7667 | 86.7667 | 65.8833
2015-05-15 17:15 | 58 | 61.2667 | 86.2667 | 65.6333
2015-05-15 17:30 | 58 | 60.7667 | 85.7667 | 65.3833
2015-05-15 17:45 | 58 | 60.2667 | 85.2667 | 65.1333
2015-05-15 18:00 | 57.9333 | 59.7667 | 84.6379 | 65
2015-05-15 18:15 | 57.6833 | 59.2667 | 83.8621 | 65
2015-05-15 18:30 | 57.4333 | 58.7667 | 83.0862 | 65
2015-05-15 18:45 | 57.1833 | 58.2667 | 82.3103 | 65
2015-05-15 19:00 | 56.9333 | 57.7667 | 81.5333 | 64.8833
2015-05-15 19:15 | 56.6833 | 57.2667 | 80.5333 | 64.6333
2015-05-15 19:30 | 56.4333 | 56.7667 | 79.5333 | 64.3833
2015-05-15 19:45 | 56.1833 | 56.2667 | 78.5333 | 64.1333
2015-05-15 20:00 | 56 | 56 | 77.65 | 64
2015-05-15 20:15 | 56 | 56 | 76.9 | 64
2015-05-15 20:30 | 56 | 56 | 76.15 | 64
2015-05-15 20:45 | 56 | 56 | 75.4 | 64
2015-05-15 21:00 | 55.9286 | 55.8833 | 74.7667 | 63.65
2015-05-15 21:15 | 55.6607 | 55.6333 | 74.2667 | 62.9
2015-05-15 21:30 | 55.3929 | 55.3833 | 73.7667 | 62.15
2015-05-15 21:45 | 55.125 | 55.1333 | 73.2667 | 61.4
2015-05-15 22:00 | 55.9333 | 54.8833 | 72.7667 | 60.7667
2015-05-15 22:15 | 55.6833 | 54.6333 | 72.2667 | 60.2667
2015-05-15 22:30 | 55.4333 | 54.3833 | 71.7667 | 59.7667
2015-05-15 22:45 | 55.1833 | 54.1333 | 71.2667 | 59.2667
2015-05-15 23:00 | 55 | 54.1628 | 71 | 58.7667
2015-05-15 23:15 | 55 | 54.5116 | 71 | 58.2667
2015-05-15 23:30 | 55 | 54.8605 | 71 | 57.7667
2015-05-15 23:45 | 55 | 55 | 70.7273 | 57.2667
2015-05-16 | 54.9333 | 54.8372 | 70.5 | 56.8833
2015-05-16 00:15 | 54.6833 | 54.4884 | 71 | 56.6333
2015-05-16 00:30 | 54.4333 | 54.1395 | 71 | 56.3833
2015-05-16 00:45 | 54.1833 | 54 | 71 | 56.1333
2015-05-16 01:00 | 54 | 54 | 70.5882 | 55.7667
2015-05-16 01:15 | 54 | 54 | 69.8837 | 55.2667
2015-05-16 01:30 | 54 | 54 | 69.5349 | 54.7667
2015-05-16 01:45 | 54 | 54 | 69.186 | 54.2667
2015-05-16 02:00 | 54 | 52.3 | 69 | 53.7667
2015-05-16 02:15 | 54 | 50.8 | 69 | 53.2667
2015-05-16 02:30 | 54 | 50.2333 | 69 | 52.7667
2015-05-16 02:45 | 54 | 50.7333 | 69 | 52.2667
2015-05-16 03:00 | 54 | 51.4667 | 68.7667 | 51.8833
2015-05-16 03:15 | 54 | 51.6889 | 68.2667 | 51.6333
2015-05-16 03:30 | 54 | 51.0222 | 67.7667 | 51.3833
2015-05-16 03:45 | 54 | 50.3556 | 67.2667 | 51.1333
2015-05-16 04:00 | 54 | 50.2333 | 67 | 51
2015-05-16 04:15 | 54 | 50.7333 | 67 | 51
2015-05-16 04:30 | 54 | 51.2333 | 67 | 51
2015-05-16 04:45 | 54 | 51.7333 | 67 | 51
2015-05-16 05:00 | 54.0667 | 52.1167 | 66.8833 | 51.1167
2015-05-16 05:15 | 54.3167 | 52.3667 | 66.6333 | 51.3667
2015-05-16 05:30 | 54.5667 | 52.6167 | 66.3833 | 51.6167
2015-05-16 05:45 | 54.8167 | 52.8667 | 66.1333 | 51.8667
2015-05-16 06:00 | 55 | 53.2333 | 66.2333 | 52.4667
2015-05-16 06:15 | 55 | 53.7333 | 66.7333 | 53.4667
2015-05-16 06:30 | 55 | 54.2333 | 67.2333 | 54.4667
2015-05-16 06:45 | 55 | 54.7333 | 67.7333 | 55.4667
2015-05-16 07:00 | 55 | 55 | 68.4667 | 56.4667
2015-05-16 07:15 | 55 | 55 | 69.4667 | 57.4667
2015-05-16 07:30 | 55 | 55 | 70.4667 | 58.4667
2015-05-16 07:45 | 55 | 55 | 71.4667 | 59.4667
2015-05-16 08:00 | 55.0667 | 55 | 72.8167 | 60.35
2015-05-16 08:15 | 55.3167 | 55 | 74.5667 | 61.1
2015-05-16 08:30 | 55.5667 | 55.6207 | 76.3167 | 61.85
2015-05-16 08:45 | 55.8167 | 57.1724 | 78.0667 | 62.6
2015-05-16 09:00 | 56 | 58.35 | 79.35 | 63.4667
2015-05-16 09:15 | 56 | 59.1 | 80.1 | 64.4667
2015-05-16 09:30 | 56 | 59.85 | 80.85 | 65.4667
2015-05-16 09:45 | 56 | 60.6 | 81.6 | 66.4667
2015-05-16 10:00 | 56.1333 | 61.2333 | 82 | 67.35
2015-05-16 10:15 | 56.6333 | 61.7333 | 82 | 68.1
2015-05-16 10:30 | 57.1333 | 62.2333 | 82 | 68.85
2015-05-16 10:45 | 57.6333 | 62.7333 | 82 | 69.6
2015-05-16 11:00 | 58 | 63.35 | 82.4667 | 70.2333
2015-05-16 11:15 | 58 | 64.1 | 83.4667 | 70.7333
2015-05-16 11:30 | 58 | 64.85 | 84.4667 | 71.2333
2015-05-16 11:45 | 58 | 65.6 | 85.4667 | 71.7333
2015-05-16 12:00 | 58 | 66.1167 | 86.1167 | 72.35
2015-05-16 12:15 | 58 | 66.3667 | 86.3667 | 73.1
2015-05-16 12:30 | 58 | 66.6167 | 86.6167 | 73.85
2015-05-16 12:45 | 58 | 66.8667 | 86.8667 | 74.6
2015-05-16 13:00 | 58.0667 | 66.8833 | 87 | 75
2015-05-16 13:15 | 58.3167 | 66.6333 | 87 | 75
2015-05-16 13:30 | 58.5667 | 66.3833 | 87 | 75
2015-05-16 13:45 | 58.8167 | 66.1333 | 87 | 75
2015-05-16 14:00 | 59.0667 | 65.8833 | 87.35 | 75
2015-05-16 14:15 | 59.3167 | 65.6333 | 88.1 | 75
2015-05-16 14:30 | 59.5667 | 65.3833 | 88.85 | 75
2015-05-16 14:45 | 59.8167 | 65.1333 | 89.6 | 75
2015-05-16 15:00 | 59.913 | 64.8833 | 89.8833 | 75.1167
2015-05-16 15:15 | 59.587 | 64.6333 | 89.6333 | 75.3667
2015-05-16 15:30 | 59.2609 | 64.3833 | 89.3833 | 75.6167
2015-05-16 15:45 | 59 | 64.1333 | 89.1333 | 75.8667
2015-05-16 16:00 | 59 | 63.8833 | 89.1167 | 76
2015-05-16 16:15 | 59 | 63.6333 | 89.3667 | 76
2015-05-16 16:30 | 59 | 63.3833 | 89.6167 | 76
2015-05-16 16:45 | 59 | 63.1333 | 89.8667 | 76
2015-05-16 17:00 | 58.9333 | 62.7667 | 89.7667 | 75.8833
2015-05-16 17:15 | 58.6833 | 62.2667 | 89.2667 | 75.6333
2015-05-16 17:30 | 58.4333 | 61.7667 | 88.7667 | 75.3833
2015-05-16 17:45 | 58.1833 | 61.2667 | 88.2667 | 75.1333
2015-05-16 18:00 | 57.9333 | 60.65 | 87.5333 | 74.8833
2015-05-16 18:15 | 57.6833 | 59.9 | 86.5333 | 74.6333
2015-05-16 18:30 | 57.4333 | 59.15 | 85.5333 | 74.3833
2015-05-16 18:45 | 57.1833 | 58.4 | 84.5333 | 74.1333
2015-05-16 19:00 | 56.9333 | 57.7667 | 83.1833 | 73.65
2015-05-16 19:15 | 56.6833 | 57.2667 | 81.4333 | 72.9
2015-05-16 19:30 | 56.4333 | 56.7667 | 79.6833 | 72.15
2015-05-16 19:45 | 56.1833 | 56.2667 | 77.9333 | 71.4
2015-05-16 20:00 | 55.9048 | 56 | 76.3 | 70.7667
2015-05-16 20:15 | 55.5476 | 56 | 74.8 | 70.2667
2015-05-16 20:30 | 55.1905 | 56 | 73.3 | 69.7667
2015-05-16 20:45 | 55 | 56 | 71.8 | 69.2667
2015-05-16 21:00 | 55 | 55.7941 | 71 | 68.65
2015-05-16 21:15 | 55 | 55.3529 | 71 | 67.9
2015-05-16 21:30 | 55 | 55 | 71 | 67.15
2015-05-16 21:45 | 55 | 55 | 71 | 66.4
2015-05-16 22:00 | 55 | 55 | 70.4167 | 65.5333
2015-05-16 22:15 | 55 | 55 | 69.1667 | 64.5333
2015-05-16 22:30 | 55 | 55 | 67.9167 | 63.5333
2015-05-16 22:45 | 55 | 55 | 66.6667 | 62.5333
2015-05-16 23:00 | 55 | 55 | 65.7667 | 61.65
2015-05-16 23:15 | 55 | 55 | 65.2667 | 60.9
2015-05-16 23:30 | 55 | 55 | 64.7667 | 60.15
2015-05-16 23:45 | 55 | 55 | 64.2667 | 59.4
2015-05-17 | 55 | 55 | 63.7667 | 58.8833
2015-05-17 00:15 | 55 | 55 | 63.2667 | 58.6333
2015-05-17 00:30 | 55 | 55 | 62.7667 | 58.3833
2015-05-17 00:45 | 55 | 55 | 62.2667 | 58.1333
2015-05-17 01:00 | 55 | 55 | 61.8833 | 57.7667
2015-05-17 01:15 | 55 | 55 | 61.6333 | 57.2667
2015-05-17 01:30 | 55 | 55 | 61.3833 | 56.7667
2015-05-17 01:45 | 55 | 55 | 61.1333 | 56.2667
2015-05-17 02:00 | 55 | 55 | 60.7667 | 55.8833
2015-05-17 02:15 | 55 | 55 | 60.2667 | 55.6333
2015-05-17 02:30 | 55 | 55 | 59.7667 | 55.3833
2015-05-17 02:45 | 55 | 55 | 59.2667 | 55.1333
2015-05-17 03:00 | 55 | 55 | 58.65 | 54.7667
2015-05-17 03:15 | 55 | 55 | 57.9 | 54.2667
2015-05-17 03:30 | 55 | 55 | 57.15 | 53.7667
2015-05-17 03:45 | 55 | 55 | 56.4 | 53.2667
2015-05-17 04:00 | 55 | 55 | 56 | 53
2015-05-17 04:15 | 55 | 55 | 56 | 53
2015-05-17 04:30 | 55 | 55 | 56 | 53
2015-05-17 04:45 | 55 | 55 | 56 | 53
2015-05-17 05:00 | 55 | 55 | 55.8833 | 53.2333
2015-05-17 05:15 | 55 | 55 | 55.6333 | 53.7333
2015-05-17 05:30 | 55 | 55 | 55.3833 | 54.2333
2015-05-17 05:45 | 55 | 55 | 55.1333 | 54.7333
2015-05-17 06:00 | 55.0667 | 55.1167 | 55.2333 | 55.1167
2015-05-17 06:15 | 55.3167 | 55.3667 | 55.7333 | 55.3667
2015-05-17 06:30 | 55.5667 | 55.6167 | 56.2333 | 55.6167
2015-05-17 06:45 | 55.8167 | 55.8667 | 56.7333 | 55.8667
2015-05-17 07:00 | 56 | 56.1167 | 57.9333 | 56.2333
2015-05-17 07:15 | 56 | 56.3667 | 59.9333 | 56.7333
2015-05-17 07:30 | 56 | 56.6167 | 61.9333 | 57.2333
2015-05-17 07:45 | 56 | 56.8667 | 63.9333 | 57.7333
2015-05-17 08:00 | 56 | 57.1167 | 65.7 | 58.35
2015-05-17 08:15 | 56 | 57.3667 | 67.2 | 59.1
2015-05-17 08:30 | 56 | 57.6167 | 68.7 | 59.85
2015-05-17 08:45 | 56 | 57.8667 | 70.2 | 60.6
2015-05-17 09:00 | 56.1333 | 58.1707 | 71.2333 | 61.2333
2015-05-17 09:15 | 56.6333 | 58.5366 | 71.7333 | 61.7333
2015-05-17 09:30 | 57.1333 | 58.9024 | 72.2333 | 62.2333
2015-05-17 09:45 | 57.6333 | 60.1579 | 72.7333 | 62.7333
2015-05-17 10:00 | 58 | 61 | 73.1167 | 63.8167
2015-05-17 10:15 | 58 | 61 | 73.3667 | 65.5667
2015-05-17 10:30 | 58 | 61 | 73.6167 | 67.3167
2015-05-17 10:45 | 58 | 61 | 73.8667 | 69.0667
2015-05-17 11:00 | 58.2 | 61.1167 | 74.35 | 70
2015-05-17 11:15 | 58.95 | 61.3667 | 75.1 | 70
2015-05-17 11:30 | 59.7 | 61.6167 | 75.85 | 70
2015-05-17 11:45 | 60.45 | 61.8667 | 76.6 | 70
2015-05-17 12:00 | 60.9333 | 62.1167 | 77.35 | 70.35
2015-05-17 12:15 | 60.6833 | 62.3667 | 78.1 | 71.1
2015-05-17 12:30 | 60.4333 | 62.6167 | 78.85 | 71.85
2015-05-17 12:45 | 60.1833 | 62.8667 | 79.6 | 72.6
2015-05-17 13:00 | 60 | 63.1167 | 80.2333 | 72.8833
2015-05-17 13:15 | 60 | 63.3667 | 80.7333 | 72.6333
2015-05-17 13:30 | 60 | 63.6167 | 81.2333 | 72.3833
2015-05-17 13:45 | 60 | 63.8667 | 81.7333 | 72.1333
2015-05-17 14:00 | 60 | 63.8833 | 82.1167 | 72.2333
2015-05-17 14:15 | 60 | 63.6333 | 82.3667 | 72.7333
2015-05-17 14:30 | 60 | 63.3833 | 82.6167 | 73.2333
2015-05-17 14:45 | 60 | 63.1333 | 82.8667 | 73.7333
2015-05-17 15:00 | 60 | 62.8833 | 83.1167 | 74.2333
2015-05-17 15:15 | 60 | 62.6333 | 83.3667 | 74.7333
2015-05-17 15:30 | 60 | 62.3833 | 83.6167 | 75.2333
2015-05-17 15:45 | 60 | 62.1333 | 83.8667 | 75.7333
2015-05-17 16:00 | 59.9333 | 61.8833 | 84.1167 | 75.8833
2015-05-17 16:15 | 59.6833 | 61.6333 | 84.3667 | 75.6333
2015-05-17 16:30 | 59.4333 | 61.3833 | 84.6167 | 75.3833
2015-05-17 16:45 | 59.1833 | 61.1333 | 84.8667 | 75.1333
2015-05-17 17:00 | 58.9333 | 60.7667 | 84.7667 | 74.7667
2015-05-17 17:15 | 58.6833 | 60.2667 | 84.2667 | 74.2667
2015-05-17 17:30 | 58.4333 | 59.7667 | 83.7667 | 73.7667
2015-05-17 17:45 | 58.1833 | 59.2667 | 83.2667 | 73.2667
2015-05-17 18:00 | 57.9333 | 58.8833 | 82.7667 | 72.8833
2015-05-17 18:15 | 57.6833 | 58.6333 | 82.2667 | 72.6333
2015-05-17 18:30 | 57.4333 | 58.3833 | 81.7667 | 72.3833
2015-05-17 18:45 | 57.1833 | 58.1333 | 81.2667 | 72.1333
2015-05-17 19:00 | 56.9333 | 57.8833 | 80.1833 | 71.65
2015-05-17 19:15 | 56.6833 | 57.6333 | 78.4333 | 70.9
2015-05-17 19:30 | 56.4333 | 57.3833 | 76.6833 | 70.15
2015-05-17 19:45 | 56.1833 | 57.1333 | 74.9333 | 69.4
2015-05-17 20:00 | 56.0667 | 56.8833 | 73.4167 | 68.7667
2015-05-17 20:15 | 56.3167 | 56.6333 | 72.1667 | 68.2667
2015-05-17 20:30 | 56.5667 | 56.3833 | 70.9167 | 67.7667
2015-05-17 20:45 | 56.8167 | 56.1333 | 69.6667 | 67.2667
2015-05-17 21:00 | 56.9333 | 56 | 68.7667 | 66.7667
2015-05-17 21:15 | 56.6833 | 56 | 68.2667 | 66.2667
2015-05-17 21:30 | 56.4333 | 56 | 67.7667 | 65.7667
2015-05-17 21:45 | 56.1833 | 56 | 67.2667 | 65.2667
2015-05-17 22:00 | 56 | 56 | 66.8833 | 64.5333
2015-05-17 22:15 | 56 | 56 | 66.6333 | 63.5333
2015-05-17 22:30 | 56 | 56 | 66.3833 | 62.5333
2015-05-17 22:45 | 56 | 56 | 66.1333 | 61.5333
2015-05-17 23:00 | 56 | 56 | 65.4167 | 60.8833
2015-05-17 23:15 | 56 | 56 | 64.1667 | 60.6333
2015-05-17 23:30 | 56 | 56 | 62.9167 | 60.3833
2015-05-17 23:45 | 56 | 56 | 61.6667 | 60.1333
2015-05-18 | 55.9333 | 56 | 60.8833 | 60
2015-05-18 00:15 | 55.6833 | 56 | 60.6333 | 60
2015-05-18 00:30 | 55.4333 | 56 | 60.3833 | 60
2015-05-18 00:45 | 55.1833 | 56 | 60.1333 | 60
2015-05-18 01:00 | 55 | 55.8542 | 60.2333 | 59.7667
2015-05-18 01:15 | 55 | 55.5417 | 60.7333 | 59.2667
2015-05-18 01:30 | 55 | 55.2292 | 61.2333 | 58.7667
2015-05-18 01:45 | 55 | 55 | 61.7333 | 58.2667
2015-05-18 02:00 | 55 | 55 | 62 | 57.8833
2015-05-18 02:15 | 55 | 55 | 62 | 57.6333
2015-05-18 02:30 | 55 | 55 | 62 | 57.3833
2015-05-18 02:45 | 55 | 55 | 62 | 57.1333
2015-05-18 03:00 | 55 | 55 | 62 | 56.8833
2015-05-18 03:15 | 55 | 55 | 62 | 56.6333
2015-05-18 03:30 | 55 | 55 | 62 | 56.3833
2015-05-18 03:45 | 55 | 55 | 62 | 56.1333
2015-05-18 04:00 | 55 | 55 | 61.65 | 56
2015-05-18 04:15 | 55 | 55 | 60.9 | 56
2015-05-18 04:30 | 55 | 55 | 60.15 | 56
2015-05-18 04:45 | 55 | 55 | 59.4 | 56
2015-05-18 05:00 | 55 | 54.8833 | 59.1167 | 56
2015-05-18 05:15 | 55 | 54.6333 | 59.3667 | 56
2015-05-18 05:30 | 55 | 54.3833 | 59.6167 | 56
2015-05-18 05:45 | 55 | 54.1333 | 59.8667 | 56
2015-05-18 06:00 | 55 | 54.1167 | 60.4667 | 56.2333
2015-05-18 06:15 | 55 | 54.3667 | 61.4667 | 56.7333
2015-05-18 06:30 | 55 | 54.6167 | 62.4667 | 57.2333
2015-05-18 06:45 | 55 | 54.8667 | 63.4667 | 57.7333
2015-05-18 07:00 | 55 | 55 | 64.5833 | 58.1167
2015-05-18 07:15 | 55 | 55 | 65.8333 | 58.3667
2015-05-18 07:30 | 55 | 55 | 67.0833 | 58.6167
2015-05-18 07:45 | 55 | 55 | 68.3333 | 58.8667
2015-05-18 08:00 | 55.0667 | 55.1167 | 69.5833 | 59.1167
2015-05-18 08:15 | 55.3167 | 55.3667 | 70.8333 | 59.3667
2015-05-18 08:30 | 55.5667 | 55.6167 | 72.0833 | 59.6167
2015-05-18 08:45 | 55.8167 | 55.8667 | 73.3333 | 59.8667
2015-05-18 09:00 | 56.0667 | 56.1167 | 74.4667 | 60.35
2015-05-18 09:15 | 56.3167 | 56.3667 | 75.4667 | 61.1
2015-05-18 09:30 | 56.5667 | 56.6167 | 76.4667 | 61.85
2015-05-18 09:45 | 56.8167 | 56.8667 | 77.4667 | 62.6
2015-05-18 10:00 | 57.0667 | 57.1167 | 78.4667 | 63.4667
2015-05-18 10:15 | 57.3167 | 57.3667 | 79.4667 | 64.4667
2015-05-18 10:30 | 57.5667 | 57.6167 | 80.4667 | 65.4667
2015-05-18 10:45 | 57.8167 | 57.8667 | 81.4667 | 66.4667
2015-05-18 11:00 | 58 | 58.1167 | 82.4667 | 67.4667
2015-05-18 11:15 | 58 | 58.3667 | 83.4667 | 68.4667
2015-05-18 11:30 | 58 | 58.6167 | 84.4667 | 69.4667
2015-05-18 11:45 | 58 | 58.8667 | 85.4667 | 70.4667
2015-05-18 12:00 | 58.0667 | 59.2456 | 86 | 71.35
2015-05-18 12:15 | 58.3167 | 59.7719 | 86 | 72.1
2015-05-18 12:30 | 58.5667 | 60.2982 | 86 | 72.85
2015-05-18 12:45 | 58.8167 | 60.8246 | 86 | 73.6
2015-05-18 13:00 | 59 | 61.35 | 86.1167 | 74
2015-05-18 13:15 | 59 | 62.1 | 86.3667 | 74
2015-05-18 13:30 | 59 | 62.85 | 86.6167 | 74
2015-05-18 13:45 | 59 | 63.6 | 86.8667 | 74
2015-05-18 14:00 | 59 | 63.7667 | 87.1167 | 74.1167
2015-05-18 14:15 | 59 | 63.2667 | 87.3667 | 74.3667
2015-05-18 14:30 | 59 | 62.7667 | 87.6167 | 74.6167
2015-05-18 14:45 | 59 | 62.2667 | 87.8667 | 74.8667
2015-05-18 15:00 | 59 | 61.8833 | 88 | 75.1167
2015-05-18 15:15 | 59 | 61.6333 | 88 | 75.3667
2015-05-18 15:30 | 59 | 61.3833 | 88 | 75.6167
2015-05-18 15:45 | 59 | 61.1333 | 88 | 75.8667
2015-05-18 16:00 | 58.9333 | 60.8833 | 87.8833 | 76
2015-05-18 16:15 | 58.6833 | 60.6333 | 87.6333 | 76
2015-05-18 16:30 | 58.4333 | 60.3833 | 87.3833 | 76
2015-05-18 16:45 | 58.1833 | 60.1333 | 87.1333 | 76
2015-05-18 17:00 | 57.9333 | 59.8833 | 86.65 | 75.8833
2015-05-18 17:15 | 57.6833 | 59.6333 | 85.9 | 75.6333
2015-05-18 17:30 | 57.4333 | 59.3833 | 85.15 | 75.3833
2015-05-18 17:45 | 57.1833 | 59.1333 | 84.4 | 75.1333
2015-05-18 18:00 | 57 | 58.8833 | 83.6379 | 74.65
2015-05-18 18:15 | 57 | 58.6333 | 82.8621 | 73.9
2015-05-18 18:30 | 57 | 58.3833 | 82.0862 | 73.15
2015-05-18 18:45 | 57 | 58.1333 | 81.3103 | 72.4
2015-05-18 19:00 | 57 | 57.8833 | 80 | 71.65
2015-05-18 19:15 | 57 | 57.6333 | 80 | 70.9
2015-05-18 19:30 | 57 | 57.3833 | 79.8519 | 70.15
2015-05-18 19:45 | 57 | 57.1333 | 79.2963 | 69.4
2015-05-18 20:00 | 57 | 57 | 78.7083 | 68.4167
2015-05-18 20:15 | 57 | 57 | 78.0833 | 67.1667
2015-05-18 20:30 | 57 | 57 | 77.6389 | 65.9167
2015-05-18 20:45 | 57 | 57 | 77.2222 | 64.6667
2015-05-18 21:00 | 57 | 57 | 77 | 63.7667
2015-05-18 21:15 | 57 | 57 | 76 | 63.2667
2015-05-18 21:30 | 57 | 57 | 76 | 62.7667
2015-05-18 21:45 | 57 | 57 | 73.2 | 62.2667
2015-05-18 22:00 | 56.9333 | 56.8833 | 70.8333 | 61.7667
2015-05-18 22:15 | 56.6833 | 56.6333 | 72.619 | 61.2667
2015-05-18 22:30 | 56.4333 | 56.3833 | 74.4048 | 60.7667
2015-05-18 22:45 | 56.1833 | 56.1333 | 73.3333 | 60.2667
2015-05-18 23:00 | 56 | 56 | 72.1167 | 59.7667
2015-05-18 23:15 | 56 | 56 | 72.3667 | 59.2667
2015-05-18 23:30 | 56 | 56 | 72.6167 | 58.7667
2015-05-18 23:45 | 56 | 56 | 72.8667 | 58.2667
2015-05-19 | 56 | 56 | 71.7273 | 57.8833
2015-05-19 00:15 | 56 | 56 | 71 | 57.6333
2015-05-19 00:30 | 56 | 56 | 71.2963 | 57.3833
2015-05-19 00:45 | 56 | 56 | 72.4074 | 57.1333
2015-05-19 01:00 | 55.8 | 56 | 72.8833 | 56.7667
2015-05-19 01:15 | 55.05 | 56 | 72.6333 | 56.2667
2015-05-19 01:30 | 55 | 56 | 72.3833 | 55.7667
2015-05-19 01:45 | 55 | 56 | 72.1333 | 55.2667
2015-05-19 02:00 | 55 | 56 | 72 | 54.8833
2015-05-19 02:15 | 55 | 56 | 72 | 54.6333
2015-05-19 02:30 | 55 | 56 | 72 | 54.3833
2015-05-19 02:45 | 55 | 56 | 72 | 54.1333
2015-05-19 03:00 | 55 | 55.8833 | 72 | 53.8833
2015-05-19 03:15 | 55 | 55.6333 | 72 | 53.6333
2015-05-19 03:30 | 55 | 55.3833 | 72 | 53.3833
2015-05-19 03:45 | 55 | 55.1333 | 72 | 53.1333
2015-05-19 04:00 | 55.931 | 55 | 72 | 52.8833
2015-05-19 04:15 | 55.6724 | 55 | 72 | 52.6333
2015-05-19 04:30 | 55.4138 | 55 | 71.8846 | 52.3833
2015-05-19 04:45 | 55.1552 | 55 | 71.3077 | 52.1333
2015-05-19 05:00 | 55 | 55 | 71.2414 | 52.2333
2015-05-19 05:15 | 55 | 55 | 71.7586 | 52.7333
2015-05-19 05:30 | 55 | 55 | 71.7419 | 53.2333
2015-05-19 05:45 | 55 | 55 | 71.2581 | 53.7333
2015-05-19 06:00 | 55.0667 | 55.1167 | 71.1207 | 54.4667
2015-05-19 06:15 | 55.3167 | 55.3667 | 71.3793 | 55.4667
2015-05-19 06:30 | 55.5667 | 55.6167 | 71.6379 | 56.4667
2015-05-19 06:45 | 55.8167 | 55.8667 | 71.8966 | 57.4667
2015-05-19 07:00 | 56 | 56.1167 | 71 | 58.4667
2015-05-19 07:15 | 56 | 56.3667 | 71.5098 | 59.4667
2015-05-19 07:30 | 56 | 56.6167 | 72.098 | 60.4667
2015-05-19 07:45 | 56 | 56.8667 | 72.6863 | 61.4667
2015-05-19 08:00 | 56 | 57.1167 | 73.5122 | 62.2333
2015-05-19 08:15 | 56 | 57.3667 | 74.6098 | 62.7333
2015-05-19 08:30 | 56 | 57.6167 | 75.7073 | 63.2333
2015-05-19 08:45 | 56 | 57.8667 | 76.5789 | 63.7333
2015-05-19 09:00 | 56.0667 | 58 | 77.4667 | 64.2333
2015-05-19 09:15 | 56.3167 | 58 | 78.4667 | 64.7333
2015-05-19 09:30 | 56.5667 | 58 | 79.4667 | 65.2333
2015-05-19 09:45 | 56.8167 | 58 | 80.4667 | 65.7333
2015-05-19 10:00 | 57 | 58 | 81.1167 | 66.35
2015-05-19 10:15 | 57.1778 | 58 | 81.3667 | 67.1
2015-05-19 10:30 | 57.8444 | 58 | 81.6167 | 67.85
2015-05-19 10:45 | 58.5111 | 58 | 81.8667 | 68.6
2015-05-19 11:00 | 59.0667 | 58.2333 | 82.4667 | 69.35
2015-05-19 11:15 | 59.3167 | 58.7333 | 83.4667 | 70.1
2015-05-19 11:30 | 59.5667 | 59.2333 | 84.4667 | 70.85
2015-05-19 11:45 | 59.8167 | 59.7333 | 85.4667 | 71.6
2015-05-19 12:00 | 60.1333 | 60.3818 | 86.1167 | 72.2333
2015-05-19 12:15 | 60.6333 | 61.2 | 86.3667 | 72.7333
2015-05-19 12:30 | 61.1333 | 62.0182 | 86.6167 | 73.2333
2015-05-19 12:45 | 61.6333 | 62.8364 | 86.8667 | 73.7333
2015-05-19 13:00 | 62 | 63.1167 | 87.3621 | 74.2333
2015-05-19 13:15 | 62 | 63.3667 | 88.1379 | 74.7333
2015-05-19 13:30 | 62 | 63.6167 | 88.9138 | 75.2333
2015-05-19 13:45 | 62 | 63.8667 | 89.6897 | 75.7333
2015-05-19 14:00 | 62 | 64.1167 | 86.75 | 76.1167
2015-05-19 14:15 | 62 | 64.3667 | 81.9286 | 76.3667
2015-05-19 14:30 | 62 | 64.6167 | 81.9688 | 76.6167
2015-05-19 14:45 | 62 | 64.8667 | 85.25 | 76.8667
2015-05-19 15:00 | 61.9333 | 64.8833 | 87.2333 | 77
2015-05-19 15:15 | 61.6833 | 64.6333 | 87.7333 | 77
2015-05-19 15:30 | 61.4333 | 64.3833 | 88.2333 | 77
2015-05-19 15:45 | 61.1833 | 64.1333 | 88.7333 | 77
2015-05-19 16:00 | 60.9333 | 63.8833 | 88.2222 | 76.8833
2015-05-19 16:15 | 60.6833 | 63.6333 | 86.4706 | 76.6333
2015-05-19 16:30 | 60.4333 | 63.3833 | 84.7059 | 76.3833
2015-05-19 16:45 | 60.1833 | 63.1333 | 82.9412 | 76.1333
2015-05-19 17:00 | 59.9245 | 62.7667 | 81.8833 | 76
2015-05-19 17:15 | 59.6415 | 62.2667 | 81.6333 | 76
2015-05-19 17:30 | 59.3585 | 61.7667 | 81.3833 | 76
2015-05-19 17:45 | 59.0755 | 61.2667 | 81.1333 | 76
2015-05-19 18:00 | 57.9333 | 60.65 | 80.8833 | 75.65
2015-05-19 18:15 | 57.6833 | 59.9 | 80.6333 | 74.9
2015-05-19 18:30 | 57.4333 | 59.15 | 80.3833 | 74.15
2015-05-19 18:45 | 57.1833 | 58.4 | 80.1333 | 73.4
2015-05-19 19:00 | 56.9333 | 57.7667 | 79.4167 | 72.7667
2015-05-19 19:15 | 56.6833 | 57.2667 | 78.1667 | 72.2667
2015-05-19 19:30 | 56.4333 | 56.7667 | 76.9167 | 71.7667
2015-05-19 19:45 | 56.1833 | 56.2667 | 75.6667 | 71.2667
2015-05-19 20:00 | 56.0667 | 56.1167 | 74.7667 | 70.8833
2015-05-19 20:15 | 56.3167 | 56.3667 | 74.2667 | 70.6333
2015-05-19 20:30 | 56.5667 | 56.6167 | 73.7667 | 70.3833
2015-05-19 20:45 | 56.8167 | 56.8667 | 73.2667 | 70.1333
2015-05-19 21:00 | 56.9333 | 56.8833 | 73.2333 | 69.5333
2015-05-19 21:15 | 56.6833 | 56.6333 | 73.7333 | 68.5333
2015-05-19 21:30 | 56.4333 | 56.3833 | 74.2333 | 67.5333
2015-05-19 21:45 | 56.1833 | 56.1333 | 74.7333 | 66.5333
2015-05-19 22:00 | 56 | 56 | 74.65 | 65.65
2015-05-19 22:15 | 56 | 56 | 73.9 | 64.9
2015-05-19 22:30 | 56 | 56 | 73.15 | 64.15
2015-05-19 22:45 | 56 | 56 | 72.4 | 63.4
2015-05-19 23:00 | 56 | 56 | 72 | 62.7667
2015-05-19 23:15 | 56 | 56 | 72 | 62.2667
2015-05-19 23:30 | 56 | 56 | 72 | 61.7667
2015-05-19 23:45 | 56 | 56 | 72 | 61.2667
2015-05-20 | 55.9111 | 56 | 72 | 60.7667
2015-05-20 00:15 | 55.5778 | 56 | 72 | 60.2667
2015-05-20 00:30 | 55.2444 | 56 | 72 | 59.7667
2015-05-20 00:45 | 55.2667 | 56 | 72 | 59.2667
2015-05-20 01:00 | 56 | 56 | 71.8833 | 58.8833
2015-05-20 01:15 | 56 | 56 | 71.6333 | 58.6333
2015-05-20 01:30 | 56 | 56 | 71.3833 | 58.3833
2015-05-20 01:45 | 56 | 56 | 71.1333 | 58.1333
2015-05-20 02:00 | 56 | 55.8833 | 70.8833 | 57.8833
2015-05-20 02:15 | 56 | 55.6333 | 70.6333 | 57.6333
2015-05-20 02:30 | 56 | 55.3833 | 70.3833 | 57.3833
2015-05-20 02:45 | 56 | 55.1333 | 70.1333 | 57.1333
2015-05-20 03:00 | 56 | 55 | 70 | 56.7667
2015-05-20 03:15 | 56 | 55 | 70 | 56.2667
2015-05-20 03:30 | 56 | 55 | 70 | 55.7667
2015-05-20 03:45 | 56 | 55 | 70 | 55.2667
2015-05-20 04:00 | 55.875 | 55 | 70 | 54.8833
2015-05-20 04:15 | 55.4062 | 55 | 70 | 54.6333
2015-05-20 04:30 | 55.0714 | 55 | 70 | 54.3833
2015-05-20 04:45 | 55.6071 | 55 | 70 | 54.1333
2015-05-20 05:00 | 56.0667 | 55 | 69.8833 | 54
2015-05-20 05:15 | 56.3167 | 55 | 69.6333 | 54
2015-05-20 05:30 | 56.5667 | 55 | 69.3833 | 54
2015-05-20 05:45 | 56.8167 | 55 | 69.1333 | 54
2015-05-20 06:00 | 57 | 55 | 68.7667 | 54.4667
2015-05-20 06:15 | 57 | 55 | 68.2667 | 55.4667
2015-05-20 06:30 | 57 | 55 | 67.7667 | 56.4667
2015-05-20 06:45 | 57 | 55 | 67.2667 | 57.4667
2015-05-20 07:00 | 56.7714 | 55.1167 | 67.35 | 58.2333
2015-05-20 07:15 | 55.9143 | 55.3667 | 68.1 | 58.7333
2015-05-20 07:30 | 55.0571 | 55.6167 | 68.85 | 59.2333
2015-05-20 07:45 | 55.56 | 55.8667 | 69.6 | 59.7333
2015-05-20 08:00 | 56 | 56.35 | 70.35 | 60.4667
2015-05-20 08:15 | 56 | 57.1 | 71.1 | 61.4667
2015-05-20 08:30 | 56 | 57.85 | 71.85 | 62.4667
2015-05-20 08:45 | 56 | 58.6 | 72.6 | 63.4667
2015-05-20 09:00 | 56.1333 | 59.1167 | 72.5 | 64.2333
2015-05-20 09:15 | 56.6333 | 59.3667 | 71.4286 | 64.7333
2015-05-20 09:30 | 57.1333 | 59.6167 | 70 | 65.2333
2015-05-20 09:45 | 57.6333 | 59.8667 | 71.5 | 65.7333
2015-05-20 10:00 | 58 | 60.2333 | 72 | 66.9333
2015-05-20 10:15 | 58 | 60.7333 | 74.15 | 68.9333
2015-05-20 10:30 | 58 | 61.2333 | 75.275 | 70.9333
2015-05-20 10:45 | 58 | 61.7333 | 76.4 | 72.9333
2015-05-20 11:00 | 58.1333 | 62.2333 | 76.16 | 74.1167
2015-05-20 11:15 | 58.6333 | 62.7333 | 74.36 | 74.3667
2015-05-20 11:30 | 59.1333 | 63.2333 | 74.3636 | 74.6167
2015-05-20 11:45 | 59.6333 | 63.7333 | 74.8182 | 74.8667
2015-05-20 12:00 | 60.0667 | 64.2333 | 75.4667 | 75.35
2015-05-20 12:15 | 60.3167 | 64.7333 | 76.4667 | 76.1
2015-05-20 12:30 | 60.5667 | 65.2333 | 77.4667 | 76.85
2015-05-20 12:45 | 60.8167 | 65.7333 | 78.4667 | 77.6
2015-05-20 13:00 | 60.9333 | 66 | 78.6667 | 78.1167
2015-05-20 13:15 | 60.6833 | 66 | 77.8571 | 78.3667
2015-05-20 13:30 | 60.4333 | 66 | 76.25 | 78.6167
2015-05-20 13:45 | 60.1833 | 66 | 78.5882 | 78.8667
2015-05-20 14:00 | 60 | 65.8833 | 80.2333 | 79.2333
2015-05-20 14:15 | 60 | 65.6333 | 80.7333 | 79.7333
2015-05-20 14:30 | 60 | 65.3833 | 81.2333 | 80.2333
2015-05-20 14:45 | 60 | 65.1333 | 81.7333 | 80.7333
2015-05-20 15:00 | 60 | 64.8833 | 82 | 80.8833
2015-05-20 15:15 | 60 | 64.6333 | 82 | 80.6333
2015-05-20 15:30 | 60 | 64.3833 | 80.4865 | 80.3833
2015-05-20 15:45 | 60 | 64.1333 | 78.8649 | 80.1333
2015-05-20 16:00 | 59.9333 | 63.8833 | 75.9 | 80
2015-05-20 16:15 | 59.6833 | 63.6333 | 75.8 | 80
2015-05-20 16:30 | 59.4333 | 63.3833 | 72.8 | 80
2015-05-20 16:45 | 59.1833 | 63.1333 | 71.4545 | 80
2015-05-20 17:00 | 59 | 62.7667 | 69.65 | 79.8833
2015-05-20 17:15 | 59 | 62.2667 | 68.9 | 79.6333
2015-05-20 17:30 | 59 | 61.7667 | 68.15 | 79.3833
2015-05-20 17:45 | 59 | 61.2667 | 67.4 | 79.1333
2015-05-20 18:00 | 58.8667 | 60.65 | 66.4167 | 78.5333
2015-05-20 18:15 | 58.3667 | 59.9 | 66 | 77.5333
2015-05-20 18:30 | 57.8667 | 59.15 | 65.697 | 76.5333
2015-05-20 18:45 | 57.3667 | 58.4 | 65.2424 | 75.5333
2015-05-20 19:00 | 57 | 58 | 64.65 | 74.4167
2015-05-20 19:15 | 57 | 58 | 63.9 | 73.1667
2015-05-20 19:30 | 57 | 58 | 63.15 | 71.9167
2015-05-20 19:45 | 57 | 58 | 62.4 | 70.6667
2015-05-20 20:00 | 57 | 58 | 61.8833 | 69.65
2015-05-20 20:15 | 57 | 58 | 61.6333 | 68.9
2015-05-20 20:30 | 57 | 58 | 61.3833 | 68.15
2015-05-20 20:45 | 57 | 58 | 61.1333 | 67.4
2015-05-20 21:00 | 57 | 57.8654 | 60.8205 | 66.8833
2015-05-20 21:15 | 57 | 57.5769 | 60.4359 | 66.6333
2015-05-20 21:30 | 57 | 57.2885 | 60.0513 | 66.3833
2015-05-20 21:45 | 57 | 57 | 60 | 66.1333
2015-05-20 22:00 | 57 | 57 | 59.8108 | 65.65
2015-05-20 22:15 | 57 | 57 | 59.4054 | 64.9
2015-05-20 22:30 | 57 | 57 | 59 | 64.15
2015-05-20 22:45 | 57 | 57 | 59 | 63.4
2015-05-20 23:00 | 56.9333 | 57 | 58.8409 | 62.65
2015-05-20 23:15 | 56.6833 | 57 | 58.5 | 61.9
2015-05-20 23:30 | 56.4333 | 57 | 58.1591 | 61.15
2015-05-20 23:45 | 56.1833 | 57 | 58 | 60.4
2015-05-21 | 55.9091 | 57 | 57.825 | 59.8833
2015-05-21 00:15 | 55.5682 | 57 | 57.45 | 59.6333
2015-05-21 00:30 | 55.2273 | 57 | 57.075 | 59.3833
2015-05-21 00:45 | 55.3125 | 57 | 57 | 59.1333
2015-05-21 01:00 | 56.1481 | 57 | 56 | 58.7667
2015-05-21 01:15 | 56.7037 | 57 | 56 | 58.2667
2015-05-21 01:30 | 56.7879 | 57 | 56 | 57.7667
2015-05-21 01:45 | 56.3333 | 57 | 56 | 57.2667
2015-05-21 02:00 | 55.8462 | 57 | 55.8793 | 57
2015-05-21 02:15 | 55.2692 | 57 | 55.6207 | 57
2015-05-21 02:30 | 55.2353 | 57 | 55.3621 | 57
2015-05-21 02:45 | 55.6765 | 57 | 55.1034 | 57
2015-05-21 03:00 | 56 | 57 | 55.4167 | 56.8833
2015-05-21 03:15 | 56 | 57 | 55 | 56.6333
2015-05-21 03:30 | 56 | 57 | 55 | 56.3833
2015-05-21 03:45 | 56 | 57 | 55 | 56.1333
2015-05-21 04:00 | 56.0909 | 57 | 55.8409 | 55.8833
2015-05-21 04:15 | 56.4318 | 57 | 55.5 | 55.6333
2015-05-21 04:30 | 56.7727 | 57 | 55.1591 | 55.3833
2015-05-21 04:45 | 57 | 57 | 55 | 55.1333
2015-05-21 05:00 | 57 | 57.1167 | 55 | 55.1167
2015-05-21 05:15 | 56.8913 | 57.3667 | 55 | 55.3667
2015-05-21 05:30 | 56.5652 | 57.6167 | 55 | 55.6167
2015-05-21 05:45 | 56.2391 | 57.8667 | 55 | 55.8667
2015-05-21 06:00 | 56 | 58.1167 | 54.8833 | 56.35
2015-05-21 06:15 | 56 | 58.3667 | 54.6333 | 57.1
2015-05-21 06:30 | 56 | 58.6167 | 54.3833 | 57.85
2015-05-21 06:45 | 56 | 58.8667 | 54.1333 | 58.6
2015-05-21 07:00 | 55.84 | 59.1167 | 54 | 59.2333
2015-05-21 07:15 | 55.24 | 59.3667 | 54 | 59.7333
2015-05-21 07:30 | 55.5143 | 59.6167 | 54 | 60.2333
2015-05-21 07:45 | 56.3714 | 59.8667 | 54 | 60.7333
2015-05-21 08:00 | 57.1379 | 60.2333 | 54 | 61.35
2015-05-21 08:15 | 57.6552 | 60.7333 | 54 | 62.1
2015-05-21 08:30 | 58.1724 | 61.2333 | 54 | 62.85
2015-05-21 08:45 | 58.6897 | 61.7333 | 54 | 63.6
2015-05-21 09:00 | 59.2759 | 62.1167 | 53.5625 | 64.1167
2015-05-21 09:15 | 60.3103 | 62.3667 | 53 | 64.3667
2015-05-21 09:30 | 61.3448 | 62.6167 | 53 | 64.6167
2015-05-21 09:45 | 62.3793 | 62.8667 | 53 | 64.8667
2015-05-21 10:00 | 63.0667 | 63.4667 | 53 | 65
2015-05-21 10:15 | 63.3167 | 64.4667 | 53.6818 | 65
2015-05-21 10:30 | 63.5667 | 65.4667 | 53 | 65
2015-05-21 10:45 | 63.8167 | 66.4667 | 53 | 65
2015-05-21 11:00 | 64 | 67 | 53.2333 | 65.35
2015-05-21 11:15 | 64 | 67 | 53.7333 | 66.1
2015-05-21 11:30 | 64 | 67 | 54.2333 | 66.85
2015-05-21 11:45 | 64.5769 | 67 | 54.7333 | 67.6
2015-05-21 12:00 | 64.9333 | 66.7667 | 55 | 68
2015-05-21 12:15 | 64.6833 | 66.2667 | 55.619 | 68
2015-05-21 12:30 | 64.4333 | 65.7667 | 56 | 68
2015-05-21 12:45 | 64.1833 | 65.2667 | 56 | 68
2015-05-21 13:00 | 64.1333 | 64.8833 | 55.86 | 67.8833
2015-05-21 13:15 | 64.6333 | 64.6333 | 55.56 | 67.6333
2015-05-21 13:30 | 65.1333 | 64.3833 | 55.26 | 67.3833
2015-05-21 13:45 | 65.6333 | 64.1333 | 55 | 67.1333
2015-05-21 14:00 | 65.8 | 64.2333 | 55 | 67.1167
2015-05-21 14:15 | 65.05 | 64.7333 | 55.5238 | 67.3667
2015-05-21 14:30 | 64.3 | 65.2333 | 56 | 67.6167
2015-05-21 14:45 | 63.55 | 65.7333 | 55.2857 | 67.8667
2015-05-21 15:00 | 62.9333 | 66 | 56 | 68
2015-05-21 15:15 | 62.6833 | 66 | 56 | 68
2015-05-21 15:30 | 62.4333 | 66 | 55.875 | 68
2015-05-21 15:45 | 62.1833 | 66 | 55.25 | 68
2015-05-21 16:00 | 62.0851 | 65.7667 | 56 | 68.1167
2015-05-21 16:15 | 62.4043 | 65.2667 | 56 | 68.3667
2015-05-21 16:30 | 62.7234 | 64.7667 | 56 | 68.6167
2015-05-21 16:45 | 62.8462 | 64.2667 | 56 | 68.8667
2015-05-21 17:00 | 61.9333 | 63.8833 | 56.4667 | 69
2015-05-21 17:15 | 61.6833 | 63.6333 | 57 | 69
2015-05-21 17:30 | 61.4333 | 63.3833 | 56.6 | 69
2015-05-21 17:45 | 61.1833 | 63.1333 | 55.25 | 69
2015-05-21 18:00 | 60.9333 | 62.8833 | 56.6316 | 68.8833
2015-05-21 18:15 | 60.6833 | 62.6333 | 56 | 68.6333
2015-05-21 18:30 | 60.4333 | 62.3833 | 56 | 68.3833
2015-05-21 18:45 | 60.1833 | 62.1333 | 56 | 68.1333
2015-05-21 19:00 | 59.9333 | 61.7667 | 56 | 68
2015-05-21 19:15 | 59.6833 | 61.2667 | 56 | 68
2015-05-21 19:30 | 59.4333 | 60.7667 | 56 | 68
2015-05-21 19:45 | 59.1833 | 60.2667 | 56 | 68
2015-05-21 20:00 | 58.9333 | 59.8833 | 56 | 67.8833
2015-05-21 20:15 | 58.6833 | 59.6333 | 56 | 67.6333
2015-05-21 20:30 | 58.4333 | 59.3833 | 56 | 67.3833
2015-05-21 20:45 | 58.1833 | 59.1333 | 56 | 67.1333
2015-05-21 21:00 | 58 | 58.8833 | 56.1167 | 67
2015-05-21 21:15 | 58 | 58.6333 | 56.3667 | 67
2015-05-21 21:30 | 58 | 58.3833 | 56.6167 | 67
2015-05-21 21:45 | 58 | 58.1333 | 56.8667 | 67
2015-05-21 22:00 | 57.9333 | 58 | 57 | 66.65
2015-05-21 22:15 | 57.6833 | 58 | 57 | 65.9
2015-05-21 22:30 | 57.4333 | 58 | 57 | 65.15
2015-05-21 22:45 | 57.1833 | 58 | 57 | 64.4
2015-05-21 23:00 | 57 | 57.4167 | 57 | 63.7667
2015-05-21 23:15 | 57 | 57 | 57 | 63.2667
2015-05-21 23:30 | 57 | 57 | 57 | 62.7667
2015-05-21 23:45 | 57.4762 | 56.381 | 57.2727 | 62.2667
2015-05-22 | 58 | 55.8542 | 58 | 61.7667
2015-05-22 00:15 | 58 | 55.5417 | 57.9211 | 61.2667
2015-05-22 00:30 | 58 | 55.2292 | 57.5263 | 60.7667
2015-05-22 00:45 | 58 | 55.6667 | 57.1316 | 60.2667
2015-05-22 01:00 | 57.9333 | 56.6316 | 57 | 59.8833
2015-05-22 01:15 | 57.6833 | 55.8421 | 57 | 59.6333
2015-05-22 01:30 | 57.4333 | 55.0526 | 57.5714 | 59.3833
2015-05-22 01:45 | 57.1833 | 54.3636 | 58 | 59.1333
2015-05-22 02:00 | 57 | 54.4375 | 58 | 59
2015-05-22 02:15 | 57 | 55 | 58 | 59
2015-05-22 02:30 | 57 | 55 | 58 | 59
2015-05-22 02:45 | 57 | 55 | 57.4286 | 59
2015-05-22 03:00 | 56.9333 | 55 | 58 | 59
2015-05-22 03:15 | 56.6833 | 55 | 58 | 59
2015-05-22 03:30 | 56.4333 | 55 | 58 | 59
2015-05-22 03:45 | 56.1833 | 55 | 58 | 59
2015-05-22 04:00 | 56 | 55 | 58 | 59
2015-05-22 04:15 | 56 | 55 | 58 | 59
2015-05-22 04:30 | 56 | 55 | 58 | 59
2015-05-22 04:45 | 56 | 55 | 58 | 59
2015-05-22 05:00 | 56.069 | 55.1167 | 57.8833 | 58.8833
2015-05-22 05:15 | 56.3276 | 55.3667 | 57.6333 | 58.6333
2015-05-22 05:30 | 56.5862 | 55.6167 | 57.3833 | 58.3833
2015-05-22 05:45 | 56.8448 | 55.8667 | 57.1333 | 58.1333
2015-05-22 06:00 | 57.0667 | 56.1167 | 57 | 58.1167
2015-05-22 06:15 | 57.3167 | 56.3667 | 57 | 58.3667
2015-05-22 06:30 | 57.5667 | 56.6167 | 57 | 58.6167
2015-05-22 06:45 | 57.8167 | 56.8667 | 57 | 58.8667
2015-05-22 07:00 | 58.069 | 57 | 57.1167 | 59.1167
2015-05-22 07:15 | 58.3276 | 57 | 57.3667 | 59.3667
2015-05-22 07:30 | 58.5862 | 57 | 57.6167 | 59.6167
2015-05-22 07:45 | 58.8448 | 57.2222 | 57.8667 | 59.8667
2015-05-22 08:00 | 59.0667 | 59.2333 | 58 | 60.1167
2015-05-22 08:15 | 59.3167 | 59.7333 | 58 | 60.3667
2015-05-22 08:30 | 59.5667 | 60.2333 | 58.3235 | 60.6167
2015-05-22 08:45 | 59.8167 | 60.7333 | 58.7647 | 60.8667
2015-05-22 09:00 | 60.2069 | 61 | 59.3182 | 61.35
2015-05-22 09:15 | 60.9828 | 61 | 60 | 62.1
2015-05-22 09:30 | 61.7586 | 61 | 61.875 | 62.85
2015-05-22 09:45 | 62.5345 | 61 | 62.7 | 63.6
2015-05-22 10:00 | 62.9333 | 61.2333 | 63 | 64.2333
2015-05-22 10:15 | 62.6833 | 61.7333 | 63.2 | 64.7333
2015-05-22 10:30 | 62.4333 | 62.2333 | 64.7 | 65.2333
2015-05-22 10:45 | 62.1833 | 62.7333 | 66.2 | 65.7333
2015-05-22 11:00 | 61.8519 | 63.1167 | 67.7778 | 66.35
2015-05-22 11:15 | 61.2963 | 63.3667 | 69.0612 | 67.1
2015-05-22 11:30 | 61.2121 | 63.6167 | 70.2857 | 67.85
2015-05-22 11:45 | 61.6667 | 63.8667 | 71.5102 | 68.6
2015-05-22 12:00 | 62 | 64.35 | 72 | 69.2333
2015-05-22 12:15 | 62 | 65.1 | 73.0769 | 69.7333
2015-05-22 12:30 | 62 | 65.85 | 74.2308 | 70.2333
2015-05-22 12:45 | 62 | 66.6 | 75.3846 | 70.7333
2015-05-22 13:00 | 61.9333 | 67 | 76.35 | 70.8833
2015-05-22 13:15 | 61.6833 | 67 | 77.1 | 70.6333
2015-05-22 13:30 | 61.4333 | 67 | 77.85 | 70.3833
2015-05-22 13:45 | 61.1833 | 67 | 78.6 | 70.1333
2015-05-22 14:00 | 61 | 67 | 79.2333 | 70.1167
2015-05-22 14:15 | 61 | 67 | 79.7333 | 70.3667
2015-05-22 14:30 | 61 | 67 | 80.2333 | 70.6167
2015-05-22 14:45 | 61 | 67 | 80.7333 | 70.8667
2015-05-22 15:00 | 61 | 66.7667 | 81.35 | 71
2015-05-22 15:15 | 61 | 66.2667 | 82.1 | 71
2015-05-22 15:30 | 61 | 65.7667 | 82.85 | 71
2015-05-22 15:45 | 61 | 65.2667 | 83.6 | 71
2015-05-22 16:00 | 61 | 64.7667 | 83.65 | 70.8833
2015-05-22 16:15 | 61 | 64.2667 | 82.9 | 70.6333
2015-05-22 16:30 | 61 | 63.7667 | 82.15 | 70.3833
2015-05-22 16:45 | 61 | 63.2667 | 81.4 | 70.1333
2015-05-22 17:00 | 59.9333 | 62.7667 | 80.0455 | 69.8833
2015-05-22 17:15 | 59.6833 | 62.2667 | 78 | 69.6333
2015-05-22 17:30 | 59.4333 | 61.7667 | 75.9545 | 69.3833
2015-05-22 17:45 | 59.1833 | 61.2667 | 73.8571 | 69.1333
2015-05-22 18:00 | 59 | 60.8833 | 73.7667 | 68.8833
2015-05-22 18:15 | 59 | 60.6333 | 73.2667 | 68.6333
2015-05-22 18:30 | 59 | 60.3833 | 72.7667 | 68.3833
2015-05-22 18:45 | 59 | 60.1333 | 72.2667 | 68.1333
2015-05-22 19:00 | 58.9333 | 59.7667 | 72 | 67.8833
2015-05-22 19:15 | 58.6833 | 59.2667 | 72 | 67.6333
2015-05-22 19:30 | 58.4333 | 58.7667 | 71.92 | 67.3833
2015-05-22 19:45 | 58.1833 | 58.2667 | 71.32 | 67.1333
2015-05-22 20:00 | 57.9333 | 58 | 71 | 66.8833
2015-05-22 20:15 | 57.6833 | 58 | 71 | 66.6333
2015-05-22 20:30 | 57.4333 | 58 | 71 | 66.3833
2015-05-22 20:45 | 57.1833 | 58 | 71 | 66.1333
2015-05-22 21:00 | 57.0667 | 57.8333 | 71 | 65.8833
2015-05-22 21:15 | 57.3167 | 57.4762 | 71 | 65.6333
2015-05-22 21:30 | 57.5667 | 57.119 | 71 | 65.3833
2015-05-22 21:45 | 57.8167 | 57.5556 | 71 | 65.1333
2015-05-22 22:00 | 57.9184 | 58 | 71 | 64.8833
2015-05-22 22:15 | 57.6122 | 58 | 71 | 64.6333
2015-05-22 22:30 | 57.3061 | 58 | 71 | 64.3833
2015-05-22 22:45 | 57 | 58 | 71 | 64.1333
2015-05-22 23:00 | 57 | 57.8833 | 71 | 63.7667
2015-05-22 23:15 | 57 | 57.6333 | 71 | 63.2667
2015-05-22 23:30 | 57 | 57.3833 | 71 | 62.7667
2015-05-22 23:45 | 57 | 57.1333 | 71 | 62.2667
2015-05-23 | 57 | 57 | 71 | 61.8833
2015-05-23 00:15 | 57 | 57 | 71 | 61.6333
2015-05-23 00:30 | 56.8125 | 57 | 71 | 61.3833
2015-05-23 00:45 | 56.3438 | 57 | 71 | 61.1333
2015-05-23 01:00 | 55.75 | 57 | 71 | 60.8833
2015-05-23 01:15 | 55.0682 | 57 | 71 | 60.6333
2015-05-23 01:30 | 55.4091 | 57 | 71 | 60.3833
2015-05-23 01:45 | 55.75 | 57 | 71 | 60.1333
2015-05-23 02:00 | 55.7895 | 56.8833 | 71.2333 | 59.7667
2015-05-23 02:15 | 55 | 56.6333 | 71.7333 | 59.2667
2015-05-23 02:30 | 55 | 56.3833 | 72.2333 | 58.7667
2015-05-23 02:45 | 55 | 56.1333 | 72.7333 | 58.2667
2015-05-23 03:00 | 54.9333 | 56.1167 | 73 | 58
2015-05-23 03:15 | 54.6833 | 56.3667 | 73 | 58
2015-05-23 03:30 | 54.4333 | 56.6167 | 73 | 58
2015-05-23 03:45 | 54.1833 | 56.8667 | 73 | 58
2015-05-23 04:00 | 54.0833 | 57 | 73 | 58
2015-05-23 04:15 | 54.3958 | 57 | 73 | 58
2015-05-23 04:30 | 54.7083 | 57 | 73 | 58
2015-05-23 04:45 | 54.9167 | 57 | 73 | 58
2015-05-23 05:00 | 54.0889 | 57.1167 | 72.8833 | 58.1167
2015-05-23 05:15 | 54.4222 | 57.3667 | 72.6333 | 58.3667
2015-05-23 05:30 | 54.7556 | 57.6167 | 72.3833 | 58.6167
2015-05-23 05:45 | 55 | 57.8667 | 72.1333 | 58.8667
2015-05-23 06:00 | 54.9333 | 57.8833 | 72 | 59.1167
2015-05-23 06:15 | 54.6833 | 57.6333 | 72 | 59.3667
2015-05-23 06:30 | 54.4333 | 57.3833 | 72 | 59.6167
2015-05-23 06:45 | 54.1833 | 57.1333 | 72 | 59.8667
2015-05-23 07:00 | 54.0667 | 57.1167 | 72.2333 | 60.4667
2015-05-23 07:15 | 54.3167 | 57.3667 | 72.7333 | 61.4667
2015-05-23 07:30 | 54.5667 | 57.6167 | 73.2333 | 62.4667
2015-05-23 07:45 | 54.8167 | 57.8667 | 73.7333 | 63.4667
2015-05-23 08:00 | 55.0667 | 58.2333 | 73.65 | 64.35
2015-05-23 08:15 | 55.3167 | 58.7333 | 72.9 | 65.1
2015-05-23 08:30 | 55.5667 | 59.2333 | 72.15 | 65.85
2015-05-23 08:45 | 55.8167 | 59.7333 | 71.4 | 66.6
2015-05-23 09:00 | 56.0667 | 60.1167 | 71.2333 | 67.35
2015-05-23 09:15 | 56.3167 | 60.3667 | 71.7333 | 68.1
2015-05-23 09:30 | 56.5667 | 60.6167 | 72.2333 | 68.85
2015-05-23 09:45 | 56.8167 | 60.8667 | 72.7333 | 69.6
2015-05-23 10:00 | 57 | 61.3256 | 73.5833 | 70.35
2015-05-23 10:15 | 57 | 62.0233 | 74.8333 | 71.1
2015-05-23 10:30 | 57 | 62.7209 | 76.0833 | 71.85
2015-05-23 10:45 | 57.5417 | 63.5294 | 77.3333 | 72.6
2015-05-23 11:00 | 58.0667 | 64.1167 | 79.5556 | 73.2333
2015-05-23 11:15 | 58.3167 | 64.3667 | 82.381 | 73.7333
2015-05-23 11:30 | 58.5667 | 64.6167 | 83.8095 | 74.2333
2015-05-23 11:45 | 58.8167 | 64.8667 | 85.2381 | 74.7333
2015-05-23 12:00 | 59 | 65.2333 | 86 | 75.1167
2015-05-23 12:15 | 59 | 65.7333 | 86 | 75.3667
2015-05-23 12:30 | 59 | 66.2333 | 86 | 75.6167
2015-05-23 12:45 | 59 | 66.7333 | 86 | 75.8667
2015-05-23 13:00 | 59.2 | 67 | 85.65 | 76.2333
2015-05-23 13:15 | 59.95 | 67 | 84.9 | 76.7333
2015-05-23 13:30 | 60.7 | 67 | 84.15 | 77.2333
2015-05-23 13:45 | 61.45 | 67 | 83.4 | 77.7333
2015-05-23 14:00 | 61.9333 | 67.2593 | 83.2333 | 78.1167
2015-05-23 14:15 | 61.6833 | 67.8148 | 83.7333 | 78.3667
2015-05-23 14:30 | 61.4333 | 67.697 | 84.2333 | 78.6167
2015-05-23 14:45 | 61.1833 | 67.2424 | 84.7333 | 78.8667
2015-05-23 15:00 | 60.9333 | 66.8833 | 84.65 | 78.8833
2015-05-23 15:15 | 60.6833 | 66.6333 | 83.9 | 78.6333
2015-05-23 15:30 | 60.4333 | 66.3833 | 83.15 | 78.3833
2015-05-23 15:45 | 60.1833 | 66.1333 | 82.4 | 78.1333
2015-05-23 16:00 | 59.9333 | 65.7667 | 75 | 77.8833
2015-05-23 16:15 | 59.6833 | 65.2667 | 64.2667 | 77.6333
2015-05-23 16:30 | 59.4333 | 64.7667 | 61 | 77.3833
2015-05-23 16:45 | 59.1833 | 64.2667 | 61 | 77.1333
2015-05-23 17:00 | 58.9333 | 63.7667 | 61.35 | 76.7667
2015-05-23 17:15 | 58.6833 | 63.2667 | 62.1 | 76.2667
2015-05-23 17:30 | 58.4333 | 62.7667 | 62.85 | 75.7667
2015-05-23 17:45 | 58.1833 | 62.2667 | 63.6 | 75.2667
2015-05-23 18:00 | 57.9245 | 61.7667 | 64.875 | 74.7667
2015-05-23 18:15 | 57.6415 | 61.2667 | 66.75 | 74.2667
2015-05-23 18:30 | 57.3585 | 60.7667 | 66.6389 | 73.7667
2015-05-23 18:45 | 57.0755 | 60.2667 | 66.2222 | 73.2667
2015-05-23 19:00 | 56 | 59.7667 | 66 | 72.7667
2015-05-23 19:15 | 56 | 59.2667 | 66 | 72.2667
2015-05-23 19:30 | 56 | 58.7667 | 66 | 71.7667
2015-05-23 19:45 | 56 | 58.2667 | 66 | 71.2667
2015-05-23 20:00 | 55.9333 | 57.7667 | 66.1167 | 70.5333
2015-05-23 20:15 | 55.6833 | 57.2667 | 66.3667 | 69.5333
2015-05-23 20:30 | 55.4333 | 56.7667 | 66.6167 | 68.5333
2015-05-23 20:45 | 55.1833 | 56.2667 | 66.8667 | 67.5333
2015-05-23 21:00 | 55 | 55.86 | 66.7667 | 66.5333
2015-05-23 21:15 | 55 | 55.56 | 66.2667 | 65.5333
2015-05-23 21:30 | 55 | 55.26 | 65.7667 | 64.5333
2015-05-23 21:45 | 55 | 55.2 | 65.2667 | 63.5333
2015-05-23 22:00 | 55 | 56 | 64.7667 | 62.8833
2015-05-23 22:15 | 55 | 56 | 64.2667 | 62.6333
2015-05-23 22:30 | 55 | 56 | 63.7667 | 62.3833
2015-05-23 22:45 | 55 | 56 | 63.2667 | 62.1333
2015-05-23 23:00 | 54.9333 | 55.8833 | 63.1167 | 61.7667
2015-05-23 23:15 | 54.6833 | 55.6333 | 63.3667 | 61.2667
2015-05-23 23:30 | 54.4333 | 55.3833 | 63.6167 | 60.7667
2015-05-23 23:45 | 54.1833 | 55.1333 | 63.8667 | 60.2667
2015-05-24 | 54 | 55 | 63.8833 | 59.8833
2015-05-24 00:15 | 54 | 55 | 63.6333 | 59.6333
2015-05-24 00:30 | 54 | 55 | 63.3833 | 59.3833
2015-05-24 00:45 | 54 | 55 | 63.1333 | 59.1333
2015-05-24 01:00 | 54 | 54.8833 | 62.7667 | 58.7667
2015-05-24 01:15 | 54 | 54.6333 | 62.2667 | 58.2667
2015-05-24 01:30 | 54 | 54.3833 | 61.7667 | 57.7667
2015-05-24 01:45 | 54 | 54.1333 | 61.2667 | 57.2667
2015-05-24 02:00 | 54 | 53.8833 | 60.8833 | 56.8833
2015-05-24 02:15 | 53.8367 | 53.6333 | 60.6333 | 56.6333
2015-05-24 02:30 | 53.5306 | 53.3833 | 60.3833 | 56.3833
2015-05-24 02:45 | 53.2245 | 53.1333 | 60.1333 | 56.1333
2015-05-24 03:00 | 52.9333 | 53 | 59.7667 | 55.8833
2015-05-24 03:15 | 52.6833 | 53 | 59.2667 | 55.6333
2015-05-24 03:30 | 52.4333 | 53 | 58.7667 | 55.3833
2015-05-24 03:45 | 52.1833 | 53 | 58.2667 | 55.1333
2015-05-24 04:00 | 52 | 52.8833 | 57.7667 | 55
2015-05-24 04:15 | 52 | 52.6333 | 57.2667 | 55
2015-05-24 04:30 | 52 | 52.3833 | 56.7667 | 55
2015-05-24 04:45 | 52 | 52.1333 | 56.2667 | 55
2015-05-24 05:00 | 52.1333 | 52.1167 | 55.8833 | 55.2333
2015-05-24 05:15 | 52.6333 | 52.3667 | 55.6333 | 55.7333
2015-05-24 05:30 | 53.1333 | 52.6167 | 55.3833 | 56.2333
2015-05-24 05:45 | 53.6333 | 52.8667 | 55.1333 | 56.7333
2015-05-24 06:00 | 54 | 53.35 | 55.4667 | 57.35
2015-05-24 06:15 | 54.2545 | 54.1 | 56.4667 | 58.1
2015-05-24 06:30 | 54.5273 | 54.85 | 57.4667 | 58.85
2015-05-24 06:45 | 54.8 | 55.6 | 58.4667 | 59.6
2015-05-24 07:00 | 55 | 56.2333 | 59.7 | 60.35
2015-05-24 07:15 | 55 | 56.7333 | 61.2 | 61.1
2015-05-24 07:30 | 55 | 57.2333 | 62.7 | 61.85
2015-05-24 07:45 | 55 | 57.7333 | 64.2 | 62.6
2015-05-24 08:00 | 55.0667 | 58.4667 | 65.7 | 63.35
2015-05-24 08:15 | 55.3167 | 59.4667 | 67.2 | 64.1
2015-05-24 08:30 | 55.5667 | 60.4667 | 68.7 | 64.85
2015-05-24 08:45 | 55.8167 | 61.4667 | 70.2 | 65.6
2015-05-24 09:00 | 56.0667 | 62.35 | 71.5833 | 66.4667
2015-05-24 09:15 | 56.3167 | 63.1 | 72.8333 | 67.4667
2015-05-24 09:30 | 56.5667 | 63.85 | 74.0833 | 68.4667
2015-05-24 09:45 | 56.8167 | 64.6 | 75.3333 | 69.4667
2015-05-24 10:00 | 57.0667 | 65.35 | 76.35 | 70.4667
2015-05-24 10:15 | 57.3167 | 66.1 | 77.1 | 71.4667
2015-05-24 10:30 | 57.5667 | 66.85 | 77.85 | 72.4667
2015-05-24 10:45 | 57.8167 | 67.6 | 78.6 | 73.4667
2015-05-24 11:00 | 58.2 | 68.1167 | 79.1167 | 74.2333
2015-05-24 11:15 | 58.95 | 68.3667 | 79.3667 | 74.7333
2015-05-24 11:30 | 59.7 | 68.6167 | 79.6167 | 75.2333
2015-05-24 11:45 | 60.45 | 68.8667 | 79.8667 | 75.7333
2015-05-24 12:00 | 60.9333 | 68.8833 | 80.1167 | 76.1167
2015-05-24 12:15 | 60.6833 | 68.6333 | 80.3667 | 76.3667
2015-05-24 12:30 | 60.4333 | 68.3833 | 80.6167 | 76.6167
2015-05-24 12:45 | 60.1833 | 68.1333 | 80.8667 | 76.8667
2015-05-24 13:00 | 60 | 68 | 81.2333 | 77.35
2015-05-24 13:15 | 60 | 68 | 81.7333 | 78.1
2015-05-24 13:30 | 60 | 68 | 82.2333 | 78.85
2015-05-24 13:45 | 60 | 68 | 82.7333 | 79.6
2015-05-24 14:00 | 59.8667 | 67.8833 | 83.1167 | 80.1167
2015-05-24 14:15 | 59.3667 | 67.6333 | 83.3667 | 80.3667
2015-05-24 14:30 | 58.8667 | 67.3833 | 83.6167 | 80.6167
2015-05-24 14:45 | 58.3667 | 67.1333 | 83.8667 | 80.8667
2015-05-24 15:00 | 58 | 66.65 | 84 | 81
2015-05-24 15:15 | 58 | 65.9 | 84 | 81
2015-05-24 15:30 | 58 | 65.15 | 84 | 81
2015-05-24 15:45 | 58 | 64.4 | 84 | 81
2015-05-24 16:00 | 57.9333 | 63.7667 | 84.1167 | 81
2015-05-24 16:15 | 57.6833 | 63.2667 | 84.3667 | 81
2015-05-24 16:30 | 57.4333 | 62.7667 | 84.6167 | 81
2015-05-24 16:45 | 57.1833 | 62.2667 | 84.8667 | 81
2015-05-24 17:00 | 56.9333 | 61.7667 | 84.8833 | 80.8833
2015-05-24 17:15 | 56.6833 | 61.2667 | 84.6333 | 80.6333
2015-05-24 17:30 | 56.4333 | 60.7667 | 84.3833 | 80.3833
2015-05-24 17:45 | 56.1833 | 60.2667 | 84.1333 | 80.1333
2015-05-24 18:00 | 56 | 59.7667 | 83.7667 | 79.8833
2015-05-24 18:15 | 56 | 59.2667 | 83.2667 | 79.6333
2015-05-24 18:30 | 56 | 58.7667 | 82.7667 | 79.3833
2015-05-24 18:45 | 56 | 58.2667 | 82.2667 | 79.1333
2015-05-24 19:00 | 55.8462 | 57.7667 | 81.5333 | 78.7667
2015-05-24 19:15 | 55.2692 | 57.2667 | 80.5333 | 78.2667
2015-05-24 19:30 | 55.2353 | 56.7667 | 79.5333 | 77.7667
2015-05-24 19:45 | 55.6765 | 56.2667 | 78.5333 | 77.2667
2015-05-24 20:00 | 56 | 56.1167 | 77.5333 | 76.7667
2015-05-24 20:15 | 56 | 56.3667 | 76.5333 | 76.2667
2015-05-24 20:30 | 56 | 56.6167 | 75.5333 | 75.7667
2015-05-24 20:45 | 56 | 56.8667 | 74.5333 | 75.2667
2015-05-24 21:00 | 56 | 57 | 73.4167 | 74.7667
2015-05-24 21:15 | 56 | 57 | 72.1667 | 74.2667
2015-05-24 21:30 | 56 | 57 | 70.9167 | 73.7667
2015-05-24 21:45 | 56 | 57 | 69.6667 | 73.2667
2015-05-24 22:00 | 56 | 57 | 69.1167 | 72.4167
2015-05-24 22:15 | 56 | 57 | 69.3667 | 71.1667
2015-05-24 22:30 | 56 | 57 | 69.6167 | 69.9167
2015-05-24 22:45 | 56 | 57 | 69.8667 | 68.6667
2015-05-24 23:00 | 56 | 57 | 70 | 67.65
2015-05-24 23:15 | 56 | 57 | 70 | 66.9
2015-05-24 23:30 | 56 | 57 | 70 | 66.15
2015-05-24 23:45 | 56 | 57 | 70 | 65.4
2015-05-25 | 55.9333 | 57 | 69.8833 | 64.7667
2015-05-25 00:15 | 55.6833 | 57 | 69.6333 | 64.2667
2015-05-25 00:30 | 55.4333 | 57 | 69.3833 | 63.7667
2015-05-25 00:45 | 55.1833 | 57 | 69.1333 | 63.2667
2015-05-25 01:00 | 55 | 57 | 68.8833 | 62.8833
2015-05-25 01:15 | 55 | 57 | 68.6333 | 62.6333
2015-05-25 01:30 | 55 | 57 | 68.3833 | 62.3833
2015-05-25 01:45 | 55 | 57 | 68.1333 | 62.1333
2015-05-25 02:00 | 54.9149 | 57 | 67.7667 | 61.7667
2015-05-25 02:15 | 54.5957 | 57 | 67.2667 | 61.2667
2015-05-25 02:30 | 54.2766 | 57 | 66.7667 | 60.7667
2015-05-25 02:45 | 53.8462 | 57 | 66.2667 | 60.2667
2015-05-25 03:00 | 53.1905 | 57 | 65.7667 | 59.8833
2015-05-25 03:15 | 53.9048 | 57 | 65.2667 | 59.6333
2015-05-25 03:30 | 53.6667 | 57 | 64.7667 | 59.3833
2015-05-25 03:45 | 53.2821 | 57 | 64.2667 | 59.1333
2015-05-25 04:00 | 53.0755 | 56.8833 | 64.2333 | 58.8833
2015-05-25 04:15 | 53.3585 | 56.6333 | 64.7333 | 58.6333
2015-05-25 04:30 | 53.6415 | 56.3833 | 65.2333 | 58.3833
2015-05-25 04:45 | 53.9245 | 56.1333 | 65.7333 | 58.1333
2015-05-25 05:00 | 53.069 | 56.1167 | 65.4167 | 58.1167
2015-05-25 05:15 | 53.3276 | 56.3667 | 64.1667 | 58.3667
2015-05-25 05:30 | 53.5862 | 56.6167 | 62.9167 | 58.6167
2015-05-25 05:45 | 53.8448 | 56.8667 | 61.6667 | 58.8667
2015-05-25 06:00 | 53.1905 | 57 | 61.2333 | 59.2333
2015-05-25 06:15 | 53.9048 | 57 | 61.7333 | 59.7333
2015-05-25 06:30 | 54 | 57 | 62.2333 | 60.2333
2015-05-25 06:45 | 54 | 57 | 62.7333 | 60.7333
2015-05-25 07:00 | 53.0667 | 57.1167 | 63.5833 | 61.5833
2015-05-25 07:15 | 53.3167 | 57.3667 | 64.8333 | 62.8333
2015-05-25 07:30 | 53.5667 | 57.6167 | 66.0833 | 64.0833
2015-05-25 07:45 | 53.8167 | 57.8667 | 67.3333 | 65.3333
2015-05-25 08:00 | 54.1333 | 58.2333 | 68.7 | 66.5833
2015-05-25 08:15 | 54.6333 | 58.7333 | 70.2 | 67.8333
2015-05-25 08:30 | 55.1333 | 59.2333 | 71.7 | 69.0833
2015-05-25 08:45 | 55.6333 | 59.7333 | 73.2 | 70.3333
2015-05-25 09:00 | 55.8 | 60.1167 | 74.5833 | 71.4667
2015-05-25 09:15 | 55.05 | 60.3667 | 75.8333 | 72.4667
2015-05-25 09:30 | 55.35 | 60.6167 | 77.0833 | 73.4667
2015-05-25 09:45 | 55.725 | 60.8667 | 78.3333 | 74.4667
2015-05-25 10:00 | 56.2 | 61.4667 | 79.1167 | 75.4667
2015-05-25 10:15 | 56.95 | 62.4667 | 79.3667 | 76.4667
2015-05-25 10:30 | 57.7 | 63.4667 | 79.6167 | 77.4667
2015-05-25 10:45 | 58.45 | 64.4667 | 79.8667 | 78.4667
2015-05-25 11:00 | 59.1333 | 65.35 | 80.35 | 79.4667
2015-05-25 11:15 | 59.6333 | 66.1 | 81.1 | 80.4667
2015-05-25 11:30 | 60.1333 | 66.85 | 81.85 | 81.4667
2015-05-25 11:45 | 60.6333 | 67.6 | 82.6 | 82.4667
2015-05-25 12:00 | 61.0667 | 67.8833 | 83 | 83.1167
2015-05-25 12:15 | 61.3167 | 67.6333 | 83 | 83.3667
2015-05-25 12:30 | 61.5667 | 67.3833 | 83 | 83.6167
2015-05-25 12:45 | 61.8167 | 67.1333 | 83 | 83.8667
2015-05-25 13:00 | 61.9333 | 66.8833 | 83.1167 | 84.35
2015-05-25 13:15 | 61.6833 | 66.6333 | 83.3667 | 85.1
2015-05-25 13:30 | 61.4333 | 66.3833 | 83.6167 | 85.85
2015-05-25 13:45 | 61.1833 | 66.1333 | 83.8667 | 86.6
2015-05-25 14:00 | 61.1702 | 66 | 84 | 86.8833
2015-05-25 14:15 | 61.8085 | 66 | 84 | 86.6333
2015-05-25 14:30 | 62.4468 | 66 | 84 | 86.3833
2015-05-25 14:45 | 62.8462 | 66 | 84 | 86.1333
2015-05-25 15:00 | 61.9333 | 65.8833 | 84.1167 | 86.1167
2015-05-25 15:15 | 61.6833 | 65.6333 | 84.3667 | 86.3667
2015-05-25 15:30 | 61.4333 | 65.3833 | 84.6167 | 86.6167
2015-05-25 15:45 | 61.1833 | 65.1333 | 84.8667 | 86.8667
2015-05-25 16:00 | 60.8667 | 64.8833 | 85 | 87
2015-05-25 16:15 | 60.3667 | 64.6333 | 85 | 87
2015-05-25 16:30 | 59.8667 | 64.3833 | 85 | 87
2015-05-25 16:45 | 59.3667 | 64.1333 | 85 | 87
2015-05-25 17:00 | 58.9333 | 63.7667 | 85 | 86.7667
2015-05-25 17:15 | 58.6833 | 63.2667 | 85 | 86.2667
2015-05-25 17:30 | 58.4333 | 62.7667 | 85 | 85.7667
2015-05-25 17:45 | 58.1833 | 62.2667 | 85 | 85.2667
2015-05-25 18:00 | 57.9333 | 61.8511 | 84.65 | 84.65
2015-05-25 18:15 | 57.6833 | 61.5319 | 83.9 | 83.9
2015-05-25 18:30 | 57.4333 | 61.2128 | 83.15 | 83.15
2015-05-25 18:45 | 57.1833 | 60.6154 | 82.4 | 82.4
2015-05-25 19:00 | 57 | 59.7667 | 81.1833 | 81.5333
2015-05-25 19:15 | 57 | 59.2667 | 79.4333 | 80.5333
2015-05-25 19:30 | 57 | 58.7667 | 77.6833 | 79.5333
2015-05-25 19:45 | 57 | 58.2667 | 75.9333 | 78.5333
2015-05-25 20:00 | 56.9333 | 57.7667 | 74.4167 | 77.65
2015-05-25 20:15 | 56.6833 | 57.2667 | 73.1667 | 76.9
2015-05-25 20:30 | 56.4333 | 57 | 71.9167 | 76.15
2015-05-25 20:45 | 56.1833 | 57 | 70.6667 | 75.4
2015-05-25 21:00 | 56 | 57 | 69.65 | 74.5333
2015-05-25 21:15 | 56 | 57 | 68.9 | 73.5333
2015-05-25 21:30 | 56 | 57 | 68.15 | 72.5333
2015-05-25 21:45 | 56 | 57 | 67.4 | 71.5333
2015-05-25 22:00 | 56 | 57.1167 | 67 | 70.65
2015-05-25 22:15 | 56 | 57.3667 | 67 | 69.9
2015-05-25 22:30 | 56 | 57.6167 | 67 | 69.15
2015-05-25 22:45 | 56 | 57.8667 | 67 | 68.4
2015-05-25 23:00 | 55.9333 | 58 | 66.8833 | 67.65
2015-05-25 23:15 | 55.6833 | 58 | 66.6333 | 66.9
2015-05-25 23:30 | 55.4333 | 58 | 66.3833 | 66.15
2015-05-25 23:45 | 55.1833 | 58 | 66.1333 | 65.4
2015-05-26 | 54.9333 | 57.8833 | 65.65 | 64.7667
2015-05-26 00:15 | 54.6833 | 57.6333 | 64.9 | 64.2667
2015-05-26 00:30 | 54.4333 | 57.3833 | 64.15 | 63.7667
2015-05-26 00:45 | 54.1833 | 57.1333 | 63.4 | 63.2667
2015-05-26 01:00 | 54.2105 | 57 | 62.65 | 62.7667
2015-05-26 01:15 | 55 | 57 | 61.9 | 62.2667
2015-05-26 01:30 | 55 | 57 | 61.15 | 61.7667
2015-05-26 01:45 | 55 | 57 | 60.4 | 61.2667
2015-05-26 02:00 | 55 | 57 | 60.1167 | 60.7667
2015-05-26 02:15 | 55 | 57 | 60.3667 | 60.2667
2015-05-26 02:30 | 55 | 57 | 60.6167 | 59.7667
2015-05-26 02:45 | 55 | 57 | 60.8667 | 59.2667
2015-05-26 03:00 | 55 | 57 | 60.65 | 58.8833
2015-05-26 03:15 | 55 | 57 | 59.9 | 58.6333
2015-05-26 03:30 | 55 | 57 | 59.15 | 58.3833
2015-05-26 03:45 | 55 | 57 | 58.4 | 58.1333
2015-05-26 04:00 | 55 | 57 | 58.35 | 57.8833
2015-05-26 04:15 | 55 | 57 | 59.1 | 57.6333
2015-05-26 04:30 | 55 | 57 | 59.85 | 57.3833
2015-05-26 04:45 | 55 | 57 | 60.6 | 57.1333
2015-05-26 05:00 | 55 | 57 | 60.7667 | 57.1167
2015-05-26 05:15 | 55 | 57 | 60.2667 | 57.3667
2015-05-26 05:30 | 55 | 57 | 59.7667 | 57.6167
2015-05-26 05:45 | 55 | 57 | 59.2667 | 57.8667
2015-05-26 06:00 | 55.0667 | 57 | 59.35 | 58.2333
2015-05-26 06:15 | 55.3167 | 57 | 60.1 | 58.7333
2015-05-26 06:30 | 55.5667 | 57 | 60.85 | 59.2333
2015-05-26 06:45 | 55.8167 | 57 | 61.6 | 59.7333
2015-05-26 07:00 | 56.0667 | 57 | 62.8167 | 60.35
2015-05-26 07:15 | 56.3167 | 57 | 64.5667 | 61.1
2015-05-26 07:30 | 56.5667 | 57 | 66.3167 | 61.85
2015-05-26 07:45 | 56.8167 | 57 | 68.0667 | 62.6
2015-05-26 08:00 | 57 | 57.2333 | 69.5833 | 63.35
2015-05-26 08:15 | 57 | 57.7333 | 70.8333 | 64.1
2015-05-26 08:30 | 57 | 58.2333 | 72.0833 | 64.85
2015-05-26 08:45 | 57 | 58.7333 | 73.3333 | 65.6
2015-05-26 09:00 | 57 | 59.2333 | 74.7 | 66.5833
2015-05-26 09:15 | 57 | 59.7333 | 76.2 | 67.8333
2015-05-26 09:30 | 57.3333 | 60.2333 | 77.7 | 69.0833
2015-05-26 09:45 | 57.7179 | 60.7333 | 79.2 | 70.3333
2015-05-26 10:00 | 58.2069 | 61.4667 | 80.1167 | 71.5833
2015-05-26 10:15 | 58.9828 | 62.4667 | 80.3667 | 72.8333
2015-05-26 10:30 | 59.7586 | 63.4667 | 80.6167 | 74.0833
2015-05-26 10:45 | 60.5345 | 64.4667 | 80.8667 | 75.3333
2015-05-26 11:00 | 60.1333 | 65.2333 | 81.4667 | 76.2333
2015-05-26 11:15 | 60.6333 | 65.7333 | 82.4667 | 76.7333
2015-05-26 11:30 | 61.1333 | 66.2333 | 83.4667 | 77.2333
2015-05-26 11:45 | 61.6333 | 66.7333 | 84.4667 | 77.7333
2015-05-26 12:00 | 62.1667 | 67.1167 | 85.2333 | 78.5833
2015-05-26 12:15 | 62.7917 | 67.3667 | 85.7333 | 79.8333
2015-05-26 12:30 | 63.4167 | 67.6167 | 86.2333 | 81.0833
2015-05-26 12:45 | 64 | 67.8667 | 86.7333 | 82.3333
2015-05-26 13:00 | 64 | 68 | 87 | 83.1167
2015-05-26 13:15 | 64 | 68 | 87 | 83.3667
2015-05-26 13:30 | 64 | 68 | 87 | 83.6167
2015-05-26 13:45 | 64 | 68 | 87 | 83.8667
2015-05-26 14:00 | 64 | 67.8833 | 87.35 | 84.1167
2015-05-26 14:15 | 64 | 67.6333 | 88.1 | 84.3667
2015-05-26 14:30 | 64 | 67.3833 | 88.85 | 84.6167
2015-05-26 14:45 | 64 | 67.1333 | 89.6 | 84.8667
2015-05-26 15:00 | 63.9333 | 67 | 90.1167 | 85
2015-05-26 15:15 | 63.6833 | 67 | 90.3667 | 85
2015-05-26 15:30 | 63.4333 | 67 | 90.6167 | 85
2015-05-26 15:45 | 63.1833 | 67 | 90.8667 | 85
2015-05-26 16:00 | 62.9333 | 66.7667 | 90.7667 | 85
2015-05-26 16:15 | 62.6833 | 66.2667 | 90.2667 | 85
2015-05-26 16:30 | 62.4333 | 65.7667 | 89.7667 | 85
2015-05-26 16:45 | 62.1833 | 65.2667 | 89.2667 | 85
2015-05-26 17:00 | 61.7647 | 64.7586 | 88.7667 | 84.7667
2015-05-26 17:15 | 60.907 | 64.2414 | 88.2667 | 84.2667
2015-05-26 17:30 | 60.2093 | 63.7241 | 87.7667 | 83.7667
2015-05-26 17:45 | 59.5116 | 63.2069 | 87.2667 | 83.2667
2015-05-26 18:00 | 58.9333 | 62.65 | 86.8833 | 82.7667
2015-05-26 18:15 | 58.6833 | 61.9 | 86.6333 | 82.2667
2015-05-26 18:30 | 58.4333 | 61.15 | 86.3833 | 81.7667
2015-05-26 18:45 | 58.1833 | 60.4 | 86.1333 | 81.2667
2015-05-26 19:00 | 58 | 59.7667 | 85.125 | 80.7667
2015-05-26 19:15 | 58 | 59.2667 | 83.9487 | 80.2667
2015-05-26 19:30 | 58 | 58.7667 | 83.1795 | 79.7667
2015-05-26 19:45 | 58 | 58.2667 | 82.4103 | 79.2667
2015-05-26 20:00 | 57.9333 | 57.7742 | 81.5333 | 78.65
2015-05-26 20:15 | 57.6833 | 57.2903 | 80.5333 | 77.9
2015-05-26 20:30 | 57.4333 | 57.2069 | 79.5333 | 77.15
2015-05-26 20:45 | 57.1833 | 57.7241 | 78.5333 | 76.4
2015-05-26 21:00 | 57 | 58 | 77.65 | 75.5333
2015-05-26 21:15 | 57 | 58 | 76.9 | 74.5333
2015-05-26 21:30 | 57 | 58 | 76.15 | 73.5333
2015-05-26 21:45 | 57 | 58 | 75.4 | 72.5333
2015-05-26 22:00 | 56.9333 | 58 | 74.8833 | 71.5333
2015-05-26 22:15 | 56.6833 | 58 | 74.6333 | 70.5333
2015-05-26 22:30 | 56.4333 | 58 | 74.3833 | 69.5333
2015-05-26 22:45 | 56.1833 | 58 | 74.1333 | 68.5333
2015-05-26 23:00 | 56 | 58 | 73.7667 | 67.65
2015-05-26 23:15 | 56 | 58 | 73.2667 | 66.9
2015-05-26 23:30 | 56 | 58 | 72.7667 | 66.15
2015-05-26 23:45 | 56 | 58 | 72.2667 | 65.4
2015-05-27 | 56.0667 | 58 | 71.7667 | 64.7667
2015-05-27 00:15 | 56.3167 | 58 | 71.2667 | 64.2667
2015-05-27 00:30 | 56.5667 | 58 | 70.7667 | 63.7667
2015-05-27 00:45 | 56.8167 | 58 | 70.2667 | 63.2667
2015-05-27 01:00 | 56.9333 | 58 | 70 | 62.65
2015-05-27 01:15 | 56.6833 | 58 | 70 | 61.9
2015-05-27 01:30 | 56.4333 | 58 | 70 | 61.15
2015-05-27 01:45 | 56.1833 | 58 | 70 | 60.4
2015-05-27 02:00 | 56 | 58 | 69.7667 | 59.8833
2015-05-27 02:15 | 56 | 58 | 69.2667 | 59.6333
2015-05-27 02:30 | 56 | 58 | 68.7667 | 59.3833
2015-05-27 02:45 | 56 | 58 | 68.2667 | 59.1333
2015-05-27 03:00 | 55.9333 | 58 | 67.8833 | 58.8833
2015-05-27 03:15 | 55.6833 | 58 | 67.6333 | 58.6333
2015-05-27 03:30 | 55.4333 | 58 | 67.3833 | 58.3833
2015-05-27 03:45 | 55.1833 | 58 | 67.1333 | 58.1333
2015-05-27 04:00 | 54.9333 | 57.8158 | 66.7667 | 57.7667
2015-05-27 04:15 | 54.6833 | 57.4211 | 66.2667 | 57.2667
2015-05-27 04:30 | 54.4333 | 57.0263 | 65.7667 | 56.7667
2015-05-27 04:45 | 54.1833 | 57.6364 | 65.2667 | 56.2667
2015-05-27 05:00 | 54 | 58 | 65.1167 | 56.2333
2015-05-27 05:15 | 54 | 58 | 65.3667 | 56.7333
2015-05-27 05:30 | 54 | 58 | 65.6167 | 57.2333
2015-05-27 05:45 | 54 | 58 | 65.8667 | 57.7333
2015-05-27 06:00 | 54.0667 | 58.1167 | 66.2333 | 58.4667
2015-05-27 06:15 | 54.3167 | 58.3667 | 66.7333 | 59.4667
2015-05-27 06:30 | 54.5667 | 58.6167 | 67.2333 | 60.4667
2015-05-27 06:45 | 54.8167 | 58.8667 | 67.7333 | 61.4667
2015-05-27 07:00 | 55.2286 | 58.8833 | 68.4667 | 62.4667
2015-05-27 07:15 | 56.0857 | 58.6333 | 69.4667 | 63.4667
2015-05-27 07:30 | 56.9429 | 58.3833 | 70.4667 | 64.4667
2015-05-27 07:45 | 57.56 | 58.1333 | 71.4667 | 65.4667
2015-05-27 08:00 | 58.0667 | 58.3684 | 72.35 | 66.4667
2015-05-27 08:15 | 58.3167 | 59.2195 | 73.1 | 67.4667
2015-05-27 08:30 | 58.5667 | 60.3171 | 73.85 | 68.4667
2015-05-27 08:45 | 58.8167 | 61.4146 | 74.6 | 69.4667
2015-05-27 09:00 | 59.0667 | 62.4667 | 75.4667 | 70.4667
2015-05-27 09:15 | 59.3167 | 63.4667 | 76.4667 | 71.4667
2015-05-27 09:30 | 59.5667 | 64.4667 | 77.4667 | 72.4667
2015-05-27 09:45 | 59.8167 | 65.4667 | 78.4667 | 73.4667
2015-05-27 10:00 | 60.5714 | 66.2333 | 79.35 | 74.4667
2015-05-27 10:15 | 61.4528 | 66.7333 | 80.1 | 75.4667
2015-05-27 10:30 | 62.0189 | 67.2333 | 80.85 | 76.4667
2015-05-27 10:45 | 62.5849 | 67.7333 | 81.6 | 77.4667
2015-05-27 11:00 | 63 | 68.2333 | 82.4667 | 78.4667
2015-05-27 11:15 | 63 | 68.7333 | 83.4667 | 79.4667
2015-05-27 11:30 | 63 | 69.2333 | 84.4667 | 80.4667
2015-05-27 11:45 | 63 | 69.7333 | 85.4667 | 81.4667
2015-05-27 12:00 | 63.0667 | 70 | 86.35 | 82.2333
2015-05-27 12:15 | 63.3167 | 70 | 87.1 | 82.7333
2015-05-27 12:30 | 63.5667 | 70 | 87.85 | 83.2333
2015-05-27 12:45 | 63.8167 | 70 | 88.6 | 83.7333
2015-05-27 13:00 | 63.8667 | 69.7667 | 89.2333 | 84.35
2015-05-27 13:15 | 63.3667 | 69.2667 | 89.7333 | 85.1
2015-05-27 13:30 | 62.8667 | 68.7667 | 90.2333 | 85.85
2015-05-27 13:45 | 62.3667 | 68.2667 | 90.7333 | 86.6
2015-05-27 14:00 | 61.9091 | 68 | 91.1167 | 87.1167
2015-05-27 14:15 | 61.5682 | 68 | 91.3667 | 87.3667
2015-05-27 14:30 | 61.2273 | 68 | 91.6167 | 87.6167
2015-05-27 14:45 | 61 | 68 | 91.8667 | 87.8667
2015-05-27 15:00 | 61 | 67.65 | 91.8833 | 88
2015-05-27 15:15 | 61 | 66.9 | 91.6333 | 88
2015-05-27 15:30 | 60.4444 | 66.15 | 91.3833 | 88
2015-05-27 15:45 | 59.6111 | 65.4 | 91.1333 | 88
2015-05-27 16:00 | 58.9333 | 64.7667 | 90.8833 | 88
2015-05-27 16:15 | 58.6833 | 64.2667 | 90.6333 | 88
2015-05-27 16:30 | 58.4333 | 63.7667 | 90.3833 | 88
2015-05-27 16:45 | 58.1833 | 63.2667 | 90.1333 | 88
2015-05-27 17:00 | 58 | 62.7667 | 89.4167 | 87.7667
2015-05-27 17:15 | 58 | 62.2667 | 88.1667 | 87.2667
2015-05-27 17:30 | 58 | 61.7667 | 86.9167 | 86.7667
2015-05-27 17:45 | 58 | 61.2667 | 85.6667 | 86.2667
2015-05-27 18:00 | 57.9333 | 60.7667 | 84.6111 | 85.65
2015-05-27 18:15 | 57.6833 | 60.2667 | 83.7778 | 84.9
2015-05-27 18:30 | 57.4333 | 59.7667 | 82.9583 | 84.15
2015-05-27 18:45 | 57.1833 | 59.2667 | 82.3333 | 83.4
2015-05-27 19:00 | 56.8621 | 58.7667 | 82 | 82.5333
2015-05-27 19:15 | 56.3448 | 58.2667 | 81.1463 | 81.5333
2015-05-27 19:30 | 55.8276 | 57.7667 | 78.5854 | 80.5333
2015-05-27 19:45 | 55.3103 | 57.2667 | 76.0244 | 79.5333
2015-05-27 20:00 | 55.9333 | 57 | 74.4615 | 78.65
2015-05-27 20:15 | 55.6833 | 57 | 72.7143 | 77.9
2015-05-27 20:30 | 55.4333 | 57 | 69 | 77.15
2015-05-27 20:45 | 55.1833 | 57 | 67.8889 | 76.4
2015-05-27 21:00 | 55 | 57 | 68.5 | 75.5333
2015-05-27 21:15 | 55 | 57 | 71.7143 | 74.5333
2015-05-27 21:30 | 55 | 57 | 72.0952 | 73.5333
2015-05-27 21:45 | 55 | 57 | 72.8095 | 72.5333
2015-05-27 22:00 | 54.9333 | 57 | 72.125 | 71.8833
2015-05-27 22:15 | 54.6833 | 57 | 72.7778 | 71.6333
2015-05-27 22:30 | 54.4333 | 57 | 72.6765 | 71.3833
2015-05-27 22:45 | 54.1833 | 57 | 72.2353 | 71.1333
2015-05-27 23:00 | 54 | 57 | 72.1167 | 70.65
2015-05-27 23:15 | 54 | 57 | 72.3667 | 69.9
2015-05-27 23:30 | 54 | 57 | 72.6167 | 69.15
2015-05-27 23:45 | 54 | 57 | 72.8667 | 68.4
2015-05-28 | 54 | 57 | 72.8833 | 67.65
2015-05-28 00:15 | 54 | 57 | 72.6333 | 66.9
2015-05-28 00:30 | 54 | 57 | 72.3833 | 66.15
2015-05-28 00:45 | 54 | 57 | 72.1333 | 65.4
2015-05-28 01:00 | 54 | 57 | 71.8833 | 64.7667
2015-05-28 01:15 | 54 | 57 | 71.6333 | 64.2667
2015-05-28 01:30 | 54 | 57 | 71.3833 | 63.7667
2015-05-28 01:45 | 54 | 57 | 71.1333 | 63.2667
2015-05-28 02:00 | 54 | 57 | 70.8793 | 62.7667
2015-05-28 02:15 | 54 | 57 | 70.6207 | 62.2667
2015-05-28 02:30 | 54 | 57 | 70.3621 | 61.7667
2015-05-28 02:45 | 54 | 57 | 70.1034 | 61.2667
2015-05-28 03:00 | 53.9333 | 56.8833 | 70 | 60.8833
2015-05-28 03:15 | 53.6833 | 56.6333 | 70 | 60.6333
2015-05-28 03:30 | 53.4333 | 56.3833 | 70 | 60.3833
2015-05-28 03:45 | 53.1833 | 56.1333 | 70 | 60.1333
2015-05-28 04:00 | 53 | 55.4167 | 70 | 59.8833
2015-05-28 04:15 | 53 | 55 | 70 | 59.6333
2015-05-28 04:30 | 53 | 55 | 70 | 59.3833
2015-05-28 04:45 | 53 | 55 | 70 | 59.1333
2015-05-28 05:00 | 53 | 56 | 70 | 59.2333
2015-05-28 05:15 | 53 | 56 | 70 | 59.7333
2015-05-28 05:30 | 53 | 56 | 70 | 60.2333
2015-05-28 05:45 | 53 | 56 | 70 | 60.7333
2015-05-28 06:00 | 53 | 56 | 70 | 61.5833
2015-05-28 06:15 | 53 | 56 | 70 | 62.8333
2015-05-28 06:30 | 53 | 56 | 70 | 64.0833
2015-05-28 06:45 | 53 | 56 | 70 | 65.3333
2015-05-28 07:00 | 53.0667 | 56.35 | 70.2333 | 66.4667
2015-05-28 07:15 | 53.3167 | 57.1 | 70.7333 | 67.4667
2015-05-28 07:30 | 53.5667 | 57.85 | 71.2333 | 68.4667
2015-05-28 07:45 | 53.8167 | 58.6 | 71.7333 | 69.4667
2015-05-28 08:00 | 54.1333 | 60 | 72.35 | 70.5833
2015-05-28 08:15 | 54.6333 | 61.1739 | 73.1 | 71.8333
2015-05-28 08:30 | 55.1333 | 61.5 | 73.85 | 73.0833
2015-05-28 08:45 | 55.6333 | 61.8261 | 74.6 | 74.3333
2015-05-28 09:00 | 55.9216 | 62.2333 | 75.2333 | 75.35
2015-05-28 09:15 | 55.6275 | 62.7333 | 75.7333 | 76.1
2015-05-28 09:30 | 55.3333 | 63.2333 | 76.2333 | 76.85
2015-05-28 09:45 | 55.0392 | 63.7333 | 76.7333 | 77.6
2015-05-28 10:00 | 56.1333 | 64.1167 | 77.2333 | 78.35
2015-05-28 10:15 | 56.6333 | 64.3667 | 77.7333 | 79.1
2015-05-28 10:30 | 57.1333 | 64.6167 | 78.2333 | 79.85
2015-05-28 10:45 | 57.6333 | 64.8667 | 78.7333 | 80.6
2015-05-28 11:00 | 58.1333 | 65.1167 | 79.4667 | 81.35
2015-05-28 11:15 | 58.6333 | 65.3667 | 80.4667 | 82.1
2015-05-28 11:30 | 59.1333 | 65.6167 | 81.4667 | 82.85
2015-05-28 11:45 | 59.6333 | 65.8667 | 82.4667 | 83.6
2015-05-28 12:00 | 60.069 | 66 | 83.5833 | 84.2333
2015-05-28 12:15 | 60.3276 | 66 | 84.8333 | 84.7333
2015-05-28 12:30 | 60.5862 | 66 | 86.0833 | 85.2333
2015-05-28 12:45 | 60.8448 | 66 | 87.3333 | 85.7333
2015-05-28 13:00 | 61.9333 | 66.2333 | 87.5333 | 86.1167
2015-05-28 13:15 | 61.6833 | 66.7333 | 86.5333 | 86.3667
2015-05-28 13:30 | 61.4333 | 67.2333 | 85.5333 | 86.6167
2015-05-28 13:45 | 61.1833 | 67.7333 | 84.5333 | 86.8667
2015-05-28 14:00 | 60.9333 | 67.8833 | 83.65 | 87.1167
2015-05-28 14:15 | 60.6833 | 67.6333 | 82.9 | 87.3667
2015-05-28 14:30 | 60.4333 | 67.3833 | 82.15 | 87.6167
2015-05-28 14:45 | 60.1833 | 67.1333 | 81.4 | 87.8667
2015-05-28 15:00 | 59.9333 | 67 | 79.32 | 88.2333
2015-05-28 15:15 | 59.6833 | 67 | 75.72 | 88.7333
2015-05-28 15:30 | 59.4333 | 67 | 76.5417 | 89.2333
2015-05-28 15:45 | 59.1833 | 67 | 69.6667 | 89.7333
2015-05-28 16:00 | 58.9333 | 66.8833 | 66.3571 | 89.8833
2015-05-28 16:15 | 58.6833 | 66.6333 | 64 | 89.6333
2015-05-28 16:30 | 58.4333 | 66.3833 | 64.7568 | 89.3833
2015-05-28 16:45 | 58.1833 | 66.1333 | 65.5676 | 89.1333
2015-05-28 17:00 | 57.8667 | 65.65 | 65.8654 | 88.7667
2015-05-28 17:15 | 57.3667 | 64.9 | 65.5769 | 88.2667
2015-05-28 17:30 | 56.8667 | 64.15 | 65.2885 | 87.7667
2015-05-28 17:45 | 56.3667 | 63.4 | 65 | 87.2667
2015-05-28 18:00 | 55.9333 | 62.65 | 65 | 86.7667
2015-05-28 18:15 | 55.6833 | 61.9 | 65 | 86.2667
2015-05-28 18:30 | 55.4333 | 61.15 | 65 | 85.7667
2015-05-28 18:45 | 55.1833 | 60.4 | 64.6667 | 85.2667
2015-05-28 19:00 | 55 | 59.5333 | 65 | 84.3
2015-05-28 19:15 | 55 | 58.5333 | 64.717 | 82.8
2015-05-28 19:30 | 55 | 57.5333 | 64.434 | 81.3
2015-05-28 19:45 | 55 | 56.5333 | 64.1509 | 79.8
2015-05-28 20:00 | 55 | 55.65 | 63.8833 | 78.8833
2015-05-28 20:15 | 55 | 55 | 63.6333 | 78.6333
2015-05-28 20:30 | 55 | 55 | 63.3833 | 78.3833
2015-05-28 20:45 | 55 | 55 | 63.1333 | 78.1333
2015-05-28 21:00 | 54.8667 | 56 | 63.2333 | 77.65
2015-05-28 21:15 | 54.3667 | 56 | 63.7333 | 76.9
2015-05-28 21:30 | 53.8667 | 56 | 64.2333 | 76.15
2015-05-28 21:45 | 53.3667 | 56 | 64.7333 | 75.4
2015-05-28 22:00 | 53 | 56 | 64.7667 | 74.7667
2015-05-28 22:15 | 53 | 56 | 64.2667 | 74.2667
2015-05-28 22:30 | 53 | 56 | 63.7667 | 73.7667
2015-05-28 22:45 | 53 | 56 | 63.2667 | 73.2667
2015-05-28 23:00 | 53.0667 | 56 | 63 | 72.65
2015-05-28 23:15 | 53.3167 | 56 | 63 | 71.9
2015-05-28 23:30 | 53.5667 | 56 | 63 | 71.15
2015-05-28 23:45 | 53.8167 | 56 | 63 | 70.4
2015-05-29 | 54 | 56 | 63 | 69.7667
2015-05-29 00:15 | 54 | 56 | 63 | 69.2667
2015-05-29 00:30 | 54 | 56 | 63 | 68.7667
2015-05-29 00:45 | 54 | 56 | 63 | 68.2667
2015-05-29 01:00 | 54 | 55.8833 | 62.7667 | 67.7667
2015-05-29 01:15 | 54 | 55.6333 | 62.2667 | 67.2667
2015-05-29 01:30 | 54 | 55.3833 | 61.7667 | 66.7667
2015-05-29 01:45 | 54 | 55.1333 | 61.2667 | 66.2667
2015-05-29 02:00 | 54 | 55 | 60.7667 | 65.7667
2015-05-29 02:15 | 54 | 55 | 60.2667 | 65.2667
2015-05-29 02:30 | 54 | 55 | 59.7667 | 64.7667
2015-05-29 02:45 | 54 | 55 | 59.2667 | 64.2667
2015-05-29 03:00 | 54 | 55.1167 | 59.2333 | 63.7667
2015-05-29 03:15 | 54 | 55.3667 | 59.7333 | 63.2667
2015-05-29 03:30 | 54 | 55.6167 | 60.2333 | 62.7667
2015-05-29 03:45 | 54 | 55.8667 | 60.7333 | 62.2667
2015-05-29 04:00 | 54 | 55.8833 | 60.8833 | 62
2015-05-29 04:15 | 54 | 55.6333 | 60.6333 | 62
2015-05-29 04:30 | 54 | 55.3833 | 60.3833 | 62
2015-05-29 04:45 | 54 | 55.1333 | 60.1333 | 62
2015-05-29 05:00 | 54 | 55.1167 | 59.7667 | 62.1167
2015-05-29 05:15 | 54 | 55.3667 | 59.2667 | 62.3667
2015-05-29 05:30 | 54 | 55.6167 | 58.7667 | 62.6167
2015-05-29 05:45 | 54 | 55.8667 | 58.2667 | 62.8667
2015-05-29 06:00 | 54 | 56 | 58.7 | 63.5833
2015-05-29 06:15 | 54 | 56 | 60.2 | 64.8333
2015-05-29 06:30 | 54 | 56 | 61.7 | 66.0833
2015-05-29 06:45 | 54 | 56 | 63.2 | 67.3333
2015-05-29 07:00 | 54.0667 | 56.1167 | 64.2333 | 68.7
2015-05-29 07:15 | 54.3167 | 56.3667 | 64.7333 | 70.2
2015-05-29 07:30 | 54.5667 | 56.6167 | 65.2333 | 71.7
2015-05-29 07:45 | 54.8167 | 56.8667 | 65.7333 | 73.2
2015-05-29 08:00 | 55.0667 | 57.2333 | 66.2333 | 74.4667
2015-05-29 08:15 | 55.3167 | 57.7333 | 66.7333 | 75.4667
2015-05-29 08:30 | 55.5667 | 58.2333 | 67.2333 | 76.4667
2015-05-29 08:45 | 55.8167 | 58.7333 | 67.7333 | 77.4667
2015-05-29 09:00 | 56.0667 | 59.5283 | 68.35 | 78.5833
2015-05-29 09:15 | 56.3167 | 60.6604 | 69.1 | 79.8333
2015-05-29 09:30 | 56.5667 | 61.7925 | 69.85 | 81.0833
2015-05-29 09:45 | 56.8167 | 62.9245 | 70.6 | 82.3333
2015-05-29 10:00 | 57.3019 | 62.35 | 71.2333 | 83.35
2015-05-29 10:15 | 58.434 | 63.1 | 71.7333 | 84.1
2015-05-29 10:30 | 59.566 | 63.85 | 72.2333 | 84.85
2015-05-29 10:45 | 60.6981 | 64.6 | 72.7333 | 85.6
2015-05-29 11:00 | 61.9333 | 65.35 | 73.2333 | 86.1167
2015-05-29 11:15 | 61.6833 | 66.1 | 73.7333 | 86.3667
2015-05-29 11:30 | 61.4333 | 66.85 | 74.2333 | 86.6167
2015-05-29 11:45 | 61.1833 | 67.6 | 74.7333 | 86.8667
2015-05-29 12:00 | 60.9333 | 68.1167 | 75.35 | 87.35
2015-05-29 12:15 | 60.6833 | 68.3667 | 76.1 | 88.1
2015-05-29 12:30 | 60.4333 | 68.6167 | 76.85 | 88.85
2015-05-29 12:45 | 60.1833 | 68.8667 | 77.6 | 89.6
2015-05-29 13:00 | 60.0667 | 69 | 78.35 | 90.35
2015-05-29 13:15 | 60.3167 | 69 | 79.1 | 91.1
2015-05-29 13:30 | 60.5667 | 69 | 79.85 | 91.85
2015-05-29 13:45 | 60.8167 | 69 | 80.6 | 92.6
2015-05-29 14:00 | 61 | 68.7667 | 81.2333 | 93
2015-05-29 14:15 | 61 | 68.2667 | 81.7333 | 93
2015-05-29 14:30 | 61 | 67.7667 | 82.2333 | 93
2015-05-29 14:45 | 61 | 67.2667 | 82.7333 | 93
2015-05-29 15:00 | 60.8667 | 67.1167 | 83.1167 | 93.1167
2015-05-29 15:15 | 60.3667 | 67.3667 | 83.3667 | 93.3667
2015-05-29 15:30 | 59.8667 | 67.6167 | 83.6167 | 93.6167
2015-05-29 15:45 | 59.3667 | 67.8667 | 83.8667 | 93.8667
2015-05-29 16:00 | 58.8222 | 67.65 | 84.1167 | 94
2015-05-29 16:15 | 58.1556 | 66.9 | 84.3667 | 94
2015-05-29 16:30 | 57.4889 | 66.15 | 84.6167 | 94
2015-05-29 16:45 | 57 | 65.4 | 84.8667 | 94
2015-05-29 17:00 | 57 | 64.7667 | 85 | 93.7667
2015-05-29 17:15 | 57 | 64.2667 | 85 | 93.2667
2015-05-29 17:30 | 56.6842 | 63.7667 | 85 | 92.7667
2015-05-29 17:45 | 56.2895 | 63.2667 | 85 | 92.2667
2015-05-29 18:00 | 55.9333 | 62.5333 | 84.7667 | 91.65
2015-05-29 18:15 | 55.6833 | 61.5333 | 84.2667 | 90.9
2015-05-29 18:30 | 55.4333 | 60.5333 | 83.7667 | 90.15
2015-05-29 18:45 | 55.1833 | 59.5333 | 83.2667 | 89.4
2015-05-29 19:00 | 54.9333 | 58.65 | 82.3 | 88.4167
2015-05-29 19:15 | 54.6833 | 57.9 | 80.8 | 87.1667
2015-05-29 19:30 | 54.4333 | 57.15 | 79.3 | 85.9167
2015-05-29 19:45 | 54.1833 | 56.4 | 77.8 | 84.6667
2015-05-29 20:00 | 54 | 56 | 76.65 | 83.7667
2015-05-29 20:15 | 54 | 56 | 75.9 | 83.2667
2015-05-29 20:30 | 54 | 56 | 75.15 | 82.7667
2015-05-29 20:45 | 54 | 56 | 74.4 | 82.2667
2015-05-29 21:00 | 54 | 55.8833 | 73.7667 | 81.65
2015-05-29 21:15 | 54 | 55.6333 | 73.2667 | 80.9
2015-05-29 21:30 | 54 | 55.3833 | 72.7667 | 80.15
2015-05-29 21:45 | 54 | 55.1333 | 72.2667 | 79.4
2015-05-29 22:00 | 54 | 55 | 72 | 78.5333
2015-05-29 22:15 | 54 | 55 | 72 | 77.5333
2015-05-29 22:30 | 54 | 55 | 72 | 76.5333
2015-05-29 22:45 | 54 | 55 | 72 | 75.5333
2015-05-29 23:00 | 54 | 55 | 71.7879 | 74.7667
2015-05-29 23:15 | 54 | 55 | 71.3333 | 74.2667
2015-05-29 23:30 | 54 | 55 | 71 | 73.7667
2015-05-29 23:45 | 54 | 55 | 71 | 73.2667
2015-05-30 | 54 | 54.8833 | 70.8333 | 72.7667
2015-05-30 00:15 | 53.8913 | 54.6333 | 70.4762 | 72.2667
2015-05-30 00:30 | 53.5652 | 54.3833 | 70.119 | 71.7667
2015-05-30 00:45 | 53.2391 | 54.1333 | 70 | 71.2667
2015-05-30 01:00 | 53 | 54.2333 | 69.14 | 70.65
2015-05-30 01:15 | 53 | 54.7333 | 69.44 | 69.9
2015-05-30 01:30 | 53 | 55.2333 | 69.74 | 69.15
2015-05-30 01:45 | 53 | 55.7333 | 70 | 68.4
2015-05-30 02:00 | 52.9333 | 55.8833 | 69.7586 | 67.8833
2015-05-30 02:15 | 52.6833 | 55.6333 | 69.2414 | 67.6333
2015-05-30 02:30 | 52.4333 | 55.3833 | 69 | 67.3833
2015-05-30 02:45 | 52.1833 | 55.1333 | 69 | 67.1333
2015-05-30 03:00 | 52.0667 | 55.1167 | 69 | 66.7667
2015-05-30 03:15 | 52.3167 | 55.3667 | 68.2727 | 66.2667
2015-05-30 03:30 | 52.5667 | 55.6167 | 67.3636 | 65.7667
2015-05-30 03:45 | 52.8167 | 55.8667 | 66.4706 | 65.2667
2015-05-30 04:00 | 53 | 55.8833 | 65.7667 | 64.8833
2015-05-30 04:15 | 53 | 55.6333 | 65.2667 | 64.6333
2015-05-30 04:30 | 53 | 55.3833 | 64.7667 | 64.3833
2015-05-30 04:45 | 53 | 55.1333 | 64.2667 | 64.1333
2015-05-30 05:00 | 53 | 55 | 64 | 64.2333
2015-05-30 05:15 | 53 | 55 | 64 | 64.7333
2015-05-30 05:30 | 53 | 55 | 64 | 65.2333
2015-05-30 05:45 | 53 | 55 | 64 | 65.7333
2015-05-30 06:00 | 53.0667 | 55 | 63.3 | 66.8167
2015-05-30 06:15 | 53.3167 | 55 | 61.8 | 68.5667
2015-05-30 06:30 | 53.5667 | 55 | 60.3 | 70.3167
2015-05-30 06:45 | 53.8167 | 55 | 58.8 | 72.0667
2015-05-30 07:00 | 54.0667 | 55 | 58.3621 | 73.7
2015-05-30 07:15 | 54.3167 | 55 | 59.1379 | 75.2
2015-05-30 07:30 | 54.5667 | 55.9091 | 59.9138 | 76.7
2015-05-30 07:45 | 54.8167 | 57.2727 | 60.6897 | 78.2
2015-05-30 08:00 | 55 | 58.7778 | 59.8727 | 79.35
2015-05-30 08:15 | 55 | 60.4444 | 59.6 | 80.1
2015-05-30 08:30 | 55 | 61 | 59.3273 | 80.85
2015-05-30 08:45 | 55 | 61 | 59.0545 | 81.6
2015-05-30 09:00 | 55.1333 | 61.2333 | 59.9333 | 82.4667
2015-05-30 09:15 | 55.6333 | 61.7333 | 61.9333 | 83.4667
2015-05-30 09:30 | 56.1333 | 62.2333 | 63.9333 | 84.4667
2015-05-30 09:45 | 56.6333 | 62.7333 | 65.9333 | 85.4667
2015-05-30 10:00 | 57.2581 | 63.1167 | 67.35 | 86.35
2015-05-30 10:15 | 58.2258 | 63.3667 | 68.1 | 87.1
2015-05-30 10:30 | 59.1034 | 63.6167 | 68.85 | 87.85
2015-05-30 10:45 | 59.6207 | 63.8667 | 69.6 | 88.6
2015-05-30 11:00 | 60.0667 | 64.35 | 70.2333 | 89.35
2015-05-30 11:15 | 60.3167 | 65.1 | 70.7333 | 90.1
2015-05-30 11:30 | 60.5667 | 65.85 | 71.2333 | 90.85
2015-05-30 11:45 | 60.8167 | 66.6 | 71.7333 | 91.6
2015-05-30 12:00 | 61.1333 | 67.2333 | 72.2333 | 92.35
2015-05-30 12:15 | 61.6333 | 67.7333 | 72.7333 | 93.1
2015-05-30 12:30 | 62.1333 | 68.2333 | 73.2333 | 93.85
2015-05-30 12:45 | 62.6333 | 68.7333 | 73.7333 | 94.6
2015-05-30 13:00 | 63 | 69.2333 | 74.2333 | 95.1167
2015-05-30 13:15 | 63 | 69.7333 | 74.7333 | 95.3667
2015-05-30 13:30 | 63 | 70.2333 | 75.2333 | 95.6167
2015-05-30 13:45 | 63 | 70.7333 | 75.7333 | 95.8667
2015-05-30 14:00 | 63 | 71.1167 | 76.2333 | 96.2333
2015-05-30 14:15 | 63 | 71.3667 | 76.7333 | 96.7333
2015-05-30 14:30 | 63 | 71.6167 | 77.2333 | 97.2333
2015-05-30 14:45 | 63 | 71.8667 | 77.7333 | 97.7333
2015-05-30 15:00 | 62.8667 | 72 | 78 | 98
2015-05-30 15:15 | 62.3667 | 72 | 78 | 98
2015-05-30 15:30 | 61.8667 | 72 | 78 | 98
2015-05-30 15:45 | 61.3667 | 72 | 78 | 98
2015-05-30 16:00 | 60.8667 | 71.65 | 77.8833 | 97.8833
2015-05-30 16:15 | 60.3667 | 70.9 | 77.6333 | 97.6333
2015-05-30 16:30 | 59.8667 | 70.15 | 77.3833 | 97.3833
2015-05-30 16:45 | 59.3667 | 69.4 | 77.1333 | 97.1333
2015-05-30 17:00 | 58.8667 | 68.5333 | 76.8833 | 96.8833
2015-05-30 17:15 | 58.3667 | 67.5333 | 76.6333 | 96.6333
2015-05-30 17:30 | 57.8667 | 66.5333 | 76.3833 | 96.3833
2015-05-30 17:45 | 57.3667 | 65.5333 | 76.1333 | 96.1333
2015-05-30 18:00 | 56.5556 | 64.4167 | 75.8833 | 95.5333
2015-05-30 18:15 | 55 | 63.1667 | 75.6333 | 94.5333
2015-05-30 18:30 | 55 | 61.9167 | 75.3833 | 93.5333
2015-05-30 18:45 | 55 | 60.6667 | 75.1333 | 92.5333
2015-05-30 19:00 | 55 | 59.65 | 74.4167 | 91.4167
2015-05-30 19:15 | 55 | 58.9 | 73.1667 | 90.1667
2015-05-30 19:30 | 55 | 58.15 | 71.9167 | 88.9167
2015-05-30 19:45 | 55 | 57.4 | 70.6667 | 87.6667
2015-05-30 20:00 | 55 | 57 | 69.7667 | 86.7667
2015-05-30 20:15 | 55 | 56.7917 | 69.2667 | 86.2667
2015-05-30 20:30 | 55 | 56.4792 | 68.7667 | 85.7667
2015-05-30 20:45 | 55 | 56.1667 | 68.2667 | 85.2667
2015-05-30 21:00 | 54.9333 | 56.1167 | 67.7667 | 84.4167
2015-05-30 21:15 | 54.6833 | 56.3667 | 67.2667 | 83.1667
2015-05-30 21:30 | 54.4333 | 56.6167 | 66.7667 | 81.9167
2015-05-30 21:45 | 54.1833 | 56.8667 | 66.2667 | 80.6667
2015-05-30 22:00 | 54 | 57 | 65.8833 | 79.8833
2015-05-30 22:15 | 54 | 57 | 65.6333 | 79.6333
2015-05-30 22:30 | 54 | 57 | 65.3833 | 79.3833
2015-05-30 22:45 | 54 | 57 | 65.1333 | 79.1333
2015-05-30 23:00 | 54 | 57 | 64.7667 | 78.4167
2015-05-30 23:15 | 54 | 57 | 64.2667 | 77.1667
2015-05-30 23:30 | 54 | 57 | 63.7667 | 75.9167
2015-05-30 23:45 | 54 | 57 | 63.2667 | 74.6667
2015-05-31 | 54 | 57 | 62.7667 | 73.7667
2015-05-31 00:15 | 54 | 57 | 62.2667 | 73.2667
2015-05-31 00:30 | 54 | 57 | 61.7667 | 72.7667
2015-05-31 00:45 | 54 | 57 | 61.2667 | 72.2667
2015-05-31 01:00 | 54 | 57 | 61 | 71.7667
2015-05-31 01:15 | 54 | 57 | 61 | 71.2667
2015-05-31 01:30 | 54 | 57 | 61 | 70.7667
2015-05-31 01:45 | 54 | 57 | 61 | 70.2667
2015-05-31 02:00 | 54 | 57 | 61 | 69.65
2015-05-31 02:15 | 54 | 57 | 61 | 68.9
2015-05-31 02:30 | 53.7222 | 57 | 60.7619 | 68.15
2015-05-31 02:45 | 53.3056 | 57 | 60.0476 | 67.4
2015-05-31 03:00 | 53.069 | 57.1167 | 61 | 67
2015-05-31 03:15 | 53.3276 | 57.3667 | 61 | 67
2015-05-31 03:30 | 53.5862 | 57.6167 | 61 | 67
2015-05-31 03:45 | 53.8448 | 57.8667 | 61 | 67
2015-05-31 04:00 | 53 | 57.8833 | 60.7667 | 66.7667
2015-05-31 04:15 | 53 | 57.6333 | 60.2667 | 66.2667
2015-05-31 04:30 | 53 | 57.3833 | 59.7667 | 65.7667
2015-05-31 04:45 | 53 | 57.1333 | 59.2667 | 65.2667
2015-05-31 05:00 | 53 | 57 | 58.65 | 65.2333
2015-05-31 05:15 | 53 | 57 | 57.9 | 65.7333
2015-05-31 05:30 | 53 | 57 | 57.15 | 66.2333
2015-05-31 05:45 | 53 | 57 | 56.4 | 66.7333
2015-05-31 06:00 | 53.0667 | 57 | 56.4667 | 67.5833
2015-05-31 06:15 | 53.3167 | 57 | 57.4667 | 68.8333
2015-05-31 06:30 | 53.5667 | 57 | 58.4667 | 70.0833
2015-05-31 06:45 | 53.8167 | 57 | 59.4667 | 71.3333
2015-05-31 07:00 | 54.2 | 57.2333 | 60.4667 | 72.35
2015-05-31 07:15 | 54.95 | 57.7333 | 61.4667 | 73.1
2015-05-31 07:30 | 55.7 | 58.2333 | 62.4667 | 73.85
2015-05-31 07:45 | 56.45 | 58.7333 | 63.4667 | 74.6
2015-05-31 08:00 | 57 | 59.3256 | 64.4667 | 75.4667
2015-05-31 08:15 | 57.5882 | 60.0233 | 65.4667 | 76.4667
2015-05-31 08:30 | 58.4706 | 60.7209 | 66.4667 | 77.4667
2015-05-31 08:45 | 59.3529 | 61 | 67.4667 | 78.4667
2015-05-31 09:00 | 60 | 61.7 | 68.2333 | 79.5833
2015-05-31 09:15 | 60 | 63.1 | 68.7333 | 80.8333
2015-05-31 09:30 | 60 | 63.85 | 69.2333 | 82.0833
2015-05-31 09:45 | 60 | 64.6 | 69.7333 | 83.3333
2015-05-31 10:00 | 60.2 | 65 | 70.4667 | 84.35
2015-05-31 10:15 | 60.95 | 65 | 71.4667 | 85.1
2015-05-31 10:30 | 61.7 | 65 | 72.4667 | 85.85
2015-05-31 10:45 | 62.45 | 65 | 73.4667 | 86.6
2015-05-31 11:00 | 63.0667 | 65 | 74.2333 | 87.5833
2015-05-31 11:15 | 63.3167 | 65 | 74.7333 | 88.8333
2015-05-31 11:30 | 63.5667 | 65 | 75.2333 | 90.0833
2015-05-31 11:45 | 63.8167 | 65 | 75.7333 | 91.3333
2015-05-31 12:00 | 64.0667 | 65.2333 | 76.2333 | 92.2333
2015-05-31 12:15 | 64.3167 | 65.7333 | 76.7333 | 92.7333
2015-05-31 12:30 | 64.5667 | 66.2333 | 77.2333 | 93.2333
2015-05-31 12:45 | 64.8167 | 66.7333 | 77.7333 | 93.7333
2015-05-31 13:00 | 65 | 67 | 78.2333 | 94.1167
2015-05-31 13:15 | 65 | 67 | 78.7333 | 94.3667
2015-05-31 13:30 | 65 | 67 | 79.2333 | 94.6167
2015-05-31 13:45 | 65 | 67 | 79.7333 | 94.8667
2015-05-31 14:00 | 64.9333 | 67.2333 | 80.1167 | 95.1167
2015-05-31 14:15 | 64.6833 | 67.7333 | 80.3667 | 95.3667
2015-05-31 14:30 | 64.4333 | 68.2333 | 80.6167 | 95.6167
2015-05-31 14:45 | 64.1833 | 68.7333 | 80.8667 | 95.8667
2015-05-31 15:00 | 64.0667 | 68.8833 | 81.1167 | 96.1167
2015-05-31 15:15 | 64.3167 | 68.6333 | 81.3667 | 96.3667
2015-05-31 15:30 | 64.5667 | 68.3833 | 81.6167 | 96.6167
2015-05-31 15:45 | 64.8167 | 68.1333 | 81.8667 | 96.8667
2015-05-31 16:00 | 64.8667 | 67.7667 | 82 | 96.4167
2015-05-31 16:15 | 64.3667 | 67.2667 | 82 | 95.1667
2015-05-31 16:30 | 63.8667 | 66.7667 | 82 | 93.9167
2015-05-31 16:45 | 63.3667 | 66.2667 | 82 | 92.6667
2015-05-31 17:00 | 62.8667 | 65.8833 | 81.7667 | 90.95
2015-05-31 17:15 | 62.3667 | 65.6333 | 81.2667 | 88.7
2015-05-31 17:30 | 61.8667 | 65.3833 | 80.7667 | 86.45
2015-05-31 17:45 | 61.3667 | 65.1333 | 80.2667 | 84.2
2015-05-31 18:00 | 60.8667 | 64.5333 | 79.8833 | 82.7667
2015-05-31 18:15 | 60.3667 | 63.5333 | 79.6333 | 82.2667
2015-05-31 18:30 | 59.8667 | 62.5333 | 79.3833 | 81.7667
2015-05-31 18:45 | 59.3667 | 61.5333 | 79.1333 | 81.2667
2015-05-31 19:00 | 58.9333 | 60.7667 | 78.65 | 80.7667
2015-05-31 19:15 | 58.6833 | 60.2667 | 77.9 | 80.2667
2015-05-31 19:30 | 58.4333 | 59.7667 | 77.15 | 79.7667
2015-05-31 19:45 | 58.1833 | 59.2667 | 76.4 | 79.2667
2015-05-31 20:00 | 58.0667 | 58.8833 | 75.65 | 78.5333
2015-05-31 20:15 | 58.3167 | 58.6333 | 74.9 | 77.5333
2015-05-31 20:30 | 58.5667 | 58.3833 | 74.15 | 76.5333
2015-05-31 20:45 | 58.8167 | 58.1333 | 73.4 | 75.5333
2015-05-31 21:00 | 59 | 58 | 72.7667 | 74.5333
2015-05-31 21:15 | 59 | 58 | 72.2667 | 73.5333
2015-05-31 21:30 | 59 | 58 | 71.7667 | 72.5333
2015-05-31 21:45 | 59 | 58 | 71.2667 | 71.5333
2015-05-31 22:00 | 59.0667 | 57.8833 | 70.7667 | 70.5333
2015-05-31 22:15 | 59.3167 | 57.6333 | 70.2667 | 69.5333
2015-05-31 22:30 | 59.5667 | 57.3833 | 69.7667 | 68.5333
2015-05-31 22:45 | 59.8167 | 57.1333 | 69.2667 | 67.5333
2015-05-31 23:00 | 59.84 | 57 | 68.8833 | 66.65
2015-05-31 23:15 | 59.24 | 57 | 68.6333 | 65.9
2015-05-31 23:30 | 59 | 57 | 68.3833 | 65.15
2015-05-31 23:45 | 59 | 57 | 68.1333 | 64.4
2015-06-01 | 59 | 56.8833 | 67.8833 | 63.7667
2015-06-01 00:15 | 59 | 56.6333 | 67.6333 | 63.2667
2015-06-01 00:30 | 59 | 56.3833 | 67.3833 | 62.7667
2015-06-01 00:45 | 59 | 56.1333 | 67.1333 | 62.2667
2015-06-01 01:00 | 59 | 55.8833 | 66.8833 | 61.65
2015-06-01 01:15 | 59 | 55.6333 | 66.6333 | 60.9
2015-06-01 01:30 | 59 | 55.3833 | 66.3833 | 60.15
2015-06-01 01:45 | 59 | 55.1333 | 66.1333 | 59.4
2015-06-01 02:00 | 59 | 55 | 65.7667 | 58.8833
2015-06-01 02:15 | 59 | 55 | 65.2667 | 58.6333
2015-06-01 02:30 | 59 | 55 | 64.7667 | 58.3833
2015-06-01 02:45 | 59 | 55 | 64.2667 | 58.1333
2015-06-01 03:00 | 59 | 55.1167 | 63.8833 | 58
2015-06-01 03:15 | 59 | 55.3667 | 63.6333 | 58
2015-06-01 03:30 | 59 | 55.6167 | 63.3833 | 58
2015-06-01 03:45 | 59 | 55.8667 | 63.1333 | 58
2015-06-01 04:00 | 59 | 56.1167 | 62.8833 | 57.8833
2015-06-01 04:15 | 59 | 56.3667 | 62.6333 | 57.6333
2015-06-01 04:30 | 59 | 56.6167 | 62.3833 | 57.3833
2015-06-01 04:45 | 59 | 56.8667 | 62.1333 | 57.1333
2015-06-01 05:00 | 59 | 57.1167 | 61.8833 | 57.1167
2015-06-01 05:15 | 59 | 57.3667 | 61.6333 | 57.3667
2015-06-01 05:30 | 59 | 57.6167 | 61.3833 | 57.6167
2015-06-01 05:45 | 59 | 57.8667 | 61.1333 | 57.8667
2015-06-01 06:00 | 59.0667 | 58.1167 | 61.1167 | 58.2333
2015-06-01 06:15 | 59.3167 | 58.3667 | 61.3667 | 58.7333
2015-06-01 06:30 | 59.5667 | 58.6167 | 61.6167 | 59.2333
2015-06-01 06:45 | 59.8167 | 58.8667 | 61.8667 | 59.7333
2015-06-01 07:00 | 60.1333 | 59.4667 | 62.8167 | 60.7
2015-06-01 07:15 | 60.6333 | 60.4667 | 64.5667 | 62.2
2015-06-01 07:30 | 61.1333 | 61.4667 | 66.3167 | 63.7
2015-06-01 07:45 | 61.6333 | 62.4667 | 68.0667 | 65.2
2015-06-01 08:00 | 62.1333 | 63.35 | 69.9333 | 66.35
2015-06-01 08:15 | 62.6333 | 64.1 | 71.9333 | 67.1
2015-06-01 08:30 | 63.1333 | 64.85 | 73.9333 | 67.85
2015-06-01 08:45 | 63.6333 | 65.6 | 75.9333 | 68.6
2015-06-01 09:00 | 64 | 66.2333 | 77.4667 | 69.35
2015-06-01 09:15 | 64 | 66.7333 | 78.4667 | 70.1
2015-06-01 09:30 | 64.5 | 67.2333 | 79.4667 | 70.85
2015-06-01 09:45 | 65.4375 | 67.7333 | 80.4667 | 71.6
2015-06-01 10:00 | 65.0667 | 68.1167 | 81.35 | 72.4667
2015-06-01 10:15 | 65.3167 | 68.3667 | 82.1 | 73.4667
2015-06-01 10:30 | 65.5667 | 68.6167 | 82.85 | 74.4667
2015-06-01 10:45 | 65.8167 | 68.8667 | 83.6 | 75.4667
2015-06-01 11:00 | 66.2667 | 69.35 | 84.2333 | 76.1167
2015-06-01 11:15 | 67.2667 | 70.1 | 84.7333 | 76.3667
2015-06-01 11:30 | 68.2667 | 70.85 | 85.2333 | 76.6167
2015-06-01 11:45 | 69.2667 | 71.6 | 85.7333 | 76.8667
2015-06-01 12:00 | 70.0667 | 72.1167 | 86.2333 | 77.5833
2015-06-01 12:15 | 70.3167 | 72.3667 | 86.7333 | 78.8333
2015-06-01 12:30 | 70.5667 | 72.6167 | 87.2333 | 80.0833
2015-06-01 12:45 | 70.8167 | 72.8667 | 87.7333 | 81.3333
2015-06-01 13:00 | 71.0667 | 73 | 88.35 | 82.2333
2015-06-01 13:15 | 71.3167 | 73 | 89.1 | 82.7333
2015-06-01 13:30 | 71.5667 | 73 | 89.85 | 83.2333
2015-06-01 13:45 | 71.8167 | 73 | 90.6 | 83.7333
2015-06-01 14:00 | 71.9333 | 73.1167 | 91 | 84.1167
2015-06-01 14:15 | 71.6833 | 73.3667 | 91 | 84.3667
2015-06-01 14:30 | 71.4333 | 73.6167 | 91 | 84.6167
2015-06-01 14:45 | 71.1833 | 73.8667 | 91 | 84.8667
2015-06-01 15:00 | 70.8667 | 73.8833 | 91 | 85
2015-06-01 15:15 | 70.3667 | 73.6333 | 91 | 85
2015-06-01 15:30 | 69.8667 | 73.3833 | 91 | 85
2015-06-01 15:45 | 69.3667 | 73.1333 | 91 | 85
2015-06-01 16:00 | 68.9024 | 72.7667 | 90.8833 | 85.1167
2015-06-01 16:15 | 68.5366 | 72.2667 | 90.6333 | 85.3667
2015-06-01 16:30 | 68.1707 | 71.7667 | 90.3833 | 85.6167
2015-06-01 16:45 | 67.5789 | 71.2667 | 90.1333 | 85.8667
2015-06-01 17:00 | 66.9333 | 70.65 | 89.7667 | 85.65
2015-06-01 17:15 | 66.6833 | 69.9 | 89.2667 | 84.9
2015-06-01 17:30 | 66.4333 | 69.15 | 88.7667 | 84.15
2015-06-01 17:45 | 66.1833 | 68.4 | 88.2667 | 83.4
2015-06-01 18:00 | 65.7838 | 67.8833 | 87.65 | 82.7667
2015-06-01 18:15 | 64.973 | 67.6333 | 86.9 | 82.2667
2015-06-01 18:30 | 64.1622 | 67.3833 | 86.15 | 81.7667
2015-06-01 18:45 | 64 | 67.1333 | 85.4 | 81.2667
2015-06-01 19:00 | 63.8667 | 66.65 | 84.5333 | 80.7667
2015-06-01 19:15 | 63.3667 | 65.9 | 83.5333 | 80.2667
2015-06-01 19:30 | 62.8667 | 65.15 | 82.5333 | 79.7667
2015-06-01 19:45 | 62.3667 | 64.4 | 81.5333 | 79.2667
2015-06-01 20:00 | 61.875 | 63.8833 | 80.5333 | 78.5333
2015-06-01 20:15 | 61.4062 | 63.6333 | 79.5333 | 77.5333
2015-06-01 20:30 | 61 | 63.3833 | 78.5333 | 76.5333
2015-06-01 20:45 | 61 | 63.1333 | 77.5333 | 75.5333
2015-06-01 21:00 | 60.9333 | 62.8833 | 76.7667 | 74.65
2015-06-01 21:15 | 60.6833 | 62.6333 | 76.2667 | 73.9
2015-06-01 21:30 | 60.4333 | 62.3833 | 75.7667 | 73.15
2015-06-01 21:45 | 60.1833 | 62.1333 | 75.2667 | 72.4
2015-06-01 22:00 | 60 | 62.3889 | 74.7667 | 71.5333
2015-06-01 22:15 | 60 | 62.8095 | 74.2667 | 70.5333
2015-06-01 22:30 | 60 | 62.0952 | 73.7667 | 69.5333
2015-06-01 22:45 | 60 | 61.381 | 73.2667 | 68.5333
2015-06-01 23:00 | 59.9333 | 60.8833 | 73 | 67.7667
2015-06-01 23:15 | 59.6833 | 60.6333 | 73 | 67.2667
2015-06-01 23:30 | 59.4333 | 60.3833 | 73 | 66.7667
2015-06-01 23:45 | 59.1833 | 60.1333 | 73 | 66.2667
2015-06-02 | 59 | 59.8833 | 72.8833 | 65.7667
2015-06-02 00:15 | 59 | 59.6333 | 72.6333 | 65.2667
2015-06-02 00:30 | 59 | 59.3833 | 72.3833 | 64.7667
2015-06-02 00:45 | 59 | 59.1333 | 72.1333 | 64.2667
2015-06-02 01:00 | 58.8431 | 59 | 71.7667 | 63.8833
2015-06-02 01:15 | 58.2549 | 59 | 71.2667 | 63.6333
2015-06-02 01:30 | 57.6667 | 59 | 70.7667 | 63.3833
2015-06-02 01:45 | 57.0784 | 59 | 70.2667 | 63.1333
2015-06-02 02:00 | 57 | 59 | 69.8833 | 62.7667
2015-06-02 02:15 | 57 | 59 | 69.6333 | 62.2667
2015-06-02 02:30 | 57 | 59 | 69.3833 | 61.7667
2015-06-02 02:45 | 57 | 59 | 69.1333 | 61.2667
2015-06-02 03:00 | 57 | 59 | 68.8833 | 61
2015-06-02 03:15 | 57 | 59 | 68.6333 | 61
2015-06-02 03:30 | 57 | 59 | 68.3833 | 61
2015-06-02 03:45 | 57 | 59 | 68.1333 | 61
2015-06-02 04:00 | 57 | 59.3333 | 67.8833 | 60.8833
2015-06-02 04:15 | 57 | 60.0476 | 67.6333 | 60.6333
2015-06-02 04:30 | 57 | 60.7619 | 67.3833 | 60.3833
2015-06-02 04:45 | 57 | 60.4444 | 67.1333 | 60.1333
2015-06-02 05:00 | 57 | 60 | 66.7667 | 60.1167
2015-06-02 05:15 | 57 | 60 | 66.2667 | 60.3667
2015-06-02 05:30 | 57 | 60 | 65.7667 | 60.6167
2015-06-02 05:45 | 57 | 60 | 65.2667 | 60.8667
2015-06-02 06:00 | 58.1333 | 60 | 65.35 | 61.2333
2015-06-02 06:15 | 58.6333 | 60 | 66.1 | 61.7333
2015-06-02 06:30 | 59.1333 | 60 | 66.85 | 62.2333
2015-06-02 06:45 | 59.6333 | 60 | 67.6 | 62.7333
2015-06-02 07:00 | 60.0667 | 60.1167 | 68.8167 | 63.35
2015-06-02 07:15 | 60.3167 | 60.3667 | 70.5667 | 64.1
2015-06-02 07:30 | 60.5667 | 60.6167 | 72.3167 | 64.85
2015-06-02 07:45 | 60.8167 | 60.8667 | 74.0667 | 65.6
2015-06-02 08:00 | 61 | 61.1167 | 75.8167 | 66.35
2015-06-02 08:15 | 61 | 61.3667 | 77.5667 | 67.1
2015-06-02 08:30 | 61 | 61.6167 | 79.3167 | 67.85
2015-06-02 08:45 | 61 | 61.8667 | 81.0667 | 68.6
2015-06-02 09:00 | 61 | 62.1167 | 82.2333 | 69.4667
2015-06-02 09:15 | 61 | 62.3667 | 82.7333 | 70.4667
2015-06-02 09:30 | 61 | 62.6167 | 83.2333 | 71.4667
2015-06-02 09:45 | 61 | 62.8667 | 83.7333 | 72.4667
2015-06-02 10:00 | 61.0667 | 63.3962 | 84.2333 | 73.35
2015-06-02 10:15 | 61.3167 | 64.2453 | 84.7333 | 74.1
2015-06-02 10:30 | 61.5667 | 65.0943 | 85.2333 | 74.85
2015-06-02 10:45 | 61.8167 | 65.9434 | 85.7333 | 75.6
2015-06-02 11:00 | 61.8667 | 66.2333 | 86.35 | 76.4667
2015-06-02 11:15 | 61.3667 | 66.7333 | 87.1 | 77.4667
2015-06-02 11:30 | 61.1333 | 67.2333 | 87.85 | 78.4667
2015-06-02 11:45 | 61.6333 | 67.7333 | 88.6 | 79.4667
2015-06-02 12:00 | 62.087 | 68.2333 | 89.1167 | 80.2333
2015-06-02 12:15 | 62.413 | 68.7333 | 89.3667 | 80.7333
2015-06-02 12:30 | 62.7391 | 69.2333 | 89.6167 | 81.2333
2015-06-02 12:45 | 63 | 69.7333 | 89.8667 | 81.7333
2015-06-02 13:00 | 63.1333 | 69.8833 | 90.35 | 82.35
2015-06-02 13:15 | 63.6333 | 69.6333 | 91.1 | 83.1
2015-06-02 13:30 | 64.1333 | 69.3833 | 91.85 | 83.85
2015-06-02 13:45 | 64.6333 | 69.1333 | 92.6 | 84.6
2015-06-02 14:00 | 64.9333 | 68.8833 | 93 | 84.8833
2015-06-02 14:15 | 64.6833 | 68.6333 | 93 | 84.6333
2015-06-02 14:30 | 64.4333 | 68.3833 | 93 | 84.3833
2015-06-02 14:45 | 64.1833 | 68.1333 | 93 | 84.1333
2015-06-02 15:00 | 64 | 68.1167 | 92.65 | 84.2333
2015-06-02 15:15 | 64 | 68.3667 | 91.9 | 84.7333
2015-06-02 15:30 | 64 | 68.6167 | 91.15 | 85.2333
2015-06-02 15:45 | 64 | 68.8667 | 90.4 | 85.7333
2015-06-02 16:00 | 63.8667 | 68.8833 | 89.65 | 85.8833
2015-06-02 16:15 | 63.3667 | 68.6333 | 88.9 | 85.6333
2015-06-02 16:30 | 62.8667 | 68.3833 | 88.15 | 85.3833
2015-06-02 16:45 | 62.3667 | 68.1333 | 87.4 | 85.1333
2015-06-02 17:00 | 61.8667 | 67.8833 | 86.3636 | 84.7667
2015-06-02 17:15 | 61.3667 | 67.6333 | 86 | 84.2667
2015-06-02 17:30 | 60.8667 | 67.3833 | 85.6765 | 83.7667
2015-06-02 17:45 | 60.3667 | 67.1333 | 85.2353 | 83.2667
2015-06-02 18:00 | 59.9333 | 66.5333 | 84.7667 | 82.7667
2015-06-02 18:15 | 59.6833 | 65.5333 | 84.2667 | 82.2667
2015-06-02 18:30 | 59.4333 | 64.5333 | 83.7667 | 81.7667
2015-06-02 18:45 | 59.1833 | 63.5333 | 83.2667 | 81.2667
2015-06-02 19:00 | 58.9333 | 62.8833 | 82.7667 | 80.65
2015-06-02 19:15 | 58.6833 | 62.6333 | 82.2667 | 79.9
2015-06-02 19:30 | 58.4333 | 62.3833 | 81.7667 | 79.15
2015-06-02 19:45 | 58.1833 | 62.1333 | 81.2667 | 78.4
2015-06-02 20:00 | 57.9333 | 61.7667 | 80.65 | 77.7667
2015-06-02 20:15 | 57.6833 | 61.2667 | 79.9 | 77.2667
2015-06-02 20:30 | 57.4333 | 60.7667 | 79.15 | 76.7667
2015-06-02 20:45 | 57.1833 | 60.2667 | 78.4 | 76.2667
2015-06-02 21:00 | 57 | 59.8833 | 77.7667 | 75.7667
2015-06-02 21:15 | 57 | 59.6333 | 77.2667 | 75.2667
2015-06-02 21:30 | 57 | 59.3833 | 76.7667 | 74.7667
2015-06-02 21:45 | 57 | 59.1333 | 76.2667 | 74.2667
2015-06-02 22:00 | 57 | 58.8833 | 75.8833 | 73.65
2015-06-02 22:15 | 57 | 58.6333 | 75.6333 | 72.9
2015-06-02 22:30 | 57 | 58.3833 | 75.3833 | 72.15
2015-06-02 22:45 | 57 | 58.1333 | 75.1333 | 71.4
2015-06-02 23:00 | 56.84 | 58 | 74.7667 | 70.65
2015-06-02 23:15 | 56.24 | 58 | 74.2667 | 69.9
2015-06-02 23:30 | 55.64 | 58 | 73.7667 | 69.15
2015-06-02 23:45 | 55.04 | 58 | 73.2667 | 68.4
2015-06-03 | 56 | 58 | 72.7667 | 67.7667
2015-06-03 00:15 | 56 | 58 | 72.2667 | 67.2667
2015-06-03 00:30 | 56 | 58 | 71.7667 | 66.7667
2015-06-03 00:45 | 56 | 58 | 71.2667 | 66.2667
2015-06-03 01:00 | 56 | 58 | 70.8833 | 65.7667
2015-06-03 01:15 | 56 | 58 | 70.6333 | 65.2667
2015-06-03 01:30 | 56 | 58 | 70.3833 | 64.7667
2015-06-03 01:45 | 56 | 58 | 70.1333 | 64.2667
2015-06-03 02:00 | 56 | 57.8833 | 69.8833 | 64.1167
2015-06-03 02:15 | 56 | 57.6333 | 69.6333 | 64.3667
2015-06-03 02:30 | 56 | 57.3833 | 69.3833 | 64.6167
2015-06-03 02:45 | 56 | 57.1333 | 69.1333 | 64.8667
2015-06-03 03:00 | 55.931 | 56.65 | 68.7667 | 64.7667
2015-06-03 03:15 | 55.6724 | 55.9 | 68.2667 | 64.2667
2015-06-03 03:30 | 55.4138 | 55.15 | 67.7667 | 63.7667
2015-06-03 03:45 | 55.1552 | 54.4 | 67.2667 | 63.2667
2015-06-03 04:00 | 55 | 53.8833 | 66.8833 | 62.7667
2015-06-03 04:15 | 55 | 53.6333 | 66.6333 | 62.2667
2015-06-03 04:30 | 55 | 53.3833 | 66.3833 | 61.7667
2015-06-03 04:45 | 55 | 53.1333 | 66.1333 | 61.2667
2015-06-03 05:00 | 55.1333 | 53.2333 | 65.8833 | 61.1167
2015-06-03 05:15 | 55.6333 | 53.7333 | 65.6333 | 61.3667
2015-06-03 05:30 | 56.1333 | 54.2333 | 65.3833 | 61.6167
2015-06-03 05:45 | 56.6333 | 54.7333 | 65.1333 | 61.8667
2015-06-03 06:00 | 57 | 55.35 | 65.2333 | 62.4667
2015-06-03 06:15 | 57 | 56.1 | 65.7333 | 63.4667
2015-06-03 06:30 | 57 | 56.85 | 66.2333 | 64.4667
2015-06-03 06:45 | 57 | 57.6 | 66.7333 | 65.4667
2015-06-03 07:00 | 56.2 | 58.35 | 67.5833 | 66.5833
2015-06-03 07:15 | 56.95 | 59.1 | 68.8333 | 67.8333
2015-06-03 07:30 | 57.7 | 59.85 | 70.0833 | 69.0833
2015-06-03 07:45 | 58.45 | 60.6 | 71.3333 | 70.3333
2015-06-03 08:00 | 59.0667 | 61.4667 | 72.8167 | 71.5833
2015-06-03 08:15 | 59.3167 | 62.4667 | 74.5667 | 72.8333
2015-06-03 08:30 | 59.5667 | 63.4667 | 76.3167 | 74.0833
2015-06-03 08:45 | 59.8167 | 64.4667 | 78.0667 | 75.3333
2015-06-03 09:00 | 60.0889 | 65.2333 | 79.5833 | 76.35
2015-06-03 09:15 | 60.4222 | 65.7333 | 80.8333 | 77.1
2015-06-03 09:30 | 60.7556 | 66.2333 | 82.0833 | 77.85
2015-06-03 09:45 | 61 | 66.7333 | 83.3333 | 78.6
2015-06-03 10:00 | 61.1333 | 67.35 | 84.4667 | 79.1167
2015-06-03 10:15 | 61.6333 | 68.1 | 85.4667 | 79.3667
2015-06-03 10:30 | 62.1333 | 68.85 | 86.4667 | 79.6167
2015-06-03 10:45 | 62.6333 | 69.6 | 87.4667 | 79.8667
2015-06-03 11:00 | 63 | 69.7667 | 88.2333 | 80.2333
2015-06-03 11:15 | 63 | 69.2667 | 88.7333 | 80.7333
2015-06-03 11:30 | 63 | 68.7667 | 89.2333 | 81.2333
2015-06-03 11:45 | 63 | 68.2667 | 89.7333 | 81.7333
2015-06-03 12:00 | 63.1333 | 68.2333 | 90.2333 | 82.35
2015-06-03 12:15 | 63.6333 | 68.7333 | 90.7333 | 83.1
2015-06-03 12:30 | 64.1333 | 69.2333 | 91.2333 | 83.85
2015-06-03 12:45 | 64.6333 | 69.7333 | 91.7333 | 84.6
2015-06-03 13:00 | 64.7333 | 69.7667 | 92.1167 | 85.1167
2015-06-03 13:15 | 63.7333 | 69.2667 | 92.3667 | 85.3667
2015-06-03 13:30 | 62.7333 | 68.7667 | 92.6167 | 85.6167
2015-06-03 13:45 | 61.7333 | 68.2667 | 92.8667 | 85.8667
2015-06-03 14:00 | 61 | 67.8833 | 93.1167 | 86
2015-06-03 14:15 | 61 | 67.6333 | 93.3667 | 86
2015-06-03 14:30 | 61 | 67.3833 | 93.6167 | 86
2015-06-03 14:45 | 60.55 | 67.1333 | 93.8667 | 86
2015-06-03 15:00 | 60 | 66.65 | 94 | 85.7667
2015-06-03 15:15 | 60 | 65.9 | 94 | 85.2667
2015-06-03 15:30 | 60 | 65.15 | 94 | 84.7667
2015-06-03 15:45 | 60 | 64.4 | 94 | 84.2667
2015-06-03 16:00 | 60 | 63.8833 | 93.8833 | 84
2015-06-03 16:15 | 60 | 63.6333 | 93.6333 | 84
2015-06-03 16:30 | 60 | 63.3833 | 93.3833 | 84
2015-06-03 16:45 | 60 | 63.1333 | 93.1333 | 84
2015-06-03 17:00 | 59.9333 | 62.7667 | 92.7667 | 83.7667
2015-06-03 17:15 | 59.6833 | 62.2667 | 92.2667 | 83.2667
2015-06-03 17:30 | 59.4333 | 61.7667 | 91.7667 | 82.7667
2015-06-03 17:45 | 59.1833 | 61.2667 | 91.2667 | 82.2667
2015-06-03 18:00 | 58.7241 | 60.7667 | 90.5333 | 81.1833
2015-06-03 18:15 | 57.6897 | 60.2667 | 89.5333 | 79.4333
2015-06-03 18:30 | 57.1613 | 59.7667 | 88.5333 | 77.6833
2015-06-03 18:45 | 57.6452 | 59.2667 | 87.5333 | 75.9333
2015-06-03 19:00 | 57.9333 | 58.8833 | 86.5333 | 74.5333
2015-06-03 19:15 | 57.6833 | 58.6333 | 85.5333 | 73.5333
2015-06-03 19:30 | 57.4333 | 58.3833 | 84.5333 | 72.5333
2015-06-03 19:45 | 57.1833 | 58.1333 | 83.5333 | 71.5333
2015-06-03 20:00 | 57 | 57.8833 | 82.65 | 70.7667
2015-06-03 20:15 | 57 | 57.6333 | 81.9 | 70.2667
2015-06-03 20:30 | 57 | 57.3833 | 81.15 | 69.7667
2015-06-03 20:45 | 57 | 57.1333 | 80.4 | 69.2667
2015-06-03 21:00 | 56.8621 | 57 | 79.65 | 68.65
2015-06-03 21:15 | 56.3448 | 57 | 78.9 | 67.9
2015-06-03 21:30 | 55.8276 | 57 | 78.15 | 67.15
2015-06-03 21:45 | 55.3103 | 57 | 77.4 | 66.4
2015-06-03 22:00 | 55.907 | 56.8833 | 76.7667 | 65.7667
2015-06-03 22:15 | 55.5581 | 56.6333 | 76.2667 | 65.2667
2015-06-03 22:30 | 55.2093 | 56.3833 | 75.7667 | 64.7667
2015-06-03 22:45 | 55.3529 | 56.1333 | 75.2667 | 64.2667
2015-06-03 23:00 | 55.9091 | 55.7667 | 74.8833 | 63.7667
2015-06-03 23:15 | 55.5682 | 55.2667 | 74.6333 | 63.2667
2015-06-03 23:30 | 55.2273 | 54.7667 | 74.3833 | 62.7667
2015-06-03 23:45 | 55 | 54.2667 | 74.1333 | 62.2667
2015-06-04 | 55 | 54.1167 | 73.7667 | 62
2015-06-04 00:15 | 55 | 54.3667 | 73.2667 | 62
2015-06-04 00:30 | 55 | 54.6167 | 72.7667 | 62
2015-06-04 00:45 | 55 | 54.8667 | 72.2667 | 62
2015-06-04 01:00 | 55 | 54.8833 | 71.8833 | 61.7667
2015-06-04 01:15 | 55 | 54.6333 | 71.6333 | 61.2667
2015-06-04 01:30 | 55 | 54.3833 | 71.3833 | 60.7667
2015-06-04 01:45 | 55 | 54.1333 | 71.1333 | 60.2667
2015-06-04 02:00 | 55 | 54 | 70.8833 | 59.8833
2015-06-04 02:15 | 55 | 54 | 70.6333 | 59.6333
2015-06-04 02:30 | 55 | 54 | 70.3833 | 59.3833
2015-06-04 02:45 | 55 | 54 | 70.1333 | 59.1333
2015-06-04 03:00 | 54.9333 | 54.1167 | 69.8833 | 58.7667
2015-06-04 03:15 | 54.6833 | 54.3667 | 69.6333 | 58.2667
2015-06-04 03:30 | 54.4333 | 54.6167 | 69.3833 | 57.7667
2015-06-04 03:45 | 54.1833 | 54.8667 | 69.1333 | 57.2667
2015-06-04 04:00 | 54 | 55 | 68.8833 | 56.8833
2015-06-04 04:15 | 54 | 55 | 68.6333 | 56.6333
2015-06-04 04:30 | 54 | 54.8519 | 68.3833 | 56.3833
2015-06-04 04:45 | 54 | 54.2963 | 68.1333 | 56.1333
2015-06-04 05:00 | 54 | 54.2333 | 67.8833 | 56.1167
2015-06-04 05:15 | 54 | 54.7333 | 67.6333 | 56.3667
2015-06-04 05:30 | 54 | 55.2333 | 67.3833 | 56.6167
2015-06-04 05:45 | 54 | 55.7333 | 67.1333 | 56.8667
2015-06-04 06:00 | 54.1333 | 56.2333 | 67.2333 | 57.35
2015-06-04 06:15 | 54.6333 | 56.7333 | 67.7333 | 58.1
2015-06-04 06:30 | 55.1333 | 57.2333 | 68.2333 | 58.85
2015-06-04 06:45 | 55.6333 | 57.7333 | 68.7333 | 59.6
2015-06-04 07:00 | 56.1 | 58.35 | 69.4667 | 60.35
2015-06-04 07:15 | 56.475 | 59.1 | 70.4667 | 61.1
2015-06-04 07:30 | 56.85 | 59.85 | 71.4667 | 61.85
2015-06-04 07:45 | 57.45 | 60.6 | 72.4667 | 62.6
2015-06-04 08:00 | 58.2 | 61.2333 | 73.4667 | 63.4667
2015-06-04 08:15 | 58.95 | 61.7333 | 74.4667 | 64.4667
2015-06-04 08:30 | 59.7 | 62.2333 | 75.4667 | 65.4667
2015-06-04 08:45 | 60.45 | 62.7333 | 76.4667 | 66.4667
2015-06-04 09:00 | 61.1333 | 63.1167 | 77.4667 | 67.5833
2015-06-04 09:15 | 61.6333 | 63.3667 | 78.4667 | 68.8333
2015-06-04 09:30 | 62.1333 | 63.6167 | 79.4667 | 70.0833
2015-06-04 09:45 | 62.6333 | 63.8667 | 80.4667 | 71.3333
2015-06-04 10:00 | 63.2 | 64.35 | 81.35 | 72.35
2015-06-04 10:15 | 63.95 | 65.1 | 82.1 | 73.1
2015-06-04 10:30 | 64.7 | 65.85 | 82.85 | 73.85
2015-06-04 10:45 | 65.45 | 66.6 | 83.6 | 74.6
2015-06-04 11:00 | 66.1333 | 67.1167 | 84.35 | 75.1167
2015-06-04 11:15 | 66.6333 | 67.3667 | 85.1 | 75.3667
2015-06-04 11:30 | 67.1333 | 67.6167 | 85.85 | 75.6167
2015-06-04 11:45 | 67.6333 | 67.8667 | 86.6 | 75.8667
2015-06-04 12:00 | 67.9333 | 68.2333 | 87.2333 | 76.35
2015-06-04 12:15 | 67.6833 | 68.7333 | 87.7333 | 77.1
2015-06-04 12:30 | 67.4333 | 69.2333 | 88.2333 | 77.85
2015-06-04 12:45 | 67.1833 | 69.7333 | 88.7333 | 78.6
2015-06-04 13:00 | 66.9333 | 70.4667 | 89.2333 | 79
2015-06-04 13:15 | 66.6833 | 71.4667 | 89.7333 | 79
2015-06-04 13:30 | 66.4333 | 72.4667 | 90.2333 | 79
2015-06-04 13:45 | 66.1833 | 73.4667 | 90.7333 | 79
2015-06-04 14:00 | 65.9333 | 73.8833 | 90.65 | 79.4667
2015-06-04 14:15 | 65.6833 | 73.6333 | 89.9 | 80.4667
2015-06-04 14:30 | 65.4333 | 73.3833 | 89.15 | 81.4667
2015-06-04 14:45 | 65.1833 | 73.1333 | 88.4 | 82.4667
2015-06-04 15:00 | 65 | 73.1167 | 87.8833 | 82.8833
2015-06-04 15:15 | 65 | 73.3667 | 87.6333 | 82.6333
2015-06-04 15:30 | 65 | 73.6167 | 87.3833 | 82.3833
2015-06-04 15:45 | 65 | 73.8667 | 87.1333 | 82.1333
2015-06-04 16:00 | 64.8667 | 73.8833 | 86.5333 | 82
2015-06-04 16:15 | 64.3667 | 73.6333 | 85.5333 | 82
2015-06-04 16:30 | 63.8667 | 73.3833 | 84.5333 | 82
2015-06-04 16:45 | 63.3667 | 73.1333 | 83.5333 | 82
2015-06-04 17:00 | 62.8667 | 72.5333 | 83 | 81.8833
2015-06-04 17:15 | 62.3667 | 71.5333 | 83 | 81.6333
2015-06-04 17:30 | 61.8667 | 70.5333 | 83 | 81.3833
2015-06-04 17:45 | 61.3667 | 69.5333 | 83 | 81.1333
2015-06-04 18:00 | 60.8667 | 68.4167 | 82.8833 | 80.65
2015-06-04 18:15 | 60.3667 | 67.1667 | 82.6333 | 79.9
2015-06-04 18:30 | 59.8667 | 65.9167 | 82.3833 | 79.15
2015-06-04 18:45 | 59.3667 | 64.6667 | 82.1333 | 78.4
2015-06-04 19:00 | 58.8 | 63.65 | 81.65 | 77.7667
2015-06-04 19:15 | 58.05 | 62.9 | 80.9 | 77.2667
2015-06-04 19:30 | 57.3 | 62.15 | 80.15 | 76.7667
2015-06-04 19:45 | 56.55 | 61.4 | 79.4 | 76.2667
2015-06-04 20:00 | 56.0667 | 60.7667 | 78.7667 | 75.7667
2015-06-04 20:15 | 56.3167 | 60.2667 | 78.2667 | 75.2667
2015-06-04 20:30 | 56.5667 | 59.7667 | 77.7667 | 74.7667
2015-06-04 20:45 | 56.8167 | 59.2667 | 77.2667 | 74.2667
2015-06-04 21:00 | 57 | 59.1167 | 76.7667 | 73.8833
2015-06-04 21:15 | 57 | 59.3667 | 76.2667 | 73.6333
2015-06-04 21:30 | 57 | 59.6167 | 75.7667 | 73.3833
2015-06-04 21:45 | 57 | 59.8667 | 75.2667 | 73.1333
2015-06-04 22:00 | 56.9333 | 59.7667 | 74.8833 | 72.65
2015-06-04 22:15 | 56.6833 | 59.2667 | 74.6333 | 71.9
2015-06-04 22:30 | 56.4333 | 58.7667 | 74.3833 | 71.15
2015-06-04 22:45 | 56.1833 | 58.2667 | 74.1333 | 70.4
2015-06-04 23:00 | 56.0667 | 57.8833 | 73.8833 | 69.65
2015-06-04 23:15 | 56.3167 | 57.6333 | 73.6333 | 68.9
2015-06-04 23:30 | 56.5667 | 57.3833 | 73.3833 | 68.15
2015-06-04 23:45 | 56.8167 | 57.1333 | 73.1333 | 67.4
2015-06-05 | 56.9333 | 56.7667 | 72.7667 | 66.8833
2015-06-05 00:15 | 56.6833 | 56.2667 | 72.2667 | 66.6333
2015-06-05 00:30 | 56.4333 | 55.7667 | 71.7667 | 66.3833
2015-06-05 00:45 | 56.1833 | 55.2667 | 71.2667 | 66.1333
2015-06-05 01:00 | 56 | 55 | 71 | 65.7667
2015-06-05 01:15 | 56 | 55 | 71 | 65.2667
2015-06-05 01:30 | 56 | 55 | 71 | 64.7667
2015-06-05 01:45 | 56 | 55 | 71 | 64.2667
2015-06-05 02:00 | 55.9333 | 54.8833 | 70.8833 | 63.5333
2015-06-05 02:15 | 55.6833 | 54.6333 | 70.6333 | 62.5333
2015-06-05 02:30 | 55.4333 | 54.3833 | 70.3833 | 61.5333
2015-06-05 02:45 | 55.1833 | 54.1333 | 70.1333 | 60.5333
2015-06-05 03:00 | 55 | 54 | 69.7667 | 59.8833
2015-06-05 03:15 | 55 | 54 | 69.2667 | 59.6333
2015-06-05 03:30 | 55 | 54 | 68.7667 | 59.3833
2015-06-05 03:45 | 55 | 54 | 68.2667 | 59.1333
2015-06-05 04:00 | 55 | 54 | 67.8833 | 58.8833
2015-06-05 04:15 | 55 | 54 | 67.6333 | 58.6333
2015-06-05 04:30 | 55 | 54 | 67.3833 | 58.3833
2015-06-05 04:45 | 55 | 54 | 67.1333 | 58.1333
2015-06-05 05:00 | 55.0667 | 54.1167 | 67 | 58.2333
2015-06-05 05:15 | 55.3167 | 54.3667 | 67 | 58.7333
2015-06-05 05:30 | 55.5667 | 54.6167 | 67 | 59.2333
2015-06-05 05:45 | 55.8167 | 54.8667 | 67 | 59.7333
2015-06-05 06:00 | 56.1333 | 55.2333 | 67.1167 | 60.4667
2015-06-05 06:15 | 56.6333 | 55.7333 | 67.3667 | 61.4667
2015-06-05 06:30 | 57.1333 | 56.2333 | 67.6167 | 62.4667
2015-06-05 06:45 | 57.6333 | 56.7333 | 67.8667 | 63.4667
2015-06-05 07:00 | 58.2667 | 57.35 | 68.4667 | 64.4667
2015-06-05 07:15 | 59.2667 | 58.1 | 69.4667 | 65.4667
2015-06-05 07:30 | 60.2667 | 58.85 | 70.4667 | 66.4667
2015-06-05 07:45 | 61 | 59.6 | 71.4667 | 67.4667
2015-06-05 08:00 | 61.1333 | 60.5833 | 72.4667 | 68.4667
2015-06-05 08:15 | 61.6333 | 61.8333 | 73.4667 | 69.4667
2015-06-05 08:30 | 62.1333 | 63.0833 | 74.4667 | 70.4667
2015-06-05 08:45 | 62.6333 | 64.3333 | 75.4667 | 71.4667
2015-06-05 09:00 | 63.0667 | 65.4667 | 76.35 | 72.35
2015-06-05 09:15 | 63.3167 | 66.4667 | 77.1 | 73.1
2015-06-05 09:30 | 63.5667 | 67.4667 | 77.85 | 73.85
2015-06-05 09:45 | 63.8167 | 68.4667 | 78.6 | 74.6
2015-06-05 10:00 | 64.2 | 69.4667 | 79.4667 | 75.35
2015-06-05 10:15 | 64.95 | 70.4667 | 80.4667 | 76.1
2015-06-05 10:30 | 65.7 | 71.4667 | 81.4667 | 76.85
2015-06-05 10:45 | 66.45 | 72.4667 | 82.4667 | 77.6
2015-06-05 11:00 | 67 | 73.35 | 83.2333 | 78.2333
2015-06-05 11:15 | 67 | 74.1 | 83.7333 | 78.7333
2015-06-05 11:30 | 67 | 74.85 | 84.2333 | 79.2333
2015-06-05 11:45 | 67 | 75.6 | 84.7333 | 79.7333
2015-06-05 12:00 | 67.2667 | 76 | 85.2333 | 80.2333
2015-06-05 12:15 | 68.2667 | 76 | 85.7333 | 80.7333
2015-06-05 12:30 | 69.2667 | 76 | 86.2333 | 81.2333
2015-06-05 12:45 | 70.2667 | 76 | 86.7333 | 81.7333
2015-06-05 13:00 | 71 | 76.1167 | 87.2333 | 82.4667
2015-06-05 13:15 | 71 | 76.3667 | 87.7333 | 83.4667
2015-06-05 13:30 | 71 | 76.6167 | 88.2333 | 84.4667
2015-06-05 13:45 | 71 | 76.8667 | 88.7333 | 85.4667
2015-06-05 14:00 | 71 | 77 | 89.1167 | 86
2015-06-05 14:15 | 71 | 77 | 89.3667 | 86
2015-06-05 14:30 | 71 | 77 | 89.6167 | 86
2015-06-05 14:45 | 71 | 77 | 89.8667 | 86
2015-06-05 15:00 | 70.8 | 76.8833 | 89.7667 | 86
2015-06-05 15:15 | 70.05 | 76.6333 | 89.2667 | 86
2015-06-05 15:30 | 69.3 | 76.3833 | 88.7667 | 86
2015-06-05 15:45 | 68.55 | 76.1333 | 88.2667 | 86
2015-06-05 16:00 | 67.8 | 75.7667 | 87.8833 | 86
2015-06-05 16:15 | 67.05 | 75.2667 | 87.6333 | 86
2015-06-05 16:30 | 66.3 | 74.7667 | 87.3833 | 86
2015-06-05 16:45 | 65.55 | 74.2667 | 87.1333 | 86
2015-06-05 17:00 | 65 | 73.4167 | 86.8833 | 85.8833
2015-06-05 17:15 | 65 | 72.1667 | 86.6333 | 85.6333
2015-06-05 17:30 | 65 | 70.9167 | 86.3833 | 85.3833
2015-06-05 17:45 | 65 | 69.6667 | 86.1333 | 85.1333
2015-06-05 18:00 | 64.9333 | 68.65 | 85.65 | 84.7667
2015-06-05 18:15 | 64.6833 | 67.9 | 84.9 | 84.2667
2015-06-05 18:30 | 64.4333 | 67.15 | 84.15 | 83.7667
2015-06-05 18:45 | 64.1833 | 66.4 | 83.4 | 83.2667
2015-06-05 19:00 | 63.6667 | 65.7667 | 82.5333 | 82.7667
2015-06-05 19:15 | 62.4167 | 65.2667 | 81.5333 | 82.2667
2015-06-05 19:30 | 61.1667 | 64.7667 | 80.5333 | 81.7667
2015-06-05 19:45 | 60.4583 | 64.2667 | 79.5333 | 81.2667
2015-06-05 20:00 | 60 | 63.8833 | 78.7667 | 80.8833
2015-06-05 20:15 | 60 | 63.6333 | 78.2667 | 80.6333
2015-06-05 20:30 | 60 | 63.3833 | 77.7667 | 80.3833
2015-06-05 20:45 | 60 | 63.1333 | 77.2667 | 80.1333
2015-06-05 21:00 | 59.9333 | 62.8833 | 76.7667 | 79.65
2015-06-05 21:15 | 59.6833 | 62.6333 | 76.2667 | 78.9
2015-06-05 21:30 | 59.4333 | 62.3833 | 75.7667 | 78.15
2015-06-05 21:45 | 59.1833 | 62.1333 | 75.2667 | 77.4
2015-06-05 22:00 | 58.9333 | 61.8833 | 74.7667 | 76.65
2015-06-05 22:15 | 58.6833 | 61.6333 | 74.2667 | 75.9
2015-06-05 22:30 | 58.4333 | 61.3833 | 73.7667 | 75.15
2015-06-05 22:45 | 58.1833 | 61.1333 | 73.2667 | 74.4
2015-06-05 23:00 | 58 | 60.7667 | 72.8833 | 73.7667
2015-06-05 23:15 | 58 | 60.2667 | 72.6333 | 73.2667
2015-06-05 23:30 | 58 | 59.7667 | 72.3833 | 72.7667
2015-06-05 23:45 | 58 | 59.2667 | 72.1333 | 72.2667
2015-06-06 | 57.9259 | 59 | 71.8833 | 71.7667
2015-06-06 00:15 | 57.6481 | 59 | 71.6333 | 71.2667
2015-06-06 00:30 | 57.3704 | 59 | 71.3833 | 70.7667
2015-06-06 00:45 | 57.0926 | 59 | 71.1333 | 70.2667
2015-06-06 01:00 | 58 | 58.7667 | 70.8833 | 69.7667
2015-06-06 01:15 | 58 | 58.2667 | 70.6333 | 69.2667
2015-06-06 01:30 | 58 | 57.7667 | 70.3833 | 68.7667
2015-06-06 01:45 | 58 | 57.2667 | 70.1333 | 68.2667
2015-06-06 02:00 | 58 | 56.8833 | 69.8833 | 67.8833
2015-06-06 02:15 | 58 | 56.6333 | 69.6333 | 67.6333
2015-06-06 02:30 | 58 | 56.3833 | 69.3833 | 67.3833
2015-06-06 02:45 | 58 | 56.1333 | 69.1333 | 67.1333
2015-06-06 03:00 | 57.8 | 56 | 69 | 66.8833
2015-06-06 03:15 | 57.05 | 56 | 69 | 66.6333
2015-06-06 03:30 | 57.35 | 56 | 69 | 66.3833
2015-06-06 03:45 | 57.725 | 56 | 69 | 66.1333
2015-06-06 04:00 | 58 | 55.8833 | 68.7667 | 65.8833
2015-06-06 04:15 | 58 | 55.6333 | 68.2667 | 65.6333
2015-06-06 04:30 | 58 | 55.3833 | 67.7667 | 65.3833
2015-06-06 04:45 | 58 | 55.1333 | 67.2667 | 65.1333
2015-06-06 05:00 | 58.0667 | 55.1167 | 67.1167 | 65.1167
2015-06-06 05:15 | 58.3167 | 55.3667 | 67.3667 | 65.3667
2015-06-06 05:30 | 58.5667 | 55.6167 | 67.6167 | 65.6167
2015-06-06 05:45 | 58.8167 | 55.8667 | 67.8667 | 65.8667
2015-06-06 06:00 | 59 | 56.2593 | 68.2333 | 66.4667
2015-06-06 06:15 | 59 | 56.8148 | 68.7333 | 67.4667
2015-06-06 06:30 | 59 | 57.303 | 69.2333 | 68.4667
2015-06-06 06:45 | 59 | 57.7576 | 69.7333 | 69.4667
2015-06-06 07:00 | 59.5714 | 58.1795 | 70.2333 | 70.35
2015-06-06 07:15 | 61.1087 | 58.5641 | 70.7333 | 71.1
2015-06-06 07:30 | 61.4348 | 58.9487 | 71.2333 | 71.85
2015-06-06 07:45 | 61.7609 | 60.2381 | 71.7333 | 72.6
2015-06-06 08:00 | 62.2 | 61.35 | 72.35 | 73.35
2015-06-06 08:15 | 62.95 | 62.1 | 73.1 | 74.1
2015-06-06 08:30 | 63.7 | 62.85 | 73.85 | 74.85
2015-06-06 08:45 | 64 | 63.6 | 74.6 | 75.6
2015-06-06 09:00 | 64.1333 | 64.5833 | 75.35 | 76.4667
2015-06-06 09:15 | 64.6333 | 65.8333 | 76.1 | 77.4667
2015-06-06 09:30 | 65.1333 | 67.0833 | 76.85 | 78.4667
2015-06-06 09:45 | 65.6333 | 68.3333 | 77.6 | 79.4667
2015-06-06 10:00 | 66 | 69.5833 | 78.35 | 80.5833
2015-06-06 10:15 | 66 | 70.8333 | 79.1 | 81.8333
2015-06-06 10:30 | 66 | 72.0833 | 79.85 | 83.0833
2015-06-06 10:45 | 66 | 73.3333 | 80.6 | 84.3333
2015-06-06 11:00 | 66.1333 | 74.4667 | 81.4667 | 85
2015-06-06 11:15 | 66.6333 | 75.4667 | 82.4667 | 85
2015-06-06 11:30 | 67.1333 | 76.4667 | 83.4667 | 85
2015-06-06 11:45 | 67.6333 | 77.4667 | 84.4667 | 85
2015-06-06 12:00 | 68.1333 | 77.8833 | 85.2333 | 85.2333
2015-06-06 12:15 | 68.6333 | 77.6333 | 85.7333 | 85.7333
2015-06-06 12:30 | 69.1333 | 77.3833 | 86.2333 | 86.2333
2015-06-06 12:45 | 69.6333 | 77.1333 | 86.7333 | 86.7333
2015-06-06 13:00 | 70.1333 | 76.8833 | 86.8833 | 87.35
2015-06-06 13:15 | 70.6333 | 76.6333 | 86.6333 | 88.1
2015-06-06 13:30 | 71.1333 | 76.3833 | 86.3833 | 88.85
2015-06-06 13:45 | 71.6333 | 76.1333 | 86.1333 | 89.6
2015-06-06 14:00 | 72 | 75.8833 | 86.1167 | 89.65
2015-06-06 14:15 | 72 | 75.6333 | 86.3667 | 88.9
2015-06-06 14:30 | 72 | 75.3833 | 86.6167 | 88.15
2015-06-06 14:45 | 72 | 75.1333 | 86.8667 | 87.4
2015-06-06 15:00 | 71.8667 | 74.8833 | 86.8833 | 87.1167
2015-06-06 15:15 | 71.3667 | 74.6333 | 86.6333 | 87.3667
2015-06-06 15:30 | 70.8667 | 74.3833 | 86.3833 | 87.6167
2015-06-06 15:45 | 70.3667 | 74.1333 | 86.1333 | 87.8667
2015-06-06 16:00 | 69.9333 | 73.65 | 85.8833 | 88.1167
2015-06-06 16:15 | 69.6833 | 72.9 | 85.6333 | 88.3667
2015-06-06 16:30 | 69.4333 | 72.15 | 85.3833 | 88.6167
2015-06-06 16:45 | 69.1833 | 71.4 | 85.1333 | 88.8667
2015-06-06 17:00 | 68.7333 | 70.65 | 85.1167 | 88.8833
2015-06-06 17:15 | 67.7333 | 69.9 | 85.3667 | 88.6333
2015-06-06 17:30 | 66.7333 | 69.15 | 85.6167 | 88.3833
2015-06-06 17:45 | 65.7333 | 68.4 | 85.8667 | 88.1333
2015-06-06 18:00 | 64.8 | 67.7667 | 85.7667 | 87.7667
2015-06-06 18:15 | 64.05 | 67.2667 | 85.2667 | 87.2667
2015-06-06 18:30 | 63.3 | 66.7667 | 84.7667 | 86.7667
2015-06-06 18:45 | 62.55 | 66.2667 | 84.2667 | 86.2667
2015-06-06 19:00 | 61.9333 | 65.7667 | 83.65 | 85.65
2015-06-06 19:15 | 61.6833 | 65.2667 | 82.9 | 84.9
2015-06-06 19:30 | 61.4333 | 64.7667 | 82.15 | 84.15
2015-06-06 19:45 | 61.1833 | 64.2667 | 81.4 | 83.4
2015-06-06 20:00 | 60.9333 | 63.7667 | 80.65 | 82.7667
2015-06-06 20:15 | 60.6833 | 63.2667 | 79.9 | 82.2667
2015-06-06 20:30 | 60.4333 | 62.7667 | 79.15 | 81.7667
2015-06-06 20:45 | 60.1833 | 62.2667 | 78.4 | 81.2667
2015-06-06 21:00 | 59.9333 | 61.8833 | 77.7667 | 80.7667
2015-06-06 21:15 | 59.6833 | 61.6333 | 77.2667 | 80.2667
2015-06-06 21:30 | 59.4333 | 61.3833 | 76.7667 | 79.7667
2015-06-06 21:45 | 59.1833 | 61.1333 | 76.2667 | 79.2667
2015-06-06 22:00 | 58.9333 | 60.8833 | 75.8833 | 78.65
2015-06-06 22:15 | 58.6833 | 60.6333 | 75.6333 | 77.9
2015-06-06 22:30 | 58.4333 | 60.3833 | 75.3833 | 77.15
2015-06-06 22:45 | 58.1833 | 60.1333 | 75.1333 | 76.4
2015-06-06 23:00 | 58 | 60 | 74.7667 | 75.7667
2015-06-06 23:15 | 58 | 60 | 74.2667 | 75.2667
2015-06-06 23:30 | 58 | 60 | 73.7667 | 74.7667
2015-06-06 23:45 | 58 | 60 | 73.2667 | 74.2667
2015-06-07 | 57.9333 | 60.4667 | 73 | 73.7667
2015-06-07 00:15 | 57.6833 | 61 | 73 | 73.2667
2015-06-07 00:30 | 57.4333 | 61 | 73 | 72.7667
2015-06-07 00:45 | 57.1833 | 61 | 73 | 72.2667
2015-06-07 01:00 | 57 | 61 | 72.8833 | 71.65
2015-06-07 01:15 | 57 | 61 | 72.6333 | 70.9
2015-06-07 01:30 | 57 | 61 | 72.3833 | 70.15
2015-06-07 01:45 | 57 | 61 | 72.1333 | 69.4
2015-06-07 02:00 | 58 | 61 | 72 | 68.8833
2015-06-07 02:15 | 58 | 61 | 72 | 68.6333
2015-06-07 02:30 | 58 | 61 | 72 | 68.3833
2015-06-07 02:45 | 58 | 61 | 72 | 68.1333
2015-06-07 03:00 | 58 | 61 | 71.8833 | 67.8833
2015-06-07 03:15 | 58 | 61 | 71.6333 | 67.6333
2015-06-07 03:30 | 58 | 61 | 71.3833 | 67.3833
2015-06-07 03:45 | 58 | 61 | 71.1333 | 67.1333
2015-06-07 04:00 | 58.0667 | 61 | 70.7667 | 67
2015-06-07 04:15 | 58.3167 | 61 | 70.2667 | 67
2015-06-07 04:30 | 58.5667 | 61 | 69.7667 | 67
2015-06-07 04:45 | 58.8167 | 61 | 69.2667 | 67
2015-06-07 05:00 | 59.0667 | 61 | 68.8833 | 67.1167
2015-06-07 05:15 | 59.3167 | 61 | 68.6333 | 67.3667
2015-06-07 05:30 | 59.5667 | 61 | 68.3833 | 67.6167
2015-06-07 05:45 | 59.8167 | 61 | 68.1333 | 67.8667
2015-06-07 06:00 | 60 | 61.2333 | 68 | 68.35
2015-06-07 06:15 | 60 | 61.7333 | 68 | 69.1
2015-06-07 06:30 | 60 | 62.2333 | 68 | 69.85
2015-06-07 06:45 | 60 | 62.7333 | 68 | 70.6
2015-06-07 07:00 | 60.0755 | 63.1489 | 68.5833 | 71.7
2015-06-07 07:15 | 60.3585 | 63.4681 | 69.8333 | 73.2
2015-06-07 07:30 | 60.6415 | 63.7872 | 71.0833 | 74.7
2015-06-07 07:45 | 60.9245 | 64.3846 | 72.3333 | 76.2
2015-06-07 08:00 | 61.1333 | 65.4667 | 73.4667 | 77.4667
2015-06-07 08:15 | 61.6333 | 66.4667 | 74.4667 | 78.4667
2015-06-07 08:30 | 62.1333 | 67.4667 | 75.4667 | 79.4667
2015-06-07 08:45 | 62.6333 | 68.4667 | 76.4667 | 80.4667
2015-06-07 09:00 | 63.0667 | 69.4667 | 77.4667 | 81.35
2015-06-07 09:15 | 63.3167 | 70.4667 | 78.4667 | 82.1
2015-06-07 09:30 | 63.5667 | 71.4667 | 79.4667 | 82.85
2015-06-07 09:45 | 63.8167 | 72.4667 | 80.4667 | 83.6
2015-06-07 10:00 | 64.1333 | 73.1167 | 81.1167 | 84.35
2015-06-07 10:15 | 64.6333 | 73.3667 | 81.3667 | 85.1
2015-06-07 10:30 | 65.1333 | 73.6167 | 81.6167 | 85.85
2015-06-07 10:45 | 65.6333 | 73.8667 | 81.8667 | 86.6
2015-06-07 11:00 | 66.2 | 74.1167 | 82.5833 | 87.35
2015-06-07 11:15 | 66.95 | 74.3667 | 83.8333 | 88.1
2015-06-07 11:30 | 67.7 | 74.6167 | 85.0833 | 88.85
2015-06-07 11:45 | 68.45 | 74.8667 | 86.3333 | 89.6
2015-06-07 12:00 | 69 | 75.5833 | 87.1167 | 90.2333
2015-06-07 12:15 | 69 | 76.8333 | 87.3667 | 90.7333
2015-06-07 12:30 | 69 | 78.0833 | 87.6167 | 91.2333
2015-06-07 12:45 | 69 | 79.3333 | 87.8667 | 91.7333
2015-06-07 13:00 | 68.9333 | 80.2333 | 88.2333 | 92.2333
2015-06-07 13:15 | 68.6833 | 80.7333 | 88.7333 | 92.7333
2015-06-07 13:30 | 68.4333 | 81.2333 | 89.2333 | 93.2333
2015-06-07 13:45 | 68.1833 | 81.7333 | 89.7333 | 93.7333
2015-06-07 14:00 | 67.9333 | 81.8833 | 89.8833 | 94
2015-06-07 14:15 | 67.6833 | 81.6333 | 89.6333 | 94
2015-06-07 14:30 | 67.4333 | 81.3833 | 89.3833 | 94
2015-06-07 14:45 | 67.1833 | 81.1333 | 89.1333 | 94
2015-06-07 15:00 | 66.9333 | 80.65 | 88.8833 | 94.2333
2015-06-07 15:15 | 66.6833 | 79.9 | 88.6333 | 94.7333
2015-06-07 15:30 | 66.4333 | 79.15 | 88.3833 | 95.2333
2015-06-07 15:45 | 66.1833 | 78.4 | 88.1333 | 95.7333
2015-06-07 16:00 | 65.8 | 77.7667 | 88.1167 | 96
2015-06-07 16:15 | 65.05 | 77.2667 | 88.3667 | 96
2015-06-07 16:30 | 64.3 | 76.7667 | 88.6167 | 96
2015-06-07 16:45 | 63.55 | 76.2667 | 88.8667 | 96
2015-06-07 17:00 | 62.9333 | 75.65 | 88.8833 | 95.7667
2015-06-07 17:15 | 62.6833 | 74.9 | 88.6333 | 95.2667
2015-06-07 17:30 | 62.4333 | 74.15 | 88.3833 | 94.7667
2015-06-07 17:45 | 62.1833 | 73.4 | 88.1333 | 94.2667
2015-06-07 18:00 | 61.8667 | 72.7667 | 87.65 | 93.8833
2015-06-07 18:15 | 61.3667 | 72.2667 | 86.9 | 93.6333
2015-06-07 18:30 | 60.8667 | 71.7667 | 86.15 | 93.3833
2015-06-07 18:45 | 60.3667 | 71.2667 | 85.4 | 93.1333
2015-06-07 19:00 | 59.8 | 70.5333 | 84.7667 | 92.65
2015-06-07 19:15 | 59.05 | 69.5333 | 84.2667 | 91.9
2015-06-07 19:30 | 58.3 | 68.5333 | 83.7667 | 91.15
2015-06-07 19:45 | 57.55 | 67.5333 | 83.2667 | 90.4
2015-06-07 20:00 | 56.9333 | 66.8833 | 82.7667 | 89.7667
2015-06-07 20:15 | 56.6833 | 66.6333 | 82.2667 | 89.2667
2015-06-07 20:30 | 56.4333 | 66.3833 | 81.7667 | 88.7667
2015-06-07 20:45 | 56.1833 | 66.1333 | 81.2667 | 88.2667
2015-06-07 21:00 | 56 | 65.8833 | 80.7667 | 87.7667
2015-06-07 21:15 | 56 | 65.6333 | 80.2667 | 87.2667
2015-06-07 21:30 | 56 | 65.3833 | 79.7667 | 86.7667
2015-06-07 21:45 | 56 | 65.1333 | 79.2667 | 86.2667
2015-06-07 22:00 | 56 | 65.1167 | 78.7667 | 85.65
2015-06-07 22:15 | 56 | 65.3667 | 78.2667 | 84.9
2015-06-07 22:30 | 56 | 65.6167 | 77.7667 | 84.15
2015-06-07 22:45 | 56 | 65.8667 | 77.2667 | 83.4
2015-06-07 23:00 | 55.9333 | 65.8833 | 76.8833 | 82.65
2015-06-07 23:15 | 55.6833 | 65.6333 | 76.6333 | 81.9
2015-06-07 23:30 | 55.4333 | 65.3833 | 76.3833 | 81.15
2015-06-07 23:45 | 55.1833 | 65.1333 | 76.1333 | 80.4
2015-06-08 | 55.0667 | 64.7667 | 75.7667 | 80
2015-06-08 00:15 | 55.3167 | 64.2667 | 75.2667 | 80
2015-06-08 00:30 | 55.5667 | 63.7667 | 74.7667 | 80
2015-06-08 00:45 | 55.8167 | 63.2667 | 74.2667 | 80
2015-06-08 01:00 | 55.9333 | 62.8833 | 73.8833 | 79.65
2015-06-08 01:15 | 55.6833 | 62.6333 | 73.6333 | 78.9
2015-06-08 01:30 | 55.4333 | 62.3833 | 73.3833 | 78.15
2015-06-08 01:45 | 55.1833 | 62.1333 | 73.1333 | 77.4
2015-06-08 02:00 | 55 | 62 | 72.8833 | 76.7667
2015-06-08 02:15 | 55 | 62 | 72.6333 | 76.2667
2015-06-08 02:30 | 55 | 62 | 72.3833 | 75.7667
2015-06-08 02:45 | 55 | 62 | 72.1333 | 75.2667
2015-06-08 03:00 | 55 | 62 | 71.8833 | 74.7667
2015-06-08 03:15 | 55 | 62 | 71.6333 | 74.2667
2015-06-08 03:30 | 55 | 62 | 71.3833 | 73.7667
2015-06-08 03:45 | 55 | 62 | 71.1333 | 73.2667
2015-06-08 04:00 | 55 | 61.8833 | 71 | 73
2015-06-08 04:15 | 55 | 61.6333 | 71 | 73
2015-06-08 04:30 | 55 | 61.3833 | 71 | 73
2015-06-08 04:45 | 55 | 61.1333 | 71 | 73
2015-06-08 05:00 | 55.0667 | 61.2333 | 70.8833 | 73.35
2015-06-08 05:15 | 55.3167 | 61.7333 | 70.6333 | 74.1
2015-06-08 05:30 | 55.5667 | 62.2333 | 70.3833 | 74.85
2015-06-08 05:45 | 55.8167 | 62.7333 | 70.1333 | 75.6
2015-06-08 06:00 | 56.3333 | 63.35 | 69.8833 | 76.5833
2015-06-08 06:15 | 57.5833 | 64.1 | 69.6333 | 77.8333
2015-06-08 06:30 | 58.8333 | 64.85 | 69.3833 | 79.0833
2015-06-08 06:45 | 60.0833 | 65.6 | 69.1333 | 80.3333
2015-06-08 07:00 | 61.2667 | 66.5833 | 69.2333 | 81.4667
2015-06-08 07:15 | 62.2667 | 67.8333 | 69.7333 | 82.4667
2015-06-08 07:30 | 63.2667 | 69.0833 | 70.2333 | 83.4667
2015-06-08 07:45 | 64.2667 | 70.3333 | 70.7333 | 84.4667
2015-06-08 08:00 | 65.1333 | 71.5833 | 71.35 | 85.35
2015-06-08 08:15 | 65.6333 | 72.8333 | 72.1 | 86.1
2015-06-08 08:30 | 66.1333 | 74.0833 | 72.85 | 86.85
2015-06-08 08:45 | 66.6333 | 75.3333 | 73.6 | 87.6
2015-06-08 09:00 | 67.3333 | 76.5833 | 74.5833 | 88.4667
2015-06-08 09:15 | 68.5833 | 77.8333 | 75.8333 | 89.4667
2015-06-08 09:30 | 69.8333 | 79.0833 | 77.0833 | 90.4667
2015-06-08 09:45 | 71.0833 | 80.3333 | 78.3333 | 91.4667
2015-06-08 10:00 | 72 | 81.4667 | 79.2333 | 92.5833
2015-06-08 10:15 | 72 | 82.4667 | 79.7333 | 93.8333
2015-06-08 10:30 | 72 | 83.4667 | 80.2333 | 95.0833
2015-06-08 10:45 | 72 | 84.4667 | 80.7333 | 96.3333
2015-06-08 11:00 | 72.2 | 85.2333 | 81.35 | 97.4667
2015-06-08 11:15 | 72.95 | 85.7333 | 82.1 | 98.4667
2015-06-08 11:30 | 73.7 | 86.2333 | 82.85 | 99.4667
2015-06-08 11:45 | 74.45 | 86.7333 | 83.6 | 100.4667
2015-06-08 12:00 | 75.5333 | 87.35 | 84.2333 | 101.2333
2015-06-08 12:15 | 77.5333 | 88.1 | 84.7333 | 101.7333
2015-06-08 12:30 | 79.5333 | 88.85 | 85.2333 | 102.2333
2015-06-08 12:45 | 81.5333 | 89.6 | 85.7333 | 102.7333
2015-06-08 13:00 | 82.8667 | 90.1167 | 86.1167 | 103
2015-06-08 13:15 | 82.3667 | 90.3667 | 86.3667 | 103
2015-06-08 13:30 | 81.8667 | 90.6167 | 86.6167 | 103
2015-06-08 13:45 | 81.3667 | 90.8667 | 86.8667 | 103
2015-06-08 14:00 | 80.9333 | 90.8833 | 87 | 103.2333
2015-06-08 14:15 | 80.6833 | 90.6333 | 87 | 103.7333
2015-06-08 14:30 | 80.4333 | 90.3833 | 87 | 104.2333
2015-06-08 14:45 | 80.1833 | 90.1333 | 87 | 104.7333
2015-06-08 15:00 | 80.1333 | 89.8833 | 87 | 104.8833
2015-06-08 15:15 | 80.6333 | 89.6333 | 87 | 104.6333
2015-06-08 15:30 | 81.1333 | 89.3833 | 87 | 104.3833
2015-06-08 15:45 | 81.6333 | 89.1333 | 87 | 104.1333
2015-06-08 16:00 | 81.8667 | 88.7667 | 87 | 104.1167
2015-06-08 16:15 | 81.3667 | 88.2667 | 87 | 104.3667
2015-06-08 16:30 | 80.8667 | 87.7667 | 87 | 104.6167
2015-06-08 16:45 | 80.3667 | 87.2667 | 87 | 104.8667
2015-06-08 17:00 | 79.7333 | 86.8833 | 86.8833 | 104.7667
2015-06-08 17:15 | 78.7333 | 86.6333 | 86.6333 | 104.2667
2015-06-08 17:30 | 77.7333 | 86.3833 | 86.3833 | 103.7667
2015-06-08 17:45 | 76.7333 | 86.1333 | 86.1333 | 103.2667
2015-06-08 18:00 | 75.5333 | 85.5333 | 85.7667 | 102.5333
2015-06-08 18:15 | 73.7833 | 84.5333 | 85.2667 | 101.5333
2015-06-08 18:30 | 72.0333 | 83.5333 | 84.7667 | 100.5333
2015-06-08 18:45 | 70.2833 | 82.5333 | 84.2667 | 99.5333
2015-06-08 19:00 | 68.5333 | 81.4167 | 83.7667 | 98.65
2015-06-08 19:15 | 66.7833 | 80.1667 | 83.2667 | 97.9
2015-06-08 19:30 | 65.0333 | 78.9167 | 82.7667 | 97.15
2015-06-08 19:45 | 63.2833 | 77.6667 | 82.2667 | 96.4
2015-06-08 20:00 | 61.9333 | 76.7667 | 81.65 | 95.7667
2015-06-08 20:15 | 61.6833 | 76.2667 | 80.9 | 95.2667
2015-06-08 20:30 | 61.4333 | 75.7667 | 80.15 | 94.7667
2015-06-08 20:45 | 61.1833 | 75.2667 | 79.4 | 94.2667
2015-06-08 21:00 | 60.9333 | 74.8833 | 78.65 | 93.5333
2015-06-08 21:15 | 60.6833 | 74.6333 | 77.9 | 92.5333
2015-06-08 21:30 | 60.4333 | 74.3833 | 77.15 | 91.5333
2015-06-08 21:45 | 60.1833 | 74.1333 | 76.4 | 90.5333
2015-06-08 22:00 | 59.8667 | 73.8833 | 75.7667 | 89.8833
2015-06-08 22:15 | 59.3667 | 73.6333 | 75.2667 | 89.6333
2015-06-08 22:30 | 58.8667 | 73.3833 | 74.7667 | 89.3833
2015-06-08 22:45 | 58.3667 | 73.1333 | 74.2667 | 89.1333
2015-06-08 23:00 | 57.9333 | 72.8833 | 73.7667 | 88.65
2015-06-08 23:15 | 57.6833 | 72.6333 | 73.2667 | 87.9
2015-06-08 23:30 | 57.4333 | 72.3833 | 72.7667 | 87.15
2015-06-08 23:45 | 57.1833 | 72.1333 | 72.2667 | 86.4
2015-06-09 | 56.9333 | 71.3 | 71.7667 | 85.7667
2015-06-09 00:15 | 56.6833 | 69.8 | 71.2667 | 85.2667
2015-06-09 00:30 | 56.4333 | 68.3 | 70.7667 | 84.7667
2015-06-09 00:45 | 56.1833 | 66.8 | 70.2667 | 84.2667
2015-06-09 01:00 | 55.9333 | 65.7667 | 70 | 83.65
2015-06-09 01:15 | 55.6833 | 65.2667 | 70 | 82.9
2015-06-09 01:30 | 55.4333 | 64.7667 | 70 | 82.15
2015-06-09 01:45 | 55.1833 | 64.2667 | 70 | 81.4
2015-06-09 02:00 | 55 | 63.8833 | 69.8833 | 80.8833
2015-06-09 02:15 | 55 | 63.6333 | 69.6333 | 80.6333
2015-06-09 02:30 | 55 | 63.3833 | 69.3833 | 80.3833
2015-06-09 02:45 | 55 | 63.1333 | 69.1333 | 80.1333
2015-06-09 03:00 | 55 | 62.8833 | 69 | 79.7667
2015-06-09 03:15 | 55 | 62.6333 | 69 | 79.2667
2015-06-09 03:30 | 55 | 62.3833 | 69 | 78.7667
2015-06-09 03:45 | 55 | 62.1333 | 69 | 78.2667
2015-06-09 04:00 | 54.9333 | 61.8833 | 68.8833 | 78
2015-06-09 04:15 | 54.6833 | 61.6333 | 68.6333 | 78
2015-06-09 04:30 | 54.4333 | 61.3833 | 68.3833 | 78
2015-06-09 04:45 | 54.1833 | 61.1333 | 68.1333 | 78
2015-06-09 05:00 | 54.1333 | 61.2333 | 68 | 78.2333
2015-06-09 05:15 | 54.6333 | 61.7333 | 68 | 78.7333
2015-06-09 05:30 | 55.1333 | 62.2333 | 68 | 79.2333
2015-06-09 05:45 | 55.6333 | 62.7333 | 68 | 79.7333
2015-06-09 06:00 | 56.3333 | 63.35 | 68.1167 | 80.1167
2015-06-09 06:15 | 57.5833 | 64.1 | 68.3667 | 80.3667
2015-06-09 06:30 | 58.8333 | 64.85 | 68.6167 | 80.6167
2015-06-09 06:45 | 60.0833 | 65.6 | 68.8667 | 80.8667
2015-06-09 07:00 | 61.1333 | 66.4667 | 69.4667 | 81.2333
2015-06-09 07:15 | 61.6333 | 67.4667 | 70.4667 | 81.7333
2015-06-09 07:30 | 62.1333 | 68.4667 | 71.4667 | 82.2333
2015-06-09 07:45 | 62.6333 | 69.4667 | 72.4667 | 82.7333
2015-06-09 08:00 | 63.2 | 70.35 | 73.5833 | 83.2333
2015-06-09 08:15 | 63.95 | 71.1 | 74.8333 | 83.7333
2015-06-09 08:30 | 64.7 | 71.85 | 76.0833 | 84.2333
2015-06-09 08:45 | 65.45 | 72.6 | 77.3333 | 84.7333
2015-06-09 09:00 | 66.0667 | 73.4667 | 78.4667 | 85.1167
2015-06-09 09:15 | 66.3167 | 74.4667 | 79.4667 | 85.3667
2015-06-09 09:30 | 66.5667 | 75.4667 | 80.4667 | 85.6167
2015-06-09 09:45 | 66.8167 | 76.4667 | 81.4667 | 85.8667
2015-06-09 10:00 | 67.0667 | 77.2333 | 82.2333 | 86
2015-06-09 10:15 | 67.3167 | 77.7333 | 82.7333 | 86
2015-06-09 10:30 | 67.5667 | 78.2333 | 83.2333 | 86
2015-06-09 10:45 | 67.8167 | 78.7333 | 83.7333 | 86
2015-06-09 11:00 | 68.1333 | 79.2333 | 84.2333 | 86.2333
2015-06-09 11:15 | 68.6333 | 79.7333 | 84.7333 | 86.7333
2015-06-09 11:30 | 69.1333 | 80.2333 | 85.2333 | 87.2333
2015-06-09 11:45 | 69.6333 | 80.7333 | 85.7333 | 87.7333
2015-06-09 12:00 | 70.2667 | 81.1167 | 86.35 | 88
2015-06-09 12:15 | 71.2667 | 81.3667 | 87.1 | 88
2015-06-09 12:30 | 72.2667 | 81.6167 | 87.85 | 88
2015-06-09 12:45 | 73.2667 | 81.8667 | 88.6 | 88
2015-06-09 13:00 | 74.0952 | 82.2333 | 89.2333 | 88.2414
2015-06-09 13:15 | 74.4524 | 82.7333 | 89.7333 | 88.7586
2015-06-09 13:30 | 74.8095 | 83.2333 | 90.2333 | 89.2759
2015-06-09 13:45 | 74.6111 | 83.7333 | 90.7333 | 89.7931
2015-06-09 14:00 | 73.9333 | 84 | 91 | 88.8833
2015-06-09 14:15 | 73.6833 | 84 | 91 | 88.6333
2015-06-09 14:30 | 73.4333 | 84 | 91 | 88.3833
2015-06-09 14:45 | 73.1833 | 84 | 91 | 88.1333
2015-06-09 15:00 | 72.3793 | 82.9348 | 91 | 89
2015-06-09 15:15 | 70.0517 | 80.6522 | 91 | 88.717
2015-06-09 15:30 | 67.7241 | 78.3696 | 91 | 88.434
2015-06-09 15:45 | 65.3966 | 76.5714 | 91 | 88.1509
2015-06-09 16:00 | 66.0667 | 75.0667 | 90.8833 | 87.65
2015-06-09 16:15 | 66.3167 | 73.0667 | 90.6333 | 86.9
2015-06-09 16:30 | 66.5667 | 71.0667 | 90.3833 | 86.15
2015-06-09 16:45 | 66.8167 | 69.0667 | 90.1333 | 85.4
2015-06-09 17:00 | 66.9333 | 68.1167 | 89.8833 | 85
2015-06-09 17:15 | 66.6833 | 68.3667 | 89.6333 | 85
2015-06-09 17:30 | 66.4333 | 68.6167 | 89.3833 | 85
2015-06-09 17:45 | 66.1833 | 68.8667 | 89.1333 | 85
2015-06-09 18:00 | 66.0667 | 69.1167 | 88.65 | 84.7667
2015-06-09 18:15 | 66.3167 | 69.3667 | 87.9 | 84.2667
2015-06-09 18:30 | 66.5667 | 69.6167 | 87.15 | 83.7667
2015-06-09 18:45 | 66.8167 | 69.8667 | 86.4 | 83.2667
2015-06-09 19:00 | 66.9333 | 70.1167 | 85.7667 | 82.8833
2015-06-09 19:15 | 66.6833 | 70.3667 | 85.2667 | 82.6333
2015-06-09 19:30 | 66.4333 | 70.6167 | 84.7667 | 82.3833
2015-06-09 19:45 | 66.1833 | 70.8667 | 84.2667 | 82.1333
2015-06-09 20:00 | 66 | 71 | 83.8833 | 81.7667
2015-06-09 20:15 | 66 | 71 | 83.6333 | 81.2667
2015-06-09 20:30 | 66 | 71 | 83.3833 | 80.7667
2015-06-09 20:45 | 66 | 71 | 83.1333 | 80.2667
2015-06-09 21:00 | 65.8667 | 71.1167 | 82.1833 | 79.8833
2015-06-09 21:15 | 65.3667 | 71.3667 | 80.4333 | 79.6333
2015-06-09 21:30 | 64.8667 | 71.6167 | 78.6833 | 79.3833
2015-06-09 21:45 | 64.3667 | 71.8667 | 76.9333 | 79.1333
2015-06-09 22:00 | 64 | 72.1167 | 75.7667 | 78.8833
2015-06-09 22:15 | 64 | 72.3667 | 75.2667 | 78.6333
2015-06-09 22:30 | 64 | 72.6167 | 74.7667 | 78.3833
2015-06-09 22:45 | 64 | 72.8667 | 74.2667 | 78.1333
2015-06-09 23:00 | 64.0667 | 72.7667 | 73.8833 | 78
2015-06-09 23:15 | 64.3167 | 72.2667 | 73.6333 | 78
2015-06-09 23:30 | 64.5667 | 71.7667 | 73.3833 | 78
2015-06-09 23:45 | 64.8167 | 71.2667 | 73.1333 | 78
2015-06-10 | 64.931 | 71 | 73 | 77.8833
2015-06-10 00:15 | 64.6724 | 71 | 73 | 77.6333
2015-06-10 00:30 | 64.4138 | 71 | 73 | 77.3833
2015-06-10 00:45 | 64.1552 | 71 | 73 | 77.1333
2015-06-10 01:00 | 63 | 71 | 72.7667 | 76.65
2015-06-10 01:15 | 63 | 71 | 72.2667 | 75.9
2015-06-10 01:30 | 63 | 71 | 71.7667 | 75.15
2015-06-10 01:45 | 63 | 71 | 71.2667 | 74.4
2015-06-10 02:00 | 62.8 | 71 | 71 | 74
2015-06-10 02:15 | 62.05 | 71 | 71 | 74
2015-06-10 02:30 | 61.3 | 71 | 71 | 74
2015-06-10 02:45 | 60.55 | 71 | 71 | 74
2015-06-10 03:00 | 59.8667 | 70.8833 | 71 | 73.8833
2015-06-10 03:15 | 59.3667 | 70.6333 | 71 | 73.6333
2015-06-10 03:30 | 58.8667 | 70.3833 | 71 | 73.3833
2015-06-10 03:45 | 58.3667 | 70.1333 | 71 | 73.1333
2015-06-10 04:00 | 58.0667 | 69.5333 | 70.8833 | 73.1167
2015-06-10 04:15 | 58.3167 | 68.5333 | 70.6333 | 73.3667
2015-06-10 04:30 | 58.5667 | 67.5333 | 70.3833 | 73.6167
2015-06-10 04:45 | 58.8167 | 66.5333 | 70.1333 | 73.8667
2015-06-10 05:00 | 59.0667 | 65.7667 | 69.8833 | 74
2015-06-10 05:15 | 59.3167 | 65.2667 | 69.6333 | 74
2015-06-10 05:30 | 59.5667 | 64.7667 | 69.3833 | 74
2015-06-10 05:45 | 59.8167 | 64.2667 | 69.1333 | 74
2015-06-10 06:00 | 60 | 64 | 69.2333 | 74.35
2015-06-10 06:15 | 60 | 64 | 69.7333 | 75.1
2015-06-10 06:30 | 60 | 64 | 70.2333 | 75.85
2015-06-10 06:45 | 60 | 64 | 70.7333 | 76.6
2015-06-10 07:00 | 60.0667 | 64.2333 | 71.5833 | 77.4667
2015-06-10 07:15 | 60.3167 | 64.7333 | 72.8333 | 78.4667
2015-06-10 07:30 | 60.5667 | 65.2333 | 74.0833 | 79.4667
2015-06-10 07:45 | 60.8167 | 65.7333 | 75.3333 | 80.4667
2015-06-10 08:00 | 61.1333 | 66.35 | 76.7 | 81.1167
2015-06-10 08:15 | 61.6333 | 67.1 | 78.2 | 81.3667
2015-06-10 08:30 | 62.1333 | 67.85 | 79.7 | 81.6167
2015-06-10 08:45 | 62.6333 | 68.6 | 81.2 | 81.8667
2015-06-10 09:00 | 63.1333 | 69.2333 | 82.4667 | 82.2333
2015-06-10 09:15 | 63.6333 | 69.7333 | 83.4667 | 82.7333
2015-06-10 09:30 | 64.1333 | 70.2333 | 84.4667 | 83.2333
2015-06-10 09:45 | 64.6333 | 70.7333 | 85.4667 | 83.7333
2015-06-10 10:00 | 65.0667 | 71.2333 | 86.2333 | 84.1167
2015-06-10 10:15 | 65.3167 | 71.7333 | 86.7333 | 84.3667
2015-06-10 10:30 | 65.5667 | 72.2333 | 87.2333 | 84.6167
2015-06-10 10:45 | 65.8167 | 72.7333 | 87.7333 | 84.8667
2015-06-10 11:00 | 66.0667 | 72.8833 | 88.35 | 85.1167
2015-06-10 11:15 | 66.3167 | 72.6333 | 89.1 | 85.3667
2015-06-10 11:30 | 66.5667 | 72.3833 | 89.85 | 85.6167
2015-06-10 11:45 | 66.8167 | 72.1333 | 90.6 | 85.8667
2015-06-10 12:00 | 66.7333 | 71.7667 | 91.2333 | 86.35
2015-06-10 12:15 | 65.7333 | 71.2667 | 91.7333 | 87.1
2015-06-10 12:30 | 64.7333 | 70.7667 | 92.2333 | 87.85
2015-06-10 12:45 | 63.7333 | 70.2667 | 92.7333 | 88.6
2015-06-10 13:00 | 62.9333 | 69.8833 | 93.1167 | 89
2015-06-10 13:15 | 62.6833 | 69.6333 | 93.3667 | 89
2015-06-10 13:30 | 62.4333 | 69.3833 | 93.6167 | 89
2015-06-10 13:45 | 62.1833 | 69.1333 | 93.8667 | 89
2015-06-10 14:00 | 61.9333 | 69 | 94.1167 | 88.7667
2015-06-10 14:15 | 61.6833 | 69 | 94.3667 | 88.2667
2015-06-10 14:30 | 61.4333 | 69 | 94.6167 | 87.7667
2015-06-10 14:45 | 61.1833 | 69 | 94.8667 | 87.2667
2015-06-10 15:00 | 61.2 | 69.2333 | 95 | 87.1167
2015-06-10 15:15 | 61.95 | 69.7333 | 95 | 87.3667
2015-06-10 15:30 | 62.7 | 70.2333 | 95 | 87.6167
2015-06-10 15:45 | 63.45 | 70.7333 | 95 | 87.8667
2015-06-10 16:00 | 63.9333 | 70.7667 | 95 | 88
2015-06-10 16:15 | 63.6833 | 70.2667 | 95 | 88
2015-06-10 16:30 | 63.4333 | 69.7667 | 95 | 88
2015-06-10 16:45 | 63.1833 | 69.2667 | 95 | 88
2015-06-10 17:00 | 62.9333 | 68.8833 | 94.7667 | 87.65
2015-06-10 17:15 | 62.6833 | 68.6333 | 94.2667 | 86.9
2015-06-10 17:30 | 62.4333 | 68.3833 | 93.7667 | 86.15
2015-06-10 17:45 | 62.1833 | 68.1333 | 93.2667 | 85.4
2015-06-10 18:00 | 61.8667 | 67.8833 | 92.65 | 84.65
2015-06-10 18:15 | 61.3667 | 67.6333 | 91.9 | 83.9
2015-06-10 18:30 | 60.8667 | 67.3833 | 91.15 | 83.15
2015-06-10 18:45 | 60.3667 | 67.1333 | 90.4 | 82.4
2015-06-10 19:00 | 59.8 | 66.8833 | 89.5333 | 81.7667
2015-06-10 19:15 | 59.05 | 66.6333 | 88.5333 | 81.2667
2015-06-10 19:30 | 58.3 | 66.3833 | 87.5333 | 80.7667
2015-06-10 19:45 | 57.55 | 66.1333 | 86.5333 | 80.2667
2015-06-10 20:00 | 57 | 66 | 85.65 | 79.7667
2015-06-10 20:15 | 57 | 66 | 84.9 | 79.2667
2015-06-10 20:30 | 57 | 66 | 84.15 | 78.7667
2015-06-10 20:45 | 57 | 66 | 83.4 | 78.2667
2015-06-10 21:00 | 57 | 65.7667 | 82.7667 | 77.65
2015-06-10 21:15 | 57 | 65.2667 | 82.2667 | 76.9
2015-06-10 21:30 | 57 | 64.7667 | 81.7667 | 76.15
2015-06-10 21:45 | 57 | 64.2667 | 81.2667 | 75.4
2015-06-10 22:00 | 57 | 63.7667 | 80.7667 | 74.65
2015-06-10 22:15 | 57 | 63.2667 | 80.2667 | 73.9
2015-06-10 22:30 | 57 | 62.7667 | 79.7667 | 73.15
2015-06-10 22:45 | 57 | 62.2667 | 79.2667 | 72.4
2015-06-10 23:00 | 56.9333 | 62.3182 | 78.7667 | 71.8833
2015-06-10 23:15 | 56.6833 | 63 | 78.2667 | 71.6333
2015-06-10 23:30 | 56.4333 | 62.6053 | 77.7667 | 71.3833
2015-06-10 23:45 | 56.1833 | 62.2105 | 77.2667 | 71.1333
2015-06-11 | 56 | 62.1458 | 76.8833 | 71
2015-06-11 00:15 | 56 | 62.4583 | 76.6333 | 71
2015-06-11 00:30 | 56 | 62.7708 | 76.3833 | 71
2015-06-11 00:45 | 56 | 62.6667 | 76.1333 | 71
2015-06-11 01:00 | 55.8571 | 61.8833 | 75.8833 | 70.8833
2015-06-11 01:15 | 55.3214 | 61.6333 | 75.6333 | 70.6333
2015-06-11 01:30 | 55 | 61.3833 | 75.3833 | 70.3833
2015-06-11 01:45 | 55 | 61.1333 | 75.1333 | 70.1333
2015-06-11 02:00 | 55 | 61 | 74.8833 | 69.7667
2015-06-11 02:15 | 55 | 61 | 74.6333 | 69.2667
2015-06-11 02:30 | 55 | 61 | 74.3833 | 68.7667
2015-06-11 02:45 | 55 | 61 | 74.1333 | 68.2667
2015-06-11 03:00 | 55 | 61 | 73.7667 | 67.8833
2015-06-11 03:15 | 55 | 61 | 73.2667 | 67.6333
2015-06-11 03:30 | 55 | 61 | 72.7667 | 67.3833
2015-06-11 03:45 | 55 | 61 | 72.2667 | 67.1333
2015-06-11 04:00 | 55 | 61 | 71.8833 | 66.8833
2015-06-11 04:15 | 55 | 61 | 71.6333 | 66.6333
2015-06-11 04:30 | 55 | 61 | 71.3833 | 66.3833
2015-06-11 04:45 | 55 | 61 | 71.1333 | 66.1333
2015-06-11 05:00 | 55.0667 | 61 | 70.8833 | 66.2333
2015-06-11 05:15 | 55.3167 | 61 | 70.6333 | 66.7333
2015-06-11 05:30 | 55.5667 | 61 | 70.3833 | 67.2333
2015-06-11 05:45 | 55.8167 | 61 | 70.1333 | 67.7333
2015-06-11 06:00 | 56.069 | 61.4516 | 70.2333 | 68.2333
2015-06-11 06:15 | 56.3276 | 62.4194 | 70.7333 | 68.7333
2015-06-11 06:30 | 56.5862 | 62.7931 | 71.2333 | 69.2333
2015-06-11 06:45 | 56.8448 | 62.2759 | 71.7333 | 69.7333
2015-06-11 07:00 | 58.0851 | 62.1591 | 72.4667 | 70.4667
2015-06-11 07:15 | 58.4043 | 62.5 | 73.4667 | 71.4667
2015-06-11 07:30 | 58.7234 | 62.8409 | 74.4667 | 72.4667
2015-06-11 07:45 | 59 | 63 | 75.4667 | 73.4667
2015-06-11 08:00 | 59.1379 | 63.4667 | 76.7 | 74.35
2015-06-11 08:15 | 59.6552 | 64.4667 | 78.2 | 75.1
2015-06-11 08:30 | 60.1724 | 65.4667 | 79.7 | 75.85
2015-06-11 08:45 | 60.6897 | 66.4667 | 81.2 | 76.6
2015-06-11 09:00 | 61 | 67.2593 | 82.4667 | 77.4667
2015-06-11 09:15 | 61.625 | 67.8148 | 83.4667 | 78.4667
2015-06-11 09:30 | 62.5625 | 68.6061 | 84.4667 | 79.4667
2015-06-11 09:45 | 63.4211 | 69.5152 | 85.4667 | 80.4667
2015-06-11 10:00 | 64.2667 | 70.35 | 86.4667 | 81.35
2015-06-11 10:15 | 65.2667 | 71.1 | 87.4667 | 82.1
2015-06-11 10:30 | 66.2667 | 71.85 | 88.4667 | 82.85
2015-06-11 10:45 | 67.2667 | 72.6 | 89.4667 | 83.6
2015-06-11 11:00 | 68.1333 | 73.35 | 90.35 | 84.35
2015-06-11 11:15 | 68.6333 | 74.1 | 91.1 | 85.1
2015-06-11 11:30 | 69.1333 | 74.85 | 91.85 | 85.85
2015-06-11 11:45 | 69.6333 | 75.6 | 92.6 | 86.6
2015-06-11 12:00 | 70.0667 | 76.4667 | 93.4667 | 87.1167
2015-06-11 12:15 | 70.3167 | 77.4667 | 94.4667 | 87.3667
2015-06-11 12:30 | 70.5667 | 78.4667 | 95.4667 | 87.6167
2015-06-11 12:45 | 70.8167 | 79.4667 | 96.4667 | 87.8667
2015-06-11 13:00 | 70.9333 | 80 | 97.1167 | 88.35
2015-06-11 13:15 | 70.6833 | 80 | 97.3667 | 89.1
2015-06-11 13:30 | 70.4333 | 80 | 97.6167 | 89.85
2015-06-11 13:45 | 70.1833 | 80 | 97.8667 | 90.6
2015-06-11 14:00 | 69.8667 | 80 | 98 | 91
2015-06-11 14:15 | 69.3667 | 80 | 98 | 91
2015-06-11 14:30 | 68.8667 | 80 | 98 | 91
2015-06-11 14:45 | 68.3667 | 80 | 98 | 91
2015-06-11 15:00 | 68 | 79.8833 | 97.5116 | 91.1167
2015-06-11 15:15 | 68 | 79.6333 | 96.4651 | 91.3667
2015-06-11 15:30 | 68 | 79.3833 | 95.4186 | 91.6167
2015-06-11 15:45 | 68 | 79.1333 | 93.8 | 91.8667
2015-06-11 16:00 | 67.9333 | 78.8833 | 95 | 92
2015-06-11 16:15 | 67.6833 | 78.6333 | 94.5333 | 92
2015-06-11 16:30 | 67.4333 | 78.3833 | 94.5385 | 92
2015-06-11 16:45 | 67.1833 | 78.1333 | 94.4706 | 92
2015-06-11 17:00 | 66.7333 | 77.8833 | 94.875 | 91.8833
2015-06-11 17:15 | 65.7333 | 77.6333 | 94.1923 | 91.6333
2015-06-11 17:30 | 64.7333 | 77.3833 | 93.3269 | 91.3833
2015-06-11 17:45 | 63.7333 | 77.1333 | 92.4615 | 91.1333
2015-06-11 18:00 | 62.7333 | 76.4167 | 91.65 | 90.7667
2015-06-11 18:15 | 61.7333 | 75.1667 | 90.9 | 90.2667
2015-06-11 18:30 | 60.7333 | 73.9167 | 90.15 | 89.7667
2015-06-11 18:45 | 59.7333 | 72.6667 | 89.4 | 89.2667
2015-06-11 19:00 | 58.8667 | 71.65 | 88.65 | 88.8833
2015-06-11 19:15 | 58.3667 | 70.9 | 87.9 | 88.6333
2015-06-11 19:30 | 57.8667 | 70.15 | 87.15 | 88.3833
2015-06-11 19:45 | 57.3667 | 69.4 | 86.4 | 88.1333
2015-06-11 20:00 | 57 | 68.7667 | 85.65 | 87.7667
2015-06-11 20:15 | 57 | 68.2667 | 84.9 | 87.2667
2015-06-11 20:30 | 57 | 67.7667 | 84.15 | 86.7667
2015-06-11 20:45 | 57 | 67.2667 | 83.4 | 86.2667
2015-06-11 21:00 | 56.9333 | 66.8833 | 82.7667 | 85.7667
2015-06-11 21:15 | 56.6833 | 66.6333 | 82.2667 | 85.2667
2015-06-11 21:30 | 56.4333 | 66.3833 | 81.7667 | 84.7667
2015-06-11 21:45 | 56.1833 | 66.1333 | 81.2667 | 84.2667
2015-06-11 22:00 | 56 | 65.8833 | 80.8833 | 83.8833
2015-06-11 22:15 | 56 | 65.6333 | 80.6333 | 83.6333
2015-06-11 22:30 | 56 | 65.3833 | 80.3833 | 83.3833
2015-06-11 22:45 | 56 | 65.1333 | 80.1333 | 83.1333
2015-06-11 23:00 | 56 | 64.65 | 79.7667 | 82.7667
2015-06-11 23:15 | 56 | 63.9 | 79.2667 | 82.2667
2015-06-11 23:30 | 56 | 63.15 | 78.7667 | 81.7667
2015-06-11 23:45 | 56 | 62.4 | 78.2667 | 81.2667
2015-06-12 | 55.9333 | 62.1167 | 77.8833 | 80.7667
2015-06-12 00:15 | 55.6833 | 62.3667 | 77.6333 | 80.2667
2015-06-12 00:30 | 55.4333 | 62.6167 | 77.3833 | 79.7667
2015-06-12 00:45 | 55.1833 | 62.8667 | 77.1333 | 79.2667
2015-06-12 01:00 | 55 | 62.8833 | 76.8833 | 78.7667
2015-06-12 01:15 | 55 | 62.6333 | 76.6333 | 78.2667
2015-06-12 01:30 | 55 | 62.3833 | 76.3833 | 77.7667
2015-06-12 01:45 | 55 | 62.1333 | 76.1333 | 77.2667
2015-06-12 02:00 | 55 | 61.7667 | 75.8833 | 76.7667
2015-06-12 02:15 | 55 | 61.2667 | 75.6333 | 76.2667
2015-06-12 02:30 | 55 | 60.7667 | 75.3833 | 75.7667
2015-06-12 02:45 | 55 | 60.2667 | 75.1333 | 75.2667
2015-06-12 03:00 | 55 | 59.8833 | 74.8833 | 74.8833
2015-06-12 03:15 | 55 | 59.6333 | 74.6333 | 74.6333
2015-06-12 03:30 | 55 | 59.3833 | 74.3833 | 74.3833
2015-06-12 03:45 | 55 | 59.1333 | 74.1333 | 74.1333
2015-06-12 04:00 | 55 | 59 | 73.8833 | 74
2015-06-12 04:15 | 55 | 59 | 73.6333 | 74
2015-06-12 04:30 | 55 | 59 | 73.3833 | 74
2015-06-12 04:45 | 55 | 58.8889 | 73.1333 | 74
2015-06-12 05:00 | 55.0667 | 58.35 | 72.8833 | 74.1167
2015-06-12 05:15 | 55.3167 | 59.1 | 72.6333 | 74.3667
2015-06-12 05:30 | 55.5667 | 59.85 | 72.3833 | 74.6167
2015-06-12 05:45 | 55.8167 | 60.6 | 72.1333 | 74.8667
2015-06-12 06:00 | 56.2667 | 61.35 | 72.1167 | 75.4667
2015-06-12 06:15 | 57.2667 | 62.1 | 72.3667 | 76.4667
2015-06-12 06:30 | 58.2667 | 62.85 | 72.6167 | 77.4667
2015-06-12 06:45 | 59.2667 | 63.6 | 72.8667 | 78.4667
2015-06-12 07:00 | 60.2 | 64.2333 | 73.35 | 79.4667
2015-06-12 07:15 | 60.95 | 64.7333 | 74.1 | 80.4667
2015-06-12 07:30 | 61.7 | 65.2333 | 74.85 | 81.4667
2015-06-12 07:45 | 62.45 | 65.7333 | 75.6 | 82.4667
2015-06-12 08:00 | 63.0667 | 66.7 | 76.5833 | 83.4667
2015-06-12 08:15 | 63.3167 | 68.2 | 77.8333 | 84.4667
2015-06-12 08:30 | 63.5667 | 69.7 | 79.0833 | 85.4667
2015-06-12 08:45 | 63.8167 | 71.2 | 80.3333 | 86.4667
2015-06-12 09:00 | 64.3333 | 72.5833 | 81.5833 | 87.2333
2015-06-12 09:15 | 65.5833 | 73.8333 | 82.8333 | 87.7333
2015-06-12 09:30 | 66.8333 | 75.0833 | 84.0833 | 88.2333
2015-06-12 09:45 | 68.0833 | 76.3333 | 85.3333 | 88.7333
2015-06-12 10:00 | 69.2 | 77.35 | 86.35 | 89.5833
2015-06-12 10:15 | 69.95 | 78.1 | 87.1 | 90.8333
2015-06-12 10:30 | 70.7 | 78.85 | 87.85 | 92.0833
2015-06-12 10:45 | 71.45 | 79.6 | 88.6 | 93.3333
2015-06-12 11:00 | 71.8667 | 80.35 | 89.4667 | 94.1167
2015-06-12 11:15 | 71.3667 | 81.1 | 90.4667 | 94.3667
2015-06-12 11:30 | 70.8667 | 81.85 | 91.4667 | 94.6167
2015-06-12 11:45 | 70.3667 | 82.6 | 92.4667 | 94.8667
2015-06-12 12:00 | 70 | 83.2333 | 93.2333 | 95.1167
2015-06-12 12:15 | 70 | 83.7333 | 93.7333 | 95.3667
2015-06-12 12:30 | 70 | 84.2333 | 94.2333 | 95.6167
2015-06-12 12:45 | 70 | 84.7333 | 94.7333 | 95.8667
2015-06-12 13:00 | 70.0667 | 85 | 95.35 | 96.1167
2015-06-12 13:15 | 70.3167 | 85 | 96.1 | 96.3667
2015-06-12 13:30 | 70.5667 | 85 | 96.85 | 96.6167
2015-06-12 13:45 | 70.8167 | 85 | 97.6 | 96.8667
2015-06-12 14:00 | 71.0667 | 84.8833 | 98.1167 | 97.2333
2015-06-12 14:15 | 71.3167 | 84.6333 | 98.3667 | 97.7333
2015-06-12 14:30 | 71.5667 | 84.3833 | 98.6167 | 98.2333
2015-06-12 14:45 | 71.8167 | 84.1333 | 98.8667 | 98.7333
2015-06-12 15:00 | 72.0667 | 83.65 | 97.6 | 99.1167
2015-06-12 15:15 | 72.3167 | 82.9 | 94.6 | 99.3667
2015-06-12 15:30 | 72.5667 | 82.15 | 91.6 | 99.6167
2015-06-12 15:45 | 72.8167 | 81.4 | 88.6 | 99.8667
2015-06-12 16:00 | 72.8667 | 81 | 86.3 | 100
2015-06-12 16:15 | 72.3667 | 81 | 84.8 | 100
2015-06-12 16:30 | 71.8667 | 81 | 83.3 | 100
2015-06-12 16:45 | 71.3667 | 81 | 81.8 | 100
2015-06-12 17:00 | 70.7333 | 80.65 | 81.35 | 99.7667
2015-06-12 17:15 | 69.7333 | 79.9 | 82.1 | 99.2667
2015-06-12 17:30 | 68.7333 | 79.15 | 82.85 | 98.7667
2015-06-12 17:45 | 67.7333 | 78.4 | 83.6 | 98.2667
2015-06-12 18:00 | 66.8667 | 77.65 | 83.7667 | 97.8833
2015-06-12 18:15 | 66.3667 | 76.9 | 83.2667 | 97.6333
2015-06-12 18:30 | 65.8667 | 76.15 | 82.7667 | 97.3833
2015-06-12 18:45 | 65.3667 | 75.4 | 82.2667 | 97.1333
2015-06-12 19:00 | 64.8667 | 74.5333 | 81.5333 | 96.5333
2015-06-12 19:15 | 64.3667 | 73.5333 | 80.5333 | 95.5333
2015-06-12 19:30 | 63.8667 | 72.5333 | 79.5333 | 94.5333
2015-06-12 19:45 | 63.3667 | 71.5333 | 78.5333 | 93.5333
2015-06-12 20:00 | 62.8667 | 70.7667 | 77.7667 | 92.7667
2015-06-12 20:15 | 62.3667 | 70.2667 | 77.2667 | 92.2667
2015-06-12 20:30 | 61.8667 | 69.7667 | 76.7667 | 91.7667
2015-06-12 20:45 | 61.3667 | 69.2667 | 76.2667 | 91.2667
2015-06-12 21:00 | 60.9333 | 68.65 | 75.7667 | 90.8833
2015-06-12 21:15 | 60.6833 | 67.9 | 75.2667 | 90.6333
2015-06-12 21:30 | 60.4333 | 67.15 | 74.7667 | 90.3833
2015-06-12 21:45 | 60.1833 | 66.4 | 74.2667 | 90.1333
2015-06-12 22:00 | 60 | 65.7667 | 73.8833 | 89.65
2015-06-12 22:15 | 60 | 65.2667 | 73.6333 | 88.9
2015-06-12 22:30 | 60 | 64.7667 | 73.3833 | 88.15
2015-06-12 22:45 | 60 | 64.2667 | 73.1333 | 87.4
2015-06-12 23:00 | 59.9333 | 63.7667 | 73 | 86.65
2015-06-12 23:15 | 59.6833 | 63.2667 | 73 | 85.9
2015-06-12 23:30 | 59.4333 | 62.7667 | 73 | 85.15
2015-06-12 23:45 | 59.1833 | 62.2667 | 73 | 84.4
2015-06-13 | 58.9333 | 62 | 73 | 83.7667
2015-06-13 00:15 | 58.6833 | 62 | 73 | 83.2667
2015-06-13 00:30 | 58.4333 | 62 | 73 | 82.7667
2015-06-13 00:45 | 58.1833 | 62 | 73 | 82.2667
2015-06-13 01:00 | 57.9333 | 61.8833 | 72.8833 | 81.8833
2015-06-13 01:15 | 57.6833 | 61.6333 | 72.6333 | 81.6333
2015-06-13 01:30 | 57.4333 | 61.3833 | 72.3833 | 81.3833
2015-06-13 01:45 | 57.1833 | 61.1333 | 72.1333 | 81.1333
2015-06-13 02:00 | 57 | 61 | 71.7667 | 80.7667
2015-06-13 02:15 | 57 | 61 | 71.2667 | 80.2667
2015-06-13 02:30 | 57 | 61 | 70.7667 | 79.7667
2015-06-13 02:45 | 57 | 61 | 70.2667 | 79.2667
2015-06-13 03:00 | 57 | 60.8833 | 69.8833 | 78.8833
2015-06-13 03:15 | 57 | 60.6333 | 69.6333 | 78.6333
2015-06-13 03:30 | 57 | 60.3833 | 69.3833 | 78.3833
2015-06-13 03:45 | 57 | 60.1333 | 69.1333 | 78.1333
2015-06-13 04:00 | 56.8596 | 60 | 69 | 77.8833
2015-06-13 04:15 | 56.3333 | 60 | 69 | 77.6333
2015-06-13 04:30 | 55.807 | 60 | 69 | 77.3833
2015-06-13 04:45 | 55.2807 | 60 | 69 | 77.1333
2015-06-13 05:00 | 57.0667 | 60 | 68.8833 | 77.35
2015-06-13 05:15 | 57.3167 | 60 | 68.6333 | 78.1
2015-06-13 05:30 | 57.5667 | 60 | 68.3833 | 78.85
2015-06-13 05:45 | 57.8167 | 60 | 68.1333 | 79.6
2015-06-13 06:00 | 58.2667 | 60.35 | 68.2333 | 80.4667
2015-06-13 06:15 | 59.2667 | 61.1 | 68.7333 | 81.4667
2015-06-13 06:30 | 60.2667 | 61.85 | 69.2333 | 82.4667
2015-06-13 06:45 | 61.2667 | 62.6 | 69.7333 | 83.4667
2015-06-13 07:00 | 62.0667 | 63.2333 | 70.5833 | 84.4667
2015-06-13 07:15 | 62.3167 | 63.7333 | 71.8333 | 85.4667
2015-06-13 07:30 | 62.5667 | 64.2333 | 73.0833 | 86.4667
2015-06-13 07:45 | 62.8167 | 64.7333 | 74.3333 | 87.4667
2015-06-13 08:00 | 63.0667 | 65.5833 | 75.35 | 88.35
2015-06-13 08:15 | 63.3167 | 66.8333 | 76.1 | 89.1
2015-06-13 08:30 | 63.5667 | 68.0833 | 76.85 | 89.85
2015-06-13 08:45 | 63.8167 | 69.3333 | 77.6 | 90.6
2015-06-13 09:00 | 64.0667 | 70.4667 | 78.4667 | 91.4667
2015-06-13 09:15 | 64.3167 | 71.4667 | 79.4667 | 92.4667
2015-06-13 09:30 | 64.5667 | 72.4667 | 80.4667 | 93.4667
2015-06-13 09:45 | 64.8167 | 73.4667 | 81.4667 | 94.4667
2015-06-13 10:00 | 65.1333 | 74.5833 | 82.35 | 95.2333
2015-06-13 10:15 | 65.6333 | 75.8333 | 83.1 | 95.7333
2015-06-13 10:30 | 66.1333 | 77.0833 | 83.85 | 96.2333
2015-06-13 10:45 | 66.6333 | 78.3333 | 84.6 | 96.7333
2015-06-13 11:00 | 67.1333 | 79.4667 | 85.35 | 97.4667
2015-06-13 11:15 | 67.6333 | 80.4667 | 86.1 | 98.4667
2015-06-13 11:30 | 68.1333 | 81.4667 | 86.85 | 99.4667
2015-06-13 11:45 | 68.6333 | 82.4667 | 87.6 | 100.4667
2015-06-13 12:00 | 69.1333 | 82.8833 | 88.35 | 101.1167
2015-06-13 12:15 | 69.6333 | 82.6333 | 89.1 | 101.3667
2015-06-13 12:30 | 70.1333 | 82.3833 | 89.85 | 101.6167
2015-06-13 12:45 | 70.6333 | 82.1333 | 90.6 | 101.8667
2015-06-13 13:00 | 71.1333 | 81.65 | 90.65 | 102.2333
2015-06-13 13:15 | 71.6333 | 80.9 | 89.9 | 102.7333
2015-06-13 13:30 | 72.1333 | 80.15 | 89.15 | 103.2333
2015-06-13 13:45 | 72.6333 | 79.4 | 88.4 | 103.7333
2015-06-13 14:00 | 72.9333 | 78.7667 | 87.3 | 104.2333
2015-06-13 14:15 | 72.6833 | 78.2667 | 86.2 | 104.7333
2015-06-13 14:30 | 72.4333 | 77.7667 | 86 | 105.2333
2015-06-13 14:45 | 72.1833 | 77.2667 | 85.4 | 105.7333
2015-06-13 15:00 | 72.3077 | 76.7667 | 81.8947 | 105.8833
2015-06-13 15:15 | 73.4615 | 76.2667 | 79.1 | 105.6333
2015-06-13 15:30 | 74.6154 | 75.7667 | 77 | 105.3833
2015-06-13 15:45 | 74.0476 | 75.2667 | 77 | 105.1333
2015-06-13 16:00 | 72.5556 | 74.8833 | 75.0909 | 104.7667
2015-06-13 16:15 | 71.6078 | 74.6333 | 75.2222 | 104.2667
2015-06-13 16:30 | 71.0196 | 74.3833 | 75.3846 | 103.7667
2015-06-13 16:45 | 70.4314 | 74.1333 | 71.875 | 103.2667
2015-06-13 17:00 | 69.8667 | 73.5333 | 70 | 102.7667
2015-06-13 17:15 | 69.3667 | 72.5333 | 70 | 102.2667
2015-06-13 17:30 | 68.8667 | 71.5333 | 70 | 101.7667
2015-06-13 17:45 | 68.3667 | 70.5333 | 70 | 101.2667
2015-06-13 18:00 | 67.5333 | 69.7667 | 70 | 100.4167
2015-06-13 18:15 | 65.7833 | 69.2667 | 70 | 99.1667
2015-06-13 18:30 | 64.0333 | 68.7667 | 71.3333 | 97.9167
2015-06-13 18:45 | 62.2833 | 68.2667 | 70.6667 | 96.6667
2015-06-13 19:00 | 60.9333 | 67.65 | 70.1818 | 95.4167
2015-06-13 19:15 | 60.6833 | 66.9 | 71.2222 | 94.1667
2015-06-13 19:30 | 60.4333 | 66.15 | 71.7778 | 92.9167
2015-06-13 19:45 | 60.1833 | 65.4 | 72 | 91.6667
2015-06-13 20:00 | 59.9333 | 64.7667 | 72.2333 | 90.5333
2015-06-13 20:15 | 59.6833 | 64.2667 | 72.7333 | 89.5333
2015-06-13 20:30 | 59.4333 | 63.7667 | 73.2333 | 88.5333
2015-06-13 20:45 | 59.1833 | 63.2667 | 73.7333 | 87.5333
2015-06-13 21:00 | 58.9333 | 62.8833 | 73.65 | 86.5333
2015-06-13 21:15 | 58.6833 | 62.6333 | 72.9 | 85.5333
2015-06-13 21:30 | 58.4333 | 62.3833 | 72.15 | 84.5333
2015-06-13 21:45 | 58.1833 | 62.1333 | 71.4 | 83.5333
2015-06-13 22:00 | 57.9333 | 61.8833 | 70.8833 | 82.5333
2015-06-13 22:15 | 57.6833 | 61.6333 | 70.6333 | 81.5333
2015-06-13 22:30 | 57.4333 | 61.3833 | 70.3833 | 80.5333
2015-06-13 22:45 | 57.1833 | 61.1333 | 70.1333 | 79.5333
2015-06-13 23:00 | 57 | 60.7667 | 69.8833 | 78.5333
2015-06-13 23:15 | 57 | 60.2667 | 69.6333 | 77.5333
2015-06-13 23:30 | 57 | 59.7667 | 69.3833 | 76.5333
2015-06-13 23:45 | 57 | 59.2667 | 69.1333 | 75.5333
2015-06-14 | 56.9333 | 58.7667 | 69 | 74.8833
2015-06-14 00:15 | 56.6833 | 58.2667 | 69 | 74.6333
2015-06-14 00:30 | 56.4333 | 57.7667 | 69 | 74.3833
2015-06-14 00:45 | 56.1833 | 57.2667 | 69 | 74.1333
2015-06-14 01:00 | 55.9333 | 57 | 68.8833 | 73.8833
2015-06-14 01:15 | 55.6833 | 57 | 68.6333 | 73.6333
2015-06-14 01:30 | 55.4333 | 57 | 68.3833 | 73.3833
2015-06-14 01:45 | 55.1833 | 57 | 68.1333 | 73.1333
2015-06-14 02:00 | 54.9333 | 56.8833 | 67.65 | 72.7667
2015-06-14 02:15 | 54.6833 | 56.6333 | 66.9 | 72.2667
2015-06-14 02:30 | 54.4333 | 56.3833 | 66.15 | 71.7667
2015-06-14 02:45 | 54.1833 | 56.1333 | 65.4 | 71.2667
2015-06-14 03:00 | 54 | 56 | 64.7667 | 70.7667
2015-06-14 03:15 | 54 | 56 | 64.2667 | 70.2667
2015-06-14 03:30 | 54 | 56 | 63.7667 | 69.7667
2015-06-14 03:45 | 54 | 56 | 63.2667 | 69.2667
2015-06-14 04:00 | 54 | 55.8108 | 62.8833 | 68.8833
2015-06-14 04:15 | 54 | 55.4054 | 62.6333 | 68.6333
2015-06-14 04:30 | 54 | 55 | 62.3833 | 68.3833
2015-06-14 04:45 | 54 | 55 | 62.1333 | 68.1333
2015-06-14 05:00 | 54.1333 | 55 | 61.7667 | 68.4667
2015-06-14 05:15 | 54.6333 | 55 | 61.2667 | 69.4667
2015-06-14 05:30 | 55.1333 | 55 | 60.7667 | 70.4667
2015-06-14 05:45 | 55.6333 | 55.3333 | 60.2667 | 71.4667
2015-06-14 06:00 | 56.2 | 56.1892 | 60.5833 | 72.1167
2015-06-14 06:15 | 56.95 | 56.5946 | 61.8333 | 72.3667
2015-06-14 06:30 | 57.7 | 57 | 63.0833 | 72.6167
2015-06-14 06:45 | 58.45 | 57.6522 | 64.3333 | 72.8667
2015-06-14 07:00 | 59.0667 | 58.35 | 65.4667 | 73.5833
2015-06-14 07:15 | 59.3167 | 59.1 | 66.4667 | 74.8333
2015-06-14 07:30 | 59.5667 | 59.85 | 67.4667 | 76.0833
2015-06-14 07:45 | 59.8167 | 60.6 | 68.4667 | 77.3333
2015-06-14 08:00 | 60.2 | 61.35 | 69.7 | 78.5833
2015-06-14 08:15 | 60.95 | 62.1 | 71.2 | 79.8333
2015-06-14 08:30 | 61.7 | 62.85 | 72.7 | 81.0833
2015-06-14 08:45 | 62.45 | 63.6 | 74.2 | 82.3333
2015-06-14 09:00 | 63.2 | 64.4667 | 75.8167 | 83.5833
2015-06-14 09:15 | 63.95 | 65.4667 | 77.5667 | 84.8333
2015-06-14 09:30 | 64.7 | 66.4667 | 79.3167 | 86.0833
2015-06-14 09:45 | 65.45 | 67.4667 | 81.0667 | 87.3333
2015-06-14 10:00 | 66.0667 | 68.5833 | 82.2333 | 88.5833
2015-06-14 10:15 | 66.3167 | 69.8333 | 82.7333 | 89.8333
2015-06-14 10:30 | 66.5667 | 71.0833 | 83.2333 | 91.0833
2015-06-14 10:45 | 66.8167 | 72.3333 | 83.7333 | 92.3333
2015-06-14 11:00 | 66.9333 | 73.1167 | 84.35 | 93.2333
2015-06-14 11:15 | 66.6833 | 73.3667 | 85.1 | 93.7333
2015-06-14 11:30 | 66.4333 | 73.6167 | 85.85 | 94.2333
2015-06-14 11:45 | 66.1833 | 73.8667 | 86.6 | 94.7333
2015-06-14 12:00 | 65.9333 | 73.8833 | 87.2333 | 95.35
2015-06-14 12:15 | 65.6833 | 73.6333 | 87.7333 | 96.1
2015-06-14 12:30 | 65.4333 | 73.3833 | 88.2333 | 96.85
2015-06-14 12:45 | 65.1833 | 73.1333 | 88.7333 | 97.6
2015-06-14 13:00 | 65 | 72.8833 | 89 | 98
2015-06-14 13:15 | 65 | 72.6333 | 89 | 98
2015-06-14 13:30 | 65 | 72.3833 | 89 | 98
2015-06-14 13:45 | 65 | 72.1333 | 89 | 98
2015-06-14 14:00 | 64.9333 | 71.8833 | 89.35 | 98.2333
2015-06-14 14:15 | 64.6833 | 71.6333 | 90.1 | 98.7333
2015-06-14 14:30 | 64.4333 | 71.3833 | 90.85 | 99.2333
2015-06-14 14:45 | 64.1833 | 71.1333 | 91.6 | 99.7333
2015-06-14 15:00 | 64 | 70.7667 | 92.2333 | 100
2015-06-14 15:15 | 64 | 70.2667 | 92.7333 | 100
2015-06-14 15:30 | 64 | 69.7667 | 93.2333 | 100
2015-06-14 15:45 | 64 | 69.2667 | 93.7333 | 100
2015-06-14 16:00 | 63.8 | 68.8833 | 93.8833 | 99.8833
2015-06-14 16:15 | 63.05 | 68.6333 | 93.6333 | 99.6333
2015-06-14 16:30 | 62.3 | 68.3833 | 93.3833 | 99.3833
2015-06-14 16:45 | 61.55 | 68.1333 | 93.1333 | 99.1333
2015-06-14 17:00 | 60.8 | 67.5333 | 92.4167 | 98.7667
2015-06-14 17:15 | 60.05 | 66.5333 | 91.1667 | 98.2667
2015-06-14 17:30 | 59.3 | 65.5333 | 89.9167 | 97.7667
2015-06-14 17:45 | 58.55 | 64.5333 | 88.6667 | 97.2667
2015-06-14 18:00 | 57.8667 | 63.65 | 87.4909 | 96.4167
2015-06-14 18:15 | 57.3667 | 62.9 | 86.4 | 95.1667
2015-06-14 18:30 | 56.8667 | 62.15 | 85.3091 | 93.9167
2015-06-14 18:45 | 56.3667 | 61.4 | 84.2182 | 92.6667
2015-06-14 19:00 | 55.8667 | 60.65 | 83.5333 | 91.5333
2015-06-14 19:15 | 55.3667 | 59.9 | 83 | 90.5333
2015-06-14 19:30 | 54.8667 | 59.15 | 77.6667 | 89.5333
2015-06-14 19:45 | 54.3667 | 58.4 | 77 | 88.5333
2015-06-14 20:00 | 54.0667 | 57.8833 | 76.3 | 87.5333
2015-06-14 20:15 | 54.3167 | 57.6333 | 74.8 | 86.5333
2015-06-14 20:30 | 54.5667 | 57.3833 | 73.3 | 85.5333
2015-06-14 20:45 | 54.8167 | 57.1333 | 71.8 | 84.5333
2015-06-14 21:00 | 55.0667 | 56.8833 | 71 | 83.65
2015-06-14 21:15 | 55.3167 | 56.6333 | 71 | 82.9
2015-06-14 21:30 | 55.5667 | 56.3833 | 72.0833 | 82.15
2015-06-14 21:45 | 55.8167 | 56.1333 | 73.3333 | 81.4
2015-06-14 22:00 | 55.9333 | 55.8833 | 73.5333 | 80.65
2015-06-14 22:15 | 55.6833 | 55.6333 | 72.5333 | 79.9
2015-06-14 22:30 | 55.4333 | 55.3833 | 71.5333 | 79.15
2015-06-14 22:45 | 55.1833 | 55.1333 | 70.5333 | 78.4
2015-06-14 23:00 | 55 | 55 | 69.8833 | 77.65
2015-06-14 23:15 | 55 | 55 | 69.6333 | 76.9
2015-06-14 23:30 | 55 | 55 | 69.3833 | 76.15
2015-06-14 23:45 | 55 | 55 | 69.1333 | 75.4
2015-06-15 | 54.9333 | 55.1167 | 69 | 74.5333
2015-06-15 00:15 | 54.6833 | 55.3667 | 69 | 73.5333
2015-06-15 00:30 | 54.4333 | 55.6167 | 69 | 72.5333
2015-06-15 00:45 | 54.1833 | 55.8667 | 69 | 71.5333
2015-06-15 01:00 | 53.9333 | 56 | 68.8833 | 70.8833
2015-06-15 01:15 | 53.6833 | 56 | 68.6333 | 70.6333
2015-06-15 01:30 | 53.4333 | 56 | 68.3833 | 70.3833
2015-06-15 01:45 | 53.1833 | 56 | 68.1333 | 70.1333
2015-06-15 02:00 | 53.0667 | 56.1167 | 68.1167 | 69.7667
2015-06-15 02:15 | 53.3167 | 56.3667 | 68.3667 | 69.2667
2015-06-15 02:30 | 53.5667 | 56.6167 | 68.6167 | 68.7667
2015-06-15 02:45 | 53.8167 | 56.8667 | 68.8667 | 68.2667
2015-06-15 03:00 | 53.9333 | 56.8833 | 68.8833 | 67.7667
2015-06-15 03:15 | 53.6833 | 56.6333 | 68.6333 | 67.2667
2015-06-15 03:30 | 53.4333 | 56.3833 | 68.3833 | 66.7667
2015-06-15 03:45 | 53.1833 | 56.1333 | 68.1333 | 66.2667
2015-06-15 04:00 | 53 | 55.8571 | 67.8833 | 65.8833
2015-06-15 04:15 | 53 | 55.551 | 67.6333 | 65.6333
2015-06-15 04:30 | 53 | 55.2449 | 67.3833 | 65.3833
2015-06-15 04:45 | 53 | 55.2727 | 67.1333 | 65.1333
2015-06-15 05:00 | 53 | 56.1167 | 67 | 65.2333
2015-06-15 05:15 | 53 | 56.3667 | 67 | 65.7333
2015-06-15 05:30 | 53 | 56.6167 | 67 | 66.2333
2015-06-15 05:45 | 53 | 56.8667 | 67 | 66.7333
2015-06-15 06:00 | 53 | 57.1167 | 67 | 67.4667
2015-06-15 06:15 | 53 | 57.3667 | 67 | 68.4667
2015-06-15 06:30 | 53 | 57.6167 | 67 | 69.4667
2015-06-15 06:45 | 53 | 57.8667 | 67 | 70.4667
2015-06-15 07:00 | 53.069 | 58.1167 | 67.4667 | 71.5833
2015-06-15 07:15 | 53.3276 | 58.3667 | 68.4667 | 72.8333
2015-06-15 07:30 | 53.5862 | 58.6167 | 69.4667 | 74.0833
2015-06-15 07:45 | 53.8448 | 58.8667 | 70.4667 | 75.3333
2015-06-15 08:00 | 54.0667 | 59.4242 | 71.5833 | 76.5833
2015-06-15 08:15 | 54.3167 | 60.3333 | 72.8333 | 77.8333
2015-06-15 08:30 | 54.5667 | 61.1481 | 74.0833 | 79.0833
2015-06-15 08:45 | 54.8167 | 61.7037 | 75.3333 | 80.3333
2015-06-15 09:00 | 55.0667 | 62.35 | 76.2333 | 81.35
2015-06-15 09:15 | 55.3167 | 63.1 | 76.7333 | 82.1
2015-06-15 09:30 | 55.5667 | 63.85 | 77.2333 | 82.85
2015-06-15 09:45 | 55.8167 | 64.6 | 77.7333 | 83.6
2015-06-15 10:00 | 56.1333 | 65.2333 | 78.2333 | 84.5833
2015-06-15 10:15 | 56.6333 | 65.7333 | 78.7333 | 85.8333
2015-06-15 10:30 | 57.1333 | 66.2333 | 79.2333 | 87.0833
2015-06-15 10:45 | 57.6333 | 66.7333 | 79.7333 | 88.3333
2015-06-15 11:00 | 58.0667 | 67.1167 | 80.35 | 89.2333
2015-06-15 11:15 | 58.3167 | 67.3667 | 81.1 | 89.7333
2015-06-15 11:30 | 58.5667 | 67.6167 | 81.85 | 90.2333
2015-06-15 11:45 | 58.8167 | 67.8667 | 82.6 | 90.7333
2015-06-15 12:00 | 59 | 67.8833 | 83.35 | 91.35
2015-06-15 12:15 | 59 | 67.6333 | 84.1 | 92.1
2015-06-15 12:30 | 59 | 67.3833 | 84.85 | 92.85
2015-06-15 12:45 | 59 | 67.1333 | 85.6 | 93.6
2015-06-15 13:00 | 58.9333 | 67.1167 | 86 | 94.35
2015-06-15 13:15 | 58.6833 | 67.3667 | 86 | 95.1
2015-06-15 13:30 | 58.4333 | 67.6167 | 86 | 95.85
2015-06-15 13:45 | 58.1833 | 67.8667 | 86 | 96.6
2015-06-15 14:00 | 58 | 67.8833 | 86 | 97.2333
2015-06-15 14:15 | 58 | 67.6333 | 86 | 97.7333
2015-06-15 14:30 | 58 | 67.3833 | 86 | 98.2333
2015-06-15 14:45 | 58 | 67.1333 | 86 | 98.7333
2015-06-15 15:00 | 58.0667 | 66.8833 | 85.8833 | 98.8833
2015-06-15 15:15 | 58.3167 | 66.6333 | 85.6333 | 98.6333
2015-06-15 15:30 | 58.5667 | 66.3833 | 85.3833 | 98.3833
2015-06-15 15:45 | 58.8167 | 66.1333 | 85.1333 | 98.1333
2015-06-15 16:00 | 59 | 66 | 85 | 97.8833
2015-06-15 16:15 | 59 | 66 | 85 | 97.6333
2015-06-15 16:30 | 59 | 66 | 85 | 97.3833
2015-06-15 16:45 | 59 | 66 | 85 | 97.1333
2015-06-15 17:00 | 58.8667 | 65.7667 | 84.8833 | 96.7667
2015-06-15 17:15 | 58.3667 | 65.2667 | 84.6333 | 96.2667
2015-06-15 17:30 | 57.8667 | 64.7667 | 84.3833 | 95.7667
2015-06-15 17:45 | 57.3667 | 64.2667 | 84.1333 | 95.2667
2015-06-15 18:00 | 56.9333 | 63.5333 | 83.7667 | 94.5333
2015-06-15 18:15 | 56.6833 | 62.5333 | 83.2667 | 93.5333
2015-06-15 18:30 | 56.4333 | 61.5333 | 82.7667 | 92.5333
2015-06-15 18:45 | 56.1833 | 60.5333 | 82.2667 | 91.5333
2015-06-15 19:00 | 56 | 59.7667 | 81.5333 | 90.4167
2015-06-15 19:15 | 56 | 59.2667 | 80.5333 | 89.1667
2015-06-15 19:30 | 56 | 58.7667 | 79.5333 | 87.9167
2015-06-15 19:45 | 56 | 58.2667 | 78.5333 | 86.6667
2015-06-15 20:00 | 56 | 57.8833 | 77.7667 | 85.65
2015-06-15 20:15 | 56 | 57.6333 | 77.2667 | 84.9
2015-06-15 20:30 | 56 | 57.3833 | 76.7667 | 84.15
2015-06-15 20:45 | 56 | 57.1333 | 76.2667 | 83.4
2015-06-15 21:00 | 55.9333 | 56.8833 | 75.7667 | 82.4167
2015-06-15 21:15 | 55.6833 | 56.6333 | 75.2667 | 81.1667
2015-06-15 21:30 | 55.4333 | 56.3833 | 74.7667 | 79.9167
2015-06-15 21:45 | 55.1833 | 56.1333 | 74.2667 | 78.6667
2015-06-15 22:00 | 55 | 56 | 73.5333 | 77.65
2015-06-15 22:15 | 55 | 56 | 72.5333 | 76.9
2015-06-15 22:30 | 55 | 56 | 71.5333 | 76.15
2015-06-15 22:45 | 55 | 56 | 70.5333 | 75.4
2015-06-15 23:00 | 55 | 55.8833 | 69.7667 | 74.7667
2015-06-15 23:15 | 55 | 55.6333 | 69.2667 | 74.2667
2015-06-15 23:30 | 55 | 55.3833 | 68.7667 | 73.7667
2015-06-15 23:45 | 55 | 55.1333 | 68.2667 | 73.2667
2015-06-16 | 54.931 | 54.8833 | 68 | 72.65
2015-06-16 00:15 | 54.6724 | 54.6333 | 68 | 71.9
2015-06-16 00:30 | 54.4138 | 54.3833 | 68 | 71.15
2015-06-16 00:45 | 54.1552 | 54.1333 | 68 | 70.4
2015-06-16 01:00 | 54 | 54.1167 | 68 | 69.7667
2015-06-16 01:15 | 54 | 54.3667 | 68 | 69.2667
2015-06-16 01:30 | 54 | 54.6167 | 68 | 68.7667
2015-06-16 01:45 | 54 | 54.8667 | 68 | 68.2667
2015-06-16 02:00 | 54 | 54.8833 | 67.65 | 67.7667
2015-06-16 02:15 | 54 | 54.6333 | 66.9 | 67.2667
2015-06-16 02:30 | 54 | 54.3833 | 66.15 | 66.7667
2015-06-16 02:45 | 54 | 54.1333 | 65.4 | 66.2667
2015-06-16 03:00 | 54 | 54 | 65.1167 | 65.8833
2015-06-16 03:15 | 54 | 54 | 65.3667 | 65.6333
2015-06-16 03:30 | 54 | 54 | 65.6167 | 65.3833
2015-06-16 03:45 | 54 | 54 | 65.8667 | 65.1333
2015-06-16 04:00 | 54 | 54.1489 | 65.8833 | 64.65
2015-06-16 04:15 | 54 | 54.4681 | 65.6333 | 63.9
2015-06-16 04:30 | 54 | 54.7872 | 65.3833 | 63.15
2015-06-16 04:45 | 54 | 54.2308 | 65.1333 | 62.4
2015-06-16 05:00 | 54 | 53.1167 | 65 | 62.2333
2015-06-16 05:15 | 54 | 53.3667 | 65 | 62.7333
2015-06-16 05:30 | 54 | 53.6167 | 65 | 63.2333
2015-06-16 05:45 | 54 | 53.8667 | 65 | 63.7333
2015-06-16 06:00 | 54.0667 | 54.35 | 65.0816 | 64.35
2015-06-16 06:15 | 54.3167 | 55.1 | 65.3878 | 65.1
2015-06-16 06:30 | 54.5667 | 55.85 | 65.6939 | 65.85
2015-06-16 06:45 | 54.8167 | 56.6 | 66 | 66.6
2015-06-16 07:00 | 55.0667 | 57 | 66.4242 | 67.7
2015-06-16 07:15 | 55.3167 | 57 | 67.3333 | 69.2
2015-06-16 07:30 | 55.5667 | 57 | 68 | 70.7
2015-06-16 07:45 | 55.8167 | 58.9565 | 68 | 72.2
2015-06-16 08:00 | 55.0877 | 60.35 | 68.35 | 73.5833
2015-06-16 08:15 | 56.4035 | 61.1 | 69.1 | 74.8333
2015-06-16 08:30 | 57.7193 | 61.85 | 69.85 | 76.0833
2015-06-16 08:45 | 59.0351 | 62.6 | 70 | 77.3333
2015-06-16 09:00 | 60.2 | 63.35 | 71 | 78.5833
2015-06-16 09:15 | 60.95 | 64.1 | 71 | 79.8333
2015-06-16 09:30 | 61.7 | 64.85 | 71.1786 | 81.0833
2015-06-16 09:45 | 62.45 | 65.6 | 71.7143 | 82.3333
2015-06-16 10:00 | 63.0667 | 66.5833 | 72.5833 | 83.35
2015-06-16 10:15 | 63.3167 | 67.8333 | 73.8333 | 84.1
2015-06-16 10:30 | 63.5667 | 69.0833 | 74.7222 | 84.85
2015-06-16 10:45 | 63.8167 | 70.3333 | 75.5556 | 85.6
2015-06-16 11:00 | 63.9333 | 71.2333 | 75.6216 | 86.4667
2015-06-16 11:15 | 63.6833 | 71.7333 | 74.8108 | 87.4667
2015-06-16 11:30 | 63.4333 | 72.2333 | 74 | 88.4667
2015-06-16 11:45 | 63.1833 | 72.7333 | 73.25 | 89.4667
2015-06-16 12:00 | 63.0667 | 73 | 73.2333 | 90.2333
2015-06-16 12:15 | 63.3167 | 73 | 73.7333 | 90.7333
2015-06-16 12:30 | 63.5667 | 73 | 74.2333 | 91.2333
2015-06-16 12:45 | 63.8167 | 73 | 74.7333 | 91.7333
2015-06-16 13:00 | 64 | 73 | 75.4667 | 92.2333
2015-06-16 13:15 | 64 | 73 | 76.4667 | 92.7333
2015-06-16 13:30 | 64 | 73 | 77.4667 | 93.2333
2015-06-16 13:45 | 64 | 73 | 78.4667 | 93.7333
2015-06-16 14:00 | 63.9333 | 73.2333 | 79.35 | 94.35
2015-06-16 14:15 | 63.6833 | 73.7333 | 80.1 | 95.1
2015-06-16 14:30 | 63.4333 | 74.2333 | 80.85 | 95.85
2015-06-16 14:45 | 63.1833 | 74.7333 | 81.6 | 96.6
2015-06-16 15:00 | 63 | 74.65 | 82.1167 | 96.8833
2015-06-16 15:15 | 63 | 73.9 | 82.3667 | 96.6333
2015-06-16 15:30 | 63 | 73.15 | 82.6167 | 96.3833
2015-06-16 15:45 | 63 | 72.4 | 82.8667 | 96.1333
2015-06-16 16:00 | 62.9333 | 72 | 82.8833 | 96.1167
2015-06-16 16:15 | 62.6833 | 72 | 82.6333 | 96.3667
2015-06-16 16:30 | 62.4333 | 72 | 82.3833 | 96.6167
2015-06-16 16:45 | 62.1833 | 72 | 82.1333 | 96.8667
2015-06-16 17:00 | 61.8 | 71.65 | 82.1167 | 96.7667
2015-06-16 17:15 | 61.05 | 70.9 | 82.3667 | 96.2667
2015-06-16 17:30 | 60.3 | 70.15 | 82.6167 | 95.7667
2015-06-16 17:45 | 59.55 | 69.4 | 82.8667 | 95.2667
2015-06-16 18:00 | 58.7949 | 68.7667 | 82.7667 | 94.65
2015-06-16 18:15 | 58.0256 | 68.2667 | 82.2667 | 93.9
2015-06-16 18:30 | 57.2564 | 67.7667 | 81.7667 | 93.15
2015-06-16 18:45 | 57 | 67.2667 | 81.2667 | 92.4
2015-06-16 19:00 | 56.8667 | 66.4167 | 80.65 | 91.3
2015-06-16 19:15 | 56.3667 | 65.1667 | 79.9 | 89.8
2015-06-16 19:30 | 55.8667 | 63.9167 | 79.15 | 88.3
2015-06-16 19:45 | 55.3667 | 62.6667 | 78.4 | 86.8
2015-06-16 20:00 | 54.9333 | 61.65 | 77.5333 | 85.8833
2015-06-16 20:15 | 54.6833 | 60.9 | 76.5333 | 85.6333
2015-06-16 20:30 | 54.4333 | 60.15 | 75.5333 | 85.3833
2015-06-16 20:45 | 54.1833 | 59.4 | 74.5333 | 85.1333
2015-06-16 21:00 | 54 | 58.7667 | 73.8833 | 84.65
2015-06-16 21:15 | 54 | 58.2667 | 73.6333 | 83.9
2015-06-16 21:30 | 54 | 57.7667 | 73.3833 | 83.15
2015-06-16 21:45 | 54 | 57.2667 | 73.1333 | 82.4
2015-06-16 22:00 | 54 | 57 | 72.8833 | 81.5333
2015-06-16 22:15 | 54 | 57 | 72.6333 | 80.5333
2015-06-16 22:30 | 54 | 57 | 72.3833 | 79.5333
2015-06-16 22:45 | 54 | 57 | 72.1333 | 78.5333
2015-06-16 23:00 | 53.9333 | 57 | 71.8833 | 77.8833
2015-06-16 23:15 | 53.6833 | 57 | 71.6333 | 77.6333
2015-06-16 23:30 | 53.4333 | 57 | 71.3833 | 77.3833
2015-06-16 23:45 | 53.1833 | 57 | 71.1333 | 77.1333
2015-06-17 | 53 | 56.7667 | 70.7667 | 76.7667
2015-06-17 00:15 | 53 | 56.2667 | 70.2667 | 76.2667
2015-06-17 00:30 | 53 | 55.7667 | 69.7667 | 75.7667
2015-06-17 00:45 | 53 | 55.2667 | 69.2667 | 75.2667
2015-06-17 01:00 | 53 | 55.1167 | 68.7667 | 74.65
2015-06-17 01:15 | 53 | 55.3667 | 68.2667 | 73.9
2015-06-17 01:30 | 53 | 55.6167 | 67.7667 | 73.15
2015-06-17 01:45 | 53 | 55.8667 | 67.2667 | 72.4
2015-06-17 02:00 | 52.9333 | 55.8833 | 66.8833 | 71.8833
2015-06-17 02:15 | 52.6833 | 55.6333 | 66.6333 | 71.6333
2015-06-17 02:30 | 52.4333 | 55.3833 | 66.3833 | 71.3833
2015-06-17 02:45 | 52.1833 | 55.1333 | 66.1333 | 71.1333
2015-06-17 03:00 | 52.0667 | 54.7667 | 66 | 70.7667
2015-06-17 03:15 | 52.3167 | 54.2667 | 66 | 70.2667
2015-06-17 03:30 | 52.5667 | 53.7667 | 66 | 69.7667
2015-06-17 03:45 | 52.8167 | 53.2667 | 66 | 69.2667
2015-06-17 04:00 | 53 | 53.1707 | 66 | 68.8833
2015-06-17 04:15 | 53 | 53.5366 | 66 | 68.6333
2015-06-17 04:30 | 53 | 53.9024 | 66 | 68.3833
2015-06-17 04:45 | 53 | 54.5789 | 66 | 68.1333
2015-06-17 05:00 | 53.0667 | 55 | 65.0667 | 68.35
2015-06-17 05:15 | 53.3167 | 55.0256 | 63.625 | 69.1
2015-06-17 05:30 | 53.5667 | 55.4103 | 64 | 69.85
2015-06-17 05:45 | 53.8167 | 55.7949 | 65 | 70.6
2015-06-17 06:00 | 54.069 | 56.25 | 65 | 71.5833
2015-06-17 06:15 | 54.3276 | 56.7857 | 65.2222 | 72.8333
2015-06-17 06:30 | 54.5862 | 57.2812 | 66 | 74.0833
2015-06-17 06:45 | 54.8448 | 57.75 | 66.3846 | 75.3333
2015-06-17 07:00 | 55.25 | 58.35 | 67.4667 | 76.35
2015-06-17 07:15 | 56.1875 | 59.1 | 68.4667 | 77.1
2015-06-17 07:30 | 57.0714 | 59.85 | 69.4667 | 77.85
2015-06-17 07:45 | 57.6071 | 60.6 | 70.4667 | 78.6
2015-06-17 08:00 | 58.1333 | 61.4667 | 71.35 | 79.5833
2015-06-17 08:15 | 58.6333 | 62.4667 | 72.1 | 80.8333
2015-06-17 08:30 | 59.1333 | 63.4667 | 72.85 | 82.0833
2015-06-17 08:45 | 59.6333 | 64.4667 | 73.6 | 83.3333
2015-06-17 09:00 | 60.2 | 65.4667 | 74 | 84.35
2015-06-17 09:15 | 60.95 | 66.4667 | 74.383 | 85.1
2015-06-17 09:30 | 61.7 | 67.4667 | 75.0213 | 85.85
2015-06-17 09:45 | 62.45 | 68.4667 | 75.6596 | 86.6
2015-06-17 10:00 | 63.1333 | 69.5833 | 76.3043 | 87.5833
2015-06-17 10:15 | 63.6333 | 70.8333 | 76.9565 | 88.8333
2015-06-17 10:30 | 64.1333 | 72.0833 | 77.6087 | 90.0833
2015-06-17 10:45 | 64.6333 | 73.3333 | 78.8571 | 91.3333
2015-06-17 11:00 | 65.069 | 74.35 | 80.1167 | 92.2333
2015-06-17 11:15 | 65.3276 | 75.1 | 80.3667 | 92.7333
2015-06-17 11:30 | 65.5862 | 75.85 | 80.6167 | 93.2333
2015-06-17 11:45 | 65.8448 | 76.6 | 80.8667 | 93.7333
2015-06-17 12:00 | 65.9333 | 77.1167 | 81.2333 | 94.35
2015-06-17 12:15 | 65.6833 | 77.3667 | 81.7333 | 95.1
2015-06-17 12:30 | 65.4333 | 77.6167 | 82.2333 | 95.85
2015-06-17 12:45 | 65.1833 | 77.8667 | 82.7333 | 96.6
2015-06-17 13:00 | 64.5 | 77.8833 | 83.1167 | 97.1167
2015-06-17 13:15 | 64 | 77.6333 | 83.3667 | 97.3667
2015-06-17 13:30 | 64 | 77.3833 | 83.6167 | 97.6167
2015-06-17 13:45 | 64 | 77.1333 | 83.8667 | 97.8667
2015-06-17 14:00 | 63.8667 | 77.2333 | 84.2333 | 98.2333
2015-06-17 14:15 | 63.3667 | 77.7333 | 84.7333 | 98.7333
2015-06-17 14:30 | 62.8667 | 78.2333 | 85.2333 | 99.2333
2015-06-17 14:45 | 62.3667 | 78.7333 | 85.7333 | 99.7333
2015-06-17 15:00 | 62 | 78.5333 | 86.1167 | 100.1167
2015-06-17 15:15 | 62 | 77.5333 | 86.3667 | 100.3667
2015-06-17 15:30 | 62 | 76.5333 | 86.6167 | 100.6167
2015-06-17 15:45 | 62 | 75.5333 | 86.8667 | 100.8667
2015-06-17 16:00 | 61.8667 | 74.8833 | 87.1167 | 101.1167
2015-06-17 16:15 | 61.3667 | 74.6333 | 87.3667 | 101.3667
2015-06-17 16:30 | 60.8667 | 74.3833 | 87.6167 | 101.6167
2015-06-17 16:45 | 60.3667 | 74.1333 | 87.8667 | 101.8667
2015-06-17 17:00 | 59.8667 | 73.65 | 87.8833 | 101.65
2015-06-17 17:15 | 59.3667 | 72.9 | 87.6333 | 100.9
2015-06-17 17:30 | 58.8667 | 72.15 | 87.3833 | 100.15
2015-06-17 17:45 | 58.3667 | 71.4 | 87.1333 | 99.4
2015-06-17 18:00 | 57.9333 | 70.5333 | 87 | 98.5333
2015-06-17 18:15 | 57.6833 | 69.5333 | 87 | 97.5333
2015-06-17 18:30 | 57.4333 | 68.5333 | 87 | 96.5333
2015-06-17 18:45 | 57.1833 | 67.5333 | 87 | 95.5333
2015-06-17 19:00 | 56.9333 | 66.5333 | 86.5333 | 94.4167
2015-06-17 19:15 | 56.6833 | 65.5333 | 85.5333 | 93.1667
2015-06-17 19:30 | 56.4333 | 64.5333 | 84.5333 | 91.9167
2015-06-17 19:45 | 56.1833 | 63.5333 | 83.5333 | 90.6667
2015-06-17 20:00 | 56 | 62.65 | 82.4167 | 89.7667
2015-06-17 20:15 | 56 | 61.9 | 81.1667 | 89.2667
2015-06-17 20:30 | 56 | 61.15 | 79.9167 | 88.7667
2015-06-17 20:45 | 56 | 60.4 | 78.6667 | 88.2667
2015-06-17 21:00 | 56 | 60 | 78 | 87.5333
2015-06-17 21:15 | 56 | 60 | 78 | 86.5333
2015-06-17 21:30 | 56 | 60 | 78 | 85.5333
2015-06-17 21:45 | 56 | 60 | 78 | 84.5333
2015-06-17 22:00 | 55.9333 | 59.7667 | 77.65 | 83.65
2015-06-17 22:15 | 55.6833 | 59.2667 | 76.9 | 82.9
2015-06-17 22:30 | 55.4333 | 58.7667 | 76.15 | 82.15
2015-06-17 22:45 | 55.1833 | 58.2667 | 75.4 | 81.4
2015-06-17 23:00 | 54.9333 | 57.7667 | 75 | 80.8833
2015-06-17 23:15 | 54.6833 | 57.2667 | 75 | 80.6333
2015-06-17 23:30 | 54.4333 | 56.7667 | 75 | 80.3833
2015-06-17 23:45 | 54.1833 | 56.2667 | 75 | 80.1333
2015-06-18 | 54 | 56.1167 | 74.7667 | 79.4167
2015-06-18 00:15 | 54 | 56.3667 | 74.2667 | 78.1667
2015-06-18 00:30 | 54 | 56.6167 | 73.7667 | 76.9167
2015-06-18 00:45 | 54 | 56.8667 | 73.2667 | 75.6667
2015-06-18 01:00 | 54 | 57.1167 | 72.8833 | 74.65
2015-06-18 01:15 | 54 | 57.3667 | 72.6333 | 73.9
2015-06-18 01:30 | 54 | 57.6167 | 72.3833 | 73.15
2015-06-18 01:45 | 54 | 57.8667 | 72.1333 | 72.4
2015-06-18 02:00 | 54 | 57.65 | 71.7667 | 72.2333
2015-06-18 02:15 | 54 | 56.9 | 71.2667 | 72.7333
2015-06-18 02:30 | 54 | 56.15 | 70.7667 | 73.2333
2015-06-18 02:45 | 54 | 55.4 | 70.2667 | 73.7333
2015-06-18 03:00 | 53.9333 | 55.1167 | 70 | 73.65
2015-06-18 03:15 | 53.6833 | 55.3667 | 70 | 72.9
2015-06-18 03:30 | 53.4333 | 55.6167 | 70 | 72.15
2015-06-18 03:45 | 53.1833 | 55.8667 | 70 | 71.4
2015-06-18 04:00 | 53 | 55.8205 | 69.8833 | 70.8833
2015-06-18 04:15 | 53 | 55.4359 | 69.6333 | 70.6333
2015-06-18 04:30 | 53 | 55.0513 | 69.3833 | 70.3833
2015-06-18 04:45 | 53 | 54.381 | 69.1333 | 70.1333
2015-06-18 05:00 | 53.1333 | 54.35 | 68.8833 | 70.4667
2015-06-18 05:15 | 53.6333 | 55.1 | 68.6333 | 71.4667
2015-06-18 05:30 | 54.1333 | 55.85 | 68.3833 | 72.4667
2015-06-18 05:45 | 54.6333 | 56.6 | 68.1333 | 73.4667
2015-06-18 06:00 | 55.1333 | 57.35 | 68.5833 | 74.4667
2015-06-18 06:15 | 55.6333 | 58.1 | 69.8333 | 75.4667
2015-06-18 06:30 | 56.1333 | 58.85 | 71.0833 | 76.4667
2015-06-18 06:45 | 56.6333 | 59.6 | 72.3333 | 77.4667
2015-06-18 07:00 | 57.1333 | 60.35 | 73.4667 | 78.4667
2015-06-18 07:15 | 57.6333 | 61.1 | 74.4667 | 79.4667
2015-06-18 07:30 | 58.1333 | 61.85 | 75.4667 | 80.4667
2015-06-18 07:45 | 58.6333 | 62.6 | 76.4667 | 81.4667
2015-06-18 08:00 | 59.0667 | 63.5833 | 77.35 | 82.2333
2015-06-18 08:15 | 59.3167 | 64.8333 | 78.1 | 82.7333
2015-06-18 08:30 | 59.5667 | 66.0833 | 78.85 | 83.2333
2015-06-18 08:45 | 59.8167 | 67.3333 | 79.6 | 83.7333
2015-06-18 09:00 | 60.0667 | 68.35 | 80.4667 | 84.5833
2015-06-18 09:15 | 60.3167 | 69.1 | 81.4667 | 85.8333
2015-06-18 09:30 | 60.5667 | 69.85 | 82.4667 | 87.0833
2015-06-18 09:45 | 60.8167 | 70.6 | 83.4667 | 88.3333
2015-06-18 10:00 | 61.1333 | 71.35 | 84.35 | 89.5833
2015-06-18 10:15 | 61.6333 | 72.1 | 85.1 | 90.8333
2015-06-18 10:30 | 62.1333 | 72.85 | 85.85 | 92.0833
2015-06-18 10:45 | 62.6333 | 73.6 | 86.6 | 93.3333
2015-06-18 11:00 | 63.1333 | 73.7667 | 87.35 | 94.2333
2015-06-18 11:15 | 63.6333 | 73.2667 | 88.1 | 94.7333
2015-06-18 11:30 | 64.1333 | 72.7667 | 88.85 | 95.2333
2015-06-18 11:45 | 64.6333 | 72.2667 | 89.6 | 95.7333
2015-06-18 12:00 | 65.0667 | 72.35 | 90.35 | 96.35
2015-06-18 12:15 | 65.3167 | 73.1 | 91.1 | 97.1
2015-06-18 12:30 | 65.5667 | 73.85 | 91.85 | 97.85
2015-06-18 12:45 | 65.8167 | 74.6 | 92.6 | 98.6
2015-06-18 13:00 | 66 | 74.8833 | 93 | 99.1167
2015-06-18 13:15 | 66 | 74.6333 | 93 | 99.3667
2015-06-18 13:30 | 66 | 74.3833 | 93 | 99.6167
2015-06-18 13:45 | 66 | 74.1333 | 93 | 99.8667
2015-06-18 14:00 | 66.0667 | 74 | 93.1167 | 100.1167
2015-06-18 14:15 | 66.3167 | 74 | 93.3667 | 100.3667
2015-06-18 14:30 | 66.5667 | 74 | 93.6167 | 100.6167
2015-06-18 14:45 | 66.8167 | 74 | 93.8667 | 100.8667
2015-06-18 15:00 | 66.9333 | 74 | 93.8372 | 101
2015-06-18 15:15 | 66.6833 | 74 | 93.4884 | 101
2015-06-18 15:30 | 66.4333 | 74 | 93.1395 | 101
2015-06-18 15:45 | 66.1833 | 74 | 92.4706 | 101
2015-06-18 16:00 | 66.0667 | 73.8833 | 91.8833 | 100.7667
2015-06-18 16:15 | 66.3167 | 73.6333 | 91.6333 | 100.2667
2015-06-18 16:30 | 66.5667 | 73.3833 | 91.3833 | 99.7667
2015-06-18 16:45 | 66.8167 | 73.1333 | 91.1333 | 99.2667
2015-06-18 17:00 | 66.8 | 72.7667 | 90.65 | 98.7667
2015-06-18 17:15 | 66.05 | 72.2667 | 89.9 | 98.2667
2015-06-18 17:30 | 65.3 | 71.7667 | 89.15 | 97.7667
2015-06-18 17:45 | 64.55 | 71.2667 | 88.4 | 97.2667
2015-06-18 18:00 | 63.8 | 70.7667 | 87.7667 | 96.4167
2015-06-18 18:15 | 63.05 | 70.2667 | 87.2667 | 95.1667
2015-06-18 18:30 | 62.3 | 69.7667 | 86.7667 | 93.9167
2015-06-18 18:45 | 61.55 | 69.2667 | 86.2667 | 92.6667
2015-06-18 19:00 | 60.8 | 68.4167 | 85.7667 | 91.4167
2015-06-18 19:15 | 60.05 | 67.1667 | 85.2667 | 90.1667
2015-06-18 19:30 | 59.3 | 65.9167 | 84.7667 | 88.9167
2015-06-18 19:45 | 58.55 | 64.6667 | 84.2667 | 87.6667
2015-06-18 20:00 | 58 | 63.7667 | 83.7667 | 86.5333
2015-06-18 20:15 | 58 | 63.2667 | 83.2667 | 85.5333
2015-06-18 20:30 | 58 | 62.7667 | 82.7667 | 84.5333
2015-06-18 20:45 | 58 | 62.2667 | 82.2667 | 83.5333
2015-06-18 21:00 | 57.8667 | 61.65 | 81.7667 | 82.4167
2015-06-18 21:15 | 57.3667 | 60.9 | 81.2667 | 81.1667
2015-06-18 21:30 | 56.8667 | 60.15 | 80.7667 | 79.9167
2015-06-18 21:45 | 56.3667 | 59.4 | 80.2667 | 78.6667
2015-06-18 22:00 | 56 | 59 | 79.65 | 77.8833
2015-06-18 22:15 | 56 | 59 | 78.9 | 77.6333
2015-06-18 22:30 | 56 | 59 | 78.15 | 77.3833
2015-06-18 22:45 | 56 | 59 | 77.4 | 77.1333
2015-06-18 23:00 | 55.8667 | 58.7667 | 76.7667 | 76.65
2015-06-18 23:15 | 55.3667 | 58.2667 | 76.2667 | 75.9
2015-06-18 23:30 | 54.8667 | 57.7667 | 75.7667 | 75.15
2015-06-18 23:45 | 54.3667 | 57.2667 | 75.2667 | 74.4
2015-06-19 | 53.9333 | 56.8833 | 74.7667 | 73.65
2015-06-19 00:15 | 53.6833 | 56.6333 | 74.2667 | 72.9
2015-06-19 00:30 | 53.4333 | 56.3833 | 73.7667 | 72.15
2015-06-19 00:45 | 53.1833 | 56.1333 | 73.2667 | 71.4
2015-06-19 01:00 | 53 | 56 | 72.8833 | 70.7667
2015-06-19 01:15 | 53 | 56 | 72.6333 | 70.2667
2015-06-19 01:30 | 53 | 56 | 72.3833 | 69.7667
2015-06-19 01:45 | 53 | 56 | 72.1333 | 69.2667
2015-06-19 02:00 | 52.9333 | 55.8833 | 71.7667 | 69
2015-06-19 02:15 | 52.6833 | 55.6333 | 71.2667 | 69
2015-06-19 02:30 | 52.4333 | 55.3833 | 70.7667 | 69
2015-06-19 02:45 | 52.1833 | 55.1333 | 70.2667 | 69
2015-06-19 03:00 | 52 | 55 | 69.8833 | 68.7667
2015-06-19 03:15 | 52 | 55 | 69.6333 | 68.2667
2015-06-19 03:30 | 51.8387 | 55 | 69.3833 | 67.7667
2015-06-19 03:45 | 51.3548 | 55 | 69.1333 | 67.2667
2015-06-19 04:00 | 51 | 54.8293 | 68.7667 | 66.7667
2015-06-19 04:15 | 51 | 54.4634 | 68.2667 | 66.2667
2015-06-19 04:30 | 51 | 54.0976 | 67.7667 | 65.7667
2015-06-19 04:45 | 51 | 54 | 67.2667 | 65.2667
2015-06-19 05:00 | 51.2 | 54.1167 | 67 | 65
2015-06-19 05:15 | 51.95 | 54.3667 | 67 | 65
2015-06-19 05:30 | 52.7 | 54.6167 | 67 | 65
2015-06-19 05:45 | 53.45 | 54.8667 | 67 | 65
2015-06-19 06:00 | 54.1333 | 55.2333 | 67.3684 | 65.4667
2015-06-19 06:15 | 54.6333 | 55.7333 | 68.1579 | 66.4667
2015-06-19 06:30 | 55.1333 | 56.2333 | 68.9474 | 67.4667
2015-06-19 06:45 | 55.6333 | 56.7333 | 69.7368 | 68.4667
2015-06-19 07:00 | 56.2 | 57.4667 | 70.35 | 69.5833
2015-06-19 07:15 | 56.95 | 58.4667 | 71.1 | 70.8333
2015-06-19 07:30 | 57.7 | 59.4667 | 71.85 | 72.0833
2015-06-19 07:45 | 58.45 | 60.4667 | 72.6 | 73.3333
2015-06-19 08:00 | 59.1333 | 61.35 | 73.4667 | 74.7
2015-06-19 08:15 | 59.6333 | 62.1 | 74.4667 | 76.2
2015-06-19 08:30 | 60.1333 | 62.85 | 75.4667 | 77.7
2015-06-19 08:45 | 60.6333 | 63.6 | 76.4667 | 79.2
2015-06-19 09:00 | 61.1333 | 64.7 | 77.35 | 80.4667
2015-06-19 09:15 | 61.6333 | 66.2 | 78.1 | 81.4667
2015-06-19 09:30 | 62.1333 | 67.7 | 78.85 | 82.4667
2015-06-19 09:45 | 62.6333 | 69.2 | 79.6 | 83.4667
2015-06-19 10:00 | 63.1333 | 70.4667 | 80.35 | 84.4667
2015-06-19 10:15 | 63.6333 | 71.4667 | 81.1 | 85.4667
2015-06-19 10:30 | 64.1333 | 72.4667 | 81.85 | 86.4667
2015-06-19 10:45 | 64.6333 | 73.4667 | 82.6 | 87.4667
2015-06-19 11:00 | 65.0667 | 74.4667 | 83.2333 | 88.35
2015-06-19 11:15 | 65.3167 | 75.4667 | 83.7333 | 89.1
2015-06-19 11:30 | 65.5667 | 76.4667 | 84.2333 | 89.85
2015-06-19 11:45 | 65.8167 | 77.4667 | 84.7333 | 90.6
2015-06-19 12:00 | 66 | 78 | 85.1167 | 91.35
2015-06-19 12:15 | 66 | 78 | 85.3667 | 92.1
2015-06-19 12:30 | 66 | 78 | 85.6167 | 92.85
2015-06-19 12:45 | 66 | 78 | 85.8667 | 93.6
2015-06-19 13:00 | 66.0667 | 78.1167 | 86.2333 | 94.2333
2015-06-19 13:15 | 66.3167 | 78.3667 | 86.7333 | 94.7333
2015-06-19 13:30 | 66.5667 | 78.6167 | 87.2333 | 95.2333
2015-06-19 13:45 | 66.8167 | 78.8667 | 87.7333 | 95.7333
2015-06-19 14:00 | 66.9333 | 79 | 88.1167 | 96.1167
2015-06-19 14:15 | 66.6833 | 79 | 88.3667 | 96.3667
2015-06-19 14:30 | 66.4333 | 79 | 88.6167 | 96.6167
2015-06-19 14:45 | 66.1833 | 79 | 88.8667 | 96.8667
2015-06-19 15:00 | 66.0667 | 79 | 89 | 97.1167
2015-06-19 15:15 | 66.3167 | 79 | 89 | 97.3667
2015-06-19 15:30 | 66.5667 | 79 | 89 | 97.6167
2015-06-19 15:45 | 66.8167 | 79 | 89 | 97.8667
2015-06-19 16:00 | 66.8667 | 78.7667 | 88.8833 | 97.8833
2015-06-19 16:15 | 66.3667 | 78.2667 | 88.6333 | 97.6333
2015-06-19 16:30 | 65.8667 | 77.7667 | 88.3833 | 97.3833
2015-06-19 16:45 | 65.3667 | 77.2667 | 88.1333 | 97.1333
2015-06-19 17:00 | 64.8 | 76.4167 | 87.8833 | 96.7667
2015-06-19 17:15 | 64.05 | 75.1667 | 87.6333 | 96.2667
2015-06-19 17:30 | 63.3 | 73.9167 | 87.3833 | 95.7667
2015-06-19 17:45 | 62.55 | 72.6667 | 87.1333 | 95.2667
2015-06-19 18:00 | 61.8667 | 71.5333 | 86.5333 | 94.5333
2015-06-19 18:15 | 61.3667 | 70.5333 | 85.5333 | 93.5333
2015-06-19 18:30 | 60.8667 | 69.5333 | 84.5333 | 92.5333
2015-06-19 18:45 | 60.3667 | 68.5333 | 83.5333 | 91.5333
2015-06-19 19:00 | 59.8 | 67.5333 | 82.5333 | 90.5333
2015-06-19 19:15 | 59.05 | 66.5333 | 81.5333 | 89.5333
2015-06-19 19:30 | 58.3 | 65.5333 | 80.5333 | 88.5333
2015-06-19 19:45 | 57.55 | 64.5333 | 79.5333 | 87.5333
2015-06-19 20:00 | 57 | 63.65 | 78.65 | 86.5333
2015-06-19 20:15 | 57 | 62.9 | 77.9 | 85.5333
2015-06-19 20:30 | 57 | 62.15 | 77.15 | 84.5333
2015-06-19 20:45 | 57 | 61.4 | 76.4 | 83.5333
2015-06-19 21:00 | 57 | 60.8833 | 75.7667 | 82.65
2015-06-19 21:15 | 57 | 60.6333 | 75.2667 | 81.9
2015-06-19 21:30 | 57 | 60.3833 | 74.7667 | 81.15
2015-06-19 21:45 | 57 | 60.1333 | 74.2667 | 80.4
2015-06-19 22:00 | 56.9333 | 59.8833 | 73.7667 | 79.7667
2015-06-19 22:15 | 56.6833 | 59.6333 | 73.2667 | 79.2667
2015-06-19 22:30 | 56.4333 | 59.3833 | 72.7667 | 78.7667
2015-06-19 22:45 | 56.1833 | 59.1333 | 72.2667 | 78.2667
2015-06-19 23:00 | 55.9333 | 58.8833 | 71.8833 | 77.7667
2015-06-19 23:15 | 55.6833 | 58.6333 | 71.6333 | 77.2667
2015-06-19 23:30 | 55.4333 | 58.3833 | 71.3833 | 76.7667
2015-06-19 23:45 | 55.1833 | 58.1333 | 71.1333 | 76.2667
2015-06-20 | 54.9333 | 58.1167 | 70.7667 | 75.5333
2015-06-20 00:15 | 54.6833 | 58.3667 | 70.2667 | 74.5333
2015-06-20 00:30 | 54.4333 | 58.6167 | 69.7667 | 73.5333
2015-06-20 00:45 | 54.1833 | 58.8667 | 69.2667 | 72.5333
2015-06-20 01:00 | 54 | 59 | 68.8833 | 71.7667
2015-06-20 01:15 | 54 | 59 | 68.6333 | 71.2667
2015-06-20 01:30 | 54 | 59 | 68.3833 | 70.7667
2015-06-20 01:45 | 54 | 59 | 68.1333 | 70.2667
2015-06-20 02:00 | 53.9333 | 59 | 68 | 69.8833
2015-06-20 02:15 | 53.6833 | 59 | 68 | 69.6333
2015-06-20 02:30 | 53.4333 | 59 | 68 | 69.3833
2015-06-20 02:45 | 53.1833 | 59 | 68 | 69.1333
2015-06-20 03:00 | 53 | 58.7667 | 67.8833 | 68.8833
2015-06-20 03:15 | 53 | 58.2667 | 67.6333 | 68.6333
2015-06-20 03:30 | 53 | 57.7667 | 67.3833 | 68.3833
2015-06-20 03:45 | 53 | 57.2667 | 67.1333 | 68.1333
2015-06-20 04:00 | 53 | 56.8833 | 67 | 67.7667
2015-06-20 04:15 | 53 | 56.6333 | 67 | 67.2667
2015-06-20 04:30 | 53 | 56.3833 | 67 | 66.7667
2015-06-20 04:45 | 53 | 56.1333 | 67 | 66.2667
2015-06-20 05:00 | 53 | 56.1167 | 66.7667 | 66.35
2015-06-20 05:15 | 53 | 56.3667 | 66.2667 | 67.1
2015-06-20 05:30 | 53 | 56.6167 | 65.7667 | 67.85
2015-06-20 05:45 | 53 | 56.8667 | 65.2667 | 68.6
2015-06-20 06:00 | 53.2 | 57.4667 | 65.35 | 69.8167
2015-06-20 06:15 | 53.95 | 58.4667 | 66.1 | 71.5667
2015-06-20 06:30 | 54.7 | 59.4667 | 66.85 | 73.3167
2015-06-20 06:45 | 55.45 | 60.4667 | 67.6 | 75.0667
2015-06-20 07:00 | 56.0667 | 61.35 | 68.7 | 76.5833
2015-06-20 07:15 | 56.3167 | 62.1 | 70.2 | 77.8333
2015-06-20 07:30 | 56.5667 | 62.85 | 71.7 | 79.0833
2015-06-20 07:45 | 56.8167 | 63.6 | 73.2 | 80.3333
2015-06-20 08:00 | 57.2667 | 64.4667 | 74.5833 | 81.2333
2015-06-20 08:15 | 58.2667 | 65.4667 | 75.8333 | 81.7333
2015-06-20 08:30 | 59.2667 | 66.4667 | 77.0833 | 82.2333
2015-06-20 08:45 | 60.2667 | 67.4667 | 78.3333 | 82.7333
2015-06-20 09:00 | 61.0667 | 68.2333 | 79.4667 | 83.5833
2015-06-20 09:15 | 61.3167 | 68.7333 | 80.4667 | 84.8333
2015-06-20 09:30 | 61.5667 | 69.2333 | 81.4667 | 86.0833
2015-06-20 09:45 | 61.8167 | 69.7333 | 82.4667 | 87.3333
2015-06-20 10:00 | 62.2667 | 70.2333 | 83.1167 | 88.4667
2015-06-20 10:15 | 63.2667 | 70.7333 | 83.3667 | 89.4667
2015-06-20 10:30 | 64.2667 | 71.2333 | 83.6167 | 90.4667
2015-06-20 10:45 | 65.2667 | 71.7333 | 83.8667 | 91.4667
2015-06-20 11:00 | 66.1333 | 72.4667 | 84.4667 | 92.35
2015-06-20 11:15 | 66.6333 | 73.4667 | 85.4667 | 93.1
2015-06-20 11:30 | 67.1333 | 74.4667 | 86.4667 | 93.85
2015-06-20 11:45 | 67.6333 | 75.4667 | 87.4667 | 94.6
2015-06-20 12:00 | 68 | 76.2333 | 88 | 95.2333
2015-06-20 12:15 | 68 | 76.7333 | 88 | 95.7333
2015-06-20 12:30 | 68 | 77.2333 | 88 | 96.2333
2015-06-20 12:45 | 68 | 77.7333 | 88 | 96.7333
2015-06-20 13:00 | 68 | 78.1167 | 88.4667 | 97.2333
2015-06-20 13:15 | 68 | 78.3667 | 89.4667 | 97.7333
2015-06-20 13:30 | 68 | 78.6167 | 90.4667 | 98.2333
2015-06-20 13:45 | 68 | 78.8667 | 91.4667 | 98.7333
2015-06-20 14:00 | 67.8667 | 78.8833 | 92.1167 | 99.1167
2015-06-20 14:15 | 67.3667 | 78.6333 | 92.3667 | 99.3667
2015-06-20 14:30 | 66.8667 | 78.3833 | 92.6167 | 99.6167
2015-06-20 14:45 | 66.3667 | 78.1333 | 92.8667 | 99.8667
2015-06-20 15:00 | 66.0667 | 77.7667 | 93.2333 | 100
2015-06-20 15:15 | 66.3167 | 77.2667 | 93.7333 | 100
2015-06-20 15:30 | 66.5667 | 76.7667 | 94.2333 | 100
2015-06-20 15:45 | 66.8167 | 76.2667 | 94.7333 | 100
2015-06-20 16:00 | 66.9333 | 76.14 | 94.8108 | 100
2015-06-20 16:15 | 66.6833 | 76.44 | 94.4054 | 100
2015-06-20 16:30 | 66.4333 | 76.74 | 94 | 100
2015-06-20 16:45 | 66.1833 | 77 | 93.3478 | 100
2015-06-20 17:00 | 65.8 | 76.65 | 92.7667 | 99.7667
2015-06-20 17:15 | 65.05 | 75.9 | 92.2667 | 99.2667
2015-06-20 17:30 | 64.3 | 75.15 | 91.7667 | 98.7667
2015-06-20 17:45 | 63.55 | 74.4 | 91.2667 | 98.2667
2015-06-20 18:00 | 62.6 | 73.5333 | 90.5625 | 97.65
2015-06-20 18:15 | 61.1 | 72.5333 | 89.5909 | 96.9
2015-06-20 18:30 | 59.6 | 71.5333 | 88.5682 | 96.15
2015-06-20 18:45 | 58.1 | 70.5333 | 87.5455 | 95.4
2015-06-20 19:00 | 56.8667 | 69.65 | 86.4167 | 94.4167
2015-06-20 19:15 | 56.3667 | 68.9 | 85.1667 | 93.1667
2015-06-20 19:30 | 55.8667 | 68.15 | 83.9167 | 91.9167
2015-06-20 19:45 | 55.3667 | 67.4 | 82.6667 | 90.6667
2015-06-20 20:00 | 55 | 66.7667 | 81.65 | 89.7667
2015-06-20 20:15 | 55 | 66.2667 | 80.9 | 89.2667
2015-06-20 20:30 | 55 | 65.7667 | 80.15 | 88.7667
2015-06-20 20:45 | 55 | 65.2667 | 79.4 | 88.2667
2015-06-20 21:00 | 54.9333 | 64.7667 | 78.7667 | 87.4167
2015-06-20 21:15 | 54.6833 | 64.2667 | 78.2667 | 86.1667
2015-06-20 21:30 | 54.4333 | 63.7667 | 77.7667 | 84.9167
2015-06-20 21:45 | 54.1833 | 63.2667 | 77.2667 | 83.6667
2015-06-20 22:00 | 54.0667 | 62.65 | 76.7667 | 82.65
2015-06-20 22:15 | 54.3167 | 61.9 | 76.2667 | 81.9
2015-06-20 22:30 | 54.5667 | 61.15 | 75.7667 | 81.15
2015-06-20 22:45 | 54.8167 | 60.4 | 75.2667 | 80.4
2015-06-20 23:00 | 55 | 59.8833 | 74.8833 | 79.65
2015-06-20 23:15 | 55 | 59.6333 | 74.6333 | 78.9
2015-06-20 23:30 | 55 | 59.3833 | 74.3833 | 78.15
2015-06-20 23:45 | 55 | 59.1333 | 74.1333 | 77.4
2015-06-21 | 55 | 58.4815 | 73.8833 | 76.8833
2015-06-21 00:15 | 55 | 57.3704 | 73.6333 | 76.6333
2015-06-21 00:30 | 55 | 57.0417 | 73.3833 | 76.3833
2015-06-21 00:45 | 55 | 57.6667 | 73.1333 | 76.1333
2015-06-21 01:00 | 55 | 57.8833 | 73 | 75.65
2015-06-21 01:15 | 55 | 57.6333 | 73 | 74.9
2015-06-21 01:30 | 55 | 57.3833 | 73 | 74.15
2015-06-21 01:45 | 55 | 57.1333 | 73 | 73.4
2015-06-21 02:00 | 55 | 57 | 72.8833 | 72.65
2015-06-21 02:15 | 55 | 57 | 72.6333 | 71.9
2015-06-21 02:30 | 55 | 57 | 72.3833 | 71.15
2015-06-21 02:45 | 55 | 57 | 72.1333 | 70.4
2015-06-21 03:00 | 55 | 57 | 71.8833 | 69.8833
2015-06-21 03:15 | 55 | 57 | 71.6333 | 69.6333
2015-06-21 03:30 | 55 | 57 | 71.3833 | 69.3833
2015-06-21 03:45 | 55 | 57 | 71.1333 | 69.1333
2015-06-21 04:00 | 55 | 57 | 71 | 69.1167
2015-06-21 04:15 | 55 | 57 | 71 | 69.3667
2015-06-21 04:30 | 55 | 57 | 71 | 69.6167
2015-06-21 04:45 | 55 | 57 | 71 | 69.8667
2015-06-21 05:00 | 55.0667 | 57.1167 | 71 | 70.1167
2015-06-21 05:15 | 55.3167 | 57.3667 | 71 | 70.3667
2015-06-21 05:30 | 55.5667 | 57.6167 | 71 | 70.6167
2015-06-21 05:45 | 55.8167 | 57.8667 | 71 | 70.8667
2015-06-21 06:00 | 56.0667 | 58.1167 | 71.1167 | 71.35
2015-06-21 06:15 | 56.3167 | 58.3667 | 71.3667 | 72.1
2015-06-21 06:30 | 56.5667 | 58.6167 | 71.6167 | 72.85
2015-06-21 06:45 | 56.8167 | 58.8667 | 71.8667 | 73.6
2015-06-21 07:00 | 57 | 59.4 | 72.4667 | 74.5833
2015-06-21 07:15 | 57 | 60.2571 | 73.4667 | 75.8333
2015-06-21 07:30 | 57.6667 | 61.08 | 74.4667 | 77.0833
2015-06-21 07:45 | 58.4359 | 61.68 | 75.4667 | 78.3333
2015-06-21 08:00 | 59.0667 | 62.2333 | 76.5833 | 79.5833
2015-06-21 08:15 | 59.3167 | 62.7333 | 77.8333 | 80.8333
2015-06-21 08:30 | 59.5667 | 63.2333 | 79.0833 | 82.0833
2015-06-21 08:45 | 59.8167 | 63.7333 | 80.3333 | 83.3333
2015-06-21 09:00 | 60 | 64.5833 | 81.35 | 84.4667
2015-06-21 09:15 | 60 | 65.8333 | 82.1 | 85.4667
2015-06-21 09:30 | 60 | 67.0833 | 82.85 | 86.4667
2015-06-21 09:45 | 60 | 68.3333 | 83.6 | 87.4667
2015-06-21 10:00 | 60.2 | 69.1167 | 84.2333 | 88.35
2015-06-21 10:15 | 60.95 | 69.3667 | 84.7333 | 89.1
2015-06-21 10:30 | 61.7 | 69.6167 | 85.2333 | 89.85
2015-06-21 10:45 | 62.45 | 69.8667 | 85.7333 | 90.6
2015-06-21 11:00 | 63 | 70.1167 | 86.2333 | 91.1167
2015-06-21 11:15 | 63 | 70.3667 | 86.7333 | 91.3667
2015-06-21 11:30 | 63 | 70.6167 | 87.2333 | 91.6167
2015-06-21 11:45 | 63 | 70.8667 | 87.7333 | 91.8667
2015-06-21 12:00 | 63.0667 | 70.8833 | 88.2333 | 92.35
2015-06-21 12:15 | 63.3167 | 70.6333 | 88.7333 | 93.1
2015-06-21 12:30 | 63.5667 | 70.3833 | 89.2333 | 93.85
2015-06-21 12:45 | 63.8167 | 70.1333 | 89.7333 | 94.6
2015-06-21 13:00 | 64.0667 | 70.1167 | 90.35 | 95.1167
2015-06-21 13:15 | 64.3167 | 70.3667 | 91.1 | 95.3667
2015-06-21 13:30 | 64.5667 | 70.6167 | 91.85 | 95.6167
2015-06-21 13:45 | 64.8167 | 70.8667 | 92.6 | 95.8667
2015-06-21 14:00 | 65.0667 | 71.2333 | 93.1167 | 95.8833
2015-06-21 14:15 | 65.3167 | 71.7333 | 93.3667 | 95.6333
2015-06-21 14:30 | 65.5667 | 72.2333 | 93.6167 | 95.3833
2015-06-21 14:45 | 65.8167 | 72.7333 | 93.8667 | 95.1333
2015-06-21 15:00 | 65.8667 | 72.65 | 93.8833 | 95
2015-06-21 15:15 | 65.3667 | 71.9 | 93.6333 | 95
2015-06-21 15:30 | 64.8667 | 71.15 | 93.3833 | 95
2015-06-21 15:45 | 64.3667 | 70.4 | 93.1333 | 95
2015-06-21 16:00 | 63.9333 | 69.8833 | 92.7667 | 95
2015-06-21 16:15 | 63.6833 | 69.6333 | 92.2667 | 95
2015-06-21 16:30 | 63.4333 | 69.3833 | 91.7667 | 95
2015-06-21 16:45 | 63.1833 | 69.1333 | 91.2667 | 95
2015-06-21 17:00 | 62.8667 | 68.72 | 90.65 | 94.7667
2015-06-21 17:15 | 62.3667 | 68.12 | 89.9 | 94.2667
2015-06-21 17:30 | 61.8667 | 67.6571 | 89.15 | 93.7667
2015-06-21 17:45 | 61.3667 | 67.2286 | 88.4 | 93.2667
2015-06-21 18:00 | 60.8667 | 66.5333 | 87.65 | 92.5333
2015-06-21 18:15 | 60.3667 | 65.5333 | 86.9 | 91.5333
2015-06-21 18:30 | 59.8667 | 64.5333 | 86.15 | 90.5333
2015-06-21 18:45 | 59.3667 | 63.5333 | 85.4 | 89.5333
2015-06-21 19:00 | 58.8667 | 62.65 | 84.65 | 88.4167
2015-06-21 19:15 | 58.3667 | 61.9 | 83.9 | 87.1667
2015-06-21 19:30 | 57.8667 | 61.15 | 83.15 | 85.9167
2015-06-21 19:45 | 57.3667 | 60.4 | 82.4 | 84.6667
2015-06-21 20:00 | 57 | 59.8833 | 81.65 | 83.65
2015-06-21 20:15 | 57 | 59.6333 | 80.9 | 82.9
2015-06-21 20:30 | 57 | 59.3833 | 80.15 | 82.15
2015-06-21 20:45 | 57 | 59.1333 | 79.4 | 81.4
2015-06-21 21:00 | 56.814 | 58.8833 | 78.65 | 80.5333
2015-06-21 21:15 | 56.1163 | 58.6333 | 77.9 | 79.5333
2015-06-21 21:30 | 55.4186 | 58.3833 | 77.15 | 78.5333
2015-06-21 21:45 | 55.3529 | 58.1333 | 76.4 | 77.5333
2015-06-21 22:00 | 56 | 57.8833 | 75.7667 | 76.7667
2015-06-21 22:15 | 56 | 57.6333 | 75.2667 | 76.2667
2015-06-21 22:30 | 56 | 57.3833 | 74.7667 | 75.7667
2015-06-21 22:45 | 56 | 57.1333 | 74.2667 | 75.2667
2015-06-21 23:00 | 56.0667 | 57 | 74 | 74.65
2015-06-21 23:15 | 56.3167 | 57 | 74 | 73.9
2015-06-21 23:30 | 56.5667 | 57 | 74 | 73.15
2015-06-21 23:45 | 56.8167 | 57 | 74 | 72.4
2015-06-22 | 56.9333 | 56.8833 | 73.5625 | 71.7667
2015-06-22 00:15 | 56.6833 | 56.6333 | 72.7778 | 71.2667
2015-06-22 00:30 | 56.4333 | 56.3833 | 72.2222 | 70.7667
2015-06-22 00:45 | 56.1833 | 56.1333 | 72 | 70.2667
2015-06-22 01:00 | 56 | 56 | 72 | 69.65
2015-06-22 01:15 | 56 | 56 | 72 | 68.9
2015-06-22 01:30 | 56 | 56 | 72 | 68.15
2015-06-22 01:45 | 56 | 56 | 72 | 67.4
2015-06-22 02:00 | 56 | 55.8833 | 72 | 66.7667
2015-06-22 02:15 | 56 | 55.6333 | 72 | 66.2667
2015-06-22 02:30 | 56 | 55.3833 | 72 | 65.7667
2015-06-22 02:45 | 56 | 55.1333 | 72 | 65.2667
2015-06-22 03:00 | 56 | 55 | 72 | 65
2015-06-22 03:15 | 56 | 55 | 72 | 65
2015-06-22 03:30 | 56 | 55 | 72 | 65
2015-06-22 03:45 | 56 | 55 | 72 | 65
2015-06-22 04:00 | 55.9 | 55.1167 | 71.8833 | 64.65
2015-06-22 04:15 | 55.525 | 55.3667 | 71.6333 | 63.9
2015-06-22 04:30 | 55.15 | 55.6167 | 71.3833 | 63.15
2015-06-22 04:45 | 55 | 55.8667 | 71.1333 | 62.4
2015-06-22 05:00 | 55 | 56.1167 | 71 | 62.35
2015-06-22 05:15 | 55 | 56.3667 | 70.95 | 63.1
2015-06-22 05:30 | 55 | 56.6167 | 70.575 | 63.85
2015-06-22 05:45 | 55 | 56.8667 | 70.2 | 64.6
2015-06-22 06:00 | 55 | 57.1167 | 70.1167 | 65.35
2015-06-22 06:15 | 55 | 57.3667 | 70.3667 | 66.1
2015-06-22 06:30 | 55 | 57.6167 | 70.6167 | 66.85
2015-06-22 06:45 | 55 | 57.8667 | 70.8667 | 67.6
2015-06-22 07:00 | 55.0667 | 58.4667 | 71.35 | 68.4667
2015-06-22 07:15 | 55.3167 | 59.4667 | 72.1 | 69.4667
2015-06-22 07:30 | 55.5667 | 60.4667 | 72.85 | 70.4667
2015-06-22 07:45 | 55.8167 | 60.0667 | 73.6 | 71.4667
2015-06-22 08:00 | 56.2069 | 59.4667 | 74.35 | 72.5833
2015-06-22 08:15 | 56.9828 | 60.4667 | 75.1 | 73.8333
2015-06-22 08:30 | 57.7586 | 61.4667 | 75.85 | 75.0833
2015-06-22 08:45 | 58.5345 | 62.4667 | 76.6 | 76.3333
2015-06-22 09:00 | 59.0667 | 63.4667 | 77.1167 | 77.5833
2015-06-22 09:15 | 59.3167 | 64.4667 | 77.3667 | 78.8333
2015-06-22 09:30 | 59.5667 | 65.4667 | 77.6167 | 80.0833
2015-06-22 09:45 | 59.8167 | 66.4667 | 77.8667 | 81.3333
2015-06-22 10:00 | 60 | 67.35 | 78.2333 | 82.35
2015-06-22 10:15 | 60 | 68.1 | 78.7333 | 83.1
2015-06-22 10:30 | 60 | 68.85 | 79.2333 | 83.85
2015-06-22 10:45 | 60 | 69.6 | 79.7333 | 84.6
2015-06-22 11:00 | 60.0667 | 70 | 80.35 | 85.4667
2015-06-22 11:15 | 60.3167 | 70 | 81.1 | 86.4667
2015-06-22 11:30 | 60.5667 | 70 | 81.85 | 87.4667
2015-06-22 11:45 | 60.8167 | 70 | 82.6 | 88.4667
2015-06-22 12:00 | 61.0667 | 69.8833 | 83.1167 | 89.1167
2015-06-22 12:15 | 61.3167 | 69.6333 | 83.3667 | 89.3667
2015-06-22 12:30 | 61.5667 | 69.3833 | 83.6167 | 89.6167
2015-06-22 12:45 | 61.8167 | 69.1333 | 83.8667 | 89.8667
2015-06-22 13:00 | 62 | 69.1167 | 84.35 | 90.4667
2015-06-22 13:15 | 62 | 69.3667 | 85.1 | 91.4667
2015-06-22 13:30 | 62 | 69.6167 | 85.85 | 92.4667
2015-06-22 13:45 | 62 | 69.8667 | 86.6 | 93.4667
2015-06-22 14:00 | 62.1333 | 70.1167 | 87 | 94.1167
2015-06-22 14:15 | 62.6333 | 70.3667 | 87 | 94.3667
2015-06-22 14:30 | 63.1333 | 70.6167 | 87 | 94.6167
2015-06-22 14:45 | 63.6333 | 70.8667 | 87 | 94.8667
2015-06-22 15:00 | 63.8667 | 70.7667 | 87 | 95.1167
2015-06-22 15:15 | 63.3667 | 70.2667 | 87 | 95.3667
2015-06-22 15:30 | 62.8667 | 69.7667 | 87 | 95.6167
2015-06-22 15:45 | 62.3667 | 69.2667 | 87 | 95.8667
2015-06-22 16:00 | 61.9333 | 68.7667 | 86.7667 | 95.8833
2015-06-22 16:15 | 61.6833 | 68.2667 | 86.2667 | 95.6333
2015-06-22 16:30 | 61.4333 | 67.7667 | 85.7667 | 95.3833
2015-06-22 16:45 | 61.1833 | 67.2667 | 85.2667 | 95.1333
2015-06-22 17:00 | 60.9333 | 66.8833 | 84.65 | 94.7667
2015-06-22 17:15 | 60.6833 | 66.6333 | 83.9 | 94.2667
2015-06-22 17:30 | 60.4333 | 66.3833 | 83.15 | 93.7667
2015-06-22 17:45 | 60.1833 | 66.1333 | 82.4 | 93.2667
2015-06-22 18:00 | 59.9333 | 65.8833 | 81.7667 | 92.5333
2015-06-22 18:15 | 59.6833 | 65.6333 | 81.2667 | 91.5333
2015-06-22 18:30 | 59.4333 | 65.3833 | 80.7667 | 90.5333
2015-06-22 18:45 | 59.1833 | 65.1333 | 80.2667 | 89.5333
2015-06-22 19:00 | 58.9333 | 64.5333 | 79.65 | 88.5333
2015-06-22 19:15 | 58.6833 | 63.5333 | 78.9 | 87.5333
2015-06-22 19:30 | 58.4333 | 62.5333 | 78.15 | 86.5333
2015-06-22 19:45 | 58.1833 | 61.5333 | 77.4 | 85.5333
2015-06-22 20:00 | 57.9333 | 60.8833 | 76.7667 | 84.65
2015-06-22 20:15 | 57.6833 | 60.6333 | 76.2667 | 83.9
2015-06-22 20:30 | 57.4333 | 60.3833 | 75.7667 | 83.15
2015-06-22 20:45 | 57.1833 | 60.1333 | 75.2667 | 82.4
2015-06-22 21:00 | 57 | 59.8833 | 74.7021 | 81.65
2015-06-22 21:15 | 57 | 59.6333 | 74.0638 | 80.9
2015-06-22 21:30 | 57 | 59.3833 | 73.4255 | 80.15
2015-06-22 21:45 | 57 | 59.1333 | 73 | 79.4
2015-06-22 22:00 | 56.9333 | 59 | 72.6818 | 78.65
2015-06-22 22:15 | 56.6833 | 59 | 72 | 77.9
2015-06-22 22:30 | 56.4333 | 59 | 72 | 77.15
2015-06-22 22:45 | 56.1833 | 59 | 72 | 76.4
2015-06-22 23:00 | 56.0667 | 58.8833 | 72 | 75.7667
2015-06-22 23:15 | 56.3167 | 58.6333 | 72 | 75.2667
2015-06-22 23:30 | 56.5667 | 58.3833 | 72 | 74.7667
2015-06-22 23:45 | 56.8167 | 58.1333 | 72 | 74.2667
2015-06-23 | 56.9333 | 57.8833 | 72 | 73.65
2015-06-23 00:15 | 56.6833 | 57.6333 | 72 | 72.9
2015-06-23 00:30 | 56.4333 | 57.3833 | 72 | 72.15
2015-06-23 00:45 | 56.1833 | 57.1333 | 72 | 71.4
2015-06-23 01:00 | 55.9333 | 57 | 72 | 70.7667
2015-06-23 01:15 | 55.6833 | 57 | 72 | 70.2667
2015-06-23 01:30 | 55.4333 | 57 | 72 | 69.7667
2015-06-23 01:45 | 55.1833 | 57 | 72 | 69.2667
2015-06-23 02:00 | 55 | 57 | 72 | 68.7667
2015-06-23 02:15 | 55 | 57 | 72 | 68.2667
2015-06-23 02:30 | 55 | 57 | 71.7222 | 67.7667
2015-06-23 02:45 | 55 | 57 | 71 | 67.2667
2015-06-23 03:00 | 54.9333 | 56.8833 | 71.1167 | 66.8833
2015-06-23 03:15 | 54.6833 | 56.6333 | 71.3667 | 66.6333
2015-06-23 03:30 | 54.4333 | 56.3833 | 71.6167 | 66.3833
2015-06-23 03:45 | 54.1833 | 56.1333 | 71.8667 | 66.1333
2015-06-23 04:00 | 54 | 55.8833 | 72.1167 | 65.8833
2015-06-23 04:15 | 54 | 55.6333 | 72.3667 | 65.6333
2015-06-23 04:30 | 54 | 55.3833 | 72.6167 | 65.3833
2015-06-23 04:45 | 54 | 55.1333 | 72.8667 | 65.1333
2015-06-23 05:00 | 54.1333 | 55.2333 | 72.8833 | 65.35
2015-06-23 05:15 | 54.6333 | 55.7333 | 72.6333 | 66.1
2015-06-23 05:30 | 55.1333 | 56.2333 | 72.3833 | 66.85
2015-06-23 05:45 | 55.6333 | 56.7333 | 72.1333 | 67.6
2015-06-23 06:00 | 56.1333 | 57.4667 | 71.5333 | 68.5833
2015-06-23 06:15 | 56.6333 | 58.4667 | 70.8372 | 69.8333
2015-06-23 06:30 | 57.1333 | 59.4667 | 70.4884 | 71.0833
2015-06-23 06:45 | 57.6333 | 60.4667 | 70.1395 | 72.3333
2015-06-23 07:00 | 58.1333 | 61.2333 | 70.2333 | 73.4667
2015-06-23 07:15 | 58.6333 | 61.7333 | 70.7333 | 74.4667
2015-06-23 07:30 | 59.1333 | 62.2333 | 71.2333 | 75.4667
2015-06-23 07:45 | 59.6333 | 62.7333 | 71.7333 | 76.4667
2015-06-23 08:00 | 60.2 | 63.35 | 72.3621 | 77.7
2015-06-23 08:15 | 60.95 | 64.1 | 73.1379 | 79.2
2015-06-23 08:30 | 61.7 | 64.85 | 73.9138 | 80.7
2015-06-23 08:45 | 62.45 | 65.6 | 74.6897 | 82.2
2015-06-23 09:00 | 63.1333 | 66.4667 | 75.1167 | 83.2333
2015-06-23 09:15 | 63.6333 | 67.4667 | 75.3667 | 83.7333
2015-06-23 09:30 | 64.1333 | 68.4667 | 75.6167 | 84.2333
2015-06-23 09:45 | 64.6333 | 69.4667 | 75.8667 | 84.7333
2015-06-23 10:00 | 65.1333 | 70.4667 | 75.8793 | 85.2333
2015-06-23 10:15 | 65.6333 | 71.4667 | 75.6207 | 85.7333
2015-06-23 10:30 | 66.1333 | 72.4667 | 75.3621 | 86.2333
2015-06-23 10:45 | 66.6333 | 73.4667 | 75.1034 | 86.7333
2015-06-23 11:00 | 67.0667 | 74.1167 | 75.125 | 87.4667
2015-06-23 11:15 | 67.3167 | 74.3667 | 73.7 | 88.4667
2015-06-23 11:30 | 67.5667 | 74.6167 | 73.2857 | 89.4667
2015-06-23 11:45 | 67.8167 | 74.8667 | 73.4118 | 90.4667
2015-06-23 12:00 | 68 | 75.1167 | 72.9333 | 91.2333
2015-06-23 12:15 | 68 | 75.3667 | 74.9333 | 91.7333
2015-06-23 12:30 | 68 | 75.6167 | 76.9333 | 92.2333
2015-06-23 12:45 | 68 | 75.8667 | 78.9333 | 92.7333
2015-06-23 13:00 | 67.8667 | 76.1167 | 80.35 | 93.1167
2015-06-23 13:15 | 67.3667 | 76.3667 | 81.1 | 93.3667
2015-06-23 13:30 | 66.8667 | 76.6167 | 81.85 | 93.6167
2015-06-23 13:45 | 66.3667 | 76.8667 | 82.6 | 93.8667
2015-06-23 14:00 | 65.9333 | 76.7667 | 83.35 | 94
2015-06-23 14:15 | 65.6833 | 76.2667 | 84.1 | 94
2015-06-23 14:30 | 65.4333 | 75.7667 | 84.85 | 94
2015-06-23 14:45 | 65.1833 | 75.2667 | 85.6 | 94
2015-06-23 15:00 | 65.0667 | 74.7667 | 86 | 94.1167
2015-06-23 15:15 | 65.3167 | 74.2667 | 86 | 94.3667
2015-06-23 15:30 | 65.5667 | 73.7667 | 86 | 94.6167
2015-06-23 15:45 | 65.8167 | 73.2667 | 86 | 94.8667
2015-06-23 16:00 | 65.9333 | 72.7667 | 85.5333 | 95
2015-06-23 16:15 | 65.6833 | 72.2667 | 84.5333 | 95
2015-06-23 16:30 | 65.4333 | 71.7667 | 83.5333 | 95
2015-06-23 16:45 | 65.1833 | 71.2667 | 82.5333 | 95
2015-06-23 17:00 | 64.8667 | 70.7667 | 82 | 94.8833
2015-06-23 17:15 | 64.3667 | 70.2667 | 82 | 94.6333
2015-06-23 17:30 | 63.8667 | 69.7667 | 82 | 94.3833
2015-06-23 17:45 | 63.3667 | 69.2667 | 82 | 94.1333
2015-06-23 18:00 | 62.9333 | 68.65 | 81.5333 | 93.65
2015-06-23 18:15 | 62.6833 | 67.9 | 80.5333 | 92.9
2015-06-23 18:30 | 62.4333 | 67.15 | 79.5333 | 92.15
2015-06-23 18:45 | 62.1833 | 66.4 | 78.5333 | 91.4
2015-06-23 19:00 | 61.8667 | 65.7667 | 77.8833 | 90.5333
2015-06-23 19:15 | 61.3667 | 65.2667 | 77.6333 | 89.5333
2015-06-23 19:30 | 60.8667 | 64.7667 | 77.3833 | 88.5333
2015-06-23 19:45 | 60.3667 | 64.2667 | 77.1333 | 87.5333
2015-06-23 20:00 | 59.9333 | 64 | 76.7667 | 86.8833
2015-06-23 20:15 | 59.6833 | 64 | 76.2667 | 86.6333
2015-06-23 20:30 | 59.4333 | 64 | 75.7667 | 86.3833
2015-06-23 20:45 | 59.1833 | 64 | 75.2667 | 86.1333
2015-06-23 21:00 | 58.8667 | 63.65 | 74.7667 | 85.65
2015-06-23 21:15 | 58.3667 | 62.9 | 74.2667 | 84.9
2015-06-23 21:30 | 57.8667 | 62.15 | 73.7667 | 84.15
2015-06-23 21:45 | 57.3667 | 61.4 | 73.2667 | 83.4
2015-06-23 22:00 | 56.9333 | 60.8833 | 72.7667 | 82.5333
2015-06-23 22:15 | 56.6833 | 60.6333 | 72.2667 | 81.5333
2015-06-23 22:30 | 56.4333 | 60.3833 | 71.7667 | 80.5333
2015-06-23 22:45 | 56.1833 | 60.1333 | 71.2667 | 79.5333
2015-06-23 23:00 | 55.931 | 59.8833 | 70.8833 | 78.65
2015-06-23 23:15 | 55.6724 | 59.6333 | 70.6333 | 77.9
2015-06-23 23:30 | 55.4138 | 59.3833 | 70.3833 | 77.15
2015-06-23 23:45 | 55.1552 | 59.1333 | 70.1333 | 76.4
2015-06-24 | 56 | 58.7667 | 70.1167 | 75.65
2015-06-24 00:15 | 56 | 58.2667 | 70.3667 | 74.9
2015-06-24 00:30 | 56 | 57.7667 | 70.6167 | 74.15
2015-06-24 00:45 | 56 | 57.2667 | 70.8667 | 73.4
2015-06-24 01:00 | 55.9333 | 57 | 71 | 72.7667
2015-06-24 01:15 | 55.6833 | 57 | 71 | 72.2667
2015-06-24 01:30 | 55.4333 | 57 | 71 | 71.7667
2015-06-24 01:45 | 55.1833 | 57 | 71 | 71.2667
2015-06-24 02:00 | 55.0667 | 56.8833 | 71 | 70.7667
2015-06-24 02:15 | 55.3167 | 56.6333 | 71 | 70.2667
2015-06-24 02:30 | 55.5667 | 56.3833 | 71 | 69.7667
2015-06-24 02:45 | 55.8167 | 56.1333 | 71 | 69.2667
2015-06-24 03:00 | 55.9333 | 56 | 71 | 68.8833
2015-06-24 03:15 | 55.6833 | 56 | 71 | 68.6333
2015-06-24 03:30 | 55.4333 | 56 | 71 | 68.3833
2015-06-24 03:45 | 55.1833 | 56 | 71 | 68.1333
2015-06-24 04:00 | 55 | 55.825 | 71 | 67.8833
2015-06-24 04:15 | 55 | 55.45 | 71 | 67.6333
2015-06-24 04:30 | 55 | 55.075 | 71 | 67.3833
2015-06-24 04:45 | 55 | 55.6 | 71 | 67.1333
2015-06-24 05:00 | 54.0667 | 56.1167 | 71 | 67.1167
2015-06-24 05:15 | 54.3167 | 56.3667 | 71 | 67.3667
2015-06-24 05:30 | 54.5667 | 56.6167 | 71 | 67.6167
2015-06-24 05:45 | 54.8167 | 56.8667 | 71 | 67.8667
2015-06-24 06:00 | 55.2 | 57.2333 | 71 | 68.35
2015-06-24 06:15 | 55.95 | 57.7333 | 71 | 69.1
2015-06-24 06:30 | 56.7 | 58.2333 | 71 | 69.85
2015-06-24 06:45 | 57.45 | 58.7333 | 71 | 70.6
2015-06-24 07:00 | 58.1333 | 59.35 | 71.1167 | 71.5833
2015-06-24 07:15 | 58.6333 | 60.1 | 71.3667 | 72.8333
2015-06-24 07:30 | 59.1333 | 60.85 | 71.6167 | 74.0833
2015-06-24 07:45 | 59.6333 | 61.6 | 71.8667 | 75.3333
2015-06-24 08:00 | 60.2667 | 62.4667 | 72.1707 | 76.7
2015-06-24 08:15 | 61.2667 | 63.4667 | 72.5366 | 78.2
2015-06-24 08:30 | 62.2667 | 64.4667 | 72.9024 | 79.7
2015-06-24 08:45 | 63.2667 | 65.4667 | 74.7368 | 81.2
2015-06-24 09:00 | 64.2 | 66.4667 | 76.3043 | 82.4667
2015-06-24 09:15 | 64.95 | 67.4667 | 76.9565 | 83.4667
2015-06-24 09:30 | 65.7 | 68.4667 | 77.6087 | 84.4667
2015-06-24 09:45 | 66.45 | 69.4667 | 78.4286 | 85.4667
2015-06-24 10:00 | 67.1333 | 70.5833 | 79.1167 | 86.4667
2015-06-24 10:15 | 67.6333 | 71.8333 | 79.3667 | 87.4667
2015-06-24 10:30 | 68.1333 | 73.0833 | 79.6167 | 88.4667
2015-06-24 10:45 | 68.6333 | 74.3333 | 79.8667 | 89.4667
2015-06-24 11:00 | 69.0667 | 75 | 80.35 | 90.35
2015-06-24 11:15 | 69.3167 | 75 | 81.1 | 91.1
2015-06-24 11:30 | 69.5667 | 75 | 81.85 | 91.85
2015-06-24 11:45 | 69.8167 | 75 | 82.6 | 92.6
2015-06-24 12:00 | 70 | 75.35 | 83.2333 | 93.2333
2015-06-24 12:15 | 70 | 76.1 | 83.7333 | 93.7333
2015-06-24 12:30 | 70 | 76.85 | 84.2333 | 94.2333
2015-06-24 12:45 | 70 | 77.6 | 84.7333 | 94.7333
2015-06-24 13:00 | 69.9333 | 78.2333 | 85 | 95.2333
2015-06-24 13:15 | 69.6833 | 78.7333 | 85 | 95.7333
2015-06-24 13:30 | 69.4333 | 79.2333 | 85 | 96.2333
2015-06-24 13:45 | 69.1833 | 79.7333 | 85 | 96.7333
2015-06-24 14:00 | 68.9333 | 79.8833 | 85.1167 | 97.1167
2015-06-24 14:15 | 68.6833 | 79.6333 | 85.3667 | 97.3667
2015-06-24 14:30 | 68.4333 | 79.3833 | 85.6167 | 97.6167
2015-06-24 14:45 | 68.1833 | 79.1333 | 85.8667 | 97.8667
2015-06-24 15:00 | 67.9333 | 78.7667 | 86.1167 | 98
2015-06-24 15:15 | 67.6833 | 78.2667 | 86.3667 | 98
2015-06-24 15:30 | 67.4333 | 77.7667 | 86.6167 | 98
2015-06-24 15:45 | 67.1833 | 77.2667 | 86.8667 | 98
2015-06-24 16:00 | 66.8667 | 76.8833 | 86.8833 | 98
2015-06-24 16:15 | 66.3667 | 76.6333 | 86.6333 | 98
2015-06-24 16:30 | 65.8667 | 76.3833 | 86.3833 | 98
2015-06-24 16:45 | 65.3667 | 76.1333 | 86.1333 | 98
2015-06-24 17:00 | 64.8667 | 75.5333 | 85.8833 | 97.8833
2015-06-24 17:15 | 64.3667 | 74.5333 | 85.6333 | 97.6333
2015-06-24 17:30 | 63.8667 | 73.5333 | 85.3833 | 97.3833
2015-06-24 17:45 | 63.3667 | 72.5333 | 85.1333 | 97.1333
2015-06-24 18:00 | 62.8667 | 71.5333 | 84.5333 | 96.65
2015-06-24 18:15 | 62.3667 | 70.5333 | 83.5333 | 95.9
2015-06-24 18:30 | 61.8667 | 69.5333 | 82.5333 | 95.15
2015-06-24 18:45 | 61.3667 | 68.5333 | 81.5333 | 94.4
2015-06-24 19:00 | 60.9333 | 67.65 | 80.8833 | 93.5333
2015-06-24 19:15 | 60.6833 | 66.9 | 80.6333 | 92.5333
2015-06-24 19:30 | 60.4333 | 66.15 | 80.3833 | 91.5333
2015-06-24 19:45 | 60.1833 | 65.4 | 80.1333 | 90.5333
2015-06-24 20:00 | 59.9333 | 64.8833 | 79.7667 | 89.65
2015-06-24 20:15 | 59.6833 | 64.6333 | 79.2667 | 88.9
2015-06-24 20:30 | 59.4333 | 64.3833 | 78.7667 | 88.15
2015-06-24 20:45 | 59.1833 | 64.1333 | 78.2667 | 87.4
2015-06-24 21:00 | 59 | 64 | 77.7667 | 86.7667
2015-06-24 21:15 | 59 | 64 | 77.2667 | 86.2667
2015-06-24 21:30 | 59 | 64 | 76.7667 | 85.7667
2015-06-24 21:45 | 59 | 64 | 76.2667 | 85.2667
2015-06-24 22:00 | 59 | 64 | 75.8833 | 84.65
2015-06-24 22:15 | 59 | 64 | 75.6333 | 83.9
2015-06-24 22:30 | 59 | 64 | 75.3833 | 83.15
2015-06-24 22:45 | 59 | 64 | 75.1333 | 82.4
2015-06-24 23:00 | 59 | 63.7667 | 74.7667 | 81.7667
2015-06-24 23:15 | 59 | 63.2667 | 74.2667 | 81.2667
2015-06-24 23:30 | 59 | 62.7667 | 73.7667 | 80.7667
2015-06-24 23:45 | 59 | 62.2667 | 73.2667 | 80.2667
2015-06-25 | 58.9333 | 61.8833 | 72.8833 | 79.7667
2015-06-25 00:15 | 58.6833 | 61.6333 | 72.6333 | 79.2667
2015-06-25 00:30 | 58.4333 | 61.3833 | 72.3833 | 78.7667
2015-06-25 00:45 | 58.1833 | 61.1333 | 72.1333 | 78.2667
2015-06-25 01:00 | 57.9333 | 60.8833 | 71.8833 | 77.7667
2015-06-25 01:15 | 57.6833 | 60.6333 | 71.6333 | 77.2667
2015-06-25 01:30 | 57.4333 | 60.3833 | 71.3833 | 76.7667
2015-06-25 01:45 | 57.1833 | 60.1333 | 71.1333 | 76.2667
2015-06-25 02:00 | 57 | 60 | 71 | 75.7667
2015-06-25 02:15 | 57 | 60 | 71 | 75.2667
2015-06-25 02:30 | 57 | 60 | 71 | 74.7667
2015-06-25 02:45 | 57 | 60 | 71 | 74.2667
2015-06-25 03:00 | 57 | 60 | 70.8833 | 73.8833
2015-06-25 03:15 | 57 | 60 | 70.6333 | 73.6333
2015-06-25 03:30 | 57 | 60 | 70.3833 | 73.3833
2015-06-25 03:45 | 57 | 60 | 70.1333 | 73.1333
2015-06-25 04:00 | 57 | 60 | 69.8833 | 73
2015-06-25 04:15 | 57 | 60 | 69.6333 | 73
2015-06-25 04:30 | 57 | 60 | 69.3833 | 73
2015-06-25 04:45 | 57 | 60 | 69.1333 | 73
2015-06-25 05:00 | 57.1333 | 60.1167 | 69 | 73.1167
2015-06-25 05:15 | 57.6333 | 60.3667 | 69 | 73.3667
2015-06-25 05:30 | 58.1333 | 60.6167 | 69 | 73.6167
2015-06-25 05:45 | 58.6333 | 60.8667 | 69 | 73.8667
2015-06-25 06:00 | 59.2667 | 61.35 | 69.2333 | 74.2333
2015-06-25 06:15 | 60.2667 | 62.1 | 69.7333 | 74.7333
2015-06-25 06:30 | 61.2667 | 62.85 | 70.2333 | 75.2333
2015-06-25 06:45 | 62.2667 | 63.6 | 70.7333 | 75.7333
2015-06-25 07:00 | 63.0667 | 64.4667 | 71.4667 | 76.7
2015-06-25 07:15 | 63.3167 | 65.4667 | 72.4667 | 78.2
2015-06-25 07:30 | 63.5667 | 66.4667 | 73.4667 | 79.7
2015-06-25 07:45 | 63.8167 | 67.4667 | 74.4667 | 81.2
2015-06-25 08:00 | 64.1333 | 68.5833 | 75.35 | 82.5833
2015-06-25 08:15 | 64.6333 | 69.8333 | 76.1 | 83.8333
2015-06-25 08:30 | 65.1333 | 71.0833 | 76.85 | 85.0833
2015-06-25 08:45 | 65.6333 | 72.3333 | 77.6 | 86.3333
2015-06-25 09:00 | 66.2 | 73.5833 | 78.5833 | 87.35
2015-06-25 09:15 | 66.95 | 74.8333 | 79.8333 | 88.1
2015-06-25 09:30 | 67.7 | 76.0833 | 81.0833 | 88.85
2015-06-25 09:45 | 68.45 | 77.3333 | 82.3333 | 89.6
2015-06-25 10:00 | 69.2 | 78.35 | 83.35 | 90.4667
2015-06-25 10:15 | 69.95 | 79.1 | 84.1 | 91.4667
2015-06-25 10:30 | 70.7 | 79.85 | 84.85 | 92.4667
2015-06-25 10:45 | 71.45 | 80.6 | 85.6 | 93.4667
2015-06-25 11:00 | 72.1333 | 81.35 | 86.2333 | 94.35
2015-06-25 11:15 | 72.6333 | 82.1 | 86.7333 | 95.1
2015-06-25 11:30 | 73.1333 | 82.85 | 87.2333 | 95.85
2015-06-25 11:45 | 73.6333 | 83.6 | 87.7333 | 96.6
2015-06-25 12:00 | 74.1333 | 84.1167 | 88.2333 | 97.35
2015-06-25 12:15 | 74.6333 | 84.3667 | 88.7333 | 98.1
2015-06-25 12:30 | 75.1333 | 84.6167 | 89.2333 | 98.85
2015-06-25 12:45 | 75.6333 | 84.8667 | 89.7333 | 99.6
2015-06-25 13:00 | 75.8667 | 85.4667 | 90.2333 | 100.2333
2015-06-25 13:15 | 75.3667 | 86.4667 | 90.7333 | 100.7333
2015-06-25 13:30 | 74.8667 | 87.4667 | 91.2333 | 101.2333
2015-06-25 13:45 | 74.3667 | 88.4667 | 91.7333 | 101.7333
2015-06-25 14:00 | 74 | 88.7667 | 92.1167 | 102.2333
2015-06-25 14:15 | 74 | 88.2667 | 92.3667 | 102.7333
2015-06-25 14:30 | 74 | 87.7667 | 92.6167 | 103.2333
2015-06-25 14:45 | 74 | 87.2667 | 92.8667 | 103.7333
2015-06-25 15:00 | 73.9333 | 86.8833 | 93.2333 | 104
2015-06-25 15:15 | 73.6833 | 86.6333 | 93.7333 | 104
2015-06-25 15:30 | 73.4333 | 86.3833 | 94.2333 | 104
2015-06-25 15:45 | 73.1833 | 86.1333 | 94.7333 | 104
2015-06-25 16:00 | 72.8667 | 85.8833 | 94.7667 | 103.8833
2015-06-25 16:15 | 72.3667 | 85.6333 | 94.2667 | 103.6333
2015-06-25 16:30 | 71.8667 | 85.3833 | 93.7667 | 103.3833
2015-06-25 16:45 | 71.3667 | 85.1333 | 93.2667 | 103.1333
2015-06-25 17:00 | 70.8 | 84.65 | 92.8833 | 103
2015-06-25 17:15 | 70.05 | 83.9 | 92.6333 | 103
2015-06-25 17:30 | 69.3 | 83.15 | 92.3833 | 103
2015-06-25 17:45 | 68.55 | 82.4 | 92.1333 | 103
2015-06-25 18:00 | 67.8667 | 81.5333 | 91.4167 | 102.65
2015-06-25 18:15 | 67.3667 | 80.5333 | 90.1667 | 101.9
2015-06-25 18:30 | 66.8667 | 79.5333 | 88.9167 | 101.15
2015-06-25 18:45 | 66.3667 | 78.5333 | 87.6667 | 100.4
2015-06-25 19:00 | 65.8 | 77.5333 | 86.65 | 99.4167
2015-06-25 19:15 | 65.05 | 76.5333 | 85.9 | 98.1667
2015-06-25 19:30 | 64.3 | 75.5333 | 85.15 | 96.9167
2015-06-25 19:45 | 63.55 | 74.5333 | 84.4 | 95.6667
2015-06-25 20:00 | 62.9333 | 73.65 | 83.7667 | 94.65
2015-06-25 20:15 | 62.6833 | 72.9 | 83.2667 | 93.9
2015-06-25 20:30 | 62.4333 | 72.15 | 82.7667 | 93.15
2015-06-25 20:45 | 62.1833 | 71.4 | 82.2667 | 92.4
2015-06-25 21:00 | 62 | 70.7667 | 81.65 | 91.65
2015-06-25 21:15 | 62 | 70.2667 | 80.9 | 90.9
2015-06-25 21:30 | 62 | 69.7667 | 80.15 | 90.15
2015-06-25 21:45 | 62 | 69.2667 | 79.4 | 89.4
2015-06-25 22:00 | 61.9333 | 68.8833 | 78.7667 | 88.4167
2015-06-25 22:15 | 61.6833 | 68.6333 | 78.2667 | 87.1667
2015-06-25 22:30 | 61.4333 | 68.3833 | 77.7667 | 85.9167
2015-06-25 22:45 | 61.1833 | 68.1333 | 77.2667 | 84.6667
2015-06-25 23:00 | 61 | 67.7667 | 76.7667 | 83.65
2015-06-25 23:15 | 61 | 67.2667 | 76.2667 | 82.9
2015-06-25 23:30 | 61 | 66.7667 | 75.7667 | 82.15
2015-06-25 23:45 | 61 | 66.2667 | 75.2667 | 81.4
2015-06-26 | 60.8667 | 66 | 74.8833 | 81
2015-06-26 00:15 | 60.3667 | 66 | 74.6333 | 81
2015-06-26 00:30 | 59.8667 | 66 | 74.3833 | 81
2015-06-26 00:45 | 59.3667 | 66 | 74.1333 | 81
2015-06-26 01:00 | 59 | 66 | 73.8833 | 80.7667
2015-06-26 01:15 | 59 | 66 | 73.6333 | 80.2667
2015-06-26 01:30 | 59 | 66 | 73.3833 | 79.7667
2015-06-26 01:45 | 59 | 66 | 73.1333 | 79.2667
2015-06-26 02:00 | 59 | 65.8833 | 72.8833 | 78.7667
2015-06-26 02:15 | 59 | 65.6333 | 72.6333 | 78.2667
2015-06-26 02:30 | 59 | 65.3833 | 72.3833 | 77.7667
2015-06-26 02:45 | 59 | 65.1333 | 72.1333 | 77.2667
2015-06-26 03:00 | 58.8667 | 64.65 | 71.8833 | 76.8833
2015-06-26 03:15 | 58.3667 | 63.9 | 71.6333 | 76.6333
2015-06-26 03:30 | 57.8667 | 63.15 | 71.3833 | 76.3833
2015-06-26 03:45 | 57.3667 | 62.4 | 71.1333 | 76.1333
2015-06-26 04:00 | 56.9333 | 61.8833 | 70.8833 | 75.7667
2015-06-26 04:15 | 56.6833 | 61.6333 | 70.6333 | 75.2667
2015-06-26 04:30 | 56.4333 | 61.3833 | 70.3833 | 74.7667
2015-06-26 04:45 | 56.1833 | 61.1333 | 70.1333 | 74.2667
2015-06-26 05:00 | 56.0667 | 61.35 | 69.8833 | 74.1167
2015-06-26 05:15 | 56.3167 | 62.1 | 69.6333 | 74.3667
2015-06-26 05:30 | 56.5667 | 62.85 | 69.3833 | 74.6167
2015-06-26 05:45 | 56.8167 | 63.6 | 69.1333 | 74.8667
2015-06-26 06:00 | 57.2 | 64.2333 | 69.35 | 75.2333
2015-06-26 06:15 | 57.95 | 64.7333 | 70.1 | 75.7333
2015-06-26 06:30 | 58.7 | 65.2333 | 70.85 | 76.2333
2015-06-26 06:45 | 59.45 | 65.7333 | 71.6 | 76.7333
2015-06-26 07:00 | 60.2 | 66.4667 | 72.8167 | 77.7
2015-06-26 07:15 | 60.95 | 67.4667 | 74.5667 | 79.2
2015-06-26 07:30 | 61.7 | 68.4667 | 76.3167 | 80.7
2015-06-26 07:45 | 62.45 | 69.4667 | 78.0667 | 82.2
2015-06-26 08:00 | 63.2 | 70.7 | 79.5833 | 83.35
2015-06-26 08:15 | 63.95 | 72.2 | 80.8333 | 84.1
2015-06-26 08:30 | 64.7 | 73.7 | 82.0833 | 84.85
2015-06-26 08:45 | 65.45 | 75.2 | 83.3333 | 85.6
2015-06-26 09:00 | 66.2 | 76.1167 | 84.5833 | 86.1167
2015-06-26 09:15 | 66.95 | 76.3667 | 85.8333 | 86.3667
2015-06-26 09:30 | 67.7 | 76.6167 | 87.0833 | 86.6167
2015-06-26 09:45 | 68.45 | 76.8667 | 88.3333 | 86.8667
2015-06-26 10:00 | 69.2 | 77.2333 | 89.2333 | 87.35
2015-06-26 10:15 | 69.95 | 77.7333 | 89.7333 | 88.1
2015-06-26 10:30 | 70.7 | 78.2333 | 90.2333 | 88.85
2015-06-26 10:45 | 71.45 | 78.7333 | 90.7333 | 89.6
2015-06-26 11:00 | 72 | 79.2333 | 91.1167 | 90.7
2015-06-26 11:15 | 72 | 79.7333 | 91.3667 | 92.2
2015-06-26 11:30 | 71.9259 | 80.2333 | 91.6167 | 93.7
2015-06-26 11:45 | 70.8148 | 80.7333 | 91.8667 | 95.2
2015-06-26 12:00 | 70.0667 | 81.2333 | 92 | 96.4667
2015-06-26 12:15 | 70.3167 | 81.7333 | 92 | 97.4667
2015-06-26 12:30 | 70.5667 | 82.2333 | 92 | 98.4667
2015-06-26 12:45 | 70.8167 | 82.7333 | 92 | 99.4667
2015-06-26 13:00 | 71 | 82.7667 | 91.3333 | 100.1167
2015-06-26 13:15 | 71 | 82.2667 | 89.5556 | 100.3667
2015-06-26 13:30 | 71 | 81.7667 | 82.8889 | 100.6167
2015-06-26 13:45 | 71 | 81.2667 | 78 | 100.8667
2015-06-26 14:00 | 71 | 81 | 80.9333 | 101.35
2015-06-26 14:15 | 71 | 81 | 82.9333 | 102.1
2015-06-26 14:30 | 71 | 81 | 84.9333 | 102.85
2015-06-26 14:45 | 71 | 81 | 86.9333 | 103.6
2015-06-26 15:00 | 70.8667 | 80.7667 | 88 | 104.1167
2015-06-26 15:15 | 70.3667 | 80.2667 | 88 | 104.3667
2015-06-26 15:30 | 69.8667 | 79.7667 | 82.1765 | 104.6167
2015-06-26 15:45 | 69.3667 | 79.2667 | 74.2353 | 104.8667
2015-06-26 16:00 | 68.9333 | 78.7667 | 67.7778 | 105
2015-06-26 16:15 | 68.6833 | 78.2667 | 68 | 105
2015-06-26 16:30 | 68.4333 | 77.7667 | 68.8 | 105
2015-06-26 16:45 | 68.1833 | 77.2667 | 70 | 105
2015-06-26 17:00 | 67.8 | 76.8833 | 69 | 104.8833
2015-06-26 17:15 | 67.05 | 76.6333 | 69.48 | 104.6333
2015-06-26 17:30 | 66.3 | 76.3833 | 70.08 | 104.3833
2015-06-26 17:45 | 65.55 | 76.1333 | 70.68 | 104.1333
2015-06-26 18:00 | 64.8667 | 75.4167 | 71.1273 | 103.7667
2015-06-26 18:15 | 64.3667 | 74.1667 | 71.4 | 103.2667
2015-06-26 18:30 | 63.8667 | 72.9167 | 71.6727 | 102.7667
2015-06-26 18:45 | 63.3667 | 71.6667 | 71.9455 | 102.2667
2015-06-26 19:00 | 62.8667 | 70.4167 | 70.2632 | 101.5333
2015-06-26 19:15 | 62.3667 | 69.1667 | 69 | 100.5333
2015-06-26 19:30 | 61.8667 | 67.9167 | 69 | 99.5333
2015-06-26 19:45 | 61.3667 | 66.6667 | 69 | 98.5333
2015-06-26 20:00 | 61 | 65.8833 | 69.2333 | 97.3
2015-06-26 20:15 | 61 | 65.6333 | 69.7333 | 95.8
2015-06-26 20:30 | 61 | 65.3833 | 70.2333 | 94.3
2015-06-26 20:45 | 61 | 65.1333 | 70.7333 | 92.8
2015-06-26 21:00 | 61 | 64.7667 | 70.65 | 91.4167
2015-06-26 21:15 | 60.8723 | 64.2667 | 69.9 | 90.1667
2015-06-26 21:30 | 60.5532 | 63.7667 | 69.15 | 88.9167
2015-06-26 21:45 | 60.234 | 63.2667 | 68.4 | 87.6667
2015-06-26 22:00 | 60 | 62.7667 | 67.8833 | 86.7667
2015-06-26 22:15 | 60 | 62.2667 | 67.6333 | 86.2667
2015-06-26 22:30 | 60 | 61.7667 | 67.3833 | 85.7667
2015-06-26 22:45 | 60 | 61.2667 | 67.1333 | 85.2667
2015-06-26 23:00 | 59.9333 | 61.1167 | 66.7667 | 84.65
2015-06-26 23:15 | 59.6833 | 61.3667 | 66.2667 | 83.9
2015-06-26 23:30 | 59.4333 | 61.6167 | 65.7667 | 83.15
2015-06-26 23:45 | 59.1833 | 61.8667 | 65.2667 | 82.4
2015-06-27 | 59 | 61.8833 | 64.8833 | 81.8833
2015-06-27 00:15 | 59 | 61.6333 | 64.6333 | 81.6333
2015-06-27 00:30 | 59 | 61.3833 | 64.3833 | 81.3833
2015-06-27 00:45 | 59 | 61.1333 | 64.1333 | 81.1333
2015-06-27 01:00 | 58.8545 | 60.8833 | 64.1167 | 80.7667
2015-06-27 01:15 | 58.3091 | 60.6333 | 64.3667 | 80.2667
2015-06-27 01:30 | 57.7636 | 60.3833 | 64.6167 | 79.7667
2015-06-27 01:45 | 57.2182 | 60.1333 | 64.8667 | 79.2667
2015-06-27 02:00 | 58.0667 | 59.7667 | 64.8833 | 78.8833
2015-06-27 02:15 | 58.3167 | 59.2667 | 64.6333 | 78.6333
2015-06-27 02:30 | 58.5667 | 58.7667 | 64.3833 | 78.3833
2015-06-27 02:45 | 58.8167 | 58.2667 | 64.1333 | 78.1333
2015-06-27 03:00 | 59 | 57.8833 | 64 | 77.5333
2015-06-27 03:15 | 59 | 57.6333 | 64 | 76.5333
2015-06-27 03:30 | 59 | 57.3833 | 64 | 75.5333
2015-06-27 03:45 | 59 | 57.1333 | 64 | 74.5333
2015-06-27 04:00 | 59 | 57.1167 | 63.8833 | 73.7667
2015-06-27 04:15 | 59 | 57.3667 | 63.6333 | 73.2667
2015-06-27 04:30 | 59 | 57.6167 | 63.3833 | 72.7667
2015-06-27 04:45 | 59 | 57.8667 | 63.1333 | 72.2667
2015-06-27 05:00 | 59 | 58 | 63 | 72
2015-06-27 05:15 | 59 | 58 | 63 | 72
2015-06-27 05:30 | 59 | 58 | 63 | 72
2015-06-27 05:45 | 59 | 58 | 63 | 72
2015-06-27 06:00 | 59.1333 | 58.2333 | 63.35 | 72.4667
2015-06-27 06:15 | 59.6333 | 58.7333 | 64.1 | 73.4667
2015-06-27 06:30 | 60.1333 | 59.2333 | 64.85 | 74.4667
2015-06-27 06:45 | 60.6333 | 59.7333 | 65.6 | 75.4667
2015-06-27 07:00 | 61.0667 | 60.35 | 66.5833 | 76.35
2015-06-27 07:15 | 61.3167 | 61.1 | 67.8333 | 77.1
2015-06-27 07:30 | 61.5667 | 61.85 | 69.0833 | 77.85
2015-06-27 07:45 | 61.8167 | 62.6 | 70.3333 | 78.6
2015-06-27 08:00 | 62.2 | 63.5833 | 71.2333 | 79.4667
2015-06-27 08:15 | 62.95 | 64.8333 | 71.7333 | 80.4667
2015-06-27 08:30 | 63.7 | 66.0833 | 72.2333 | 81.4667
2015-06-27 08:45 | 64.45 | 67.3333 | 72.7333 | 82.4667
2015-06-27 09:00 | 65.1333 | 68.5833 | 73.35 | 83.5833
2015-06-27 09:15 | 65.6333 | 69.8333 | 74.1 | 84.8333
2015-06-27 09:30 | 66.1333 | 71.0833 | 74.85 | 86.0833
2015-06-27 09:45 | 66.6333 | 72.3333 | 75.6 | 87.3333
2015-06-27 10:00 | 67.0667 | 73.7 | 76.35 | 88.5833
2015-06-27 10:15 | 67.3167 | 75.2 | 77.1 | 89.8333
2015-06-27 10:30 | 67.5667 | 76.7 | 77.85 | 91.0833
2015-06-27 10:45 | 67.8167 | 78.2 | 78.6 | 92.3333
2015-06-27 11:00 | 68.2 | 78.8833 | 79.2333 | 93.35
2015-06-27 11:15 | 68.95 | 78.6333 | 79.7333 | 94.1
2015-06-27 11:30 | 69.7 | 78.3833 | 80.2333 | 94.85
2015-06-27 11:45 | 70.45 | 78.1333 | 80.7333 | 95.6
2015-06-27 12:00 | 71.0667 | 77.8833 | 81.5833 | 96.2333
2015-06-27 12:15 | 71.3167 | 77.6333 | 82.8333 | 96.7333
2015-06-27 12:30 | 71.5667 | 77.3833 | 84.0833 | 97.2333
2015-06-27 12:45 | 71.8167 | 77.1333 | 85.3333 | 97.7333
2015-06-27 13:00 | 72.1333 | 77.1167 | 86 | 98.2333
2015-06-27 13:15 | 72.6333 | 77.3667 | 86 | 98.7333
2015-06-27 13:30 | 73.1333 | 77.6167 | 86 | 99.2333
2015-06-27 13:45 | 73.6333 | 77.8667 | 86 | 99.7333
2015-06-27 14:00 | 73.9333 | 77.8833 | 86.2333 | 99.8833
2015-06-27 14:15 | 73.6833 | 77.6333 | 86.7333 | 99.6333
2015-06-27 14:30 | 73.4333 | 77.3833 | 87.2333 | 99.3833
2015-06-27 14:45 | 73.1833 | 77.1333 | 87.7333 | 99.1333
2015-06-27 15:00 | 72.9333 | 77.1167 | 86.7273 | 99
2015-06-27 15:15 | 72.6833 | 77.3667 | 82.2188 | 99
2015-06-27 15:30 | 72.4333 | 77.6167 | 77.0625 | 99
2015-06-27 15:45 | 72.1833 | 77.8667 | 73.9412 | 99
2015-06-27 16:00 | 72 | 77.7667 | 73.8167 | 99
2015-06-27 16:15 | 72 | 77.2667 | 75.5667 | 99
2015-06-27 16:30 | 72 | 76.7667 | 77.3167 | 99
2015-06-27 16:45 | 72 | 76.2667 | 79.0667 | 99
2015-06-27 17:00 | 71.9333 | 75.65 | 80 | 98.8833
2015-06-27 17:15 | 71.6833 | 74.9 | 80 | 98.6333
2015-06-27 17:30 | 71.4333 | 74.15 | 80 | 98.3833
2015-06-27 17:45 | 71.1833 | 73.4 | 80 | 98.1333
2015-06-27 18:00 | 70.8 | 72.65 | 79.8833 | 97.7667
2015-06-27 18:15 | 70.05 | 71.9 | 79.6333 | 97.2667
2015-06-27 18:30 | 69.3 | 71.15 | 79.3833 | 96.7667
2015-06-27 18:45 | 68.55 | 70.4 | 79.1333 | 96.2667
2015-06-27 19:00 | 67.8 | 69.8833 | 78.65 | 95.5333
2015-06-27 19:15 | 67.05 | 69.6333 | 77.9 | 94.5333
2015-06-27 19:30 | 66.3 | 69.3833 | 77.15 | 93.5333
2015-06-27 19:45 | 65.55 | 69.1333 | 76.4 | 92.5333
2015-06-27 20:00 | 64.8667 | 68.7667 | 75.7667 | 91.4167
2015-06-27 20:15 | 64.3667 | 68.2667 | 75.2667 | 90.1667
2015-06-27 20:30 | 63.8667 | 67.7667 | 74.7667 | 88.9167
2015-06-27 20:45 | 63.3667 | 67.2667 | 74.2667 | 87.6667
2015-06-27 21:00 | 63 | 66.8833 | 74 | 86.7667
2015-06-27 21:15 | 63 | 66.6333 | 74 | 86.2667
2015-06-27 21:30 | 63 | 66.3833 | 74 | 85.7667
2015-06-27 21:45 | 63 | 66.1333 | 74 | 85.2667
2015-06-27 22:00 | 63 | 65.7667 | 73.7667 | 84.7667
2015-06-27 22:15 | 63 | 65.2667 | 73.2667 | 84.2667
2015-06-27 22:30 | 63 | 64.7667 | 72.7667 | 83.7667
2015-06-27 22:45 | 63 | 64.2667 | 72.2667 | 83.2667
2015-06-27 23:00 | 63 | 64 | 71.7667 | 82.65
2015-06-27 23:15 | 63 | 64 | 71.2667 | 81.9
2015-06-27 23:30 | 63 | 64 | 70.7667 | 81.15
2015-06-27 23:45 | 63 | 64 | 70.2667 | 80.4
2015-06-28 | 63 | 63.8833 | 69.8833 | 79.7667
2015-06-28 00:15 | 63 | 63.6333 | 69.6333 | 79.2667
2015-06-28 00:30 | 63 | 63.3833 | 69.3833 | 78.7667
2015-06-28 00:45 | 63 | 63.1333 | 69.1333 | 78.2667
2015-06-28 01:00 | 63 | 63 | 68.7667 | 77.7667
2015-06-28 01:15 | 63 | 63 | 68.2667 | 77.2667
2015-06-28 01:30 | 63 | 63 | 67.7667 | 76.7667
2015-06-28 01:45 | 63 | 63 | 67.2667 | 76.2667
2015-06-28 02:00 | 62.9333 | 63.1167 | 67 | 76
2015-06-28 02:15 | 62.6833 | 63.3667 | 67 | 76
2015-06-28 02:30 | 62.4333 | 63.6167 | 67 | 76
2015-06-28 02:45 | 62.1833 | 63.8667 | 67 | 76
2015-06-28 03:00 | 61.9333 | 63.8833 | 66.7667 | 75.7667
2015-06-28 03:15 | 61.6833 | 63.6333 | 66.2667 | 75.2667
2015-06-28 03:30 | 61.4333 | 63.3833 | 65.7667 | 74.7667
2015-06-28 03:45 | 61.1833 | 63.1333 | 65.2667 | 74.2667
2015-06-28 04:00 | 61.2667 | 62.8833 | 65 | 73.8833
2015-06-28 04:15 | 62.2667 | 62.6333 | 65 | 73.6333
2015-06-28 04:30 | 62.8667 | 62.3833 | 65 | 73.3833
2015-06-28 04:45 | 62.3667 | 62.1333 | 65 | 73.1333
2015-06-28 05:00 | 62.2667 | 62.5 | 64.8833 | 73
2015-06-28 05:15 | 62.8222 | 63.1739 | 64.6333 | 73
2015-06-28 05:30 | 62.1556 | 63.5 | 64.3833 | 73
2015-06-28 05:45 | 61.4889 | 63.8261 | 64.1333 | 73
2015-06-28 06:00 | 61.0667 | 64.1167 | 64.35 | 73.1167
2015-06-28 06:15 | 61.3167 | 64.3667 | 65.1 | 73.3667
2015-06-28 06:30 | 61.5667 | 64.6167 | 65.85 | 73.6167
2015-06-28 06:45 | 61.8167 | 64.8667 | 66.6 | 73.8667
2015-06-28 07:00 | 62.1333 | 65.1321 | 67.5833 | 74.2333
2015-06-28 07:15 | 62.6333 | 65.4151 | 68.8333 | 74.7333
2015-06-28 07:30 | 63.1333 | 65.6981 | 70.0833 | 75.2333
2015-06-28 07:45 | 63.6333 | 65.9811 | 71.3333 | 75.7333
2015-06-28 08:00 | 64.0667 | 67.35 | 72.2333 | 76.2333
2015-06-28 08:15 | 64.3167 | 68.1 | 72.7333 | 76.7333
2015-06-28 08:30 | 64.5667 | 68.85 | 73.2333 | 77.2333
2015-06-28 08:45 | 64.8167 | 69.6 | 73.7333 | 77.7333
2015-06-28 09:00 | 65.1143 | 70.2333 | 74.35 | 78.4667
2015-06-28 09:15 | 65.5429 | 70.7333 | 75.1 | 79.4667
2015-06-28 09:30 | 65.9714 | 71.2333 | 75.85 | 80.4667
2015-06-28 09:45 | 67.12 | 71.7333 | 76.6 | 81.4667
2015-06-28 10:00 | 68.0667 | 72.1167 | 77.35 | 82.4667
2015-06-28 10:15 | 68.3167 | 72.3667 | 78.1 | 83.4667
2015-06-28 10:30 | 68.5667 | 72.6167 | 78.85 | 84.4667
2015-06-28 10:45 | 68.8167 | 72.8667 | 79.6 | 85.4667
2015-06-28 11:00 | 69.0667 | 73 | 80.35 | 86.2333
2015-06-28 11:15 | 69.3167 | 73 | 81.1 | 86.7333
2015-06-28 11:30 | 69.5667 | 73 | 81.85 | 87.2333
2015-06-28 11:45 | 69.8167 | 73 | 82.6 | 87.7333
2015-06-28 12:00 | 70.0667 | 73.1167 | 83.2333 | 88.4667
2015-06-28 12:15 | 70.3167 | 73.3667 | 83.7333 | 89.4667
2015-06-28 12:30 | 70.5667 | 73.6167 | 84.2333 | 90.4667
2015-06-28 12:45 | 70.8167 | 73.8667 | 84.7333 | 91.4667
2015-06-28 13:00 | 71 | 73.8833 | 85.1167 | 92.2333
2015-06-28 13:15 | 71 | 73.6333 | 85.3667 | 92.7333
2015-06-28 13:30 | 71 | 73.3833 | 85.6167 | 93.2333
2015-06-28 13:45 | 71 | 73.1333 | 85.8667 | 93.7333
2015-06-28 14:00 | 70.9333 | 73 | 86.1167 | 94
2015-06-28 14:15 | 70.6833 | 73 | 86.3667 | 94
2015-06-28 14:30 | 70.4333 | 73 | 86.6167 | 94
2015-06-28 14:45 | 70.1833 | 73 | 86.8667 | 94
2015-06-28 15:00 | 69.8667 | 72.8833 | 87.1167 | 94.1167
2015-06-28 15:15 | 69.3667 | 72.6333 | 87.3667 | 94.3667
2015-06-28 15:30 | 68.8667 | 72.3833 | 87.6167 | 94.6167
2015-06-28 15:45 | 68.3667 | 72.1333 | 87.8667 | 94.8667
2015-06-28 16:00 | 68 | 72 | 87.7667 | 94.8833
2015-06-28 16:15 | 68 | 72 | 87.2667 | 94.6333
2015-06-28 16:30 | 68 | 72 | 86.7667 | 94.3833
2015-06-28 16:45 | 68 | 72 | 86.2667 | 94.1333
2015-06-28 17:00 | 67.8 | 71.7667 | 86.1167 | 94.1167
2015-06-28 17:15 | 67.05 | 71.2667 | 86.3667 | 94.3667
2015-06-28 17:30 | 66.3 | 70.7667 | 86.6167 | 94.6167
2015-06-28 17:45 | 65.55 | 70.2667 | 86.8667 | 94.8667
2015-06-28 18:00 | 64.7838 | 69.65 | 86.7667 | 94.7667
2015-06-28 18:15 | 63.973 | 68.9 | 86.2667 | 94.2667
2015-06-28 18:30 | 63.1622 | 68.15 | 85.7667 | 93.7667
2015-06-28 18:45 | 63 | 67.4 | 85.2667 | 93.2667
2015-06-28 19:00 | 62.9333 | 66.5333 | 84.7667 | 92.5333
2015-06-28 19:15 | 62.6833 | 65.5333 | 84.2667 | 91.5333
2015-06-28 19:30 | 62.4333 | 64.5333 | 83.7667 | 90.5333
2015-06-28 19:45 | 62.1833 | 63.5333 | 83.2667 | 89.5333
2015-06-28 20:00 | 61.8667 | 62.8833 | 82.65 | 88.7667
2015-06-28 20:15 | 61.3667 | 62.6333 | 81.9 | 88.2667
2015-06-28 20:30 | 60.8667 | 62.3833 | 81.15 | 87.7667
2015-06-28 20:45 | 60.3667 | 62.1333 | 80.4 | 87.2667
2015-06-28 21:00 | 60.1212 | 61.8833 | 79.7667 | 86.5333
2015-06-28 21:15 | 60.5758 | 61.6333 | 79.2667 | 85.5333
2015-06-28 21:30 | 60.963 | 61.3833 | 78.7667 | 84.5333
2015-06-28 21:45 | 60.4074 | 61.1333 | 78.2667 | 83.5333
2015-06-28 22:00 | 59.9333 | 61.4516 | 77.7667 | 82.7667
2015-06-28 22:15 | 59.6833 | 62.4194 | 77.2667 | 82.2667
2015-06-28 22:30 | 59.4333 | 62.7931 | 76.7667 | 81.7667
2015-06-28 22:45 | 59.1833 | 62.2759 | 76.2667 | 81.2667
2015-06-28 23:00 | 59 | 62 | 75.7667 | 80.65
2015-06-28 23:15 | 59 | 62 | 75.2667 | 79.9
2015-06-28 23:30 | 59 | 62 | 74.7667 | 79.15
2015-06-28 23:45 | 59 | 62 | 74.2667 | 78.4
2015-06-29 | 59 | 62 | 73.8833 | 77.7667
2015-06-29 00:15 | 59 | 62 | 73.6333 | 77.2667
2015-06-29 00:30 | 59 | 62 | 73.3833 | 76.7667
2015-06-29 00:45 | 59 | 62 | 73.1333 | 76.2667
2015-06-29 01:00 | 58.7419 | 61.8833 | 72.8833 | 75.8833
2015-06-29 01:15 | 57.7742 | 61.6333 | 72.6333 | 75.6333
2015-06-29 01:30 | 57.1034 | 61.3833 | 72.3833 | 75.3833
2015-06-29 01:45 | 57.6207 | 61.1333 | 72.1333 | 75.1333
2015-06-29 02:00 | 58 | 61 | 72 | 74.7667
2015-06-29 02:15 | 58 | 61 | 72 | 74.2667
2015-06-29 02:30 | 58 | 61 | 72 | 73.7667
2015-06-29 02:45 | 58 | 61 | 72 | 73.2667
2015-06-29 03:00 | 57.9 | 60.8833 | 71.8833 | 72.8833
2015-06-29 03:15 | 57.525 | 60.6333 | 71.6333 | 72.6333
2015-06-29 03:30 | 57.15 | 60.3833 | 71.3833 | 72.3833
2015-06-29 03:45 | 57 | 60.1333 | 71.1333 | 72.1333
2015-06-29 04:00 | 57 | 60.1429 | 70.8833 | 71.8833
2015-06-29 04:15 | 57 | 60.449 | 70.6333 | 71.6333
2015-06-29 04:30 | 57 | 60.7551 | 70.3833 | 71.3833
2015-06-29 04:45 | 57 | 60.4545 | 70.1333 | 71.1333
2015-06-29 05:00 | 57 | 59 | 69.65 | 71
2015-06-29 05:15 | 57 | 59 | 68.9 | 71
2015-06-29 05:30 | 57 | 59 | 68.15 | 71
2015-06-29 05:45 | 57 | 59 | 67.4 | 71
2015-06-29 06:00 | 57 | 59.1167 | 67.35 | 71
2015-06-29 06:15 | 57 | 59.3667 | 68.1 | 71
2015-06-29 06:30 | 57 | 59.6167 | 68.85 | 71
2015-06-29 06:45 | 57 | 59.8667 | 69.6 | 71
2015-06-29 07:00 | 57 | 60 | 70.5833 | 71.4667
2015-06-29 07:15 | 57 | 60 | 71.8333 | 72.4667
2015-06-29 07:30 | 57 | 60 | 73.0833 | 73.4667
2015-06-29 07:45 | 57 | 60 | 74.3333 | 74.4667
2015-06-29 08:00 | 57.3902 | 60.35 | 75.4667 | 75.35
2015-06-29 08:15 | 58.8537 | 61.1 | 76.4667 | 76.1
2015-06-29 08:30 | 60.3171 | 61.85 | 77.4667 | 76.85
2015-06-29 08:45 | 61.4211 | 62.6 | 78.4667 | 77.6
2015-06-29 09:00 | 62.4211 | 63.35 | 79.4667 | 78.7
2015-06-29 09:15 | 64 | 64.1 | 80.4667 | 80.2
2015-06-29 09:30 | 64 | 64.85 | 81.4667 | 81.7
2015-06-29 09:45 | 64 | 65.6 | 82.4667 | 83.2
2015-06-29 10:00 | 65 | 66.35 | 83.2333 | 84.1167
2015-06-29 10:15 | 65 | 67.1 | 83.7333 | 84.3667
2015-06-29 10:30 | 65 | 67.85 | 84.2333 | 84.6167
2015-06-29 10:45 | 65 | 68.6 | 84.7333 | 84.8667
2015-06-29 11:00 | 65.1333 | 69.2333 | 85.35 | 85.1167
2015-06-29 11:15 | 65.6333 | 69.7333 | 86.1 | 85.3667
2015-06-29 11:30 | 66.1333 | 70.2333 | 86.85 | 85.6167
2015-06-29 11:45 | 66.6333 | 70.7333 | 87.6 | 85.8667
2015-06-29 12:00 | 67 | 71.35 | 88.1167 | 86.35
2015-06-29 12:15 | 67 | 72.1 | 88.3667 | 87.1
2015-06-29 12:30 | 67 | 72.85 | 88.6167 | 87.85
2015-06-29 12:45 | 67 | 73.6 | 88.8667 | 88.6
2015-06-29 13:00 | 67.0667 | 74.2333 | 89.2333 | 89.5833
2015-06-29 13:15 | 67.3167 | 74.7333 | 89.7333 | 90.8333
2015-06-29 13:30 | 67.5667 | 75.2333 | 90.2333 | 92.0833
2015-06-29 13:45 | 67.8167 | 75.7333 | 90.7333 | 93.3333
2015-06-29 14:00 | 68 | 76.1167 | 91.1167 | 94.2333
2015-06-29 14:15 | 68 | 76.3667 | 91.3667 | 94.7333
2015-06-29 14:30 | 68 | 76.6167 | 91.6167 | 95.2333
2015-06-29 14:45 | 68 | 76.8667 | 91.8667 | 95.7333
2015-06-29 15:00 | 68 | 77 | 92 | 96.2333
2015-06-29 15:15 | 68 | 77 | 92 | 96.7333
2015-06-29 15:30 | 68 | 77 | 92 | 97.2333
2015-06-29 15:45 | 68 | 77 | 92 | 97.7333
2015-06-29 16:00 | 67.8667 | 76.8833 | 92 | 97.8833
2015-06-29 16:15 | 67.3667 | 76.6333 | 92 | 97.6333
2015-06-29 16:30 | 66.8667 | 76.3833 | 92 | 97.3833
2015-06-29 16:45 | 66.3667 | 76.1333 | 92 | 97.1333
2015-06-29 17:00 | 65.8667 | 75.65 | 91.8833 | 96.8833
2015-06-29 17:15 | 65.3667 | 74.9 | 91.6333 | 96.6333
2015-06-29 17:30 | 64.8667 | 74.15 | 91.3833 | 96.3833
2015-06-29 17:45 | 64.3667 | 73.4 | 91.1333 | 96.1333
2015-06-29 18:00 | 63.7333 | 72.65 | 90.7667 | 95.7667
2015-06-29 18:15 | 62.7333 | 71.9 | 90.2667 | 95.2667
2015-06-29 18:30 | 61.7333 | 71.15 | 89.7667 | 94.7667
2015-06-29 18:45 | 60.7333 | 70.4 | 89.2667 | 94.2667
2015-06-29 19:00 | 59.9333 | 69.65 | 88.5333 | 93.65
2015-06-29 19:15 | 59.6833 | 68.9 | 87.5333 | 92.9
2015-06-29 19:30 | 59.4333 | 68.15 | 86.5333 | 92.15
2015-06-29 19:45 | 59.1833 | 67.4 | 85.5333 | 91.4
2015-06-29 20:00 | 59 | 66.7667 | 84.65 | 90.7667
2015-06-29 20:15 | 59 | 66.2667 | 83.9 | 90.2667
2015-06-29 20:30 | 59 | 65.7667 | 83.15 | 89.7667
2015-06-29 20:45 | 59 | 65.2667 | 82.4 | 89.2667
2015-06-29 21:00 | 59 | 64.8833 | 81.7667 | 88.7667
2015-06-29 21:15 | 59 | 64.6333 | 81.2667 | 88.2667
2015-06-29 21:30 | 59 | 64.3833 | 80.7667 | 87.7667
2015-06-29 21:45 | 59 | 64.1333 | 80.2667 | 87.2667
2015-06-29 22:00 | 59 | 63.8833 | 79.7667 | 86.7667
2015-06-29 22:15 | 59 | 63.6333 | 79.2667 | 86.2667
2015-06-29 22:30 | 59 | 63.3833 | 78.7667 | 85.7667
2015-06-29 22:45 | 59 | 63.1333 | 78.2667 | 85.2667
2015-06-29 23:00 | 58.9333 | 63 | 77.8833 | 84.8833
2015-06-29 23:15 | 58.6833 | 63 | 77.6333 | 84.6333
2015-06-29 23:30 | 58.4333 | 63 | 77.3833 | 84.3833
2015-06-29 23:45 | 58.1833 | 63 | 77.1333 | 84.1333
2015-06-30 | 58 | 62.8833 | 76.8833 | 83.7667
2015-06-30 00:15 | 58 | 62.6333 | 76.6333 | 83.2667
2015-06-30 00:30 | 58 | 62.3833 | 76.3833 | 82.7667
2015-06-30 00:45 | 58 | 62.1333 | 76.1333 | 82.2667
2015-06-30 01:00 | 57.9333 | 62 | 75.7667 | 81.65
2015-06-30 01:15 | 57.6833 | 62 | 75.2667 | 80.9
2015-06-30 01:30 | 57.4333 | 62 | 74.7667 | 80.15
2015-06-30 01:45 | 57.1833 | 62 | 74.2667 | 79.4
2015-06-30 02:00 | 56.9333 | 61.7083 | 73.7667 | 78.8833
2015-06-30 02:15 | 56.6833 | 61.0833 | 73.2667 | 78.6333
2015-06-30 02:30 | 56.4333 | 61.3611 | 72.7667 | 78.3833
2015-06-30 02:45 | 56.1833 | 61.7778 | 72.2667 | 78.1333
2015-06-30 03:00 | 55.9333 | 61.8833 | 71.72 | 77.8833
2015-06-30 03:15 | 55.6833 | 61.6333 | 71.12 | 77.6333
2015-06-30 03:30 | 55.4333 | 61.3833 | 70.52 | 77.3833
2015-06-30 03:45 | 55.1833 | 61.1333 | 70.2 | 77.1333
2015-06-30 04:00 | 55 | 61 | 70.8833 | 76.8833
2015-06-30 04:15 | 55 | 61 | 70.6333 | 76.6333
2015-06-30 04:30 | 55 | 61 | 70.3833 | 76.3833
2015-06-30 04:45 | 55 | 61 | 70.1333 | 76.1333
2015-06-30 05:00 | 55.0667 | 61.1167 | 69.6216 | 76.1167
2015-06-30 05:15 | 55.3167 | 61.3667 | 68.8108 | 76.3667
2015-06-30 05:30 | 55.5667 | 61.6167 | 68 | 76.6167
2015-06-30 05:45 | 55.8167 | 61.8667 | 68 | 76.8667
2015-06-30 06:00 | 56.2 | 62.2333 | 67.3636 | 77.5833
2015-06-30 06:15 | 56.95 | 62.7333 | 66 | 78.8333
2015-06-30 06:30 | 57.7 | 63.2333 | 64.6364 | 80.0833
2015-06-30 06:45 | 58.45 | 63.7333 | 63.2727 | 81.3333
2015-06-30 07:00 | 59.2667 | 64.4667 | 63.4667 | 82.35
2015-06-30 07:15 | 60.2667 | 65.4667 | 64.4667 | 83.1
2015-06-30 07:30 | 61.2667 | 66.4667 | 65.4667 | 83.85
2015-06-30 07:45 | 62.2667 | 67.4667 | 66.4667 | 84.6
2015-06-30 08:00 | 63.2 | 68.4667 | 67.4667 | 85.4667
2015-06-30 08:15 | 63.95 | 69.4667 | 68.4667 | 86.4667
2015-06-30 08:30 | 64.7 | 70.4667 | 69.4667 | 87.4667
2015-06-30 08:45 | 65.45 | 71.4667 | 70.4667 | 88.4667
2015-06-30 09:00 | 66.0667 | 72.5833 | 71.4667 | 89.1167
2015-06-30 09:15 | 66.3167 | 73.8333 | 72.4667 | 89.3667
2015-06-30 09:30 | 66.5667 | 75.0833 | 73.4667 | 89.6167
2015-06-30 09:45 | 66.8167 | 76.3333 | 74.4667 | 89.8667
2015-06-30 10:00 | 67.3333 | 77.4667 | 75.7 | 90.7
2015-06-30 10:15 | 68.5833 | 78.4667 | 77.2 | 92.2
2015-06-30 10:30 | 69.8333 | 79.4667 | 78.7 | 93.7
2015-06-30 10:45 | 71.0833 | 80.4667 | 80.2 | 95.2
2015-06-30 11:00 | 72.2 | 81.5833 | 81.1167 | 96.35
2015-06-30 11:15 | 72.95 | 82.8333 | 81.3667 | 97.1
2015-06-30 11:30 | 73.7 | 84.0833 | 81.6167 | 97.85
2015-06-30 11:45 | 74.45 | 85.3333 | 81.8667 | 98.6
2015-06-30 12:00 | 75.1333 | 86.2333 | 82.2333 | 99.4667
2015-06-30 12:15 | 75.6333 | 86.7333 | 82.7333 | 100.4667
2015-06-30 12:30 | 76.1333 | 87.2333 | 83.2333 | 101.4667
2015-06-30 12:45 | 76.6333 | 87.7333 | 83.7333 | 102.4667
2015-06-30 13:00 | 76.9333 | 88.1167 | 84.35 | 103
2015-06-30 13:15 | 76.6833 | 88.3667 | 85.1 | 103
2015-06-30 13:30 | 76.4333 | 88.6167 | 85.85 | 103
2015-06-30 13:45 | 76.1833 | 88.8667 | 86.6 | 103
2015-06-30 14:00 | 76.0667 | 89.35 | 87.2333 | 103.2333
2015-06-30 14:15 | 76.3167 | 90.1 | 87.7333 | 103.7333
2015-06-30 14:30 | 76.5667 | 90.85 | 88.2333 | 104.2333
2015-06-30 14:45 | 76.8167 | 91.6 | 88.7333 | 104.7333
2015-06-30 15:00 | 76.6667 | 91.8833 | 89 | 104.8833
2015-06-30 15:15 | 75.4167 | 91.6333 | 89 | 104.6333
2015-06-30 15:30 | 74.1667 | 91.3833 | 89 | 104.3833
2015-06-30 15:45 | 72.9167 | 91.1333 | 89 | 104.1333
2015-06-30 16:00 | 71.8 | 90.7667 | 88.8833 | 104.1167
2015-06-30 16:15 | 71.05 | 90.2667 | 88.6333 | 104.3667
2015-06-30 16:30 | 70.3 | 89.7667 | 88.3833 | 104.6167
2015-06-30 16:45 | 69.55 | 89.2667 | 88.1333 | 104.8667
2015-06-30 17:00 | 69 | 88.4167 | 87.8833 | 104.8833
2015-06-30 17:15 | 69 | 87.1667 | 87.6333 | 104.6333
2015-06-30 17:30 | 69 | 85.9167 | 87.3833 | 104.3833
2015-06-30 17:45 | 69 | 84.6667 | 87.1333 | 104.1333
2015-06-30 18:00 | 68.8 | 83.5333 | 86.7667 | 103.7667
2015-06-30 18:15 | 68.05 | 82.5333 | 86.2667 | 103.2667
2015-06-30 18:30 | 67.3 | 81.5333 | 85.7667 | 102.7667
2015-06-30 18:45 | 66.55 | 80.5333 | 85.2667 | 102.2667
2015-06-30 19:00 | 65.7333 | 79.7667 | 84.7667 | 101.5333
2015-06-30 19:15 | 64.7333 | 79.2667 | 84.2667 | 100.5333
2015-06-30 19:30 | 63.7333 | 78.7667 | 83.7667 | 99.5333
2015-06-30 19:45 | 62.7333 | 78.2667 | 83.2667 | 98.5333
2015-06-30 20:00 | 61.8667 | 77.5333 | 82.65 | 97.7667
2015-06-30 20:15 | 61.3667 | 76.5333 | 81.9 | 97.2667
2015-06-30 20:30 | 60.8667 | 75.5333 | 81.15 | 96.7667
2015-06-30 20:45 | 60.3667 | 74.5333 | 80.4 | 96.2667
2015-06-30 21:00 | 59.8667 | 73.7667 | 79.5333 | 95.7667
2015-06-30 21:15 | 59.3667 | 73.2667 | 78.5333 | 95.2667
2015-06-30 21:30 | 58.8667 | 72.7667 | 77.5333 | 94.7667
2015-06-30 21:45 | 58.3667 | 72.2667 | 76.5333 | 94.2667
2015-06-30 22:00 | 58.0667 | 71.7667 | 75.7667 | 93.5333
2015-06-30 22:15 | 58.3167 | 71.2667 | 75.2667 | 92.5333
2015-06-30 22:30 | 58.5667 | 70.7667 | 74.7667 | 91.5333
2015-06-30 22:45 | 58.8167 | 70.2667 | 74.2667 | 90.5333
2015-06-30 23:00 | 58.9333 | 69.7667 | 73.7667 | 89.7667
2015-06-30 23:15 | 58.6833 | 69.2667 | 73.2667 | 89.2667
2015-06-30 23:30 | 58.4333 | 68.7667 | 72.7667 | 88.7667
2015-06-30 23:45 | 58.1833 | 68.2667 | 72.2667 | 88.2667
2015-07-01 | 57.9333 | 67.7667 | 71.8833 | 87.8833
2015-07-01 00:15 | 57.6833 | 67.2667 | 71.6333 | 87.6333
2015-07-01 00:30 | 57.4333 | 66.7667 | 71.3833 | 87.3833
2015-07-01 00:45 | 57.1833 | 66.2667 | 71.1333 | 87.1333
2015-07-01 01:00 | 56.9333 | 66 | 70.8833 | 86.65
2015-07-01 01:15 | 56.6833 | 66 | 70.6333 | 85.9
2015-07-01 01:30 | 56.4333 | 66 | 70.3833 | 85.15
2015-07-01 01:45 | 56.1833 | 66 | 70.1333 | 84.4
2015-07-01 02:00 | 56 | 65.8833 | 69.8833 | 83.7667
2015-07-01 02:15 | 56 | 65.6333 | 69.6333 | 83.2667
2015-07-01 02:30 | 56 | 65.3833 | 69.3833 | 82.7667
2015-07-01 02:45 | 56 | 65.1333 | 69.1333 | 82.2667
2015-07-01 03:00 | 56.0667 | 64.7667 | 69.1167 | 82
2015-07-01 03:15 | 56.3167 | 64.2667 | 69.3667 | 82
2015-07-01 03:30 | 56.5667 | 63.7667 | 69.6167 | 82
2015-07-01 03:45 | 56.8167 | 63.2667 | 69.8667 | 82
2015-07-01 04:00 | 56.9333 | 63.1167 | 70 | 81.8833
2015-07-01 04:15 | 56.6833 | 63.3667 | 70 | 81.6333
2015-07-01 04:30 | 56.4333 | 63.6167 | 70 | 81.3833
2015-07-01 04:45 | 56.1833 | 63.8667 | 70 | 81.1333
2015-07-01 05:00 | 56.1333 | 64 | 69.8833 | 80.8833
2015-07-01 05:15 | 56.6333 | 64 | 69.6333 | 80.6333
2015-07-01 05:30 | 57.1333 | 64 | 69.3833 | 80.3833
2015-07-01 05:45 | 57.6333 | 64 | 69.1333 | 80.1333
2015-07-01 06:00 | 58.2 | 64.2333 | 69.1167 | 79.8833
2015-07-01 06:15 | 58.95 | 64.7333 | 69.3667 | 79.6333
2015-07-01 06:30 | 59.7 | 65.2333 | 69.6167 | 79.3833
2015-07-01 06:45 | 60.45 | 65.7333 | 69.8667 | 79.1333
2015-07-01 07:00 | 61.2667 | 66.5833 | 70.4667 | 79.4667
2015-07-01 07:15 | 62.2667 | 67.8333 | 71.4667 | 80.4667
2015-07-01 07:30 | 63.2667 | 69.0833 | 72.4667 | 81.4667
2015-07-01 07:45 | 64.2667 | 70.3333 | 73.4667 | 82.4667
2015-07-01 08:00 | 65.2 | 71.9333 | 74.4667 | 83.7
2015-07-01 08:15 | 65.95 | 73.9333 | 75.4667 | 85.2
2015-07-01 08:30 | 66.7 | 75.9333 | 76.4667 | 86.7
2015-07-01 08:45 | 67.45 | 77.9333 | 77.4667 | 88.2
2015-07-01 09:00 | 68.1333 | 79.7 | 78.35 | 89.4667
2015-07-01 09:15 | 68.6333 | 81.2 | 79.1 | 90.4667
2015-07-01 09:30 | 69.1333 | 82.7 | 79.85 | 91.4667
2015-07-01 09:45 | 69.6333 | 84.2 | 80.6 | 92.4667
2015-07-01 10:00 | 70.2 | 84.8833 | 81.4667 | 93.1167
2015-07-01 10:15 | 70.95 | 84.6333 | 82.4667 | 93.3667
2015-07-01 10:30 | 71.7 | 84.3833 | 83.4667 | 93.6167
2015-07-01 10:45 | 72.45 | 84.1333 | 84.4667 | 93.8667
2015-07-01 11:00 | 72.8 | 83.8833 | 85.2333 | 94.1167
2015-07-01 11:15 | 72.05 | 83.6333 | 85.7333 | 94.3667
2015-07-01 11:30 | 71.3 | 83.3833 | 86.2333 | 94.6167
2015-07-01 11:45 | 70.55 | 83.1333 | 86.7333 | 94.8667
2015-07-01 12:00 | 69.9333 | 83 | 87.4667 | 95.2333
2015-07-01 12:15 | 69.6833 | 83 | 88.4667 | 95.7333
2015-07-01 12:30 | 69.4333 | 83 | 89.4667 | 96.2333
2015-07-01 12:45 | 69.1833 | 83 | 90.4667 | 96.7333
2015-07-01 13:00 | 69.1538 | 82.8833 | 90.7667 | 97.1167
2015-07-01 13:15 | 69.7308 | 82.6333 | 90.2667 | 97.3667
2015-07-01 13:30 | 70.4706 | 82.3833 | 89.7667 | 97.6167
2015-07-01 13:45 | 71.3529 | 82.1333 | 89.2667 | 97.8667
2015-07-01 14:00 | 71.8667 | 81.8833 | 89.1167 | 97.7742
2015-07-01 14:15 | 71.3667 | 81.6333 | 89.3667 | 97.2903
2015-07-01 14:30 | 70.8667 | 81.3833 | 89.6167 | 97.4615
2015-07-01 14:45 | 70.3667 | 81.1333 | 89.8667 | 98.6154
2015-07-01 15:00 | 70 | 80.5333 | 90.1167 | 98
2015-07-01 15:15 | 70 | 79.5333 | 90.3667 | 98.7647
2015-07-01 15:30 | 70 | 78.5333 | 90.6167 | 99.6471
2015-07-01 15:45 | 70 | 77.5333 | 90.8667 | 100.5294
2015-07-01 16:00 | 69.6 | 76.8833 | 90.8833 | 101
2015-07-01 16:15 | 68.1 | 76.6333 | 90.6333 | 101
2015-07-01 16:30 | 66.6 | 76.3833 | 90.3833 | 101
2015-07-01 16:45 | 65.1 | 76.1333 | 90.1333 | 101
2015-07-01 17:00 | 63.8667 | 75.7667 | 89.8833 | 100.8833
2015-07-01 17:15 | 63.3667 | 75.2667 | 89.6333 | 100.6333
2015-07-01 17:30 | 62.8667 | 74.7667 | 89.3833 | 100.3833
2015-07-01 17:45 | 62.3667 | 74.2667 | 89.1333 | 100.1333
2015-07-01 18:00 | 62 | 73.8833 | 88.65 | 99.5333
2015-07-01 18:15 | 62 | 73.6333 | 87.9 | 98.5333
2015-07-01 18:30 | 62 | 73.3833 | 87.15 | 97.5333
2015-07-01 18:45 | 62 | 73.1333 | 86.4 | 96.5333
2015-07-01 19:00 | 62.0667 | 72.8833 | 85.5333 | 95.625
2015-07-01 19:15 | 62.3167 | 72.6333 | 84.5333 | 94.8214
2015-07-01 19:30 | 62.5667 | 72.3833 | 83.5333 | 94.0179
2015-07-01 19:45 | 62.8167 | 72.1333 | 82.5333 | 93.2143
2015-07-01 20:00 | 62.8667 | 72 | 81.65 | 93.1515
2015-07-01 20:15 | 62.3667 | 72 | 80.9 | 91.3333
2015-07-01 20:30 | 61.8667 | 72 | 80.15 | 89.7037
2015-07-01 20:45 | 61.3667 | 72 | 79.4 | 88.5926
2015-07-01 21:00 | 61 | 71.8833 | 78.7667 | 87.6111
2015-07-01 21:15 | 61 | 71.6333 | 78.2667 | 87
2015-07-01 21:30 | 61 | 71.3833 | 77.7667 | 87
2015-07-01 21:45 | 61 | 71.1333 | 77.2667 | 87
2015-07-01 22:00 | 61 | 70.7667 | 76.7667 | 87
2015-07-01 22:15 | 61 | 70.2667 | 76.2667 | 87
2015-07-01 22:30 | 61 | 69.7667 | 75.7667 | 87
2015-07-01 22:45 | 61 | 69.2667 | 75.2667 | 87
2015-07-01 23:00 | 60.9333 | 68.8833 | 74.8833 | 86.7667
2015-07-01 23:15 | 60.6833 | 68.6333 | 74.6333 | 86.2667
2015-07-01 23:30 | 60.4333 | 68.3833 | 74.3833 | 85.7667
2015-07-01 23:45 | 60.1833 | 68.1333 | 74.1333 | 85.2667
2015-07-02 | 59.9333 | 68 | 73.8833 | 84.7667
2015-07-02 00:15 | 59.6833 | 68 | 73.6333 | 84.2667
2015-07-02 00:30 | 59.4333 | 68 | 73.3833 | 83.7667
2015-07-02 00:45 | 59.1833 | 68 | 73.1333 | 83.2667
2015-07-02 01:00 | 59 | 68 | 72.8833 | 83
2015-07-02 01:15 | 59 | 68 | 72.6333 | 83
2015-07-02 01:30 | 59 | 68 | 72.3833 | 83
2015-07-02 01:45 | 59 | 68 | 72.1333 | 83
2015-07-02 02:00 | 58.9333 | 67.8833 | 71.8833 | 82.7667
2015-07-02 02:15 | 58.6833 | 67.6333 | 71.6333 | 82.2667
2015-07-02 02:30 | 58.4333 | 67.3833 | 71.3833 | 81.7667
2015-07-02 02:45 | 58.1833 | 67.1333 | 71.1333 | 81.2667
2015-07-02 03:00 | 58 | 67 | 71 | 81
2015-07-02 03:15 | 58 | 67 | 71 | 81
2015-07-02 03:30 | 58 | 67 | 71 | 81
2015-07-02 03:45 | 58 | 67 | 71 | 81
2015-07-02 04:00 | 58.0667 | 66.7667 | 70.8833 | 80.8833
2015-07-02 04:15 | 58.3167 | 66.2667 | 70.6333 | 80.6333
2015-07-02 04:30 | 58.5667 | 65.7667 | 70.3833 | 80.3833
2015-07-02 04:45 | 58.8167 | 65.2667 | 70.1333 | 80.1333
2015-07-02 05:00 | 59.1333 | 64.8833 | 69.8833 | 80
2015-07-02 05:15 | 59.6333 | 64.6333 | 69.6333 | 80
2015-07-02 05:30 | 60.1333 | 64.3833 | 69.3833 | 80
2015-07-02 05:45 | 60.6333 | 64.1333 | 69.1333 | 80
2015-07-02 06:00 | 60.8667 | 64.1167 | 69.1167 | 79.8833
2015-07-02 06:15 | 60.3667 | 64.3667 | 69.3667 | 79.6333
2015-07-02 06:30 | 59.8667 | 64.6167 | 69.6167 | 79.3833
2015-07-02 06:45 | 59.3667 | 64.8667 | 69.8667 | 79.1333
2015-07-02 07:00 | 59.2667 | 65.2333 | 70.4667 | 79.2333
2015-07-02 07:15 | 60.2667 | 65.7333 | 71.4667 | 79.7333
2015-07-02 07:30 | 61.2667 | 66.2333 | 72.4667 | 80.2333
2015-07-02 07:45 | 62.2667 | 66.7333 | 73.4667 | 80.7333
2015-07-02 08:00 | 63.2 | 67.5833 | 74.35 | 81.4667
2015-07-02 08:15 | 63.95 | 68.8333 | 75.1 | 82.4667
2015-07-02 08:30 | 64.7 | 70.0833 | 75.85 | 83.4667
2015-07-02 08:45 | 65.45 | 71.3333 | 76.6 | 84.4667
2015-07-02 09:00 | 66.1333 | 72.35 | 77.5833 | 85.1167
2015-07-02 09:15 | 66.6333 | 73.1 | 78.8333 | 85.3667
2015-07-02 09:30 | 67.1333 | 73.85 | 80.0833 | 85.6167
2015-07-02 09:45 | 67.6333 | 74.6 | 81.3333 | 85.8667
2015-07-02 10:00 | 68.2 | 75.2333 | 82.2333 | 86.1167
2015-07-02 10:15 | 68.95 | 75.7333 | 82.7333 | 86.3667
2015-07-02 10:30 | 69.7 | 76.2333 | 83.2333 | 86.6167
2015-07-02 10:45 | 70.45 | 76.7333 | 83.7333 | 86.8667
2015-07-02 11:00 | 70.9333 | 77.1167 | 84.2333 | 87.1167
2015-07-02 11:15 | 70.6833 | 77.3667 | 84.7333 | 87.3667
2015-07-02 11:30 | 70.4333 | 77.6167 | 85.2333 | 87.6167
2015-07-02 11:45 | 70.1833 | 77.8667 | 85.7333 | 87.8667
2015-07-02 12:00 | 70 | 78 | 86.2333 | 88.35
2015-07-02 12:15 | 70 | 78 | 86.7333 | 89.1
2015-07-02 12:30 | 70 | 78 | 87.2333 | 89.85
2015-07-02 12:45 | 70 | 78 | 87.7333 | 90.6
2015-07-02 13:00 | 69.1333 | 78 | 88.35 | 91
2015-07-02 13:15 | 69.6333 | 78 | 89.1 | 91
2015-07-02 13:30 | 70.1333 | 78 | 89.85 | 91
2015-07-02 13:45 | 70.6333 | 78 | 90.6 | 91
2015-07-02 14:00 | 71 | 77.7667 | 91.2333 | 91.5833
2015-07-02 14:15 | 71 | 77.2667 | 91.7333 | 92.8333
2015-07-02 14:30 | 71 | 76.7667 | 92.2333 | 94.0833
2015-07-02 14:45 | 71 | 76.2667 | 92.7333 | 95.3333
2015-07-02 15:00 | 70.8667 | 76 | 92.8833 | 95.7667
2015-07-02 15:15 | 70.3667 | 76 | 92.6333 | 95.2667
2015-07-02 15:30 | 69.8667 | 76 | 92.3833 | 94.7667
2015-07-02 15:45 | 69.3667 | 76 | 92.1333 | 94.2667
2015-07-02 16:00 | 68.8667 | 75.65 | 92 | 93.7667
2015-07-02 16:15 | 68.3667 | 74.9 | 92 | 93.2667
2015-07-02 16:30 | 67.8667 | 74.15 | 92 | 92.7667
2015-07-02 16:45 | 67.3667 | 73.4 | 92 | 92.2667
2015-07-02 17:00 | 66.9333 | 72.65 | 91.65 | 91.8833
2015-07-02 17:15 | 66.6833 | 71.9 | 90.9 | 91.6333
2015-07-02 17:30 | 66.4333 | 71.15 | 90.15 | 91.3833
2015-07-02 17:45 | 66.1833 | 70.4 | 89.4 | 91.1333
2015-07-02 18:00 | 65.8667 | 69.7667 | 88.5333 | 91
2015-07-02 18:15 | 65.3667 | 69.2667 | 87.5333 | 91
2015-07-02 18:30 | 64.8667 | 68.7667 | 86.5333 | 91
2015-07-02 18:45 | 64.3667 | 68.2667 | 85.5333 | 91
2015-07-02 19:00 | 63.9333 | 67.7667 | 84.5333 | 90.7667
2015-07-02 19:15 | 63.6833 | 67.2667 | 83.5333 | 90.2667
2015-07-02 19:30 | 63.4333 | 66.7667 | 82.5333 | 89.7667
2015-07-02 19:45 | 63.1833 | 66.2667 | 81.5333 | 89.2667
2015-07-02 20:00 | 62.9333 | 65.8833 | 80.5333 | 88.7667
2015-07-02 20:15 | 62.6833 | 65.6333 | 79.5333 | 88.2667
2015-07-02 20:30 | 62.4333 | 65.3833 | 78.5333 | 87.7667
2015-07-02 20:45 | 62.1833 | 65.1333 | 77.5333 | 87.2667
2015-07-02 21:00 | 62 | 65 | 76.8833 | 86.7667
2015-07-02 21:15 | 62 | 65 | 76.6333 | 86.2667
2015-07-02 21:30 | 62 | 65 | 76.3833 | 85.7667
2015-07-02 21:45 | 62 | 65 | 76.1333 | 85.2667
2015-07-02 22:00 | 61.8947 | 64.8833 | 75.8833 | 84.65
2015-07-02 22:15 | 61.5 | 64.6333 | 75.6333 | 83.9
2015-07-02 22:30 | 61.1053 | 64.3833 | 75.3833 | 83.15
2015-07-02 22:45 | 60.5 | 64.1333 | 75.1333 | 82.4
2015-07-02 23:00 | 60 | 64 | 74.7667 | 81.7667
2015-07-02 23:15 | 60 | 64 | 74.2667 | 81.2667
2015-07-02 23:30 | 60 | 64 | 73.7667 | 80.7667
2015-07-02 23:45 | 60 | 64 | 73.2667 | 80.2667
2015-07-03 | 59.9333 | 64 | 72.8833 | 79.65
2015-07-03 00:15 | 59.6833 | 64 | 72.6333 | 78.9
2015-07-03 00:30 | 59.4333 | 64 | 72.3833 | 78.15
2015-07-03 00:45 | 59.1833 | 64 | 72.1333 | 77.4
2015-07-03 01:00 | 59 | 63.8833 | 72 | 76.8833
2015-07-03 01:15 | 59 | 63.6333 | 72 | 76.6333
2015-07-03 01:30 | 59 | 63.3833 | 72 | 76.3833
2015-07-03 01:45 | 59 | 63.1333 | 72 | 76.1333
2015-07-03 02:00 | 59 | 63 | 71.8833 | 75.8833
2015-07-03 02:15 | 59 | 63 | 71.6333 | 75.6333
2015-07-03 02:30 | 59 | 63 | 71.3833 | 75.3833
2015-07-03 02:45 | 59 | 63 | 71.1333 | 75.1333
2015-07-03 03:00 | 59 | 63.1167 | 70.8833 | 74.7667
2015-07-03 03:15 | 59 | 63.3667 | 70.6333 | 74.2667
2015-07-03 03:30 | 59 | 63.6167 | 70.3833 | 73.7667
2015-07-03 03:45 | 59 | 63.8667 | 70.1333 | 73.2667
2015-07-03 04:00 | 59 | 64 | 70 | 72.8833
2015-07-03 04:15 | 59 | 64 | 70 | 72.6333
2015-07-03 04:30 | 59 | 64 | 70 | 72.3833
2015-07-03 04:45 | 59 | 63.5 | 70 | 72.1333
2015-07-03 05:00 | 59.1333 | 63 | 69.8833 | 72.2333
2015-07-03 05:15 | 59.6333 | 63 | 69.6333 | 72.7333
2015-07-03 05:30 | 60.1333 | 63 | 69.3833 | 73.2333
2015-07-03 05:45 | 60.6333 | 63 | 69.1333 | 73.7333
2015-07-03 06:00 | 61.1333 | 63.2333 | 69.1167 | 74.4667
2015-07-03 06:15 | 61.6333 | 63.7333 | 69.3667 | 75.4667
2015-07-03 06:30 | 62.1333 | 64.2333 | 69.6167 | 76.4667
2015-07-03 06:45 | 62.6333 | 64.7333 | 69.8667 | 77.4667
2015-07-03 07:00 | 63.1333 | 65.2333 | 70.4667 | 78.4667
2015-07-03 07:15 | 63.6333 | 65.7333 | 71.4667 | 79.4667
2015-07-03 07:30 | 64.1333 | 66.2333 | 72.4667 | 80.4667
2015-07-03 07:45 | 64.6333 | 66.7333 | 73.4667 | 81.4667
2015-07-03 08:00 | 65.0667 | 67.35 | 74.35 | 82.4667
2015-07-03 08:15 | 65.3167 | 68.1 | 75.1 | 83.4667
2015-07-03 08:30 | 65.5667 | 68.85 | 75.85 | 84.4667
2015-07-03 08:45 | 65.8167 | 69.6 | 76.6 | 85.4667
2015-07-03 09:00 | 66.0667 | 70.4667 | 77.2333 | 86.4667
2015-07-03 09:15 | 66.3167 | 71.4667 | 77.7333 | 87.4667
2015-07-03 09:30 | 66.5667 | 72.4667 | 78.2333 | 88.4667
2015-07-03 09:45 | 66.8167 | 73.4667 | 78.7333 | 89.4667
2015-07-03 10:00 | 67.2 | 74.1167 | 79 | 90.4667
2015-07-03 10:15 | 67.95 | 74.3667 | 79 | 91.4667
2015-07-03 10:30 | 68.7 | 74.6167 | 79 | 92.4667
2015-07-03 10:45 | 69.45 | 74.8667 | 79.9091 | 93.4667
2015-07-03 11:00 | 70.1333 | 75.35 | 81.2333 | 94.35
2015-07-03 11:15 | 70.6333 | 76.1 | 81.7333 | 95.1
2015-07-03 11:30 | 71.1333 | 76.85 | 82.2333 | 95.85
2015-07-03 11:45 | 71.6333 | 77.6 | 82.7333 | 96.6
2015-07-03 12:00 | 72 | 78.1167 | 83.1167 | 97.1167
2015-07-03 12:15 | 72 | 78.3667 | 83.3667 | 97.3667
2015-07-03 12:30 | 72 | 78.6167 | 83.6167 | 97.6167
2015-07-03 12:45 | 72 | 78.8667 | 83.8667 | 97.8667
2015-07-03 13:00 | 72 | 79.1167 | 84.1167 | 98.35
2015-07-03 13:15 | 72 | 79.3667 | 84.3667 | 99.1
2015-07-03 13:30 | 72 | 79.6167 | 84.6167 | 99.85
2015-07-03 13:45 | 71.0476 | 79.8667 | 84.8667 | 100.6
2015-07-03 14:00 | 69.9333 | 80 | 85.1167 | 101.1167
2015-07-03 14:15 | 69.6833 | 80 | 85.3667 | 101.3667
2015-07-03 14:30 | 69.4333 | 80 | 85.6167 | 101.6167
2015-07-03 14:45 | 69.1833 | 80 | 85.8667 | 101.8667
2015-07-03 15:00 | 68.9333 | 79.8833 | 86 | 101.8833
2015-07-03 15:15 | 68.6833 | 79.6333 | 86 | 101.6333
2015-07-03 15:30 | 68.4333 | 79.3833 | 86 | 101.3833
2015-07-03 15:45 | 68.1833 | 79.1333 | 86 | 101.1333
2015-07-03 16:00 | 67.8667 | 78.5333 | 86 | 100.7667
2015-07-03 16:15 | 67.3667 | 77.5333 | 86 | 100.2667
2015-07-03 16:30 | 66.8667 | 76.5333 | 86 | 99.7667
2015-07-03 16:45 | 66.3667 | 75.5333 | 86 | 99.2667
2015-07-03 17:00 | 65.8667 | 74.65 | 85.8833 | 98.8833
2015-07-03 17:15 | 65.3667 | 73.9 | 85.6333 | 98.6333
2015-07-03 17:30 | 64.8667 | 73.15 | 85.3833 | 98.3833
2015-07-03 17:45 | 64.3667 | 72.4 | 85.1333 | 98.1333
2015-07-03 18:00 | 63.8667 | 71.65 | 84.7667 | 97.8833
2015-07-03 18:15 | 63.3667 | 70.9 | 84.2667 | 97.6333
2015-07-03 18:30 | 62.8667 | 70.15 | 83.7667 | 97.3833
2015-07-03 18:45 | 62.3667 | 69.4 | 83.2667 | 97.1333
2015-07-03 19:00 | 61.8667 | 68.65 | 82.8833 | 96.65
2015-07-03 19:15 | 61.3667 | 67.9 | 82.6333 | 95.9
2015-07-03 19:30 | 60.8667 | 67.15 | 82.3833 | 95.15
2015-07-03 19:45 | 60.3667 | 66.4 | 82.1333 | 94.4
2015-07-03 20:00 | 60 | 65.7667 | 81.65 | 93.65
2015-07-03 20:15 | 60 | 65.2667 | 80.9 | 92.9
2015-07-03 20:30 | 60 | 64.7667 | 80.15 | 92.15
2015-07-03 20:45 | 60 | 64.2667 | 79.4 | 91.4
2015-07-03 21:00 | 60 | 63.8833 | 78.8833 | 90.65
2015-07-03 21:15 | 60 | 63.6333 | 78.6333 | 89.9
2015-07-03 21:30 | 60 | 63.3833 | 78.3833 | 89.15
2015-07-03 21:45 | 60 | 63.1333 | 78.1333 | 88.4
2015-07-03 22:00 | 59.9333 | 62.8833 | 77.7667 | 87.7667
2015-07-03 22:15 | 59.6833 | 62.6333 | 77.2667 | 87.2667
2015-07-03 22:30 | 59.4333 | 62.3833 | 76.7667 | 86.7667
2015-07-03 22:45 | 59.1833 | 62.1333 | 76.2667 | 86.2667
2015-07-03 23:00 | 59 | 62.1207 | 75.8833 | 85.65
2015-07-03 23:15 | 59 | 62.3793 | 75.6333 | 84.9
2015-07-03 23:30 | 59 | 62.6379 | 75.3833 | 84.15
2015-07-03 23:45 | 59 | 62.8966 | 75.1333 | 83.4
2015-07-04 | 58.9333 | 62.4667 | 74.8833 | 82.7667
2015-07-04 00:15 | 58.6833 | 63 | 74.6333 | 82.2667
2015-07-04 00:30 | 58.4333 | 63 | 74.3833 | 81.7667
2015-07-04 00:45 | 58.1833 | 63 | 74.1333 | 81.2667
2015-07-04 01:00 | 58 | 63 | 74 | 80.8833
2015-07-04 01:15 | 58 | 63 | 74 | 80.6333
2015-07-04 01:30 | 58 | 63 | 74 | 80.3833
2015-07-04 01:45 | 58 | 63 | 74 | 80.1333
2015-07-04 02:00 | 58 | 63 | 74 | 79.65
2015-07-04 02:15 | 58 | 63.2549 | 74 | 78.9
2015-07-04 02:30 | 58 | 63.549 | 74 | 78.15
2015-07-04 02:45 | 58 | 63.8431 | 74 | 77.4
2015-07-04 03:00 | 57.7778 | 64 | 73.8833 | 76.8833
2015-07-04 03:15 | 57.0238 | 64 | 73.6333 | 76.6333
2015-07-04 03:30 | 57.381 | 64 | 73.3833 | 76.3833
2015-07-04 03:45 | 57.7381 | 64 | 73.1333 | 76.1333
2015-07-04 04:00 | 58.0667 | 63.8833 | 72.8833 | 75.7667
2015-07-04 04:15 | 58.3167 | 63.6333 | 72.6333 | 75.2667
2015-07-04 04:30 | 58.5667 | 63.3833 | 72.3833 | 74.7667
2015-07-04 04:45 | 58.8167 | 63.1333 | 72.1333 | 74.2667
2015-07-04 05:00 | 59 | 63 | 71.8833 | 74.1167
2015-07-04 05:15 | 59 | 63 | 71.6333 | 74.3667
2015-07-04 05:30 | 59 | 63 | 71.3833 | 74.6167
2015-07-04 05:45 | 59 | 63 | 71.1333 | 74.8667
2015-07-04 06:00 | 59.0667 | 63.1167 | 71.1167 | 75.4667
2015-07-04 06:15 | 59.3167 | 63.3667 | 71.3667 | 76.4667
2015-07-04 06:30 | 59.5667 | 63.6167 | 71.6167 | 77.4667
2015-07-04 06:45 | 59.8167 | 63.8667 | 71.8667 | 78.4667
2015-07-04 07:00 | 60.3 | 64.3111 | 72.35 | 79.4667
2015-07-04 07:15 | 61.425 | 64.9778 | 73.1 | 80.4667
2015-07-04 07:30 | 62.55 | 65.6444 | 73.85 | 81.4667
2015-07-04 07:45 | 63.45 | 66 | 74.6 | 82.4667
2015-07-04 08:00 | 64.2 | 66.5833 | 75.2333 | 83.35
2015-07-04 08:15 | 64.95 | 67.8333 | 75.7333 | 84.1
2015-07-04 08:30 | 65.7 | 69.0833 | 76.2333 | 84.85
2015-07-04 08:45 | 66.45 | 70.3333 | 76.7333 | 85.6
2015-07-04 09:00 | 67.0667 | 71.35 | 77.2333 | 86.4667
2015-07-04 09:15 | 67.3167 | 72.1 | 77.7333 | 87.4667
2015-07-04 09:30 | 67.5667 | 72.85 | 78.2333 | 88.4667
2015-07-04 09:45 | 67.8167 | 73.6 | 78.7333 | 89.4667
2015-07-04 10:00 | 68.0667 | 74.4667 | 79.35 | 90.4667
2015-07-04 10:15 | 68.3167 | 75.4667 | 80.1 | 91.4667
2015-07-04 10:30 | 68.5667 | 76.4667 | 80.85 | 92.4667
2015-07-04 10:45 | 68.8167 | 77.4667 | 81.6 | 93.4667
2015-07-04 11:00 | 69 | 78.1167 | 82.1167 | 94.2333
2015-07-04 11:15 | 69 | 78.3667 | 82.3667 | 94.7333
2015-07-04 11:30 | 69 | 78.6167 | 82.6167 | 95.2333
2015-07-04 11:45 | 69 | 78.8667 | 82.8667 | 95.7333
2015-07-04 12:00 | 69 | 78.7667 | 83.4667 | 96.35
2015-07-04 12:15 | 69 | 78.2667 | 84.4667 | 97.1
2015-07-04 12:30 | 69 | 77.7667 | 85.4667 | 97.85
2015-07-04 12:45 | 69 | 77.2667 | 86.4667 | 98.6
2015-07-04 13:00 | 69.0667 | 77.1167 | 87 | 99.1167
2015-07-04 13:15 | 69.3167 | 77.3667 | 87 | 99.3667
2015-07-04 13:30 | 69.5667 | 77.6167 | 87 | 99.6167
2015-07-04 13:45 | 69.8167 | 77.8667 | 87 | 99.8667
2015-07-04 14:00 | 69.9333 | 78 | 87 | 100.2333
2015-07-04 14:15 | 69.6833 | 78 | 87 | 100.7333
2015-07-04 14:30 | 69.4333 | 78 | 87 | 101.2333
2015-07-04 14:45 | 69.1833 | 78 | 87 | 101.7333
2015-07-04 15:00 | 68.9333 | 77.8833 | 87.1167 | 102
2015-07-04 15:15 | 68.6833 | 77.6333 | 87.3667 | 102
2015-07-04 15:30 | 68.4333 | 77.3833 | 87.6167 | 102
2015-07-04 15:45 | 68.1833 | 77.1333 | 87.8667 | 102
2015-07-04 16:00 | 67.9333 | 76.7667 | 88 | 102
2015-07-04 16:15 | 67.6833 | 76.2667 | 88 | 102
2015-07-04 16:30 | 67.4333 | 75.7667 | 88 | 102
2015-07-04 16:45 | 67.1833 | 75.2667 | 88 | 102
2015-07-04 17:00 | 66.8667 | 74.65 | 87.7667 | 101.8833
2015-07-04 17:15 | 66.3667 | 73.9 | 87.2667 | 101.6333
2015-07-04 17:30 | 65.8667 | 73.15 | 86.7667 | 101.3833
2015-07-04 17:45 | 65.3667 | 72.4 | 86.2667 | 101.1333
2015-07-04 18:00 | 64.8667 | 71.65 | 85.8833 | 100.65
2015-07-04 18:15 | 64.3667 | 70.9 | 85.6333 | 99.9
2015-07-04 18:30 | 63.8667 | 70.15 | 85.3833 | 99.15
2015-07-04 18:45 | 63.3667 | 69.4 | 85.1333 | 98.4
2015-07-04 19:00 | 62.8667 | 68.65 | 84.7667 | 97.5333
2015-07-04 19:15 | 62.3667 | 67.9 | 84.2667 | 96.5333
2015-07-04 19:30 | 61.8667 | 67.15 | 83.7667 | 95.5333
2015-07-04 19:45 | 61.3667 | 66.4 | 83.2667 | 94.5333
2015-07-04 20:00 | 61 | 65.7667 | 82.7667 | 93.5333
2015-07-04 20:15 | 61 | 65.2667 | 82.2667 | 92.5333
2015-07-04 20:30 | 61 | 64.7667 | 81.7667 | 91.5333
2015-07-04 20:45 | 61 | 64.2667 | 81.2667 | 90.5333
2015-07-04 21:00 | 61 | 63.8833 | 80.7667 | 89.65
2015-07-04 21:15 | 61 | 63.6333 | 80.2667 | 88.9
2015-07-04 21:30 | 61 | 63.3833 | 79.7667 | 88.15
2015-07-04 21:45 | 61 | 63.1333 | 79.2667 | 87.4
2015-07-04 22:00 | 61 | 63 | 78.8833 | 86.5333
2015-07-04 22:15 | 61 | 63 | 78.6333 | 85.5333
2015-07-04 22:30 | 61 | 63 | 78.3833 | 84.5333
2015-07-04 22:45 | 61 | 63 | 78.1333 | 83.5333
2015-07-04 23:00 | 61 | 62.8833 | 77.8833 | 82.65
2015-07-04 23:15 | 61 | 62.6333 | 77.6333 | 81.9
2015-07-04 23:30 | 61 | 62.3833 | 77.3833 | 81.15
2015-07-04 23:45 | 61 | 62.1333 | 77.1333 | 80.4
2015-07-05 | 61 | 62 | 76.8833 | 79.65
2015-07-05 00:15 | 61 | 62 | 76.6333 | 78.9
2015-07-05 00:30 | 61 | 62 | 76.3833 | 78.15
2015-07-05 00:45 | 61 | 62 | 76.1333 | 77.4
2015-07-05 01:00 | 61 | 62 | 76 | 76.8833
2015-07-05 01:15 | 61 | 62 | 76 | 76.6333
2015-07-05 01:30 | 60.9286 | 62 | 76 | 76.3833
2015-07-05 01:45 | 60.3929 | 62 | 76 | 76.1333
2015-07-05 02:00 | 60.1538 | 62.2917 | 75.7667 | 75.8833
2015-07-05 02:15 | 60.7308 | 62.9167 | 75.2667 | 75.6333
2015-07-05 02:30 | 61 | 62.6389 | 74.7667 | 75.3833
2015-07-05 02:45 | 61 | 62.2222 | 74.2667 | 75.1333
2015-07-05 03:00 | 61 | 61.875 | 74 | 74.7667
2015-07-05 03:15 | 61 | 61.6071 | 74 | 74.2667
2015-07-05 03:30 | 61 | 61.3393 | 74 | 73.7667
2015-07-05 03:45 | 61 | 61.0714 | 74 | 73.2667
2015-07-05 04:00 | 60.9333 | 61 | 74 | 72.8833
2015-07-05 04:15 | 60.6833 | 61 | 74 | 72.6333
2015-07-05 04:30 | 60.4333 | 60.6053 | 74 | 72.3833
2015-07-05 04:45 | 60.1833 | 60.2105 | 74 | 72.1333
2015-07-05 05:00 | 60 | 60.1707 | 73.8833 | 72.1167
2015-07-05 05:15 | 60 | 60.5366 | 73.6333 | 72.3667
2015-07-05 05:30 | 60 | 60.9024 | 73.3833 | 72.6167
2015-07-05 05:45 | 60 | 61 | 73.1333 | 72.8667
2015-07-05 06:00 | 60.2 | 61.2333 | 73 | 73.35
2015-07-05 06:15 | 60.95 | 61.7333 | 73 | 74.1
2015-07-05 06:30 | 61.7 | 62.2333 | 73 | 74.85
2015-07-05 06:45 | 62.45 | 62.7333 | 73 | 75.6
2015-07-05 07:00 | 63.2 | 63.4667 | 73.4667 | 76.35
2015-07-05 07:15 | 63.95 | 64.4667 | 74.4667 | 77.1
2015-07-05 07:30 | 64.7 | 65.4667 | 75.4667 | 77.85
2015-07-05 07:45 | 65.45 | 66.4667 | 76.4667 | 78.6
2015-07-05 08:00 | 66.2 | 67.35 | 77.5833 | 79.4667
2015-07-05 08:15 | 66.95 | 68.1 | 78.8333 | 80.4667
2015-07-05 08:30 | 67.7 | 68.85 | 80.0833 | 81.4667
2015-07-05 08:45 | 68.45 | 69.6 | 81.3333 | 82.4667
2015-07-05 09:00 | 69.0667 | 70.4667 | 82.4667 | 83.35
2015-07-05 09:15 | 69.3167 | 71.4667 | 83.4667 | 84.1
2015-07-05 09:30 | 69.5667 | 72.4667 | 84.4667 | 84.85
2015-07-05 09:45 | 69.8167 | 73.4667 | 85.4667 | 85.6
2015-07-05 10:00 | 70.2 | 74.35 | 86.2593 | 86.35
2015-07-05 10:15 | 70.95 | 75.1 | 86.8148 | 87.1
2015-07-05 10:30 | 71.7 | 75.85 | 87.3704 | 87.85
2015-07-05 10:45 | 72.45 | 76.6 | 87.9259 | 88.6
2015-07-05 11:00 | 73 | 77.2333 | 87.5333 | 89.2333
2015-07-05 11:15 | 73 | 77.7333 | 87 | 89.7333
2015-07-05 11:30 | 73 | 78.2333 | 87 | 90.2333
2015-07-05 11:45 | 73 | 78.7333 | 87 | 90.7333
2015-07-05 12:00 | 73.2 | 78.8833 | 86 | 91.35
2015-07-05 12:15 | 73.95 | 78.6333 | 87 | 92.1
2015-07-05 12:30 | 74.7 | 78.3833 | 88 | 92.85
2015-07-05 12:45 | 75.45 | 78.1333 | 89 | 93.6
2015-07-05 13:00 | 75.8667 | 78 | 88 | 94.35
2015-07-05 13:15 | 75.3667 | 78 | 88.8491 | 95.1
2015-07-05 13:30 | 74.8667 | 78 | 89.6981 | 95.85
2015-07-05 13:45 | 74.3667 | 78 | 90.5472 | 96.6
2015-07-05 14:00 | 73.9333 | 77.8833 | 90.6111 | 96.8833
2015-07-05 14:15 | 73.6833 | 77.6333 | 89.68 | 96.6333
2015-07-05 14:30 | 73.4333 | 77.3833 | 88.48 | 96.3833
2015-07-05 14:45 | 73.1833 | 77.1333 | 88.5294 | 96.1333
2015-07-05 15:00 | 73 | 76.8833 | 88.65 | 96.1167
2015-07-05 15:15 | 73 | 76.6333 | 87.9 | 96.3667
2015-07-05 15:30 | 73 | 76.3833 | 87.15 | 96.6167
2015-07-05 15:45 | 73 | 76.1333 | 86.4 | 96.8667
2015-07-05 16:00 | 72.8 | 75.7667 | 86.2333 | 96.8833
2015-07-05 16:15 | 72.05 | 75.2667 | 86.7333 | 96.6333
2015-07-05 16:30 | 71.3 | 74.7667 | 87.2333 | 96.3833
2015-07-05 16:45 | 70.55 | 74.2667 | 87.7333 | 96.1333
2015-07-05 17:00 | 69.6667 | 73.7667 | 88 | 95.8833
2015-07-05 17:15 | 68.4167 | 73.2667 | 88 | 95.6333
2015-07-05 17:30 | 67.1667 | 72.7667 | 88 | 95.3833
2015-07-05 17:45 | 65.9167 | 72.2667 | 88 | 95.1333
2015-07-05 18:00 | 64.8667 | 71.5333 | 87.5333 | 94.7667
2015-07-05 18:15 | 64.3667 | 70.5333 | 86.5333 | 94.2667
2015-07-05 18:30 | 63.8667 | 69.5333 | 85.5333 | 93.7667
2015-07-05 18:45 | 63.3667 | 68.5333 | 84.5333 | 93.2667
2015-07-05 19:00 | 63 | 67.5333 | 83.65 | 92.5333
2015-07-05 19:15 | 63 | 66.5333 | 82.9 | 91.5333
2015-07-05 19:30 | 63 | 65.5333 | 82.15 | 90.5333
2015-07-05 19:45 | 63 | 64.5333 | 81.4 | 89.5333
2015-07-05 20:00 | 62.9333 | 63.8833 | 80.7667 | 88.5333
2015-07-05 20:15 | 62.6833 | 63.6333 | 80.2667 | 87.5333
2015-07-05 20:30 | 62.4333 | 63.3833 | 79.7667 | 86.5333
2015-07-05 20:45 | 62.1833 | 63.1333 | 79.2667 | 85.5333
2015-07-05 21:00 | 62 | 63 | 78.8833 | 84.65
2015-07-05 21:15 | 62 | 63 | 78.6333 | 83.9
2015-07-05 21:30 | 62 | 63 | 78.3833 | 83.15
2015-07-05 21:45 | 62 | 63 | 78.1333 | 82.4
2015-07-05 22:00 | 62 | 63 | 78 | 81.65
2015-07-05 22:15 | 62 | 63 | 78 | 80.9
2015-07-05 22:30 | 62 | 63 | 78 | 80.15
2015-07-05 22:45 | 62 | 63 | 78 | 79.4
2015-07-05 23:00 | 61.9333 | 63 | 77.8833 | 78.65
2015-07-05 23:15 | 61.6833 | 63 | 77.6333 | 77.9
2015-07-05 23:30 | 61.4333 | 63 | 77.3833 | 77.15
2015-07-05 23:45 | 61.1833 | 63 | 77.1333 | 76.4
2015-07-06 | 61.0667 | 63 | 77 | 75.7667
2015-07-06 00:15 | 61.3167 | 63 | 77 | 75.2667
2015-07-06 00:30 | 61.5667 | 63 | 77 | 74.7667
2015-07-06 00:45 | 61.8167 | 63 | 77 | 74.2667
2015-07-06 01:00 | 61.9333 | 63 | 76.8833 | 73.8833
2015-07-06 01:15 | 61.6833 | 63 | 76.6333 | 73.6333
2015-07-06 01:30 | 61.4333 | 63 | 76.3833 | 73.3833
2015-07-06 01:45 | 61.1833 | 63 | 76.1333 | 73.1333
2015-07-06 02:00 | 61 | 63 | 75.8833 | 73
2015-07-06 02:15 | 61 | 63 | 75.6333 | 73
2015-07-06 02:30 | 61 | 63 | 75.3833 | 73
2015-07-06 02:45 | 61 | 63 | 75.1333 | 73
2015-07-06 03:00 | 61 | 63 | 74.8833 | 72.7667
2015-07-06 03:15 | 61 | 63 | 74.6333 | 72.2667
2015-07-06 03:30 | 61 | 63 | 74.3833 | 71.7667
2015-07-06 03:45 | 61 | 63 | 74.1333 | 71.2667
2015-07-06 04:00 | 61 | 63 | 73.7667 | 70.7667
2015-07-06 04:15 | 61 | 63 | 73.2667 | 70.2667
2015-07-06 04:30 | 61 | 63 | 72.7667 | 69.7667
2015-07-06 04:45 | 61 | 63 | 72.2667 | 69.2667
2015-07-06 05:00 | 61 | 63 | 72.1167 | 69.2333
2015-07-06 05:15 | 61 | 63 | 72.3667 | 69.7333
2015-07-06 05:30 | 61 | 63 | 72.6167 | 70.2333
2015-07-06 05:45 | 61 | 63 | 72.8667 | 70.7333
2015-07-06 06:00 | 61 | 63.1167 | 73.2333 | 71.2333
2015-07-06 06:15 | 61 | 63.3667 | 73.7333 | 71.7333
2015-07-06 06:30 | 61 | 63.6167 | 74.2333 | 72.2333
2015-07-06 06:45 | 61 | 63.8667 | 74.7333 | 72.7333
2015-07-06 07:00 | 61.0667 | 64.1167 | 75.7 | 73.4667
2015-07-06 07:15 | 61.3167 | 64.3667 | 77.2 | 74.4667
2015-07-06 07:30 | 61.5667 | 64.6167 | 78.7 | 75.4667
2015-07-06 07:45 | 61.8167 | 64.8667 | 80.2 | 76.4667
2015-07-06 08:00 | 62.1379 | 65.2 | 81.4667 | 77.2333
2015-07-06 08:15 | 62.6552 | 65.6286 | 82.4667 | 77.7333
2015-07-06 08:30 | 63.1724 | 66.16 | 83.4667 | 78.2333
2015-07-06 08:45 | 63.6897 | 67.36 | 84.4667 | 78.7333
2015-07-06 09:00 | 64.2 | 68.2333 | 85.1167 | 79.35
2015-07-06 09:15 | 64.95 | 68.7333 | 85.3667 | 80.1
2015-07-06 09:30 | 65.7 | 69.2333 | 85.6167 | 80.85
2015-07-06 09:45 | 66.45 | 69.7333 | 85.8667 | 81.6
2015-07-06 10:00 | 67.1333 | 70.2333 | 86.4667 | 82.35
2015-07-06 10:15 | 67.6333 | 70.7333 | 87.4667 | 83.1
2015-07-06 10:30 | 68.1333 | 71.2333 | 88.4667 | 83.85
2015-07-06 10:45 | 68.6333 | 71.7333 | 89.4667 | 84.6
2015-07-06 11:00 | 69.0667 | 72.35 | 90.35 | 85.35
2015-07-06 11:15 | 69.3167 | 73.1 | 91.1 | 86.1
2015-07-06 11:30 | 69.5667 | 73.85 | 91.85 | 86.85
2015-07-06 11:45 | 69.8167 | 74.6 | 92.6 | 87.6
2015-07-06 12:00 | 70.0667 | 75.1167 | 93.2333 | 88.35
2015-07-06 12:15 | 70.3167 | 75.3667 | 93.7333 | 89.1
2015-07-06 12:30 | 70.5667 | 75.6167 | 94.2333 | 89.85
2015-07-06 12:45 | 70.8167 | 75.8667 | 94.7333 | 90.6
2015-07-06 13:00 | 70.9333 | 76 | 92.8125 | 91.2333
2015-07-06 13:15 | 70.6833 | 76 | 89.1429 | 91.7333
2015-07-06 13:30 | 70.4333 | 76 | 87 | 92.2333
2015-07-06 13:45 | 70.1833 | 76 | 83.087 | 92.7333
2015-07-06 14:00 | 70 | 75.8833 | 80.2759 | 93
2015-07-06 14:15 | 70 | 75.6333 | 78.7241 | 93
2015-07-06 14:30 | 70 | 75.3833 | 77.1724 | 93
2015-07-06 14:45 | 70 | 75.1333 | 75.6207 | 93
2015-07-06 15:00 | 70.0667 | 74.8833 | 74.7667 | 93.1167
2015-07-06 15:15 | 70.3167 | 74.6333 | 74.2667 | 93.3667
2015-07-06 15:30 | 70.5667 | 74.3833 | 73.7667 | 93.6167
2015-07-06 15:45 | 70.8167 | 74.1333 | 73.2667 | 93.8667
2015-07-06 16:00 | 70.9333 | 73.8833 | 73.2333 | 94
2015-07-06 16:15 | 70.6833 | 73.6333 | 73.7333 | 94
2015-07-06 16:30 | 70.4333 | 73.3833 | 74.2333 | 94
2015-07-06 16:45 | 70.1833 | 73.1333 | 74.7333 | 94
2015-07-06 17:00 | 69.8667 | 73 | 75.2333 | 93.65
2015-07-06 17:15 | 69.3667 | 73 | 75.7333 | 92.9
2015-07-06 17:30 | 68.8667 | 73 | 76.2333 | 92.15
2015-07-06 17:45 | 68.3667 | 73 | 76.7333 | 91.4
2015-07-06 18:00 | 67.8667 | 72.7667 | 77.1167 | 90.65
2015-07-06 18:15 | 67.3667 | 72.2667 | 77.3667 | 89.9
2015-07-06 18:30 | 66.8667 | 71.7667 | 77.6167 | 89.15
2015-07-06 18:45 | 66.3667 | 71.2667 | 77.8667 | 88.4
2015-07-06 19:00 | 65.8 | 70.65 | 78 | 87.5333
2015-07-06 19:15 | 65.05 | 69.9 | 78 | 86.5333
2015-07-06 19:30 | 64.3 | 69.15 | 78 | 85.5333
2015-07-06 19:45 | 63.55 | 68.4 | 78 | 84.5333
2015-07-06 20:00 | 63 | 67.8833 | 77.65 | 83.7667
2015-07-06 20:15 | 63 | 67.6333 | 76.9 | 83.2667
2015-07-06 20:30 | 63 | 67.3833 | 76.15 | 82.7667
2015-07-06 20:45 | 63 | 67.1333 | 75.4 | 82.2667
2015-07-06 21:00 | 63 | 66.7667 | 74.8833 | 81.7667
2015-07-06 21:15 | 63 | 66.2667 | 74.6333 | 81.2667
2015-07-06 21:30 | 63 | 65.7667 | 74.3833 | 80.7667
2015-07-06 21:45 | 63 | 65.2667 | 74.1333 | 80.2667
2015-07-06 22:00 | 63 | 64.8833 | 74.2333 | 79.65
2015-07-06 22:15 | 63 | 64.6333 | 74.7333 | 78.9
2015-07-06 22:30 | 63 | 64.3833 | 75.2333 | 78.15
2015-07-06 22:45 | 63 | 64.1333 | 75.7333 | 77.4
2015-07-06 23:00 | 63 | 64 | 75.8833 | 76.7667
2015-07-06 23:15 | 63 | 64 | 75.6333 | 76.2667
2015-07-06 23:30 | 63 | 64 | 75.3833 | 75.7667
2015-07-06 23:45 | 63 | 64 | 75.1333 | 75.2667
2015-07-07 | 63 | 64 | 74.8833 | 74.8833
2015-07-07 00:15 | 63 | 64 | 74.6333 | 74.6333
2015-07-07 00:30 | 63 | 64 | 74.3833 | 74.3833
2015-07-07 00:45 | 63 | 64 | 74.1333 | 74.1333
2015-07-07 01:00 | 62.9333 | 64 | 74 | 73.65
2015-07-07 01:15 | 62.6833 | 64 | 74 | 72.9
2015-07-07 01:30 | 62.4333 | 64 | 74 | 72.15
2015-07-07 01:45 | 62.1833 | 64 | 74 | 71.4
2015-07-07 02:00 | 62 | 63.8833 | 73.7667 | 70.8833
2015-07-07 02:15 | 62 | 63.6333 | 73.2667 | 70.6333
2015-07-07 02:30 | 62 | 63.3833 | 72.7667 | 70.3833
2015-07-07 02:45 | 62 | 63.1333 | 72.2667 | 70.1333
2015-07-07 03:00 | 62.0667 | 63 | 72 | 69.8833
2015-07-07 03:15 | 62.3167 | 63 | 72 | 69.6333
2015-07-07 03:30 | 62.5667 | 63 | 71.6667 | 69.3833
2015-07-07 03:45 | 62.8167 | 63 | 71.5385 | 69.1333
2015-07-07 04:00 | 63 | 63 | 71 | 68.8833
2015-07-07 04:15 | 63 | 63 | 71 | 68.6333
2015-07-07 04:30 | 63 | 63 | 71 | 68.3833
2015-07-07 04:45 | 63 | 63 | 71 | 68.1333
2015-07-07 05:00 | 63.069 | 63.1167 | 71 | 68
2015-07-07 05:15 | 63.3276 | 63.3667 | 71 | 68
2015-07-07 05:30 | 63.5862 | 63.6167 | 71 | 68
2015-07-07 05:45 | 63.8448 | 63.8667 | 71 | 68
2015-07-07 06:00 | 64 | 64.1167 | 71 | 68.35
2015-07-07 06:15 | 64 | 64.3667 | 71 | 69.1
2015-07-07 06:30 | 64 | 64.6167 | 71 | 69.85
2015-07-07 06:45 | 64 | 64.8667 | 71 | 70.6
2015-07-07 07:00 | 65.0667 | 65.1167 | 71.2414 | 71.4667
2015-07-07 07:15 | 65.3167 | 65.3667 | 71.7586 | 72.4667
2015-07-07 07:30 | 65.5667 | 65.6167 | 72.2759 | 73.4667
2015-07-07 07:45 | 65.8167 | 65.8667 | 72.7931 | 74.4667
2015-07-07 08:00 | 66.1333 | 66.1167 | 72.1167 | 75.4667
2015-07-07 08:15 | 66.6333 | 66.3667 | 72.3667 | 76.4667
2015-07-07 08:30 | 67.1333 | 66.6167 | 72.6167 | 77.4667
2015-07-07 08:45 | 67.6333 | 66.8667 | 72.8667 | 78.4667
2015-07-07 09:00 | 68.0667 | 67.35 | 73.7292 | 79.2333
2015-07-07 09:15 | 68.3167 | 68.1 | 75.2917 | 79.7333
2015-07-07 09:30 | 68.5667 | 68.85 | 76.8542 | 80.2333
2015-07-07 09:45 | 68.8167 | 69.6 | 77.6 | 80.7333
2015-07-07 10:00 | 69.2069 | 70 | 78 | 81.35
2015-07-07 10:15 | 69.9828 | 70.5745 | 78.566 | 82.1
2015-07-07 10:30 | 70.7586 | 71.5319 | 79.1321 | 82.85
2015-07-07 10:45 | 71.5345 | 72.4894 | 79.6981 | 83.6
2015-07-07 11:00 | 72 | 73.35 | 80 | 84.35
2015-07-07 11:15 | 72 | 74.1 | 80 | 85.1
2015-07-07 11:30 | 72 | 74.85 | 80.2581 | 85.85
2015-07-07 11:45 | 72 | 75.6 | 80.7419 | 86.6
2015-07-07 12:00 | 71.9333 | 76 | 81.4667 | 87.2333
2015-07-07 12:15 | 71.6833 | 76 | 82.4667 | 87.7333
2015-07-07 12:30 | 71.4333 | 76 | 83.4667 | 88.2333
2015-07-07 12:45 | 71.1833 | 76 | 84.4667 | 88.7333
2015-07-07 13:00 | 71.1333 | 76 | 85.1167 | 89
2015-07-07 13:15 | 71.6333 | 76 | 85.3667 | 89
2015-07-07 13:30 | 72.1333 | 76 | 85.6167 | 89
2015-07-07 13:45 | 72.6333 | 76 | 85.8667 | 89
2015-07-07 14:00 | 72.9333 | 76 | 85.7667 | 89.35
2015-07-07 14:15 | 72.6833 | 76 | 85.2667 | 90.1
2015-07-07 14:30 | 72.4333 | 76 | 84.7667 | 90.85
2015-07-07 14:45 | 72.1833 | 76 | 84.2667 | 91.6
2015-07-07 15:00 | 71.8 | 75.7667 | 84.5833 | 92.1167
2015-07-07 15:15 | 71.05 | 75.2667 | 85.8333 | 92.3667
2015-07-07 15:30 | 70.3 | 74.7667 | 87.0833 | 92.6167
2015-07-07 15:45 | 69.55 | 74.2667 | 88.3333 | 92.8667
2015-07-07 16:00 | 68.907 | 73.7667 | 88.5333 | 93
2015-07-07 16:15 | 68.5581 | 73.2667 | 87.5333 | 93
2015-07-07 16:30 | 68.2093 | 72.7667 | 86.5333 | 93
2015-07-07 16:45 | 67.6471 | 72.2667 | 85.5333 | 93
2015-07-07 17:00 | 66.8667 | 71.7667 | 84.8833 | 92.8833
2015-07-07 17:15 | 66.3667 | 71.2667 | 84.6333 | 92.6333
2015-07-07 17:30 | 65.8667 | 70.7667 | 84.3833 | 92.3833
2015-07-07 17:45 | 65.3667 | 70.2667 | 84.1333 | 92.1333
2015-07-07 18:00 | 64.8 | 69.65 | 83.8833 | 91.5333
2015-07-07 18:15 | 64.05 | 68.9 | 83.6333 | 90.5333
2015-07-07 18:30 | 63.3 | 68.15 | 83.3833 | 89.5333
2015-07-07 18:45 | 62.55 | 67.4 | 83.1333 | 88.5333
2015-07-07 19:00 | 61.875 | 66.7667 | 82.0345 | 87.65
2015-07-07 19:15 | 61.4062 | 66.2667 | 79.9655 | 86.9
2015-07-07 19:30 | 61 | 65.7667 | 78.4839 | 86.15
2015-07-07 19:45 | 61 | 65.2667 | 77.5161 | 85.4
2015-07-07 20:00 | 61 | 64.7667 | 76.7667 | 84.65
2015-07-07 20:15 | 61 | 64.2667 | 76.2667 | 83.9
2015-07-07 20:30 | 61 | 63.7667 | 75.7667 | 83.15
2015-07-07 20:45 | 61 | 63.2667 | 75.2667 | 82.4
2015-07-07 21:00 | 61 | 62.8833 | 74.8833 | 81.65
2015-07-07 21:15 | 61 | 62.6333 | 74.6333 | 80.9
2015-07-07 21:30 | 61 | 62.3833 | 74.3833 | 80.15
2015-07-07 21:45 | 61 | 62.1333 | 74.1333 | 79.4
2015-07-07 22:00 | 61 | 62 | 73.8833 | 78.65
2015-07-07 22:15 | 61 | 62 | 73.6333 | 77.9
2015-07-07 22:30 | 61.3158 | 62 | 73.3833 | 77.15
2015-07-07 22:45 | 61.7105 | 62 | 73.1333 | 76.4
2015-07-07 23:00 | 62 | 61.8833 | 72.8833 | 75.65
2015-07-07 23:15 | 62 | 61.6333 | 72.6333 | 74.9
2015-07-07 23:30 | 62 | 61.3833 | 72.3833 | 74.15
2015-07-07 23:45 | 62 | 61.1333 | 72.1333 | 73.4
2015-07-08 | 61.9333 | 61 | 71.8833 | 72.7667
2015-07-08 00:15 | 61.6833 | 61 | 71.6333 | 72.2667
2015-07-08 00:30 | 61.4333 | 61 | 71.3833 | 71.7667
2015-07-08 00:45 | 61.1833 | 61 | 71.1333 | 71.2667
2015-07-08 01:00 | 61 | 60.8833 | 70.8833 | 70.7667
2015-07-08 01:15 | 61 | 60.6333 | 70.6333 | 70.2667
2015-07-08 01:30 | 61 | 60.3833 | 70.3833 | 69.7667
2015-07-08 01:45 | 61 | 60.1333 | 70.1333 | 69.2667
2015-07-08 02:00 | 61 | 60.5 | 70.1167 | 68.8833
2015-07-08 02:15 | 61 | 61 | 70.3667 | 68.6333
2015-07-08 02:30 | 61 | 61 | 70.6167 | 68.3833
2015-07-08 02:45 | 61 | 61 | 70.8667 | 68.1333
2015-07-08 03:00 | 61 | 60.8833 | 70.7667 | 68
2015-07-08 03:15 | 61 | 60.6333 | 70.2667 | 68
2015-07-08 03:30 | 61 | 60.3833 | 69.7667 | 68
2015-07-08 03:45 | 61 | 60.1333 | 69.2667 | 68
2015-07-08 04:00 | 61 | 60.1167 | 68.8833 | 67.7667
2015-07-08 04:15 | 61 | 60.3667 | 68.6333 | 67.2667
2015-07-08 04:30 | 61 | 60.6167 | 68.3833 | 66.7667
2015-07-08 04:45 | 61 | 60.8667 | 68.1333 | 66.2667
2015-07-08 05:00 | 61 | 61 | 67.8833 | 66.1167
2015-07-08 05:15 | 61 | 61 | 67.6333 | 66.3667
2015-07-08 05:30 | 61 | 61 | 67.3833 | 66.6167
2015-07-08 05:45 | 61 | 61 | 67.1333 | 66.8667
2015-07-08 06:00 | 61 | 61.1167 | 67.1321 | 67.35
2015-07-08 06:15 | 61 | 61.3667 | 67.4151 | 68.1
2015-07-08 06:30 | 61 | 61.6167 | 67.6981 | 68.85
2015-07-08 06:45 | 61 | 61.8667 | 67.9811 | 69.6
2015-07-08 07:00 | 61 | 62 | 68.2333 | 70.2333
2015-07-08 07:15 | 61 | 62 | 68.7333 | 70.7333
2015-07-08 07:30 | 61 | 62 | 69.2333 | 71.2333
2015-07-08 07:45 | 61 | 62 | 69.7333 | 71.7333
2015-07-08 08:00 | 61.1333 | 62.1167 | 70 | 72.35
2015-07-08 08:15 | 61.6333 | 62.3667 | 70.125 | 73.1
2015-07-08 08:30 | 62.1333 | 62.6167 | 71 | 73.85
2015-07-08 08:45 | 62.6333 | 62.8667 | 71.6 | 74.6
2015-07-08 09:00 | 63 | 63.1167 | 73.3 | 75.4667
2015-07-08 09:15 | 63 | 63.3667 | 73 | 76.4667
2015-07-08 09:30 | 63 | 63.6167 | 73 | 77.4667
2015-07-08 09:45 | 63 | 63.8667 | 74.1111 | 78.4667
2015-07-08 10:00 | 63.0667 | 64.1167 | 75.3111 | 79.35
2015-07-08 10:15 | 63.3167 | 64.3667 | 75.9778 | 80.1
2015-07-08 10:30 | 63.5667 | 64.6167 | 76.6444 | 80.85
2015-07-08 10:45 | 63.8167 | 64.8667 | 77.4667 | 81.6
2015-07-08 11:00 | 64.1333 | 65.175 | 78.2333 | 82.35
2015-07-08 11:15 | 64.6333 | 65.55 | 78.7333 | 83.1
2015-07-08 11:30 | 65.1333 | 65.925 | 79.2333 | 83.85
2015-07-08 11:45 | 65.6333 | 67.8 | 79.7333 | 84.6
2015-07-08 12:00 | 66.1333 | 69.4667 | 80.2333 | 85.35
2015-07-08 12:15 | 66.6333 | 70.4667 | 80.7333 | 86.1
2015-07-08 12:30 | 67.1333 | 71.4667 | 81.2333 | 86.85
2015-07-08 12:45 | 67.6333 | 72.4667 | 81.7333 | 87.6
2015-07-08 13:00 | 68 | 72.65 | 82.5833 | 88.2333
2015-07-08 13:15 | 68 | 71.9 | 83.8333 | 88.7333
2015-07-08 13:30 | 68 | 71.15 | 85.0833 | 89.2333
2015-07-08 13:45 | 68 | 70.4 | 86.3333 | 89.7333
2015-07-08 14:00 | 67.8 | 69.7667 | 87 | 90.1167
2015-07-08 14:15 | 67.05 | 69.2667 | 87 | 90.3667
2015-07-08 14:30 | 66.3 | 68.7667 | 87 | 90.6167
2015-07-08 14:45 | 65.55 | 68.2667 | 87 | 90.8667
2015-07-08 15:00 | 65.1111 | 68.1167 | 87.2333 | 90.8833
2015-07-08 15:15 | 65.5278 | 68.3667 | 87.7333 | 90.6333
2015-07-08 15:30 | 65.9444 | 68.6167 | 88.2333 | 90.3833
2015-07-08 15:45 | 66 | 68.8667 | 88.7333 | 90.1333
2015-07-08 16:00 | 65.7333 | 69 | 88.8833 | 90
2015-07-08 16:15 | 64.7333 | 69 | 88.6333 | 90
2015-07-08 16:30 | 63.7333 | 69 | 88.3833 | 90
2015-07-08 16:45 | 62.7333 | 69 | 88.1333 | 90
2015-07-08 17:00 | 61.9333 | 68.7667 | 87.8833 | 89.7667
2015-07-08 17:15 | 61.6833 | 68.2667 | 87.6333 | 89.2667
2015-07-08 17:30 | 61.4333 | 67.7667 | 87.3833 | 88.7667
2015-07-08 17:45 | 61.1833 | 67.2667 | 87.1333 | 88.2667
2015-07-08 18:00 | 61.1739 | 66.7667 | 86.5333 | 87.65
2015-07-08 18:15 | 61.8261 | 66.2667 | 85.5333 | 86.9
2015-07-08 18:30 | 62.4783 | 65.7667 | 84.5333 | 86.15
2015-07-08 18:45 | 62.5714 | 65.2667 | 83.5333 | 85.4
2015-07-08 19:00 | 61.0667 | 64.7667 | 82.7667 | 84.3
2015-07-08 19:15 | 61.3167 | 64.2667 | 82.2667 | 82.8
2015-07-08 19:30 | 61.5667 | 63.7667 | 81.7667 | 81.3
2015-07-08 19:45 | 61.8167 | 63.2667 | 81.2667 | 79.8
2015-07-08 20:00 | 61.9333 | 62.8833 | 80.65 | 78.4167
2015-07-08 20:15 | 61.6833 | 62.6333 | 79.9 | 77.1667
2015-07-08 20:30 | 61.4333 | 62.3833 | 79.15 | 75.9167
2015-07-08 20:45 | 61.1833 | 62.1333 | 78.4 | 74.6667
2015-07-08 21:00 | 61.0667 | 62 | 77.7667 | 73.7667
2015-07-08 21:15 | 61.3167 | 62 | 77.2667 | 73.2667
2015-07-08 21:30 | 61.5667 | 62 | 76.7667 | 72.7667
2015-07-08 21:45 | 61.8167 | 62 | 76.2667 | 72.2667
2015-07-08 22:00 | 61.9333 | 62.1321 | 76 | 71.65
2015-07-08 22:15 | 61.6833 | 62.4151 | 76 | 70.9
2015-07-08 22:30 | 61.4333 | 62.6981 | 76 | 70.15
2015-07-08 22:45 | 61.1833 | 62.9811 | 76 | 69.4
2015-07-08 23:00 | 60.9333 | 61 | 75.8833 | 68.7667
2015-07-08 23:15 | 60.6833 | 61 | 75.6333 | 68.2667
2015-07-08 23:30 | 60.4333 | 61 | 75.3833 | 67.7667
2015-07-08 23:45 | 60.1833 | 61 | 75.1333 | 67.2667
2015-07-09 | 60 | 61 | 74.8833 | 66.8833
2015-07-09 00:15 | 60 | 61 | 74.6333 | 66.6333
2015-07-09 00:30 | 60 | 61 | 74.3833 | 66.3833
2015-07-09 00:45 | 60 | 61 | 74.1333 | 66.1333
2015-07-09 01:00 | 60 | 61 | 74 | 65.8833
2015-07-09 01:15 | 60 | 61 | 74 | 65.6333
2015-07-09 01:30 | 60 | 61 | 74 | 65.3833
2015-07-09 01:45 | 60 | 61 | 74 | 65.1333
2015-07-09 02:00 | 60.069 | 61 | 74 | 64.8833
2015-07-09 02:15 | 60.3276 | 61 | 74 | 64.6333
2015-07-09 02:30 | 60.5862 | 61 | 74 | 64.3833
2015-07-09 02:45 | 60.8448 | 61 | 74 | 64.1333
2015-07-09 03:00 | 59 | 61 | 73.8833 | 63.8833
2015-07-09 03:15 | 59 | 61 | 73.6333 | 63.6333
2015-07-09 03:30 | 59 | 61 | 73.3833 | 63.3833
2015-07-09 03:45 | 59 | 61 | 73.1333 | 63.1333
2015-07-09 04:00 | 59 | 61 | 73 | 63
2015-07-09 04:15 | 59 | 61 | 73 | 63
2015-07-09 04:30 | 59 | 61 | 73 | 63
2015-07-09 04:45 | 59 | 61 | 73 | 63
2015-07-09 05:00 | 59 | 61 | 72.7667 | 63
2015-07-09 05:15 | 59 | 61 | 72.2667 | 63
2015-07-09 05:30 | 59 | 61 | 71.7667 | 63
2015-07-09 05:45 | 59 | 61 | 71.2667 | 63
2015-07-09 06:00 | 59.1379 | 61.1167 | 71.1167 | 63.2333
2015-07-09 06:15 | 59.6552 | 61.3667 | 71.3667 | 63.7333
2015-07-09 06:30 | 60.1724 | 61.6167 | 71.6167 | 64.2333
2015-07-09 06:45 | 60.6897 | 61.8667 | 71.8667 | 64.7333
2015-07-09 07:00 | 60.069 | 62.1167 | 72.35 | 65
2015-07-09 07:15 | 60.3276 | 62.3667 | 73.1 | 65
2015-07-09 07:30 | 60.5862 | 62.6167 | 73.85 | 65
2015-07-09 07:45 | 60.8448 | 62.8667 | 74.6 | 65
2015-07-09 08:00 | 61.1333 | 63.2333 | 75.35 | 65.2121
2015-07-09 08:15 | 61.6333 | 63.7333 | 76.1 | 65.6667
2015-07-09 08:30 | 62.1333 | 64.2333 | 76.85 | 66.1481
2015-07-09 08:45 | 62.6333 | 64.7333 | 77.6 | 66.7037
2015-07-09 09:00 | 63 | 65.1167 | 78.4667 | 67.175
2015-07-09 09:15 | 63 | 65.3667 | 79.4667 | 67.55
2015-07-09 09:30 | 63 | 65.6167 | 80.4667 | 67.925
2015-07-09 09:45 | 63 | 65.8667 | 81.4667 | 68.6
2015-07-09 10:00 | 63.2 | 66.1167 | 82.35 | 69.1167
2015-07-09 10:15 | 63.95 | 66.3667 | 83.1 | 69.3667
2015-07-09 10:30 | 64.7 | 66.6167 | 83.85 | 69.6167
2015-07-09 10:45 | 65.45 | 66.8667 | 84.6 | 69.8667
2015-07-09 11:00 | 66 | 67.1167 | 85.35 | 70.4667
2015-07-09 11:15 | 66 | 67.3667 | 86.1 | 71.4667
2015-07-09 11:30 | 66.2778 | 67.6167 | 86.85 | 72.4667
2015-07-09 11:45 | 66.6944 | 67.8667 | 87.6 | 73.4667
2015-07-09 12:00 | 66.931 | 68.5833 | 88.35 | 74.4667
2015-07-09 12:15 | 66.6724 | 69.8333 | 89.1 | 75.4667
2015-07-09 12:30 | 66.4138 | 71.0833 | 89.85 | 76.4667
2015-07-09 12:45 | 66.1552 | 72.3333 | 90.6 | 77.4667
2015-07-09 13:00 | 66.9333 | 72.8833 | 90.8833 | 78.35
2015-07-09 13:15 | 66.6833 | 72.6333 | 90.6333 | 79.1
2015-07-09 13:30 | 66.4333 | 72.3833 | 90.3833 | 79.85
2015-07-09 13:45 | 66.1833 | 72.1333 | 90.1333 | 80.6
2015-07-09 14:00 | 65.8 | 71.7667 | 88.3529 | 80.8833
2015-07-09 14:15 | 65.05 | 71.2667 | 86.381 | 80.6333
2015-07-09 14:30 | 64.3 | 70.7667 | 89.2381 | 80.3833
2015-07-09 14:45 | 63.55 | 70.2667 | 88.8421 | 80.1333
2015-07-09 15:00 | 62.9333 | 70 | 87.5 | 80.2333
2015-07-09 15:15 | 62.6833 | 70 | 86.4286 | 80.7333
2015-07-09 15:30 | 62.4333 | 70 | 85.3571 | 81.2333
2015-07-09 15:45 | 62.1833 | 70 | 84.4444 | 81.7333
2015-07-09 16:00 | 62.0667 | 69.7667 | 84 | 82.1167
2015-07-09 16:15 | 62.3167 | 69.2667 | 84 | 82.3667
2015-07-09 16:30 | 62.5667 | 68.7667 | 84 | 82.6167
2015-07-09 16:45 | 62.8167 | 68.2667 | 84 | 82.8667
2015-07-09 17:00 | 63 | 67.65 | 84 | 83
2015-07-09 17:15 | 63 | 66.9 | 84 | 83
2015-07-09 17:30 | 63 | 66.15 | 84 | 83
2015-07-09 17:45 | 63 | 65.4 | 84 | 83
2015-07-09 18:00 | 62.9333 | 65 | 83.7667 | 82.7667
2015-07-09 18:15 | 62.6833 | 65 | 83.2667 | 82.2667
2015-07-09 18:30 | 62.4333 | 65 | 82.7667 | 81.7667
2015-07-09 18:45 | 62.1833 | 65 | 82.2667 | 81.2667
2015-07-09 19:00 | 62 | 64.8833 | 81.65 | 80.7667
2015-07-09 19:15 | 62 | 64.6333 | 80.9 | 80.2667
2015-07-09 19:30 | 62 | 64.3833 | 80.15 | 79.7667
2015-07-09 19:45 | 62 | 64.1333 | 79.4 | 79.2667
2015-07-09 20:00 | 61.9333 | 64 | 79 | 78.4167
2015-07-09 20:15 | 61.6833 | 64 | 79 | 77.1667
2015-07-09 20:30 | 61.4333 | 64 | 79 | 75.9167
2015-07-09 20:45 | 61.1833 | 64 | 79 | 74.6667
2015-07-09 21:00 | 61 | 64 | 79 | 73.7667
2015-07-09 21:15 | 61 | 64 | 79 | 73.2667
2015-07-09 21:30 | 61 | 64 | 79 | 72.7667
2015-07-09 21:45 | 61 | 64 | 79 | 72.2667
2015-07-09 22:00 | 61 | 63.8833 | 79 | 71.7667
2015-07-09 22:15 | 61 | 63.6333 | 79 | 71.2667
2015-07-09 22:30 | 61 | 63.3833 | 79 | 70.7667
2015-07-09 22:45 | 61 | 63.1333 | 79 | 70.2667
2015-07-09 23:00 | 61 | 63 | 78.8833 | 69.7667
2015-07-09 23:15 | 61 | 63 | 78.6333 | 69.2667
2015-07-09 23:30 | 61 | 63 | 78.3833 | 68.7667
2015-07-09 23:45 | 61 | 63 | 78.1333 | 68.2667
2015-07-10 | 61 | 62.8833 | 77.8833 | 67.8833
2015-07-10 00:15 | 61 | 62.6333 | 77.6333 | 67.6333
2015-07-10 00:30 | 61 | 62.3833 | 77.3833 | 67.3833
2015-07-10 00:45 | 61 | 62.1333 | 77.1333 | 67.1333
2015-07-10 01:00 | 61 | 62 | 76.8833 | 66.8833
2015-07-10 01:15 | 61 | 62 | 76.6333 | 66.6333
2015-07-10 01:30 | 61 | 62 | 76.3833 | 66.3833
2015-07-10 01:45 | 61 | 62 | 76.1333 | 66.1333
2015-07-10 02:00 | 61 | 62 | 75.8833 | 66
2015-07-10 02:15 | 61 | 62 | 75.6333 | 66
2015-07-10 02:30 | 61 | 62 | 75.3833 | 66
2015-07-10 02:45 | 61 | 62 | 75.1333 | 66
2015-07-10 03:00 | 61 | 62 | 74.7667 | 66
2015-07-10 03:15 | 61 | 62 | 74.2667 | 66
2015-07-10 03:30 | 61 | 62 | 73.7667 | 66
2015-07-10 03:45 | 61 | 62 | 73.2667 | 66
2015-07-10 04:00 | 60.9333 | 62.1321 | 73 | 66
2015-07-10 04:15 | 60.6833 | 62.4151 | 73 | 66
2015-07-10 04:30 | 60.4333 | 62.6981 | 73 | 66
2015-07-10 04:45 | 60.1833 | 62.9811 | 73 | 66
2015-07-10 05:00 | 60.0667 | 62 | 72.8833 | 66
2015-07-10 05:15 | 60.3167 | 62 | 72.6333 | 66
2015-07-10 05:30 | 60.5667 | 62 | 72.3833 | 66
2015-07-10 05:45 | 60.8167 | 62 | 72.1333 | 66
2015-07-10 06:00 | 61.0667 | 62.1167 | 72 | 66
2015-07-10 06:15 | 61.3167 | 62.3667 | 72 | 66
2015-07-10 06:30 | 61.5667 | 62.6167 | 72 | 66
2015-07-10 06:45 | 61.8167 | 62.8667 | 72 | 66
2015-07-10 07:00 | 62.0667 | 63 | 72.1167 | 66.2333
2015-07-10 07:15 | 62.3167 | 63 | 72.3667 | 66.7333
2015-07-10 07:30 | 62.5667 | 63 | 72.6167 | 67.2333
2015-07-10 07:45 | 62.8167 | 63 | 72.8667 | 67.7333
2015-07-10 08:00 | 63.1333 | 63.2333 | 73.4667 | 68.2333
2015-07-10 08:15 | 63.6333 | 63.7333 | 74.4667 | 68.7333
2015-07-10 08:30 | 64.1333 | 64.2333 | 75.4667 | 69.2333
2015-07-10 08:45 | 64.6333 | 64.7333 | 76.4667 | 69.7333
2015-07-10 09:00 | 65 | 65 | 77 | 70.35
2015-07-10 09:15 | 65 | 65 | 77 | 71.1
2015-07-10 09:30 | 65 | 65 | 77 | 71.85
2015-07-10 09:45 | 65 | 65 | 77 | 72.6
2015-07-10 10:00 | 64.4286 | 65.2333 | 77.7 | 73
2015-07-10 10:15 | 64.4528 | 65.7333 | 79.2 | 73
2015-07-10 10:30 | 65.0189 | 66.2333 | 80.7 | 73
2015-07-10 10:45 | 65.5849 | 66.7333 | 82.2 | 73
2015-07-10 11:00 | 66.0667 | 67.4118 | 83.35 | 73.2333
2015-07-10 11:15 | 66.3167 | 68.3488 | 84.1 | 73.7333
2015-07-10 11:30 | 66.5667 | 69.3953 | 84.85 | 74.2333
2015-07-10 11:45 | 66.8167 | 70.4419 | 85.6 | 74.7333
2015-07-10 12:00 | 67.1333 | 71 | 86.1167 | 75.35
2015-07-10 12:15 | 67.6333 | 71 | 86.3667 | 76.1
2015-07-10 12:30 | 68.1333 | 71 | 86.6167 | 76.85
2015-07-10 12:45 | 68.6333 | 71 | 86.8667 | 77.6
2015-07-10 13:00 | 69.0667 | 71.1167 | 87 | 78.35
2015-07-10 13:15 | 69.3167 | 71.3667 | 87 | 79.1
2015-07-10 13:30 | 69.5667 | 71.6167 | 87 | 79.85
2015-07-10 13:45 | 69.8167 | 71.8667 | 87 | 80.6
2015-07-10 14:00 | 69.9333 | 72 | 87 | 81.4667
2015-07-10 14:15 | 69.6833 | 72 | 87 | 82.4667
2015-07-10 14:30 | 69.4333 | 72 | 87 | 83.4667
2015-07-10 14:45 | 69.1833 | 72 | 87 | 84.4667
2015-07-10 15:00 | 69.0667 | 72 | 87 | 85.1167
2015-07-10 15:15 | 69.3167 | 72 | 87 | 85.3667
2015-07-10 15:30 | 69.5667 | 72 | 87 | 85.6167
2015-07-10 15:45 | 69.8167 | 72 | 87 | 85.8667
2015-07-10 16:00 | 69.9333 | 71.65 | 87.2333 | 85.8833
2015-07-10 16:15 | 69.6833 | 70.9 | 87.7333 | 85.6333
2015-07-10 16:30 | 69.4333 | 70.15 | 88.2333 | 85.3833
2015-07-10 16:45 | 69.1833 | 69.4 | 88.7333 | 85.1333
2015-07-10 17:00 | 68.8 | 69.1167 | 88.8833 | 84.8833
2015-07-10 17:15 | 68.05 | 69.3667 | 88.6333 | 84.6333
2015-07-10 17:30 | 67.3 | 69.6167 | 88.3833 | 84.3833
2015-07-10 17:45 | 66.55 | 69.8667 | 88.1333 | 84.1333
2015-07-10 18:00 | 65.8667 | 69.65 | 87.8833 | 83.65
2015-07-10 18:15 | 65.3667 | 68.9 | 87.6333 | 82.9
2015-07-10 18:30 | 64.8667 | 68.15 | 87.3833 | 82.15
2015-07-10 18:45 | 64.3667 | 67.4 | 87.1333 | 81.4
2015-07-10 19:00 | 63.9333 | 66.7667 | 86.7667 | 80.7667
2015-07-10 19:15 | 63.6833 | 66.2667 | 86.2667 | 80.2667
2015-07-10 19:30 | 63.4333 | 65.7667 | 85.7667 | 79.7667
2015-07-10 19:45 | 63.1833 | 65.2667 | 85.2667 | 79.2667
2015-07-10 20:00 | 63 | 64.8833 | 84.7667 | 78.7667
2015-07-10 20:15 | 63 | 64.6333 | 84.2667 | 78.2667
2015-07-10 20:30 | 63 | 64.3833 | 83.7667 | 77.7667
2015-07-10 20:45 | 63 | 64.1333 | 83.2667 | 77.2667
2015-07-10 21:00 | 62.9333 | 63.8833 | 82.8833 | 76.7667
2015-07-10 21:15 | 62.6833 | 63.6333 | 82.6333 | 76.2667
2015-07-10 21:30 | 62.4333 | 63.3833 | 82.3833 | 75.7667
2015-07-10 21:45 | 62.1833 | 63.1333 | 82.1333 | 75.2667
2015-07-10 22:00 | 62 | 62.8833 | 81.8833 | 74.65
2015-07-10 22:15 | 62 | 62.6333 | 81.6333 | 73.9
2015-07-10 22:30 | 62 | 62.3833 | 81.3833 | 73.15
2015-07-10 22:45 | 62 | 62.1333 | 81.1333 | 72.4
2015-07-10 23:00 | 62 | 61.8833 | 80.8833 | 71.8833
2015-07-10 23:15 | 62 | 61.6333 | 80.6333 | 71.6333
2015-07-10 23:30 | 62 | 61.3833 | 80.3833 | 71.3833
2015-07-10 23:45 | 62 | 61.1333 | 80.1333 | 71.1333
2015-07-11 | 61.9333 | 61 | 79.65 | 70.65
2015-07-11 00:15 | 61.6833 | 61 | 78.9 | 69.9
2015-07-11 00:30 | 61.4333 | 61 | 78.15 | 69.15
2015-07-11 00:45 | 61.1833 | 61 | 77.4 | 68.4
2015-07-11 01:00 | 61 | 61.1167 | 76.7667 | 67.8833
2015-07-11 01:15 | 61 | 61.3667 | 76.2667 | 67.6333
2015-07-11 01:30 | 61 | 61.6167 | 75.7667 | 67.3833
2015-07-11 01:45 | 61 | 61.8667 | 75.2667 | 67.1333
2015-07-11 02:00 | 61 | 61.65 | 74.8833 | 66.8833
2015-07-11 02:15 | 61 | 60.9 | 74.6333 | 66.6333
2015-07-11 02:30 | 61 | 60.15 | 74.3833 | 66.3833
2015-07-11 02:45 | 61 | 59.4 | 74.1333 | 66.1333
2015-07-11 03:00 | 61 | 59 | 73.8833 | 65.7667
2015-07-11 03:15 | 61 | 59 | 73.6333 | 65.2667
2015-07-11 03:30 | 61 | 59 | 73.3833 | 64.7667
2015-07-11 03:45 | 61 | 59 | 73.1333 | 64.2667
2015-07-11 04:00 | 61 | 59 | 72.7667 | 63.8833
2015-07-11 04:15 | 61 | 59 | 72.2667 | 63.6333
2015-07-11 04:30 | 61 | 59 | 71.7667 | 63.3833
2015-07-11 04:45 | 61 | 59 | 71.2667 | 63.1333
2015-07-11 05:00 | 61 | 59 | 70.8833 | 63.1167
2015-07-11 05:15 | 61.1087 | 59 | 70.6333 | 63.3667
2015-07-11 05:30 | 61.4348 | 59 | 70.3833 | 63.6167
2015-07-11 05:45 | 61.7609 | 59.5 | 70.1333 | 63.8667
2015-07-11 06:00 | 62.0667 | 60.2333 | 70 | 64.35
2015-07-11 06:15 | 62.3167 | 60.7333 | 70 | 65.1
2015-07-11 06:30 | 62.5667 | 61.2333 | 70 | 65.85
2015-07-11 06:45 | 62.8167 | 61.7333 | 70 | 66.6
2015-07-11 07:00 | 63.2 | 62.2333 | 70.4667 | 67.4667
2015-07-11 07:15 | 63.95 | 62.7333 | 71.4667 | 68.4667
2015-07-11 07:30 | 64.7 | 63.2333 | 72.4667 | 69.4667
2015-07-11 07:45 | 65.45 | 63.7333 | 73.4667 | 70.4667
2015-07-11 08:00 | 66.0667 | 64.1167 | 74.4667 | 71.4667
2015-07-11 08:15 | 66.3167 | 64.3667 | 75.4667 | 72.4667
2015-07-11 08:30 | 66.5667 | 64.6167 | 76.4667 | 73.4667
2015-07-11 08:45 | 66.8167 | 64.8667 | 77.9333 | 74.4667
2015-07-11 09:00 | 67.0667 | 65.7 | 79.5833 | 75.4667
2015-07-11 09:15 | 67.3167 | 66.48 | 80.8333 | 76.4667
2015-07-11 09:30 | 67.5667 | 67.08 | 82.0833 | 77.4667
2015-07-11 09:45 | 67.8167 | 67.68 | 83.3333 | 78.4667
2015-07-11 10:00 | 68.0667 | 68.35 | 84.35 | 79.2333
2015-07-11 10:15 | 68.3167 | 69.1 | 85.1 | 79.7333
2015-07-11 10:30 | 68.5667 | 69.85 | 85.85 | 80.2333
2015-07-11 10:45 | 68.8167 | 70.6 | 86.6 | 80.7333
2015-07-11 11:00 | 69.0667 | 71.2333 | 87.2333 | 81.4667
2015-07-11 11:15 | 69.3167 | 71.7333 | 87.7333 | 82.4667
2015-07-11 11:30 | 69.5667 | 72.2333 | 88.2333 | 83.4667
2015-07-11 11:45 | 69.8167 | 72.7333 | 88.7333 | 84.4667
2015-07-11 12:00 | 70.0667 | 73 | 89.1167 | 85.35
2015-07-11 12:15 | 70.3167 | 73 | 89.3667 | 86.1
2015-07-11 12:30 | 70.5667 | 73 | 89.6167 | 86.85
2015-07-11 12:45 | 70.8167 | 73 | 89.8667 | 87.6
2015-07-11 13:00 | 71 | 73.1167 | 90.35 | 88
2015-07-11 13:15 | 71 | 73.3667 | 91.1 | 88
2015-07-11 13:30 | 71 | 73.6167 | 91.85 | 88
2015-07-11 13:45 | 71 | 73.8667 | 92.6 | 88
2015-07-11 14:00 | 70.9333 | 74 | 93.2333 | 88.1167
2015-07-11 14:15 | 70.6833 | 74 | 93.7333 | 88.3667
2015-07-11 14:30 | 70.4333 | 74 | 94.2333 | 88.6167
2015-07-11 14:45 | 70.1833 | 74 | 94.7333 | 88.8667
2015-07-11 15:00 | 69.9333 | 74 | 95 | 89.1167
2015-07-11 15:15 | 69.6833 | 74 | 95 | 89.3667
2015-07-11 15:30 | 69.4333 | 74 | 95 | 89.6167
2015-07-11 15:45 | 69.1833 | 74 | 95 | 89.8667
2015-07-11 16:00 | 69 | 73.65 | 95 | 89.8833
2015-07-11 16:15 | 69 | 72.9 | 95 | 89.6333
2015-07-11 16:30 | 69 | 72.15 | 95 | 89.3833
2015-07-11 16:45 | 69 | 71.4 | 95 | 89.1333
2015-07-11 17:00 | 68.8667 | 70.8833 | 94.7667 | 89.1167
2015-07-11 17:15 | 68.3667 | 70.6333 | 94.2667 | 89.3667
2015-07-11 17:30 | 67.8667 | 70.3833 | 93.7667 | 89.6167
2015-07-11 17:45 | 67.3667 | 70.1333 | 93.2667 | 89.8667
2015-07-11 18:00 | 66.8667 | 69.7667 | 92.5333 | 89.7667
2015-07-11 18:15 | 66.3667 | 69.2667 | 91.5333 | 89.2667
2015-07-11 18:30 | 65.8667 | 68.7667 | 90.5333 | 88.7667
2015-07-11 18:45 | 65.3667 | 68.2667 | 89.5333 | 88.2667
2015-07-11 19:00 | 64.9333 | 67.7667 | 88.5333 | 87.4167
2015-07-11 19:15 | 64.6833 | 67.2667 | 87.5333 | 86.1667
2015-07-11 19:30 | 64.4333 | 66.7667 | 86.5333 | 84.9167
2015-07-11 19:45 | 64.1833 | 66.2667 | 85.5333 | 83.6667
2015-07-11 20:00 | 63.9333 | 66 | 84.7667 | 82.7667
2015-07-11 20:15 | 63.6833 | 66 | 84.2667 | 82.2667
2015-07-11 20:30 | 63.4333 | 66 | 83.7667 | 81.7667
2015-07-11 20:45 | 63.1833 | 66 | 83.2667 | 81.2667
2015-07-11 21:00 | 63 | 65.7667 | 82.65 | 80.65
2015-07-11 21:15 | 63 | 65.2667 | 81.9 | 79.9
2015-07-11 21:30 | 63 | 64.7667 | 81.15 | 79.15
2015-07-11 21:45 | 63 | 64.2667 | 80.4 | 78.4
2015-07-11 22:00 | 63 | 64 | 79.7667 | 77.65
2015-07-11 22:15 | 63 | 64 | 79.2667 | 76.9
2015-07-11 22:30 | 63 | 64 | 78.7667 | 76.15
2015-07-11 22:45 | 63 | 64 | 78.2667 | 75.4
2015-07-11 23:00 | 63 | 63.8833 | 77.8833 | 74.65
2015-07-11 23:15 | 63 | 63.6333 | 77.6333 | 73.9
2015-07-11 23:30 | 63 | 63.3833 | 77.3833 | 73.15
2015-07-11 23:45 | 63 | 63.1333 | 77.1333 | 72.4
2015-07-12 | 62.9333 | 62.8833 | 76.7667 | 71.7667
2015-07-12 00:15 | 62.6833 | 62.6333 | 76.2667 | 71.2667
2015-07-12 00:30 | 62.4333 | 62.3833 | 75.7667 | 70.7667
2015-07-12 00:45 | 62.1833 | 62.1333 | 75.2667 | 70.2667
2015-07-12 01:00 | 62 | 62 | 74.8833 | 69.8833
2015-07-12 01:15 | 62 | 62 | 74.6333 | 69.6333
2015-07-12 01:30 | 62 | 62 | 74.3833 | 69.3833
2015-07-12 01:45 | 62 | 62 | 74.1333 | 69.1333
2015-07-12 02:00 | 62 | 62.1167 | 73.8833 | 68.7667
2015-07-12 02:15 | 62 | 62.3667 | 73.6333 | 68.2667
2015-07-12 02:30 | 62 | 62.6167 | 73.3833 | 67.7667
2015-07-12 02:45 | 62 | 62.8667 | 73.1333 | 67.2667
2015-07-12 03:00 | 62 | 62.7667 | 72.7667 | 66.8833
2015-07-12 03:15 | 62 | 62.2667 | 72.2667 | 66.6333
2015-07-12 03:30 | 62 | 61.7667 | 71.7667 | 66.3833
2015-07-12 03:45 | 62 | 61.2667 | 71.2667 | 66.1333
2015-07-12 04:00 | 62 | 61.1167 | 70.8833 | 65.8833
2015-07-12 04:15 | 62 | 61.3667 | 70.6333 | 65.6333
2015-07-12 04:30 | 62 | 61.6167 | 70.3833 | 65.3833
2015-07-12 04:45 | 62 | 61.8667 | 70.1333 | 65.1333
2015-07-12 05:00 | 62 | 62 | 69.8833 | 65.2333
2015-07-12 05:15 | 62 | 62 | 69.6333 | 65.7333
2015-07-12 05:30 | 62 | 62 | 69.3833 | 66.2333
2015-07-12 05:45 | 62 | 62 | 69.1333 | 66.7333
2015-07-12 06:00 | 62.1333 | 62.2333 | 69.2333 | 67.2333
2015-07-12 06:15 | 62.6333 | 62.7333 | 69.7333 | 67.7333
2015-07-12 06:30 | 63.1333 | 63.2333 | 70.2333 | 68.2333
2015-07-12 06:45 | 63.6333 | 63.7333 | 70.7333 | 68.7333
2015-07-12 07:00 | 64.1333 | 64.2333 | 71.7 | 69.2333
2015-07-12 07:15 | 64.6333 | 64.7333 | 73.2 | 69.7333
2015-07-12 07:30 | 65.1333 | 65.2333 | 74.7 | 70.2333
2015-07-12 07:45 | 65.6333 | 65.7333 | 76.2 | 70.7333
2015-07-12 08:00 | 66.2 | 66.35 | 77.5833 | 71.4667
2015-07-12 08:15 | 66.95 | 67.1 | 78.8333 | 72.4667
2015-07-12 08:30 | 67.7 | 67.85 | 80.0833 | 73.4667
2015-07-12 08:45 | 68.45 | 68.6 | 81.3333 | 74.4667
2015-07-12 09:00 | 69.1333 | 69.35 | 82.5833 | 75.1167
2015-07-12 09:15 | 69.6333 | 70.1 | 83.8333 | 75.3667
2015-07-12 09:30 | 70.1333 | 70.85 | 85.0833 | 75.6167
2015-07-12 09:45 | 70.6333 | 71.6 | 86.3333 | 75.8667
2015-07-12 10:00 | 71.1333 | 72.1167 | 87.35 | 76.7
2015-07-12 10:15 | 71.6333 | 72.3667 | 88.1 | 78.2
2015-07-12 10:30 | 72.1333 | 72.6167 | 88.85 | 79.7
2015-07-12 10:45 | 72.6333 | 72.8667 | 89.6 | 81.2
2015-07-12 11:00 | 73 | 73.2333 | 90.35 | 82.2333
2015-07-12 11:15 | 73 | 73.7333 | 91.1 | 82.7333
2015-07-12 11:30 | 73 | 74.2333 | 91.85 | 83.2333
2015-07-12 11:45 | 73 | 74.7333 | 92.6 | 83.7333
2015-07-12 12:00 | 72.9333 | 75 | 93.2333 | 84.5833
2015-07-12 12:15 | 72.6833 | 75 | 93.7333 | 85.8333
2015-07-12 12:30 | 72.4333 | 75 | 94.2333 | 87.0833
2015-07-12 12:45 | 72.1833 | 75 | 94.7333 | 88.3333
2015-07-12 13:00 | 72.0667 | 75 | 95.2333 | 89.2333
2015-07-12 13:15 | 72.3167 | 75 | 95.7333 | 89.7333
2015-07-12 13:30 | 72.5667 | 75 | 96.2333 | 90.2333
2015-07-12 13:45 | 72.8167 | 75 | 96.7333 | 90.7333
2015-07-12 14:00 | 72.8667 | 75 | 97.1167 | 91.1167
2015-07-12 14:15 | 72.3667 | 75 | 97.3667 | 91.3667
2015-07-12 14:30 | 71.8667 | 75 | 97.6167 | 91.6167
2015-07-12 14:45 | 71.3667 | 75 | 97.8667 | 91.8667
2015-07-12 15:00 | 71 | 74.7667 | 98.1167 | 91.7667
2015-07-12 15:15 | 71 | 74.2667 | 98.3667 | 91.2667
2015-07-12 15:30 | 71 | 73.7667 | 98.6167 | 90.7667
2015-07-12 15:45 | 71 | 73.2667 | 98.8667 | 90.2667
2015-07-12 16:00 | 70.9333 | 72.8833 | 98.7667 | 90.2333
2015-07-12 16:15 | 70.6833 | 72.6333 | 98.2667 | 90.7333
2015-07-12 16:30 | 70.4333 | 72.3833 | 97.7667 | 91.2333
2015-07-12 16:45 | 70.1833 | 72.1333 | 97.2667 | 91.7333
2015-07-12 17:00 | 69.8667 | 71.8833 | 96.7667 | 91.5333
2015-07-12 17:15 | 69.3667 | 71.6333 | 96.2667 | 90.5333
2015-07-12 17:30 | 68.8667 | 71.3833 | 95.7667 | 89.5333
2015-07-12 17:45 | 68.3667 | 71.1333 | 95.2667 | 88.5333
2015-07-12 18:00 | 67.8667 | 70.65 | 94.7667 | 87.7667
2015-07-12 18:15 | 67.3667 | 69.9 | 94.2667 | 87.2667
2015-07-12 18:30 | 66.8667 | 69.15 | 93.7667 | 86.7667
2015-07-12 18:45 | 66.3667 | 68.4 | 93.2667 | 86.2667
2015-07-12 19:00 | 65.8667 | 67.8833 | 92.5333 | 85.65
2015-07-12 19:15 | 65.3667 | 67.6333 | 91.5333 | 84.9
2015-07-12 19:30 | 64.8667 | 67.3833 | 90.5333 | 84.15
2015-07-12 19:45 | 64.3667 | 67.1333 | 89.5333 | 83.4
2015-07-12 20:00 | 63.9333 | 66.8833 | 88.65 | 82.65
2015-07-12 20:15 | 63.6833 | 66.6333 | 87.9 | 81.9
2015-07-12 20:30 | 63.4333 | 66.3833 | 87.15 | 81.15
2015-07-12 20:45 | 63.1833 | 66.1333 | 86.4 | 80.4
2015-07-12 21:00 | 63 | 65.8833 | 85.65 | 79.7667
2015-07-12 21:15 | 63 | 65.6333 | 84.9 | 79.2667
2015-07-12 21:30 | 63 | 65.3833 | 84.15 | 78.7667
2015-07-12 21:45 | 63 | 65.1333 | 83.4 | 78.2667
2015-07-12 22:00 | 63 | 64.8833 | 82.7667 | 77.7667
2015-07-12 22:15 | 63 | 64.6333 | 82.2667 | 77.2667
2015-07-12 22:30 | 63 | 64.3833 | 81.7667 | 76.7667
2015-07-12 22:45 | 63 | 64.1333 | 81.2667 | 76.2667
2015-07-12 23:00 | 63 | 63.8833 | 80.7667 | 75.7667
2015-07-12 23:15 | 63 | 63.6333 | 80.2667 | 75.2667
2015-07-12 23:30 | 63 | 63.3833 | 79.7667 | 74.7667
2015-07-12 23:45 | 63 | 63.1333 | 79.2667 | 74.2667
2015-07-13 | 63.0667 | 63 | 78.7667 | 73.7667
2015-07-13 00:15 | 63.3167 | 63 | 78.2667 | 73.2667
2015-07-13 00:30 | 63.5667 | 63 | 77.7667 | 72.7667
2015-07-13 00:45 | 63.8167 | 63 | 77.2667 | 72.2667
2015-07-13 01:00 | 63.8857 | 62.8833 | 76.7667 | 71.8833
2015-07-13 01:15 | 63.4571 | 62.6333 | 76.2667 | 71.6333
2015-07-13 01:30 | 63.0286 | 62.3833 | 75.7667 | 71.3833
2015-07-13 01:45 | 63.56 | 62.1333 | 75.2667 | 71.1333
2015-07-13 02:00 | 63.9333 | 62 | 74.7667 | 70.8833
2015-07-13 02:15 | 63.6833 | 62 | 74.2667 | 70.6333
2015-07-13 02:30 | 63.4333 | 62 | 73.7667 | 70.3833
2015-07-13 02:45 | 63.1833 | 62 | 73.2667 | 70.1333
2015-07-13 03:00 | 63 | 61.6957 | 72.8833 | 69.8833
2015-07-13 03:15 | 63 | 61.0435 | 72.6333 | 69.6333
2015-07-13 03:30 | 63 | 60.6216 | 72.3833 | 69.3833
2015-07-13 03:45 | 63 | 60.2162 | 72.1333 | 69.1333
2015-07-13 04:00 | 63 | 60.2414 | 71.7667 | 68.8833
2015-07-13 04:15 | 63 | 60.7586 | 71.2667 | 68.6333
2015-07-13 04:30 | 63 | 61 | 70.7667 | 68.3833
2015-07-13 04:45 | 63 | 61 | 70.2667 | 68.1333
2015-07-13 05:00 | 63 | 61 | 69.8833 | 68
2015-07-13 05:15 | 63 | 61 | 69.6333 | 68
2015-07-13 05:30 | 63 | 61 | 69.3833 | 68
2015-07-13 05:45 | 63 | 61 | 69.1333 | 68
2015-07-13 06:00 | 63 | 61.2857 | 69.1167 | 68.35
2015-07-13 06:15 | 63 | 61.898 | 69.3667 | 69.1
2015-07-13 06:30 | 63 | 62.5102 | 69.6167 | 69.85
2015-07-13 06:45 | 63 | 63 | 69.8667 | 70.6
2015-07-13 07:00 | 63.0667 | 63.35 | 71.05 | 71.2333
2015-07-13 07:15 | 63.3167 | 64.1 | 73.3 | 71.7333
2015-07-13 07:30 | 63.5667 | 64.85 | 75.55 | 72.2333
2015-07-13 07:45 | 63.8167 | 65.6 | 77.8 | 72.7333
2015-07-13 08:00 | 64 | 66.1167 | 79.7 | 73.35
2015-07-13 08:15 | 64 | 66.3667 | 81.2 | 74.1
2015-07-13 08:30 | 64 | 66.6167 | 82.7 | 74.85
2015-07-13 08:45 | 64 | 66.8667 | 84.2 | 75.6
2015-07-13 09:00 | 64.1633 | 67.2333 | 85.4667 | 76.4667
2015-07-13 09:15 | 64.7755 | 67.7333 | 86.4667 | 77.4667
2015-07-13 09:30 | 65.3878 | 68.2333 | 87.4667 | 78.4667
2015-07-13 09:45 | 66 | 68.7333 | 88.4667 | 79.4667
2015-07-13 10:00 | 67.1111 | 69.4667 | 89.4667 | 80.35
2015-07-13 10:15 | 66.5882 | 70.4667 | 90.4667 | 81.1
2015-07-13 10:30 | 67.4706 | 71.4667 | 91.4667 | 81.85
2015-07-13 10:45 | 68.3529 | 72.4667 | 92.4667 | 82.6
2015-07-13 11:00 | 69.1333 | 73.1167 | 93.35 | 83.4667
2015-07-13 11:15 | 69.6333 | 73.3667 | 94.1 | 84.4667
2015-07-13 11:30 | 70.1333 | 73.6167 | 94.85 | 85.4667
2015-07-13 11:45 | 70.6333 | 73.8667 | 95.6 | 86.4667
2015-07-13 12:00 | 71 | 74.2333 | 96.2333 | 87.35
2015-07-13 12:15 | 71 | 74.7333 | 96.7333 | 88.1
2015-07-13 12:30 | 71 | 75.2333 | 97.2333 | 88.85
2015-07-13 12:45 | 71 | 75.7333 | 97.7333 | 89.6
2015-07-13 13:00 | 70.9333 | 76.1167 | 98.2333 | 90.2333
2015-07-13 13:15 | 70.6833 | 76.3667 | 98.7333 | 90.7333
2015-07-13 13:30 | 70.4333 | 76.6167 | 99.2333 | 91.2333
2015-07-13 13:45 | 70.1833 | 76.8667 | 99.7333 | 91.7333
2015-07-13 14:00 | 70 | 77 | 100 | 92.1167
2015-07-13 14:15 | 70 | 77 | 100 | 92.3667
2015-07-13 14:30 | 70 | 77 | 100 | 92.6167
2015-07-13 14:45 | 70 | 77 | 100 | 92.8667
2015-07-13 15:00 | 70 | 76.7667 | 99.8833 | 93.1167
2015-07-13 15:15 | 70 | 76.2667 | 99.6333 | 93.3667
2015-07-13 15:30 | 70 | 75.7667 | 99.3833 | 93.6167
2015-07-13 15:45 | 70 | 75.2667 | 99.1333 | 93.8667
2015-07-13 16:00 | 69.8667 | 74.7667 | 99 | 93.8833
2015-07-13 16:15 | 69.3667 | 74.2667 | 99 | 93.6333
2015-07-13 16:30 | 68.8667 | 73.7667 | 99 | 93.3833
2015-07-13 16:45 | 68.3667 | 73.2667 | 99 | 93.1333
2015-07-13 17:00 | 67.9333 | 72.7667 | 98.7667 | 92.7667
2015-07-13 17:15 | 67.6833 | 72.2667 | 98.2667 | 92.2667
2015-07-13 17:30 | 67.4333 | 71.7667 | 97.7667 | 91.7667
2015-07-13 17:45 | 67.1833 | 71.2667 | 97.2667 | 91.2667
2015-07-13 18:00 | 66.8 | 71 | 96.65 | 90.8833
2015-07-13 18:15 | 66.05 | 71 | 95.9 | 90.6333
2015-07-13 18:30 | 65.3 | 71 | 95.15 | 90.3833
2015-07-13 18:45 | 64.55 | 71 | 94.4 | 90.1333
2015-07-13 19:00 | 64 | 70.65 | 93.65 | 89.5333
2015-07-13 19:15 | 64 | 69.9 | 92.9 | 88.5333
2015-07-13 19:30 | 64 | 69.15 | 92.15 | 87.5333
2015-07-13 19:45 | 64 | 68.4 | 91.4 | 86.5333
2015-07-13 20:00 | 63.9333 | 67.8833 | 90.5333 | 85.65
2015-07-13 20:15 | 63.6833 | 67.6333 | 89.5333 | 84.9
2015-07-13 20:30 | 63.4333 | 67.3833 | 88.5333 | 84.15
2015-07-13 20:45 | 63.1833 | 67.1333 | 87.5333 | 83.4
2015-07-13 21:00 | 62.9333 | 66.7667 | 86.65 | 82.65
2015-07-13 21:15 | 62.6833 | 66.2667 | 85.9 | 81.9
2015-07-13 21:30 | 62.4333 | 65.7667 | 85.15 | 81.15
2015-07-13 21:45 | 62.1833 | 65.2667 | 84.4 | 80.4
2015-07-13 22:00 | 62 | 64.8833 | 83.7667 | 79.65
2015-07-13 22:15 | 62 | 64.6333 | 83.2667 | 78.9
2015-07-13 22:30 | 62 | 64.3833 | 82.7667 | 78.15
2015-07-13 22:45 | 62 | 64.1333 | 82.2667 | 77.4
2015-07-13 23:00 | 62 | 63.8833 | 81.65 | 76.7667
2015-07-13 23:15 | 62 | 63.6333 | 80.9 | 76.2667
2015-07-13 23:30 | 62 | 63.3833 | 80.15 | 75.7667
2015-07-13 23:45 | 62 | 63.1333 | 79.4 | 75.2667
2015-07-14 | 61.931 | 62.8833 | 78.8833 | 74.7667
2015-07-14 00:15 | 61.6724 | 62.6333 | 78.6333 | 74.2667
2015-07-14 00:30 | 61.4138 | 62.3833 | 78.3833 | 73.7667
2015-07-14 00:45 | 61.1552 | 62.1333 | 78.1333 | 73.2667
2015-07-14 01:00 | 60.9333 | 62 | 77.7667 | 72.65
2015-07-14 01:15 | 60.6833 | 62 | 77.2667 | 71.9
2015-07-14 01:30 | 60.4333 | 62 | 76.7667 | 71.15
2015-07-14 01:45 | 60.1833 | 62 | 76.2667 | 70.4
2015-07-14 02:00 | 59.9333 | 61.8833 | 75.7667 | 70
2015-07-14 02:15 | 59.6833 | 61.6333 | 75.2667 | 70
2015-07-14 02:30 | 59.4333 | 61.3833 | 74.7667 | 70
2015-07-14 02:45 | 59.1833 | 61.1333 | 74.2667 | 70
2015-07-14 03:00 | 59 | 61.2917 | 74 | 69.7667
2015-07-14 03:15 | 59 | 61.9167 | 74 | 69.2667
2015-07-14 03:30 | 59 | 62.5417 | 74 | 68.7667
2015-07-14 03:45 | 59 | 62.3333 | 74 | 68.2667
2015-07-14 04:00 | 59 | 61 | 73.65 | 67.7667
2015-07-14 04:15 | 59 | 61 | 72.9 | 67.2667
2015-07-14 04:30 | 59 | 61 | 72.15 | 66.7667
2015-07-14 04:45 | 59 | 60.4706 | 71.4 | 66.2667
2015-07-14 05:00 | 59 | 60.1795 | 70.7667 | 66.1167
2015-07-14 05:15 | 59 | 60.5641 | 70.2667 | 66.3667
2015-07-14 05:30 | 59 | 60.9487 | 69.7667 | 66.6167
2015-07-14 05:45 | 59 | 61.619 | 69.2667 | 66.8667
2015-07-14 06:00 | 59.0667 | 62.1167 | 69.35 | 67.4667
2015-07-14 06:15 | 59.3167 | 62.3667 | 70.1 | 68.4667
2015-07-14 06:30 | 59.5667 | 62.6167 | 70.85 | 69.4667
2015-07-14 06:45 | 59.8167 | 62.8667 | 71.6 | 70.4667
2015-07-14 07:00 | 60 | 63.35 | 72.9333 | 71.4667
2015-07-14 07:15 | 60 | 64.1 | 74.9333 | 72.4667
2015-07-14 07:30 | 60 | 64.85 | 76.9333 | 73.4667
2015-07-14 07:45 | 60 | 65.6 | 78.9333 | 74.4667
2015-07-14 08:00 | 60.0667 | 66.2333 | 80.7 | 75.5833
2015-07-14 08:15 | 60.3167 | 66.7333 | 82.2 | 76.8333
2015-07-14 08:30 | 60.5667 | 67.2333 | 83.7 | 78.0833
2015-07-14 08:45 | 60.8167 | 67.7333 | 85.2 | 79.3333
2015-07-14 09:00 | 61.0667 | 68.2333 | 86.4667 | 80.35
2015-07-14 09:15 | 61.3167 | 68.7333 | 87.4667 | 81.1
2015-07-14 09:30 | 61.5667 | 69.2333 | 88.4667 | 81.85
2015-07-14 09:45 | 61.8167 | 69.7333 | 89.4667 | 82.6
2015-07-14 10:00 | 62.1667 | 70.2333 | 90.5833 | 83.4667
2015-07-14 10:15 | 62.7917 | 70.7333 | 91.8333 | 84.4667
2015-07-14 10:30 | 63 | 71.2333 | 93.0833 | 85.4667
2015-07-14 10:45 | 63 | 71.7333 | 94.3333 | 86.4667
2015-07-14 11:00 | 63.1333 | 72.1167 | 95.2333 | 87.35
2015-07-14 11:15 | 63.6333 | 72.3667 | 95.7333 | 88.1
2015-07-14 11:30 | 64.1333 | 72.6167 | 96.2333 | 88.85
2015-07-14 11:45 | 64.6333 | 72.8667 | 96.7333 | 89.6
2015-07-14 12:00 | 65.1081 | 73 | 97 | 90.35
2015-07-14 12:15 | 65.5135 | 73 | 97 | 91.1
2015-07-14 12:30 | 65.9189 | 73 | 97 | 91.85
2015-07-14 12:45 | 67.0435 | 73 | 97 | 92.6
2015-07-14 13:00 | 67.9333 | 73 | 97.2333 | 93.1167
2015-07-14 13:15 | 67.6833 | 73 | 97.7333 | 93.3667
2015-07-14 13:30 | 67.4333 | 73 | 98.2333 | 93.6167
2015-07-14 13:45 | 67.1833 | 73 | 98.7333 | 93.8667
2015-07-14 14:00 | 66.8667 | 73 | 99.4667 | 94.1167
2015-07-14 14:15 | 66.3667 | 73 | 100.4667 | 94.3667
2015-07-14 14:30 | 65.8667 | 73 | 101.4667 | 94.6167
2015-07-14 14:45 | 65.3667 | 73 | 102.4667 | 94.8667
2015-07-14 15:00 | 64.9333 | 72.7667 | 102.8833 | 94.8833
2015-07-14 15:15 | 64.6833 | 72.2667 | 102.6333 | 94.6333
2015-07-14 15:30 | 64.4333 | 71.7667 | 102.3833 | 94.3833
2015-07-14 15:45 | 64.1833 | 71.2667 | 102.1333 | 94.1333
2015-07-14 16:00 | 63.8667 | 70.7667 | 101.7667 | 93.8833
2015-07-14 16:15 | 63.3667 | 70.2667 | 101.2667 | 93.6333
2015-07-14 16:30 | 62.8667 | 69.7667 | 100.7667 | 93.3833
2015-07-14 16:45 | 62.3667 | 69.2667 | 100.2667 | 93.1333
2015-07-14 17:00 | 62 | 68.65 | 99.7667 | 92.8833
2015-07-14 17:15 | 62 | 67.9 | 99.2667 | 92.6333
2015-07-14 17:30 | 62 | 67.15 | 98.7667 | 92.3833
2015-07-14 17:45 | 62 | 66.4 | 98.2667 | 92.1333
2015-07-14 18:00 | 61.9333 | 65.7667 | 97.5333 | 91.7667
2015-07-14 18:15 | 61.6833 | 65.2667 | 96.5333 | 91.2667
2015-07-14 18:30 | 61.4333 | 64.7667 | 95.5333 | 90.7667
2015-07-14 18:45 | 61.1833 | 64.2667 | 94.5333 | 90.2667
2015-07-14 19:00 | 61 | 63.7667 | 93.5333 | 89.4167
2015-07-14 19:15 | 61 | 63.2667 | 92.5333 | 88.1667
2015-07-14 19:30 | 61 | 62.7667 | 91.5333 | 86.9167
2015-07-14 19:45 | 61 | 62.2667 | 90.5333 | 85.6667
2015-07-14 20:00 | 61 | 62.2258 | 89.65 | 84.4167
2015-07-14 20:15 | 61 | 62.7097 | 88.9 | 83.1667
2015-07-14 20:30 | 61 | 62.7931 | 88.15 | 81.9167
2015-07-14 20:45 | 61 | 62.2759 | 87.4 | 80.6667
2015-07-14 21:00 | 61 | 61.8833 | 86.7667 | 79.65
2015-07-14 21:15 | 61 | 61.6333 | 86.2667 | 78.9
2015-07-14 21:30 | 61 | 61.3833 | 85.7667 | 78.15
2015-07-14 21:45 | 61 | 61.1333 | 85.2667 | 77.4
2015-07-14 22:00 | 61 | 61.1167 | 84.65 | 76.65
2015-07-14 22:15 | 61 | 61.3667 | 83.9 | 75.9
2015-07-14 22:30 | 61 | 61.6167 | 83.15 | 75.15
2015-07-14 22:45 | 61 | 61.8667 | 82.4 | 74.4
2015-07-14 23:00 | 61 | 62.5385 | 81.8833 | 73.7667
2015-07-14 23:15 | 61 | 62.8085 | 81.6333 | 73.2667
2015-07-14 23:30 | 61 | 62.4894 | 81.3833 | 72.7667
2015-07-14 23:45 | 61 | 62.1702 | 81.1333 | 72.2667
2015-07-15 | 61.0667 | 62 | 80.7667 | 71.7667
2015-07-15 00:15 | 61.3167 | 62 | 80.2667 | 71.2667
2015-07-15 00:30 | 61.5667 | 62 | 79.7667 | 70.7667
2015-07-15 00:45 | 61.8167 | 62 | 79.2667 | 70.2667
2015-07-15 01:00 | 61.9333 | 62 | 78.7667 | 69.7667
2015-07-15 01:15 | 61.6833 | 62 | 78.2667 | 69.2667
2015-07-15 01:30 | 61.4333 | 62 | 77.7667 | 68.7667
2015-07-15 01:45 | 61.1833 | 62 | 77.2667 | 68.2667
2015-07-15 02:00 | 61 | 62 | 76.8833 | 67.7667
2015-07-15 02:15 | 61 | 62 | 76.6333 | 67.2667
2015-07-15 02:30 | 61 | 62 | 76.3833 | 66.7667
2015-07-15 02:45 | 61 | 62 | 76.1333 | 66.2667
2015-07-15 03:00 | 61 | 62 | 75.8833 | 65.8833
2015-07-15 03:15 | 61 | 62 | 75.6333 | 65.6333
2015-07-15 03:30 | 61 | 62 | 75.3833 | 65.3833
2015-07-15 03:45 | 61 | 62 | 75.1333 | 65.1333
2015-07-15 04:00 | 59.9333 | 61.8627 | 74.7667 | 64.8833
2015-07-15 04:15 | 59.6833 | 61.5686 | 74.2667 | 64.6333
2015-07-15 04:30 | 59.4333 | 61.2745 | 73.7667 | 64.3833
2015-07-15 04:45 | 59.1833 | 61 | 73.2667 | 64.1333
2015-07-15 05:00 | 59 | 61 | 73 | 64.1167
2015-07-15 05:15 | 59 | 61 | 73 | 64.3667
2015-07-15 05:30 | 59 | 61 | 73 | 64.6167
2015-07-15 05:45 | 59 | 61 | 73 | 64.8667
2015-07-15 06:00 | 59.2 | 61 | 73 | 65.35
2015-07-15 06:15 | 59.95 | 61.2326 | 73 | 66.1
2015-07-15 06:30 | 60.7 | 61.9302 | 73 | 66.85
2015-07-15 06:45 | 61.45 | 62.6279 | 73 | 67.6
2015-07-15 07:00 | 62.2 | 63.2333 | 73.4667 | 68.5833
2015-07-15 07:15 | 62.95 | 63.7333 | 74.4667 | 69.8333
2015-07-15 07:30 | 63.7 | 64.2333 | 75.4667 | 71.0833
2015-07-15 07:45 | 64.45 | 64.7333 | 76.4667 | 72.3333
2015-07-15 08:00 | 65.1333 | 65.2333 | 77.7 | 73.5833
2015-07-15 08:15 | 65.6333 | 65.7333 | 79.2 | 74.8333
2015-07-15 08:30 | 66.1333 | 66.2333 | 80.7 | 76.0833
2015-07-15 08:45 | 66.6333 | 66.7333 | 82.2 | 77.3333
2015-07-15 09:00 | 67.0667 | 67.35 | 83.5833 | 78.35
2015-07-15 09:15 | 67.3167 | 68.1 | 84.8333 | 79.1
2015-07-15 09:30 | 67.5667 | 68.85 | 86.0833 | 79.85
2015-07-15 09:45 | 67.8167 | 69.6 | 87.3333 | 80.6
2015-07-15 10:00 | 68.0667 | 70.5833 | 88.2333 | 81.4667
2015-07-15 10:15 | 68.3167 | 71.8333 | 88.7333 | 82.4667
2015-07-15 10:30 | 68.5667 | 73.0833 | 89.2333 | 83.4667
2015-07-15 10:45 | 68.8167 | 74.3333 | 89.7333 | 84.4667
2015-07-15 11:00 | 69.2 | 75.35 | 90.35 | 85.35
2015-07-15 11:15 | 69.95 | 76.1 | 91.1 | 86.1
2015-07-15 11:30 | 70.7 | 76.85 | 91.85 | 86.85
2015-07-15 11:45 | 71.45 | 77.6 | 92.6 | 87.6
2015-07-15 12:00 | 72.069 | 78.5833 | 93.35 | 88.35
2015-07-15 12:15 | 72.3276 | 79.8333 | 94.1 | 89.1
2015-07-15 12:30 | 72.5862 | 81.0833 | 94.85 | 89.85
2015-07-15 12:45 | 72.8448 | 82.3333 | 95.6 | 90.6
2015-07-15 13:00 | 73.1333 | 82.8833 | 96.1167 | 91.2333
2015-07-15 13:15 | 73.6333 | 82.6333 | 96.3667 | 91.7333
2015-07-15 13:30 | 74.1333 | 82.3833 | 96.6167 | 92.2333
2015-07-15 13:45 | 74.6333 | 82.1333 | 96.8667 | 92.7333
2015-07-15 14:00 | 75 | 81.8833 | 97.2333 | 93.1167
2015-07-15 14:15 | 75 | 81.6333 | 97.7333 | 93.3667
2015-07-15 14:30 | 75 | 81.3833 | 98.2333 | 93.6167
2015-07-15 14:45 | 75.9 | 81.1333 | 98.7333 | 93.8667
2015-07-15 15:00 | 76.8667 | 81 | 99 | 94.1167
2015-07-15 15:15 | 76.3667 | 81 | 99 | 94.3667
2015-07-15 15:30 | 75.8667 | 81 | 99 | 94.6167
2015-07-15 15:45 | 75.3667 | 81 | 99 | 94.8667
2015-07-15 16:00 | 74.8667 | 80.7667 | 98.4474 | 95
2015-07-15 16:15 | 74.3667 | 80.2667 | 97.2632 | 95
2015-07-15 16:30 | 73.8667 | 79.7667 | 96.0789 | 95
2015-07-15 16:45 | 73.3667 | 79.2667 | 95.2632 | 95
2015-07-15 17:00 | 72.6667 | 78.65 | 93.6667 | 94.7667
2015-07-15 17:15 | 71.4167 | 77.9 | 92.8 | 94.2667
2015-07-15 17:30 | 70.1667 | 77.15 | 90.125 | 93.7667
2015-07-15 17:45 | 68.9167 | 76.4 | 92 | 93.2667
2015-07-15 18:00 | 67.8667 | 75.5333 | 92.65 | 92.7667
2015-07-15 18:15 | 67.3667 | 74.5333 | 91.9 | 92.2667
2015-07-15 18:30 | 66.8667 | 73.5333 | 91.15 | 91.7667
2015-07-15 18:45 | 66.3667 | 72.5333 | 90.4 | 91.2667
2015-07-15 19:00 | 65.8667 | 71.65 | 89.7667 | 90.5333
2015-07-15 19:15 | 65.3667 | 70.9 | 89.2667 | 89.5333
2015-07-15 19:30 | 64.8667 | 70.15 | 88.7667 | 88.5333
2015-07-15 19:45 | 64.3667 | 69.4 | 88.2667 | 87.5333
2015-07-15 20:00 | 63.9333 | 68.7667 | 87.7667 | 86.7667
2015-07-15 20:15 | 63.6833 | 68.2667 | 87.2667 | 86.2667
2015-07-15 20:30 | 63.4333 | 67.7667 | 86.7667 | 85.7667
2015-07-15 20:45 | 63.1833 | 67.2667 | 86.2667 | 85.2667
2015-07-15 21:00 | 62.9333 | 66.7667 | 85.7667 | 84.5333
2015-07-15 21:15 | 62.6833 | 66.2667 | 85.2667 | 83.5333
2015-07-15 21:30 | 62.4333 | 65.7667 | 84.7667 | 82.5333
2015-07-15 21:45 | 62.1833 | 65.2667 | 84.2667 | 81.5333
2015-07-15 22:00 | 61.9333 | 64.7667 | 83.8833 | 80.65
2015-07-15 22:15 | 61.6833 | 64.2667 | 83.6333 | 79.9
2015-07-15 22:30 | 61.4333 | 63.7667 | 83.3833 | 79.15
2015-07-15 22:45 | 61.1833 | 63.2667 | 83.1333 | 78.4
2015-07-15 23:00 | 61 | 62.7667 | 82.7667 | 77.7667
2015-07-15 23:15 | 61 | 62.2667 | 82.2667 | 77.2667
2015-07-15 23:30 | 61 | 61.7667 | 81.7667 | 76.7667
2015-07-15 23:45 | 61 | 61.2667 | 81.2667 | 76.2667
2015-07-16 | 61 | 61 | 80.8833 | 75.65
2015-07-16 00:15 | 61 | 61 | 80.6333 | 74.9
2015-07-16 00:30 | 61 | 61 | 80.3833 | 74.15
2015-07-16 00:45 | 60.44 | 61 | 80.1333 | 73.4
2015-07-16 01:00 | 60.3636 | 60.8833 | 79.7667 | 72.7667
2015-07-16 01:15 | 61 | 60.6333 | 79.2667 | 72.2667
2015-07-16 01:30 | 61 | 60.3833 | 78.7667 | 71.7667
2015-07-16 01:45 | 61 | 60.1333 | 78.2667 | 71.2667
2015-07-16 02:00 | 61 | 59.8833 | 77.7667 | 70.7667
2015-07-16 02:15 | 61 | 59.6333 | 77.2667 | 70.2667
2015-07-16 02:30 | 61 | 59.3833 | 76.7667 | 69.7667
2015-07-16 02:45 | 60.55 | 59.1333 | 76.2667 | 69.2667
2015-07-16 03:00 | 60.16 | 59 | 75.7667 | 68.8833
2015-07-16 03:15 | 60.76 | 59 | 75.2667 | 68.6333
2015-07-16 03:30 | 60.7429 | 59 | 74.7667 | 68.3833
2015-07-16 03:45 | 60.3143 | 59 | 74.2667 | 68.1333
2015-07-16 04:00 | 60 | 58.8833 | 73.8833 | 67.8833
2015-07-16 04:15 | 60 | 58.6333 | 73.6333 | 67.6333
2015-07-16 04:30 | 60 | 58.3833 | 73.3833 | 67.3833
2015-07-16 04:45 | 60 | 58.1333 | 73.1333 | 67.1333
2015-07-16 05:00 | 60 | 57.8372 | 72.8833 | 67.1167
2015-07-16 05:15 | 60 | 57.4884 | 72.6333 | 67.3667
2015-07-16 05:30 | 60 | 57.1395 | 72.3833 | 67.6167
2015-07-16 05:45 | 60 | 58.0588 | 72.1333 | 67.8667
2015-07-16 06:00 | 60.1333 | 59.25 | 72.1167 | 68.5833
2015-07-16 06:15 | 60.6333 | 59.7857 | 72.3667 | 69.8333
2015-07-16 06:30 | 61.1333 | 60.3214 | 72.6167 | 71.0833
2015-07-16 06:45 | 61.6333 | 60.8571 | 72.8667 | 72.3333
2015-07-16 07:00 | 62.1333 | 60.35 | 73.4667 | 73.7
2015-07-16 07:15 | 62.6333 | 61.1 | 74.4667 | 75.2
2015-07-16 07:30 | 63.1333 | 61.85 | 75.4667 | 76.7
2015-07-16 07:45 | 63.6333 | 62.6 | 76.4667 | 78.2
2015-07-16 08:00 | 64.1481 | 63.5833 | 77.5833 | 79.35
2015-07-16 08:15 | 64.7037 | 64.8333 | 78.8333 | 80.1
2015-07-16 08:30 | 65.2593 | 66.0833 | 80.0833 | 80.85
2015-07-16 08:45 | 65.8148 | 67.3333 | 81.3333 | 81.6
2015-07-16 09:00 | 66.1333 | 68.5833 | 82.7 | 82.35
2015-07-16 09:15 | 66.6333 | 69.8333 | 84.2 | 83.1
2015-07-16 09:30 | 67.1333 | 71.0833 | 85.7 | 83.85
2015-07-16 09:45 | 67.6333 | 72.3333 | 87.2 | 84.6
2015-07-16 10:00 | 68.1333 | 73.5833 | 88.5833 | 85.35
2015-07-16 10:15 | 68.6333 | 74.8333 | 89.8333 | 86.1
2015-07-16 10:30 | 69.1333 | 76.0833 | 91.0833 | 86.85
2015-07-16 10:45 | 69.6333 | 77.3333 | 92.3333 | 87.6
2015-07-16 11:00 | 70.0667 | 78.4667 | 93.4667 | 88.5833
2015-07-16 11:15 | 70.3167 | 79.4667 | 94.4667 | 89.8333
2015-07-16 11:30 | 70.5667 | 80.4667 | 95.4667 | 91.0833
2015-07-16 11:45 | 70.8167 | 81.4667 | 96.4667 | 92.3333
2015-07-16 12:00 | 71.0667 | 82.35 | 97 | 93.35
2015-07-16 12:15 | 71.3167 | 83.1 | 97 | 94.1
2015-07-16 12:30 | 71.5667 | 83.85 | 97 | 94.85
2015-07-16 12:45 | 71.8167 | 84.6 | 97 | 95.6
2015-07-16 13:00 | 72.2 | 84.65 | 97.2333 | 96.2333
2015-07-16 13:15 | 72.95 | 83.9 | 97.7333 | 96.7333
2015-07-16 13:30 | 73.7 | 83.15 | 98.2333 | 97.2333
2015-07-16 13:45 | 74.45 | 82.4 | 98.7333 | 97.7333
2015-07-16 14:00 | 75.0667 | 81.65 | 99 | 98.1167
2015-07-16 14:15 | 75.3167 | 80.9 | 99 | 98.3667
2015-07-16 14:30 | 75.5667 | 80.15 | 99 | 98.6167
2015-07-16 14:45 | 75.8167 | 79.4 | 99 | 98.8667
2015-07-16 15:00 | 75.8 | 78.8833 | 99.2333 | 99
2015-07-16 15:15 | 75.05 | 78.6333 | 99.7333 | 99
2015-07-16 15:30 | 74.3 | 78.3833 | 100.2333 | 99
2015-07-16 15:45 | 73.55 | 78.1333 | 100.7333 | 99
2015-07-16 16:00 | 72.9333 | 78 | 100.7667 | 98.8833
2015-07-16 16:15 | 72.6833 | 78 | 100.2667 | 98.6333
2015-07-16 16:30 | 72.4333 | 78 | 99.7667 | 98.3833
2015-07-16 16:45 | 72.1833 | 78 | 99.2667 | 98.1333
2015-07-16 17:00 | 71.6667 | 77.65 | 98.8833 | 97.8833
2015-07-16 17:15 | 70.4167 | 76.9 | 98.6333 | 97.6333
2015-07-16 17:30 | 69.1667 | 76.15 | 98.3833 | 97.3833
2015-07-16 17:45 | 67.9167 | 75.4 | 98.1333 | 97.1333
2015-07-16 18:00 | 66.8 | 74.5333 | 97.5333 | 96.65
2015-07-16 18:15 | 66.05 | 73.5333 | 96.5333 | 95.9
2015-07-16 18:30 | 65.3 | 72.5333 | 95.5333 | 95.15
2015-07-16 18:45 | 64.55 | 71.5333 | 94.5333 | 94.4
2015-07-16 19:00 | 63.8 | 70.5333 | 93.5333 | 93.65
2015-07-16 19:15 | 63.05 | 69.5333 | 92.5333 | 92.9
2015-07-16 19:30 | 62.3 | 68.5333 | 91.5333 | 92.15
2015-07-16 19:45 | 61.55 | 67.5333 | 90.5333 | 91.4
2015-07-16 20:00 | 61 | 66.7667 | 89.5333 | 90.65
2015-07-16 20:15 | 61 | 66.2667 | 88.5333 | 89.9
2015-07-16 20:30 | 61 | 65.7667 | 87.5333 | 89.15
2015-07-16 20:45 | 61 | 65.2667 | 86.5333 | 88.4
2015-07-16 21:00 | 61 | 64.8833 | 85.65 | 87.7667
2015-07-16 21:15 | 61 | 64.6333 | 84.9 | 87.2667
2015-07-16 21:30 | 61 | 64.3833 | 84.15 | 86.7667
2015-07-16 21:45 | 61 | 64.1333 | 83.4 | 86.2667
2015-07-16 22:00 | 60.9333 | 63.8833 | 82.7667 | 85.5333
2015-07-16 22:15 | 60.6833 | 63.6333 | 82.2667 | 84.5333
2015-07-16 22:30 | 60.4333 | 63.3833 | 81.7667 | 83.5333
2015-07-16 22:45 | 60.1833 | 63.1333 | 81.2667 | 82.5333
2015-07-16 23:00 | 60 | 63 | 80.7667 | 81.7667
2015-07-16 23:15 | 60 | 63 | 80.2667 | 81.2667
2015-07-16 23:30 | 60 | 63 | 79.7667 | 80.7667
2015-07-16 23:45 | 60 | 63 | 79.2667 | 80.2667
2015-07-17 | 60.0833 | 62.7667 | 78.8833 | 79.65
2015-07-17 00:15 | 60.3958 | 62.2667 | 78.6333 | 78.9
2015-07-17 00:30 | 60.7083 | 61.7667 | 78.3833 | 78.15
2015-07-17 00:45 | 60.9167 | 61.2667 | 78.1333 | 77.4
2015-07-17 01:00 | 59.907 | 61 | 77.8833 | 76.7667
2015-07-17 01:15 | 59.5581 | 61 | 77.6333 | 76.2667
2015-07-17 01:30 | 59.2093 | 61 | 77.3833 | 75.7667
2015-07-17 01:45 | 59 | 61 | 77.1333 | 75.2667
2015-07-17 02:00 | 59.1379 | 61 | 76.7667 | 74.7667
2015-07-17 02:15 | 59.6552 | 61 | 76.2667 | 74.2667
2015-07-17 02:30 | 60.1724 | 61 | 75.7667 | 73.7667
2015-07-17 02:45 | 60.6897 | 61 | 75.2667 | 73.2667
2015-07-17 03:00 | 60 | 60.8833 | 74.8833 | 72.7667
2015-07-17 03:15 | 60 | 60.6333 | 74.6333 | 72.2667
2015-07-17 03:30 | 60 | 60.3833 | 74.3833 | 71.7667
2015-07-17 03:45 | 60 | 60.1333 | 74.1333 | 71.2667
2015-07-17 04:00 | 60 | 59.8833 | 73.8833 | 70.7667
2015-07-17 04:15 | 60 | 59.6333 | 73.6333 | 70.2667
2015-07-17 04:30 | 60 | 59.3833 | 73.3833 | 69.7667
2015-07-17 04:45 | 60 | 59.1333 | 73.1333 | 69.2667
2015-07-17 05:00 | 60.0667 | 59 | 72.7667 | 69.1167
2015-07-17 05:15 | 60.3167 | 59 | 72.2667 | 69.3667
2015-07-17 05:30 | 60.5667 | 59 | 71.7667 | 69.6167
2015-07-17 05:45 | 60.8167 | 59 | 71.2667 | 69.8667
2015-07-17 06:00 | 61.0667 | 59.2333 | 71.1167 | 70.4667
2015-07-17 06:15 | 61.3167 | 59.7333 | 71.3667 | 71.4667
2015-07-17 06:30 | 61.5667 | 60.2333 | 71.6167 | 72.4667
2015-07-17 06:45 | 61.8167 | 60.7333 | 71.8667 | 73.4667
2015-07-17 07:00 | 62.0667 | 61.4667 | 72.5833 | 74.5833
2015-07-17 07:15 | 62.3167 | 62.4667 | 73.8333 | 75.8333
2015-07-17 07:30 | 62.5667 | 63.4667 | 75.0833 | 77.0833
2015-07-17 07:45 | 62.8167 | 64.4667 | 76.3333 | 78.3333
2015-07-17 08:00 | 63.16 | 65.35 | 77.8167 | 79.5833
2015-07-17 08:15 | 63.76 | 66.1 | 79.5667 | 80.8333
2015-07-17 08:30 | 64.5143 | 66.85 | 81.3167 | 82.0833
2015-07-17 08:45 | 65.3714 | 67.6 | 83.0667 | 83.3333
2015-07-17 09:00 | 66.1333 | 68.4667 | 84.5833 | 84.2333
2015-07-17 09:15 | 66.6333 | 69.4667 | 85.8333 | 84.7333
2015-07-17 09:30 | 67.1333 | 70.4667 | 87.0833 | 85.2333
2015-07-17 09:45 | 67.6333 | 71.4667 | 88.3333 | 85.7333
2015-07-17 10:00 | 68.1333 | 72.5833 | 89.35 | 86.4667
2015-07-17 10:15 | 68.6333 | 73.8333 | 90.1 | 87.4667
2015-07-17 10:30 | 69.1333 | 75.0833 | 90.85 | 88.4667
2015-07-17 10:45 | 69.6333 | 76.3333 | 91.6 | 89.4667
2015-07-17 11:00 | 70.2 | 77.1167 | 92.4667 | 90.4667
2015-07-17 11:15 | 70.95 | 77.3667 | 93.4667 | 91.4667
2015-07-17 11:30 | 71.7 | 77.6167 | 94.4667 | 92.4667
2015-07-17 11:45 | 72.45 | 77.8667 | 95.4667 | 93.4667
2015-07-17 12:00 | 72.8667 | 78.2333 | 96.2333 | 94.4667
2015-07-17 12:15 | 72.3667 | 78.7333 | 96.7333 | 95.4667
2015-07-17 12:30 | 71.8667 | 79.2333 | 97.2333 | 96.4667
2015-07-17 12:45 | 71.3667 | 79.7333 | 97.7333 | 97.4667
2015-07-17 13:00 | 71.0667 | 80 | 98 | 98.1167
2015-07-17 13:15 | 71.3167 | 80 | 98 | 98.3667
2015-07-17 13:30 | 71.5667 | 80 | 98 | 98.6167
2015-07-17 13:45 | 71.8167 | 80 | 98 | 98.8667
2015-07-17 14:00 | 72 | 79.8833 | 98.2333 | 99.1167
2015-07-17 14:15 | 72 | 79.6333 | 98.7333 | 99.3667
2015-07-17 14:30 | 72 | 79.3833 | 99.2333 | 99.6167
2015-07-17 14:45 | 72 | 79.1333 | 99.7333 | 99.8667
2015-07-17 15:00 | 71.8667 | 78.8833 | 100.1167 | 100
2015-07-17 15:15 | 71.3667 | 78.6333 | 100.3667 | 100
2015-07-17 15:30 | 70.8667 | 78.3833 | 100.6167 | 100
2015-07-17 15:45 | 70.3667 | 78.1333 | 100.8667 | 100
2015-07-17 16:00 | 69.8667 | 78 | 100.65 | 100
2015-07-17 16:15 | 69.3667 | 78 | 99.9 | 100
2015-07-17 16:30 | 68.8667 | 78 | 99.15 | 100
2015-07-17 16:45 | 68.3667 | 78 | 98.4 | 100
2015-07-17 17:00 | 67.8 | 77.65 | 97.8833 | 99.7667
2015-07-17 17:15 | 67.05 | 76.9 | 97.6333 | 99.2667
2015-07-17 17:30 | 66.3 | 76.15 | 97.3833 | 98.7667
2015-07-17 17:45 | 65.55 | 75.4 | 97.1333 | 98.2667
2015-07-17 18:00 | 64.8667 | 74.5333 | 96.65 | 97.7667
2015-07-17 18:15 | 64.3667 | 73.5333 | 95.9 | 97.2667
2015-07-17 18:30 | 63.8667 | 72.5333 | 95.15 | 96.7667
2015-07-17 18:45 | 63.3667 | 71.5333 | 94.4 | 96.2667
2015-07-17 19:00 | 62.8667 | 70.65 | 93.4167 | 95.5333
2015-07-17 19:15 | 62.3667 | 69.9 | 92.1667 | 94.5333
2015-07-17 19:30 | 61.8667 | 69.15 | 90.9167 | 93.5333
2015-07-17 19:45 | 61.3667 | 68.4 | 89.6667 | 92.5333
2015-07-17 20:00 | 61 | 67.65 | 88.65 | 91.65
2015-07-17 20:15 | 61 | 66.9 | 87.9 | 90.9
2015-07-17 20:30 | 61 | 66.15 | 87.15 | 90.15
2015-07-17 20:45 | 61 | 65.4 | 86.4 | 89.4
2015-07-17 21:00 | 61 | 64.8833 | 85.7667 | 88.5333
2015-07-17 21:15 | 61 | 64.6333 | 85.2667 | 87.5333
2015-07-17 21:30 | 61 | 64.3833 | 84.7667 | 86.5333
2015-07-17 21:45 | 61 | 64.1333 | 84.2667 | 85.5333
2015-07-17 22:00 | 60.9333 | 63.8833 | 83.7667 | 84.7667
2015-07-17 22:15 | 60.6833 | 63.6333 | 83.2667 | 84.2667
2015-07-17 22:30 | 60.4333 | 63.3833 | 82.7667 | 83.7667
2015-07-17 22:45 | 60.1833 | 63.1333 | 82.2667 | 83.2667
2015-07-17 23:00 | 60 | 62.8833 | 81.8833 | 82.65
2015-07-17 23:15 | 60 | 62.6333 | 81.6333 | 81.9
2015-07-17 23:30 | 60 | 62.3833 | 81.3833 | 81.15
2015-07-17 23:45 | 60 | 62.1333 | 81.1333 | 80.4
2015-07-18 | 60 | 62 | 80.8833 | 79.65
2015-07-18 00:15 | 60 | 62 | 80.6333 | 78.9
2015-07-18 00:30 | 60 | 62 | 80.3833 | 78.15
2015-07-18 00:45 | 60 | 62 | 80.1333 | 77.4
2015-07-18 01:00 | 60 | 62 | 79.7667 | 76.7667
2015-07-18 01:15 | 60 | 62 | 79.2667 | 76.2667
2015-07-18 01:30 | 60 | 62 | 78.7667 | 75.7667
2015-07-18 01:45 | 60 | 62 | 78.2667 | 75.2667
2015-07-18 02:00 | 59.9333 | 61.65 | 77.8833 | 74.7667
2015-07-18 02:15 | 59.6833 | 60.9 | 77.6333 | 74.2667
2015-07-18 02:30 | 59.4333 | 60.15 | 77.3833 | 73.7667
2015-07-18 02:45 | 59.1833 | 59.4 | 77.1333 | 73.2667
2015-07-18 03:00 | 59 | 59.1167 | 76.8833 | 72.8833
2015-07-18 03:15 | 59 | 59.3667 | 76.6333 | 72.6333
2015-07-18 03:30 | 59 | 59.6167 | 76.3833 | 72.3833
2015-07-18 03:45 | 59 | 59.8667 | 76.1333 | 72.1333
2015-07-18 04:00 | 59.0667 | 59.8833 | 75.7667 | 71.8833
2015-07-18 04:15 | 59.3167 | 59.6333 | 75.2667 | 71.6333
2015-07-18 04:30 | 59.5667 | 59.3833 | 74.7667 | 71.3833
2015-07-18 04:45 | 59.8167 | 59.1333 | 74.2667 | 71.1333
2015-07-18 05:00 | 60.069 | 59 | 74 | 71.2333
2015-07-18 05:15 | 60.3276 | 59.1364 | 74 | 71.7333
2015-07-18 05:30 | 60.5862 | 59.4773 | 74 | 72.2333
2015-07-18 05:45 | 60.8448 | 59.8182 | 74 | 72.7333
2015-07-18 06:00 | 61.0667 | 60.25 | 74.1167 | 73.2333
2015-07-18 06:15 | 61.3167 | 60.7857 | 74.3667 | 73.7333
2015-07-18 06:30 | 61.5667 | 61 | 74.6167 | 74.2333
2015-07-18 06:45 | 61.8167 | 61 | 74.8667 | 74.7333
2015-07-18 07:00 | 62.1333 | 61.4828 | 75.5833 | 75.4667
2015-07-18 07:15 | 62.6333 | 62.5172 | 76.8333 | 76.4667
2015-07-18 07:30 | 63.1333 | 63.2581 | 78.0833 | 77.4667
2015-07-18 07:45 | 63.6333 | 63.7419 | 79.3333 | 78.4667
2015-07-18 08:00 | 64.1333 | 64.35 | 80.5833 | 79.4667
2015-07-18 08:15 | 64.6333 | 65.1 | 81.8333 | 80.4667
2015-07-18 08:30 | 65.1333 | 65.85 | 83.0833 | 81.4667
2015-07-18 08:45 | 65.6333 | 66.6 | 84.3333 | 82.4667
2015-07-18 09:00 | 66 | 67.35 | 85.4667 | 83.4667
2015-07-18 09:15 | 66 | 68.1 | 86.4667 | 84.4667
2015-07-18 09:30 | 66.8919 | 68.85 | 87.4667 | 85.4667
2015-07-18 09:45 | 68.1081 | 69.6 | 88.4667 | 86.4667
2015-07-18 10:00 | 69.1333 | 70.5833 | 89.5833 | 87.5833
2015-07-18 10:15 | 69.6333 | 71.8333 | 90.8333 | 88.8333
2015-07-18 10:30 | 70.1333 | 73.0833 | 92.0833 | 90.0833
2015-07-18 10:45 | 70.6333 | 74.3333 | 93.3333 | 91.3333
2015-07-18 11:00 | 71.1333 | 75.2333 | 94.1167 | 92.2333
2015-07-18 11:15 | 71.6333 | 75.7333 | 94.3667 | 92.7333
2015-07-18 11:30 | 72.1333 | 76.2333 | 94.6167 | 93.2333
2015-07-18 11:45 | 72.6333 | 76.7333 | 94.8667 | 93.7333
2015-07-18 12:00 | 73.1333 | 77.1167 | 95.35 | 94.2333
2015-07-18 12:15 | 73.6333 | 77.3667 | 96.1 | 94.7333
2015-07-18 12:30 | 74.1333 | 77.6167 | 96.85 | 95.2333
2015-07-18 12:45 | 74.6333 | 77.8667 | 97.6 | 95.7333
2015-07-18 13:00 | 75 | 78 | 98.1167 | 96.35
2015-07-18 13:15 | 75 | 78 | 98.3667 | 97.1
2015-07-18 13:30 | 75 | 78 | 98.6167 | 97.85
2015-07-18 13:45 | 75 | 78 | 98.8667 | 98.6
2015-07-18 14:00 | 75 | 78.1167 | 99 | 99
2015-07-18 14:15 | 75 | 78.3667 | 99 | 99
2015-07-18 14:30 | 75 | 78.6167 | 99 | 99
2015-07-18 14:45 | 75 | 78.8667 | 99 | 99
2015-07-18 15:00 | 74.9333 | 78.65 | 99.1167 | 98.8833
2015-07-18 15:15 | 74.6833 | 77.9 | 99.3667 | 98.6333
2015-07-18 15:30 | 74.4333 | 77.15 | 99.6167 | 98.3833
2015-07-18 15:45 | 74.1833 | 76.4 | 99.8667 | 98.1333
2015-07-18 16:00 | 73.9333 | 76 | 100 | 97.8833
2015-07-18 16:15 | 73.6833 | 76 | 100 | 97.6333
2015-07-18 16:30 | 73.4333 | 76 | 100 | 97.3833
2015-07-18 16:45 | 73.1833 | 76 | 100 | 97.1333
2015-07-18 17:00 | 72.8 | 75.8833 | 99.65 | 96.65
2015-07-18 17:15 | 72.05 | 75.6333 | 98.9 | 95.9
2015-07-18 17:30 | 71.3 | 75.3833 | 98.15 | 95.15
2015-07-18 17:45 | 70.55 | 75.1333 | 97.4 | 94.4
2015-07-18 18:00 | 69.8667 | 74.65 | 96.65 | 93.2222
2015-07-18 18:15 | 69.3667 | 73.9 | 95.9 | 89.2105
2015-07-18 18:30 | 68.8667 | 73.15 | 95.15 | 80.5
2015-07-18 18:45 | 68.3667 | 72.4 | 94.4 | 79
2015-07-18 19:00 | 67.9333 | 71.7667 | 93.5333 | 79.1167
2015-07-18 19:15 | 67.6833 | 71.2667 | 92.5333 | 79.3667
2015-07-18 19:30 | 67.4333 | 70.7667 | 91.5333 | 79.6167
2015-07-18 19:45 | 67.1833 | 70.2667 | 90.5333 | 79.8667
2015-07-18 20:00 | 66.9333 | 69.7667 | 89.65 | 79.6957
2015-07-18 20:15 | 66.6833 | 69.2667 | 88.9 | 79.0435
2015-07-18 20:30 | 66.4333 | 68.7667 | 88.15 | 78.2432
2015-07-18 20:45 | 66.1833 | 68.2667 | 87.4 | 77.4324
2015-07-18 21:00 | 66 | 67.8833 | 86.7667 | 77.1167
2015-07-18 21:15 | 66 | 67.6333 | 86.2667 | 77.3667
2015-07-18 21:30 | 66 | 67.3833 | 85.7667 | 77.6167
2015-07-18 21:45 | 66 | 67.1333 | 85.2667 | 77.8667
2015-07-18 22:00 | 66 | 67 | 84.7667 | 78.1167
2015-07-18 22:15 | 66 | 67 | 84.2667 | 78.3667
2015-07-18 22:30 | 66 | 67 | 83.7667 | 78.6167
2015-07-18 22:45 | 66 | 67 | 83.2667 | 78.8667
2015-07-18 23:00 | 66 | 66.8833 | 82.8833 | 78.8833
2015-07-18 23:15 | 66 | 66.6333 | 82.6333 | 78.6333
2015-07-18 23:30 | 66 | 66.3833 | 82.3833 | 78.3833
2015-07-18 23:45 | 66 | 66.1333 | 82.1333 | 78.1333
2015-07-19 | 66 | 65.8833 | 81.7667 | 78
2015-07-19 00:15 | 66 | 65.6333 | 81.2667 | 78
2015-07-19 00:30 | 66 | 65.3833 | 80.7667 | 78
2015-07-19 00:45 | 66 | 65.1333 | 80.2667 | 78
2015-07-19 01:00 | 65.9333 | 65 | 79.8833 | 77.8833
2015-07-19 01:15 | 65.6833 | 65 | 79.6333 | 77.6333
2015-07-19 01:30 | 65.4333 | 65 | 79.3833 | 77.3833
2015-07-19 01:45 | 65.1833 | 65 | 79.1333 | 77.1333
2015-07-19 02:00 | 64.9333 | 65 | 78.8833 | 76.8833
2015-07-19 02:15 | 64.6833 | 65 | 78.6333 | 76.6333
2015-07-19 02:30 | 64.4333 | 65 | 78.3833 | 76.3833
2015-07-19 02:45 | 64.1833 | 65 | 78.1333 | 76.1333
2015-07-19 03:00 | 64 | 65 | 77.7667 | 75.8833
2015-07-19 03:15 | 64 | 65 | 77.2667 | 75.6333
2015-07-19 03:30 | 64 | 65 | 76.7667 | 75.3833
2015-07-19 03:45 | 64 | 65 | 76.2667 | 75.1333
2015-07-19 04:00 | 63.9333 | 65 | 76 | 75
2015-07-19 04:15 | 63.6833 | 65 | 76 | 75
2015-07-19 04:30 | 63.4333 | 65 | 76 | 75
2015-07-19 04:45 | 63.1833 | 65 | 76 | 75
2015-07-19 05:00 | 63.1333 | 65.1167 | 75.8833 | 74.8833
2015-07-19 05:15 | 63.6333 | 65.3667 | 75.6333 | 74.6333
2015-07-19 05:30 | 64.1333 | 65.6167 | 75.3833 | 74.3833
2015-07-19 05:45 | 64.6333 | 65.8667 | 75.1333 | 74.1333
2015-07-19 06:00 | 65.0667 | 66.1167 | 75.1167 | 73.8833
2015-07-19 06:15 | 65.3167 | 66.3667 | 75.3667 | 73.6333
2015-07-19 06:30 | 65.5667 | 66.6167 | 75.6167 | 73.3833
2015-07-19 06:45 | 65.8167 | 66.8667 | 75.8667 | 73.1333
2015-07-19 07:00 | 66.1333 | 67.1167 | 76.4667 | 73.35
2015-07-19 07:15 | 66.6333 | 67.3667 | 77.4667 | 74.1
2015-07-19 07:30 | 67.1333 | 67.6167 | 78.4667 | 74.85
2015-07-19 07:45 | 67.6333 | 67.8667 | 79.4667 | 75.6
2015-07-19 08:00 | 68.1333 | 68.2333 | 80.4667 | 76.2333
2015-07-19 08:15 | 68.6333 | 68.7333 | 81.4667 | 76.7333
2015-07-19 08:30 | 69.1333 | 69.2333 | 82.4667 | 77.2333
2015-07-19 08:45 | 69.6333 | 69.7333 | 83.4667 | 77.7333
2015-07-19 09:00 | 70.0667 | 70.2333 | 84.5833 | 77.7667
2015-07-19 09:15 | 70.3167 | 70.7333 | 85.8333 | 77.2667
2015-07-19 09:30 | 70.5667 | 71.2333 | 87.0833 | 76.7667
2015-07-19 09:45 | 70.8167 | 71.7333 | 88.3333 | 76.2667
2015-07-19 10:00 | 71.3333 | 72.2333 | 89.4667 | 76.35
2015-07-19 10:15 | 72.5833 | 72.7333 | 90.4667 | 77.1
2015-07-19 10:30 | 73.8333 | 73.2333 | 91.4667 | 77.85
2015-07-19 10:45 | 75.0833 | 73.7333 | 92.4667 | 78.6
2015-07-19 11:00 | 75.7333 | 74.5833 | 93.4667 | 79.4667
2015-07-19 11:15 | 75.0889 | 75.8333 | 94.4667 | 80.4667
2015-07-19 11:30 | 75.4222 | 77.0833 | 95.4667 | 81.4667
2015-07-19 11:45 | 75.7556 | 78.3333 | 96.4667 | 82.4667
2015-07-19 12:00 | 76.2 | 79.4667 | 97.1167 | 83
2015-07-19 12:15 | 76.95 | 80.4667 | 97.3667 | 83
2015-07-19 12:30 | 77.7 | 81.4667 | 97.6167 | 83
2015-07-19 12:45 | 78.45 | 82.4667 | 97.8667 | 83
2015-07-19 13:00 | 79.5333 | 83.4667 | 98.1167 | 83.4667
2015-07-19 13:15 | 81.5333 | 84.4667 | 98.3667 | 84.4667
2015-07-19 13:30 | 83.5333 | 85.4667 | 98.6167 | 85.4667
2015-07-19 13:45 | 85.5333 | 86.4667 | 98.8667 | 86.4667
2015-07-19 14:00 | 87.25 | 87.2333 | 98.7667 | 87.2333
2015-07-19 14:15 | 87.5909 | 87.7333 | 98.2667 | 87.7333
2015-07-19 14:30 | 85.5455 | 88.2333 | 97.7667 | 88.2333
2015-07-19 14:45 | 83.5 | 88.7333 | 97.2667 | 88.7333
2015-07-19 15:00 | 81.8 | 88.65 | 96.0233 | 89.1167
2015-07-19 15:15 | 81.05 | 87.9 | 93.9302 | 89.3667
2015-07-19 15:30 | 80.3 | 87.15 | 91.8372 | 89.6167
2015-07-19 15:45 | 79.55 | 86.4 | 88.3529 | 89.8667
2015-07-19 16:00 | 78.8667 | 85.65 | 86 | 90
2015-07-19 16:15 | 78.3667 | 84.9 | 85.8 | 90
2015-07-19 16:30 | 77.8667 | 84.15 | 85 | 90
2015-07-19 16:45 | 77.3667 | 83.4 | 85 | 90
2015-07-19 17:00 | 76.7333 | 82.65 | 85.2333 | 89.7667
2015-07-19 17:15 | 75.7333 | 81.9 | 85.7333 | 89.2667
2015-07-19 17:30 | 74.7333 | 81.15 | 86.2333 | 88.7667
2015-07-19 17:45 | 73.7333 | 80.4 | 86.7333 | 88.2667
2015-07-19 18:00 | 72.8667 | 79.65 | 87 | 87.7667
2015-07-19 18:15 | 72.3667 | 78.9 | 87 | 87.2667
2015-07-19 18:30 | 71.8667 | 78.15 | 87 | 86.7667
2015-07-19 18:45 | 71.3667 | 77.4 | 87 | 86.2667
2015-07-19 19:00 | 71 | 76.7667 | 87 | 85.7667
2015-07-19 19:15 | 71 | 76.2667 | 87 | 85.2667
2015-07-19 19:30 | 71 | 75.7667 | 87 | 84.7667
2015-07-19 19:45 | 71 | 75.2667 | 87 | 84.2667
2015-07-19 20:00 | 71.1333 | 74.8833 | 86.7667 | 83.7667
2015-07-19 20:15 | 71.6333 | 74.6333 | 86.2667 | 83.2667
2015-07-19 20:30 | 72.1333 | 74.3833 | 85.7667 | 82.7667
2015-07-19 20:45 | 72.6333 | 74.1333 | 85.2667 | 82.2667
2015-07-19 21:00 | 73 | 73.8833 | 84.7667 | 82
2015-07-19 21:15 | 73 | 73.6333 | 84.2667 | 82
2015-07-19 21:30 | 73 | 73.3833 | 83.7667 | 82
2015-07-19 21:45 | 73 | 73.1333 | 83.2667 | 82
2015-07-19 22:00 | 72.8667 | 72.8833 | 83 | 82
2015-07-19 22:15 | 72.3667 | 72.6333 | 83 | 82
2015-07-19 22:30 | 71.8667 | 72.3833 | 83 | 82
2015-07-19 22:45 | 71.3667 | 72.1333 | 83 | 82
2015-07-19 23:00 | 70.9333 | 71.8833 | 82.8833 | 81.7667
2015-07-19 23:15 | 70.6833 | 71.6333 | 82.6333 | 81.2667
2015-07-19 23:30 | 70.4333 | 71.3833 | 82.3833 | 80.7667
2015-07-19 23:45 | 70.1833 | 71.1333 | 82.1333 | 80.2667
2015-07-20 | 69.8667 | 70.8833 | 81.7667 | 79.8833
2015-07-20 00:15 | 69.3667 | 70.6333 | 81.2667 | 79.6333
2015-07-20 00:30 | 68.8667 | 70.3833 | 80.7667 | 79.3833
2015-07-20 00:45 | 68.3667 | 70.1333 | 80.2667 | 79.1333
2015-07-20 01:00 | 68.0667 | 70 | 79.7667 | 78.8833
2015-07-20 01:15 | 68.3167 | 70 | 79.2667 | 78.6333
2015-07-20 01:30 | 68.5667 | 70 | 78.7667 | 78.3833
2015-07-20 01:45 | 68.8167 | 70 | 78.2667 | 78.1333
2015-07-20 02:00 | 69.0667 | 69.8833 | 78 | 77.7667
2015-07-20 02:15 | 69.3167 | 69.6333 | 78 | 77.2667
2015-07-20 02:30 | 69.5667 | 69.3833 | 78 | 76.7667
2015-07-20 02:45 | 69.8167 | 69.1333 | 78 | 76.2667
2015-07-20 03:00 | 69.9333 | 69 | 77.8833 | 76
2015-07-20 03:15 | 69.6833 | 69 | 77.6333 | 76
2015-07-20 03:30 | 69.4333 | 69 | 77.3833 | 76
2015-07-20 03:45 | 69.1833 | 69 | 77.1333 | 76
2015-07-20 04:00 | 69 | 69 | 76.7667 | 76
2015-07-20 04:15 | 69 | 69 | 76.2667 | 76
2015-07-20 04:30 | 69 | 69 | 75.7667 | 76
2015-07-20 04:45 | 69 | 69 | 75.2667 | 76
2015-07-20 05:00 | 68.9333 | 69.2333 | 74.8833 | 76.1167
2015-07-20 05:15 | 68.6833 | 69.7333 | 74.6333 | 76.3667
2015-07-20 05:30 | 68.4333 | 70.2333 | 74.3833 | 76.6167
2015-07-20 05:45 | 68.1833 | 70.7333 | 74.1333 | 76.8667
2015-07-20 06:00 | 68.2 | 71.1167 | 74.1167 | 77.35
2015-07-20 06:15 | 68.95 | 71.3667 | 74.3667 | 78.1
2015-07-20 06:30 | 69.7 | 71.6167 | 74.6167 | 78.85
2015-07-20 06:45 | 70.45 | 71.8667 | 74.8667 | 79.6
2015-07-20 07:00 | 71.1333 | 72.4667 | 75.7 | 80.2333
2015-07-20 07:15 | 71.6333 | 73.4667 | 77.2 | 80.7333
2015-07-20 07:30 | 72.1333 | 74.4667 | 78.7 | 81.2333
2015-07-20 07:45 | 72.6333 | 75.4667 | 80.2 | 81.7333
2015-07-20 08:00 | 73.1333 | 76.5833 | 81.8167 | 82.2333
2015-07-20 08:15 | 73.6333 | 77.8333 | 83.5667 | 82.7333
2015-07-20 08:30 | 74.1333 | 79.0833 | 85.3167 | 83.2333
2015-07-20 08:45 | 74.6333 | 80.3333 | 87.0667 | 83.7333
2015-07-20 09:00 | 75.0667 | 81.4667 | 88.35 | 84.1167
2015-07-20 09:15 | 75.3167 | 82.4667 | 89.1 | 84.3667
2015-07-20 09:30 | 75.5667 | 83.4667 | 89.85 | 84.6167
2015-07-20 09:45 | 75.8167 | 84.4667 | 90.6 | 84.8667
2015-07-20 10:00 | 75.9333 | 85.1167 | 91.2333 | 85.4667
2015-07-20 10:15 | 75.6833 | 85.3667 | 91.7333 | 86.4667
2015-07-20 10:30 | 75.4333 | 85.6167 | 92.2333 | 87.4667
2015-07-20 10:45 | 75.1833 | 85.8667 | 92.7333 | 88.4667
2015-07-20 11:00 | 74.8667 | 86 | 93.35 | 89
2015-07-20 11:15 | 74.3667 | 86 | 94.1 | 89
2015-07-20 11:30 | 73.8667 | 86 | 94.85 | 89
2015-07-20 11:45 | 73.3667 | 86 | 95.6 | 89
2015-07-20 12:00 | 72.9333 | 86 | 96.2333 | 89.35
2015-07-20 12:15 | 72.6833 | 86 | 96.7333 | 90.1
2015-07-20 12:30 | 72.4333 | 86 | 97.2333 | 90.85
2015-07-20 12:45 | 72.1833 | 86 | 97.7333 | 91.6
2015-07-20 13:00 | 72.0667 | 86 | 98.2333 | 92.35
2015-07-20 13:15 | 72.3167 | 86 | 98.7333 | 93.1
2015-07-20 13:30 | 72.5667 | 86 | 99.2333 | 93.85
2015-07-20 13:45 | 72.8167 | 86 | 99.7333 | 94.6
2015-07-20 14:00 | 73 | 85.8833 | 100 | 95
2015-07-20 14:15 | 73 | 85.6333 | 100 | 95
2015-07-20 14:30 | 73 | 85.3833 | 100 | 95
2015-07-20 14:45 | 73 | 85.1333 | 100 | 95
2015-07-20 15:00 | 72.8 | 85 | 99.65 | 94.8833
2015-07-20 15:15 | 72.05 | 85 | 98.9 | 94.6333
2015-07-20 15:30 | 71.3 | 85 | 98.15 | 94.3833
2015-07-20 15:45 | 70.55 | 85 | 97.4 | 94.1333
2015-07-20 16:00 | 69.7333 | 84.65 | 96.8542 | 94
2015-07-20 16:15 | 68.7333 | 83.9 | 96.5417 | 94
2015-07-20 16:30 | 67.7333 | 83.15 | 96.2292 | 94
2015-07-20 16:45 | 66.7333 | 82.4 | 94 | 94
2015-07-20 17:00 | 66 | 81.4167 | 88.6 | 93.8833
2015-07-20 17:15 | 66 | 80.1667 | 81.1429 | 93.6333
2015-07-20 17:30 | 66 | 78.9167 | 72.5714 | 93.3833
2015-07-20 17:45 | 66 | 77.6667 | 73.6667 | 93.1333
2015-07-20 18:00 | 65.8 | 76.4167 | 74 | 92.8833
2015-07-20 18:15 | 65.05 | 75.1667 | 73.0769 | 92.6333
2015-07-20 18:30 | 64.3 | 73.9167 | 73.9333 | 92.3833
2015-07-20 18:45 | 63.55 | 72.6667 | 74.6364 | 92.1333
2015-07-20 19:00 | 62.9333 | 71.8833 | 75.1167 | 91.65
2015-07-20 19:15 | 62.6833 | 71.6333 | 75.3667 | 90.9
2015-07-20 19:30 | 62.4333 | 71.3833 | 75.6167 | 90.15
2015-07-20 19:45 | 62.1833 | 71.1333 | 75.8667 | 89.4
2015-07-20 20:00 | 62 | 70.7667 | 76.1167 | 88.7667
2015-07-20 20:15 | 62 | 70.2667 | 76.3667 | 88.2667
2015-07-20 20:30 | 62 | 69.7667 | 76.6167 | 87.7667
2015-07-20 20:45 | 62 | 69.2667 | 76.8667 | 87.2667
2015-07-20 21:00 | 62 | 68.7667 | 77 | 86.8833
2015-07-20 21:15 | 62 | 68.2667 | 77 | 86.6333
2015-07-20 21:30 | 62 | 67.7667 | 77 | 86.3833
2015-07-20 21:45 | 62 | 67.2667 | 77 | 86.1333
2015-07-20 22:00 | 61.8667 | 66.8833 | 76.8833 | 85.65
2015-07-20 22:15 | 61.3667 | 66.6333 | 76.6333 | 84.9
2015-07-20 22:30 | 60.8667 | 66.3833 | 76.3833 | 84.15
2015-07-20 22:45 | 60.3667 | 66.1333 | 76.1333 | 83.4
2015-07-20 23:00 | 60.069 | 65.7667 | 76.1167 | 82.8833
2015-07-20 23:15 | 60.3276 | 65.2667 | 76.3667 | 82.6333
2015-07-20 23:30 | 60.5862 | 64.7667 | 76.6167 | 82.3833
2015-07-20 23:45 | 60.8448 | 64.2667 | 76.8667 | 82.1333
2015-07-21 | 60 | 63.8833 | 76.8833 | 81.8833
2015-07-21 00:15 | 60 | 63.6333 | 76.6333 | 81.6333
2015-07-21 00:30 | 60 | 63.3833 | 76.3833 | 81.3833
2015-07-21 00:45 | 60 | 63.1333 | 76.1333 | 81.1333
2015-07-21 01:00 | 60.2222 | 63 | 76 | 80.8833
2015-07-21 01:15 | 60.9762 | 63 | 76 | 80.6333
2015-07-21 01:30 | 60.619 | 63 | 76 | 80.3833
2015-07-21 01:45 | 60.2619 | 63 | 76 | 80.1333
2015-07-21 02:00 | 60 | 62.8833 | 75.7667 | 80
2015-07-21 02:15 | 60 | 62.6333 | 75.2667 | 80
2015-07-21 02:30 | 60 | 62.3833 | 74.7667 | 80
2015-07-21 02:45 | 60 | 62.1333 | 74.2667 | 80
2015-07-21 03:00 | 60 | 62.7 | 74.2333 | 80
2015-07-21 03:15 | 60 | 62.76 | 74.7333 | 80
2015-07-21 03:30 | 60 | 62.46 | 75.2333 | 80
2015-07-21 03:45 | 60 | 62.16 | 75.7333 | 80
2015-07-21 04:00 | 60 | 62.1373 | 75.65 | 79.7667
2015-07-21 04:15 | 60 | 62.4314 | 74.9 | 79.2667
2015-07-21 04:30 | 60 | 62.7255 | 74.15 | 78.7667
2015-07-21 04:45 | 60 | 62.8889 | 73.4 | 78.2667
2015-07-21 05:00 | 60.1081 | 62.1167 | 72.65 | 78.1167
2015-07-21 05:15 | 60.5135 | 62.3667 | 71.9 | 78.3667
2015-07-21 05:30 | 60.9189 | 62.6167 | 71.15 | 78.6167
2015-07-21 05:45 | 60.4783 | 62.8667 | 70.4 | 78.8667
2015-07-21 06:00 | 60.0667 | 63.1167 | 70.2333 | 79
2015-07-21 06:15 | 60.3167 | 63.3667 | 70.7333 | 79
2015-07-21 06:30 | 60.5667 | 63.6167 | 71.2333 | 79
2015-07-21 06:45 | 60.8167 | 63.8667 | 71.7333 | 79
2015-07-21 07:00 | 61.1905 | 64 | 72.35 | 79.4667
2015-07-21 07:15 | 61.9048 | 64 | 73.1 | 80.4667
2015-07-21 07:30 | 62.619 | 64.2963 | 73.85 | 81.4667
2015-07-21 07:45 | 63.3889 | 65.4074 | 74.6 | 82.4667
2015-07-21 08:00 | 64.0667 | 66.35 | 75.4038 | 83.35
2015-07-21 08:15 | 64.3167 | 67.1 | 76.2692 | 84.1
2015-07-21 08:30 | 64.5667 | 67.85 | 77.1346 | 84.85
2015-07-21 08:45 | 64.8167 | 68.6 | 78 | 85.6
2015-07-21 09:00 | 65.0667 | 69.35 | 78.35 | 86.35
2015-07-21 09:15 | 65.3167 | 70.1 | 79.1 | 87.1
2015-07-21 09:30 | 65.5667 | 70.85 | 79.85 | 87.85
2015-07-21 09:45 | 65.8167 | 71.6 | 80.6 | 88.6
2015-07-21 10:00 | 66.1333 | 72.35 | 81.35 | 89.2333
2015-07-21 10:15 | 66.6333 | 73.1 | 82.1 | 89.7333
2015-07-21 10:30 | 67.1333 | 73.85 | 82.85 | 90.2333
2015-07-21 10:45 | 67.6333 | 74.6 | 83.6 | 90.7333
2015-07-21 11:00 | 68.0667 | 74.8833 | 84.35 | 91.2333
2015-07-21 11:15 | 68.3167 | 74.6333 | 85.1 | 91.7333
2015-07-21 11:30 | 68.5667 | 74.3833 | 85.85 | 92.2333
2015-07-21 11:45 | 68.8167 | 74.1333 | 86.6 | 92.7333
2015-07-21 12:00 | 69.0667 | 74.1167 | 87.2333 | 93.35
2015-07-21 12:15 | 69.3167 | 74.3667 | 87.7333 | 94.1
2015-07-21 12:30 | 69.5667 | 74.6167 | 88.2333 | 94.85
2015-07-21 12:45 | 69.8167 | 74.8667 | 88.7333 | 95.6
2015-07-21 13:00 | 69.9333 | 75.1167 | 89.35 | 96
2015-07-21 13:15 | 69.6833 | 75.3667 | 90.1 | 96
2015-07-21 13:30 | 69.4333 | 75.6167 | 90.85 | 96
2015-07-21 13:45 | 69.1833 | 75.8667 | 91.6 | 96
2015-07-21 14:00 | 68.8667 | 75.8833 | 92.5957 | 96.1167
2015-07-21 14:15 | 68.3667 | 75.6333 | 93.8723 | 96.3667
2015-07-21 14:30 | 67.8667 | 75.3833 | 95.1489 | 96.6167
2015-07-21 14:45 | 67.3667 | 75.1333 | 94.8462 | 96.8667
2015-07-21 15:00 | 66.7333 | 74.7667 | 92.125 | 97.1167
2015-07-21 15:15 | 65.7333 | 74.2667 | 87.4231 | 97.3667
2015-07-21 15:30 | 64.7333 | 73.7667 | 82.5192 | 97.6167
2015-07-21 15:45 | 64.2667 | 73.2667 | 77.6154 | 97.8667
2015-07-21 16:00 | 64.9333 | 72.8833 | 75 | 98
2015-07-21 16:15 | 64.6833 | 72.6333 | 75 | 98
2015-07-21 16:30 | 64.4333 | 72.3833 | 75 | 98
2015-07-21 16:45 | 64.1833 | 72.1333 | 75.6522 | 98
2015-07-21 17:00 | 63.9333 | 71.65 | 75.8833 | 97.8833
2015-07-21 17:15 | 63.6833 | 70.9 | 75.6333 | 97.6333
2015-07-21 17:30 | 63.4333 | 70.15 | 75.3833 | 97.3833
2015-07-21 17:45 | 63.1833 | 69.4 | 75.1333 | 97.1333
2015-07-21 18:00 | 62.9333 | 68.65 | 75.2333 | 96.5333
2015-07-21 18:15 | 62.6833 | 67.9 | 75.7333 | 95.5333
2015-07-21 18:30 | 62.4333 | 67.15 | 76.2333 | 94.5333
2015-07-21 18:45 | 62.1833 | 66.4 | 76.7333 | 93.5333
2015-07-21 19:00 | 62.1379 | 65.7667 | 76.8833 | 92.5333
2015-07-21 19:15 | 62.6552 | 65.2667 | 76.6333 | 91.5333
2015-07-21 19:30 | 62.6774 | 64.7667 | 76.3833 | 90.5333
2015-07-21 19:45 | 61.7097 | 64.2667 | 76.1333 | 89.5333
2015-07-21 20:00 | 61 | 64 | 76 | 88.5333
2015-07-21 20:15 | 61 | 64 | 76 | 87.5333
2015-07-21 20:30 | 61 | 64 | 76 | 86.5333
2015-07-21 20:45 | 61 | 64 | 76 | 85.5333
2015-07-21 21:00 | 61.0667 | 63.8833 | 75.8833 | 84.65
2015-07-21 21:15 | 61.3167 | 63.6333 | 75.6333 | 83.9
2015-07-21 21:30 | 61.5667 | 63.3833 | 75.3833 | 83.15
2015-07-21 21:45 | 61.8167 | 63.1333 | 75.1333 | 82.4
2015-07-21 22:00 | 61.931 | 63 | 74.8833 | 81.7667
2015-07-21 22:15 | 61.6724 | 63 | 74.6333 | 81.2667
2015-07-21 22:30 | 61.4138 | 63 | 74.3833 | 80.7667
2015-07-21 22:45 | 61.1552 | 63 | 74.1333 | 80.2667
2015-07-21 23:00 | 61.0667 | 62.8833 | 73.8833 | 79.8833
2015-07-21 23:15 | 61.3167 | 62.6333 | 73.6333 | 79.6333
2015-07-21 23:30 | 61.5667 | 62.3833 | 73.3833 | 79.3833
2015-07-21 23:45 | 61.8167 | 62.1333 | 73.1333 | 79.1333
2015-07-22 | 61.9333 | 62 | 73 | 78.7667
2015-07-22 00:15 | 61.6833 | 62 | 73 | 78.2667
2015-07-22 00:30 | 61.4333 | 62 | 73 | 77.7667
2015-07-22 00:45 | 61.1833 | 62 | 73 | 77.2667
2015-07-22 01:00 | 61 | 61.8833 | 72.7667 | 76.8833
2015-07-22 01:15 | 61 | 61.6333 | 72.2667 | 76.6333
2015-07-22 01:30 | 61 | 61.3833 | 71.7667 | 76.3833
2015-07-22 01:45 | 61 | 61.1333 | 71.2667 | 76.1333
2015-07-22 02:00 | 61 | 60.8833 | 71 | 75.8833
2015-07-22 02:15 | 61 | 60.6333 | 71 | 75.6333
2015-07-22 02:30 | 61 | 60.3833 | 71 | 75.3833
2015-07-22 02:45 | 61 | 60.1333 | 71 | 75.1333
2015-07-22 03:00 | 60.9333 | 60 | 70.8833 | 74.8833
2015-07-22 03:15 | 60.6833 | 60 | 70.6333 | 74.6333
2015-07-22 03:30 | 60.4333 | 60 | 70.3833 | 74.3833
2015-07-22 03:45 | 60.1833 | 60 | 70.1333 | 74.1333
2015-07-22 04:00 | 60 | 60.14 | 69.8833 | 73.8833
2015-07-22 04:15 | 60 | 60.44 | 69.6333 | 73.6333
2015-07-22 04:30 | 60 | 60.74 | 69.3833 | 73.3833
2015-07-22 04:45 | 60 | 60.8 | 69.1333 | 73.1333
2015-07-22 05:00 | 60.0667 | 60 | 69 | 73
2015-07-22 05:15 | 60.3167 | 60 | 69 | 73
2015-07-22 05:30 | 60.5667 | 60 | 69 | 73
2015-07-22 05:45 | 60.8167 | 60 | 69 | 73
2015-07-22 06:00 | 61.0667 | 60.2333 | 69.2333 | 73.2333
2015-07-22 06:15 | 61.3167 | 60.7333 | 69.7333 | 73.7333
2015-07-22 06:30 | 61.5667 | 61.2333 | 70.2333 | 74.2333
2015-07-22 06:45 | 61.8167 | 61.7333 | 70.7333 | 74.7333
2015-07-22 07:00 | 62.1333 | 62.2333 | 71.35 | 75.4667
2015-07-22 07:15 | 62.6333 | 62.7333 | 72.1 | 76.4667
2015-07-22 07:30 | 63.1333 | 63.2333 | 72.85 | 77.4667
2015-07-22 07:45 | 63.6333 | 63.7333 | 73.6 | 78.4667
2015-07-22 08:00 | 64.0667 | 64.4667 | 74.8167 | 79.35
2015-07-22 08:15 | 64.3167 | 65.4667 | 76.5667 | 80.1
2015-07-22 08:30 | 64.5667 | 66.4667 | 78.3167 | 80.85
2015-07-22 08:45 | 64.8167 | 67.4667 | 80.0667 | 81.6
2015-07-22 09:00 | 64.8621 | 68.35 | 81.35 | 82.4667
2015-07-22 09:15 | 64.3448 | 69.1 | 82.1 | 83.4667
2015-07-22 09:30 | 64.1613 | 69.85 | 82.85 | 84.4667
2015-07-22 09:45 | 64.6452 | 70.6 | 83.6 | 85.4667
2015-07-22 10:00 | 64.9333 | 71.5833 | 84.4667 | 86.35
2015-07-22 10:15 | 64.6833 | 72.8333 | 85.4667 | 87.1
2015-07-22 10:30 | 64.4333 | 74.0833 | 86.4667 | 87.85
2015-07-22 10:45 | 64.1833 | 75.3333 | 87.4667 | 88.6
2015-07-22 11:00 | 64 | 75.7667 | 88.2333 | 89.2333
2015-07-22 11:15 | 64 | 75.2667 | 88.7333 | 89.7333
2015-07-22 11:30 | 64.1613 | 74.7667 | 89.2333 | 90.2333
2015-07-22 11:45 | 64.6452 | 74.2667 | 89.7333 | 90.7333
2015-07-22 12:00 | 65.1333 | 74 | 90.35 | 91.2333
2015-07-22 12:15 | 65.6333 | 74 | 91.1 | 91.7333
2015-07-22 12:30 | 66.1333 | 74 | 91.85 | 92.2333
2015-07-22 12:45 | 66.6333 | 74 | 92.6 | 92.7333
2015-07-22 13:00 | 66.8667 | 74 | 93.1167 | 93.1167
2015-07-22 13:15 | 66.3667 | 74 | 93.3667 | 93.3667
2015-07-22 13:30 | 65.8667 | 74 | 93.6167 | 93.6167
2015-07-22 13:45 | 65.3667 | 74 | 93.8667 | 93.8667
2015-07-22 14:00 | 65.0667 | 73.7667 | 94.35 | 94.2333
2015-07-22 14:15 | 65.3167 | 73.2667 | 95.1 | 94.7333
2015-07-22 14:30 | 65.5667 | 72.7667 | 95.85 | 95.2333
2015-07-22 14:45 | 65.8167 | 72.2667 | 96.6 | 95.7333
2015-07-22 15:00 | 65.9333 | 71.8833 | 97.1167 | 95.8833
2015-07-22 15:15 | 65.6833 | 71.6333 | 97.3667 | 95.6333
2015-07-22 15:30 | 65.4333 | 71.3833 | 97.6167 | 95.3833
2015-07-22 15:45 | 65.1833 | 71.1333 | 97.8667 | 95.1333
2015-07-22 16:00 | 64.8667 | 70.7667 | 97.8833 | 94.7667
2015-07-22 16:15 | 64.3667 | 70.2667 | 97.6333 | 94.2667
2015-07-22 16:30 | 63.8667 | 69.7667 | 97.3833 | 93.7667
2015-07-22 16:45 | 63.3667 | 69.2667 | 97.1333 | 93.2667
2015-07-22 17:00 | 63 | 68.65 | 96.7667 | 92.8833
2015-07-22 17:15 | 63 | 67.9 | 96.2667 | 92.6333
2015-07-22 17:30 | 63 | 67.15 | 95.7667 | 92.3833
2015-07-22 17:45 | 63 | 66.4 | 95.2667 | 92.1333
2015-07-22 18:00 | 62.9333 | 65.8833 | 94.5625 | 91.4167
2015-07-22 18:15 | 62.6833 | 65.6333 | 93.625 | 90.1667
2015-07-22 18:30 | 62.4333 | 65.3833 | 92.6 | 88.9167
2015-07-22 18:45 | 62.1833 | 65.1333 | 91.4 | 87.6667
2015-07-22 19:00 | 62 | 64.7667 | 92 | 86.5333
2015-07-22 19:15 | 62 | 64.2667 | 87.3333 | 85.5333
2015-07-22 19:30 | 62 | 63.7667 | 87.3784 | 84.5333
2015-07-22 19:45 | 62 | 63.2667 | 87.7838 | 83.5333
2015-07-22 20:00 | 61.9333 | 62.8833 | 87.8833 | 82.7667
2015-07-22 20:15 | 61.6833 | 62.6333 | 87.6333 | 82.2667
2015-07-22 20:30 | 61.4333 | 62.3833 | 87.3833 | 81.7667
2015-07-22 20:45 | 61.1833 | 62.1333 | 87.1333 | 81.2667
2015-07-22 21:00 | 61.0667 | 61.8833 | 86.7667 | 80.5333
2015-07-22 21:15 | 61.3167 | 61.6333 | 86.2667 | 79.5333
2015-07-22 21:30 | 61.5667 | 61.3833 | 85.7667 | 78.5333
2015-07-22 21:45 | 61.8167 | 61.1333 | 85.2667 | 77.5333
2015-07-22 22:00 | 61.9333 | 61 | 84.7667 | 76.65
2015-07-22 22:15 | 61.6833 | 61 | 84.2667 | 75.9
2015-07-22 22:30 | 61.4333 | 61 | 83.7667 | 75.15
2015-07-22 22:45 | 61.1833 | 61 | 83.2667 | 74.4
2015-07-22 23:00 | 61 | 61 | 82.7667 | 73.7667
2015-07-22 23:15 | 61 | 61 | 82.2667 | 73.2667
2015-07-22 23:30 | 61 | 61 | 81.7667 | 72.7667
2015-07-22 23:45 | 61 | 61 | 81.2667 | 72.2667
2015-07-23 | 61 | 60.8833 | 80.8833 | 71.7667
2015-07-23 00:15 | 61 | 60.6333 | 80.6333 | 71.2667
2015-07-23 00:30 | 61 | 60.3833 | 80.3833 | 70.7667
2015-07-23 00:45 | 61 | 60.1333 | 80.1333 | 70.2667
2015-07-23 01:00 | 61 | 59.8833 | 79.8833 | 69.8833
2015-07-23 01:15 | 61 | 59.6333 | 79.6333 | 69.6333
2015-07-23 01:30 | 61 | 59.3833 | 79.3833 | 69.3833
2015-07-23 01:45 | 61 | 59.1333 | 79.1333 | 69.1333
2015-07-23 02:00 | 60.9333 | 59 | 78.8833 | 68.7667
2015-07-23 02:15 | 60.6833 | 59 | 78.6333 | 68.2667
2015-07-23 02:30 | 60.4333 | 59 | 78.3833 | 67.7667
2015-07-23 02:45 | 60.1833 | 59 | 78.1333 | 67.2667
2015-07-23 03:00 | 60 | 59 | 77.7667 | 66.7667
2015-07-23 03:15 | 60 | 59 | 77.2667 | 66.2667
2015-07-23 03:30 | 60 | 59 | 76.7667 | 65.7667
2015-07-23 03:45 | 60 | 59 | 76.2667 | 65.2667
2015-07-23 04:00 | 60 | 59 | 75.8833 | 65
2015-07-23 04:15 | 60 | 58.8 | 75.6333 | 65
2015-07-23 04:30 | 60 | 57.8 | 75.3833 | 65
2015-07-23 04:45 | 60 | 59 | 75.1333 | 65
2015-07-23 05:00 | 60 | 58.8833 | 74.8833 | 64.8833
2015-07-23 05:15 | 60 | 58.6333 | 74.6333 | 64.6333
2015-07-23 05:30 | 60 | 58.3833 | 74.3833 | 64.3833
2015-07-23 05:45 | 60 | 58.1333 | 74.1333 | 64.1333
2015-07-23 06:00 | 60 | 58.35 | 74.1167 | 64.35
2015-07-23 06:15 | 60 | 59.1 | 74.3667 | 65.1
2015-07-23 06:30 | 60 | 59.85 | 74.6167 | 65.85
2015-07-23 06:45 | 60 | 60.6 | 74.8667 | 66.6
2015-07-23 07:00 | 60.0667 | 61 | 75.35 | 67.35
2015-07-23 07:15 | 60.3167 | 61 | 76.1 | 68.1
2015-07-23 07:30 | 60.5667 | 61 | 76.85 | 68.85
2015-07-23 07:45 | 60.8167 | 62.0588 | 77.6 | 69.6
2015-07-23 08:00 | 61.0667 | 63.2414 | 78.5833 | 70.5833
2015-07-23 08:15 | 61.3167 | 63.7586 | 79.8333 | 71.8333
2015-07-23 08:30 | 61.5667 | 64.2581 | 81.0833 | 73.0833
2015-07-23 08:45 | 61.8167 | 64.7419 | 82.3333 | 74.3333
2015-07-23 09:00 | 62 | 65.35 | 83.4667 | 75.5833
2015-07-23 09:15 | 62 | 66.1 | 84.4667 | 76.8333
2015-07-23 09:30 | 62 | 66.85 | 85.4667 | 78.0833
2015-07-23 09:45 | 62 | 67.6 | 86.4667 | 79.3333
2015-07-23 10:00 | 62.1333 | 68.4667 | 87.35 | 80.5833
2015-07-23 10:15 | 62.6333 | 69.4667 | 88.1 | 81.8333
2015-07-23 10:30 | 63.1333 | 70.4667 | 88.85 | 83.0833
2015-07-23 10:45 | 63.6333 | 71.4667 | 89.6 | 84.3333
2015-07-23 11:00 | 63.9333 | 72.1167 | 90.4667 | 85.1167
2015-07-23 11:15 | 63.6833 | 72.3667 | 91.4667 | 85.3667
2015-07-23 11:30 | 63.4333 | 72.6167 | 92.4667 | 85.6167
2015-07-23 11:45 | 63.1833 | 72.8667 | 93.4667 | 85.8667
2015-07-23 12:00 | 63.2667 | 73 | 94.1167 | 86.5833
2015-07-23 12:15 | 64.2667 | 73 | 94.3667 | 87.8333
2015-07-23 12:30 | 65.2667 | 73 | 94.6167 | 89.0833
2015-07-23 12:45 | 66.2667 | 73 | 94.8667 | 90.3333
2015-07-23 13:00 | 66.9333 | 72.8833 | 95.35 | 91.1167
2015-07-23 13:15 | 66.6833 | 72.6333 | 96.1 | 91.3667
2015-07-23 13:30 | 66.4333 | 72.3833 | 96.85 | 91.6167
2015-07-23 13:45 | 66.1833 | 72.1333 | 97.6 | 91.8667
2015-07-23 14:00 | 66 | 71.8833 | 98 | 91.8833
2015-07-23 14:15 | 66 | 71.6333 | 98 | 91.6333
2015-07-23 14:30 | 66 | 71.3833 | 98 | 91.3833
2015-07-23 14:45 | 66 | 71.1333 | 98 | 91.1333
2015-07-23 15:00 | 66 | 71 | 98.1167 | 91
2015-07-23 15:15 | 66 | 71 | 98.3667 | 91
2015-07-23 15:30 | 66 | 71 | 98.6167 | 91
2015-07-23 15:45 | 66 | 71 | 98.8667 | 91
2015-07-23 16:00 | 66 | 70.8833 | 99.1167 | 91
2015-07-23 16:15 | 66 | 70.6333 | 99.3667 | 91
2015-07-23 16:30 | 66 | 70.3833 | 99.6167 | 91
2015-07-23 16:45 | 66 | 70.1333 | 99.8667 | 91
2015-07-23 17:00 | 65.8667 | 69.7667 | 99.65 | 90.8833
2015-07-23 17:15 | 65.3667 | 69.2667 | 98.9 | 90.6333
2015-07-23 17:30 | 64.8667 | 68.7667 | 98.15 | 90.3833
2015-07-23 17:45 | 64.3667 | 68.2667 | 97.4 | 90.1333
2015-07-23 18:00 | 63.8667 | 67.65 | 96.7667 | 89.65
2015-07-23 18:15 | 63.3667 | 66.9 | 96.2667 | 88.9
2015-07-23 18:30 | 62.8667 | 66.15 | 95.7667 | 88.15
2015-07-23 18:45 | 62.3667 | 65.4 | 95.2667 | 87.4
2015-07-23 19:00 | 61.9333 | 64.7667 | 94.5333 | 86.65
2015-07-23 19:15 | 61.6833 | 64.2667 | 93.5333 | 85.9
2015-07-23 19:30 | 61.4333 | 63.7667 | 92.5333 | 85.15
2015-07-23 19:45 | 61.1833 | 63.2667 | 91.5333 | 84.4
2015-07-23 20:00 | 61 | 62.8833 | 90.65 | 83.7667
2015-07-23 20:15 | 61 | 62.6333 | 89.9 | 83.2667
2015-07-23 20:30 | 61 | 62.3833 | 89.15 | 82.7667
2015-07-23 20:45 | 61 | 62.1333 | 88.4 | 82.2667
2015-07-23 21:00 | 61 | 61.8833 | 87.7667 | 81.5333
2015-07-23 21:15 | 61 | 61.6333 | 87.2667 | 80.5333
2015-07-23 21:30 | 61 | 61.3833 | 86.7667 | 79.5333
2015-07-23 21:45 | 61 | 61.1333 | 86.2667 | 78.5333
2015-07-23 22:00 | 60.9333 | 61 | 85.65 | 77.65
2015-07-23 22:15 | 60.6833 | 61 | 84.9 | 76.9
2015-07-23 22:30 | 60.4333 | 61 | 84.15 | 76.15
2015-07-23 22:45 | 60.1833 | 61 | 83.4 | 75.4
2015-07-23 23:00 | 60.0667 | 60.8833 | 82.8833 | 74.65
2015-07-23 23:15 | 60.3167 | 60.6333 | 82.6333 | 73.9
2015-07-23 23:30 | 60.5667 | 60.3833 | 82.3833 | 73.15
2015-07-23 23:45 | 60.8167 | 60.1333 | 82.1333 | 72.4
2015-07-24 | 61 | 60 | 81.8833 | 71.7667
2015-07-24 00:15 | 61 | 60 | 81.6333 | 71.2667
2015-07-24 00:30 | 61 | 60 | 81.3833 | 70.7667
2015-07-24 00:45 | 61 | 60 | 81.1333 | 70.2667
2015-07-24 01:00 | 61 | 59.7667 | 80.7667 | 69.8833
2015-07-24 01:15 | 61 | 59.2667 | 80.2667 | 69.6333
2015-07-24 01:30 | 61 | 58.7667 | 79.7667 | 69.3833
2015-07-24 01:45 | 61 | 58.2667 | 79.2667 | 69.1333
2015-07-24 02:00 | 60.9333 | 58 | 78.65 | 68.7667
2015-07-24 02:15 | 60.6833 | 58 | 77.9 | 68.2667
2015-07-24 02:30 | 60.4333 | 58 | 77.15 | 67.7667
2015-07-24 02:45 | 60.1833 | 58 | 76.4 | 67.2667
2015-07-24 03:00 | 59.8919 | 57.7667 | 75.8833 | 66.7667
2015-07-24 03:15 | 59.4865 | 57.2667 | 75.6333 | 66.2667
2015-07-24 03:30 | 59.0811 | 56.7667 | 75.3833 | 65.7667
2015-07-24 03:45 | 59 | 56.2667 | 75.1333 | 65.2667
2015-07-24 04:00 | 58.9333 | 55.86 | 74.8833 | 64.8833
2015-07-24 04:15 | 58.6833 | 55.56 | 74.6333 | 64.6333
2015-07-24 04:30 | 58.4333 | 55.26 | 74.3833 | 64.3833
2015-07-24 04:45 | 58.1833 | 55 | 74.1333 | 64.1333
2015-07-24 05:00 | 58.1333 | 55.1167 | 73.7667 | 64.1167
2015-07-24 05:15 | 58.6333 | 55.3667 | 73.2667 | 64.3667
2015-07-24 05:30 | 59.1333 | 55.6167 | 72.7667 | 64.6167
2015-07-24 05:45 | 59.6333 | 55.8667 | 72.2667 | 64.8667
2015-07-24 06:00 | 60.1333 | 56.4667 | 72.2333 | 65.35
2015-07-24 06:15 | 60.6333 | 57.4667 | 72.7333 | 66.1
2015-07-24 06:30 | 61.1333 | 58.4667 | 73.2333 | 66.85
2015-07-24 06:45 | 61.6333 | 59.4667 | 73.7333 | 67.6
2015-07-24 07:00 | 62.0667 | 60.35 | 74.4667 | 68.5833
2015-07-24 07:15 | 62.3167 | 61.1 | 75.4667 | 69.8333
2015-07-24 07:30 | 62.5667 | 61.85 | 76.4667 | 71.0833
2015-07-24 07:45 | 62.8167 | 62.6 | 77.4667 | 72.3333
2015-07-24 08:00 | 63.2 | 63.2333 | 78.5833 | 73.4667
2015-07-24 08:15 | 63.95 | 63.7333 | 79.8333 | 74.4667
2015-07-24 08:30 | 64.7 | 64.2333 | 81.0833 | 75.4667
2015-07-24 08:45 | 65.45 | 64.7333 | 82.3333 | 76.4667
2015-07-24 09:00 | 66.1333 | 65.35 | 83.7 | 77.4667
2015-07-24 09:15 | 66.6333 | 66.1 | 85.2 | 78.4667
2015-07-24 09:30 | 67.1333 | 66.85 | 86.7 | 79.4667
2015-07-24 09:45 | 67.6333 | 67.6 | 88.2 | 80.4667
2015-07-24 10:00 | 68.1333 | 68.35 | 89.35 | 81.5833
2015-07-24 10:15 | 68.6333 | 69.1 | 90.1 | 82.8333
2015-07-24 10:30 | 69.1333 | 69.85 | 90.85 | 84.0833
2015-07-24 10:45 | 69.6333 | 70.6 | 91.6 | 85.3333
2015-07-24 11:00 | 70.0667 | 71.35 | 92.35 | 86.35
2015-07-24 11:15 | 70.3167 | 72.1 | 93.1 | 87.1
2015-07-24 11:30 | 70.5667 | 72.85 | 93.85 | 87.85
2015-07-24 11:45 | 70.8167 | 73.6 | 94.6 | 88.6
2015-07-24 12:00 | 71.0667 | 74.2333 | 95.2333 | 89.2333
2015-07-24 12:15 | 71.3167 | 74.7333 | 95.7333 | 89.7333
2015-07-24 12:30 | 71.5667 | 75.2333 | 96.2333 | 90.2333
2015-07-24 12:45 | 71.8167 | 75.7333 | 96.7333 | 90.7333
2015-07-24 13:00 | 72 | 76.1167 | 97.2333 | 91.2333
2015-07-24 13:15 | 72 | 76.3667 | 97.7333 | 91.7333
2015-07-24 13:30 | 72 | 76.6167 | 98.2333 | 92.2333
2015-07-24 13:45 | 72 | 76.8667 | 98.7333 | 92.7333
2015-07-24 14:00 | 71.9333 | 77.1167 | 99 | 93.1167
2015-07-24 14:15 | 71.6833 | 77.3667 | 99 | 93.3667
2015-07-24 14:30 | 71.4333 | 77.6167 | 99 | 93.6167
2015-07-24 14:45 | 71.1833 | 77.8667 | 99 | 93.8667
2015-07-24 15:00 | 70.8667 | 77.8833 | 99.1167 | 94.1167
2015-07-24 15:15 | 70.3667 | 77.6333 | 99.3667 | 94.3667
2015-07-24 15:30 | 69.8667 | 77.3833 | 99.6167 | 94.6167
2015-07-24 15:45 | 69.3667 | 77.1333 | 99.8667 | 94.8667
2015-07-24 16:00 | 68.9333 | 76.65 | 99.8833 | 95
2015-07-24 16:15 | 68.6833 | 75.9 | 99.6333 | 95
2015-07-24 16:30 | 68.4333 | 75.15 | 99.3833 | 95
2015-07-24 16:45 | 68.1833 | 74.4 | 99.1333 | 95
2015-07-24 17:00 | 67.9333 | 73.65 | 98.7667 | 94.7667
2015-07-24 17:15 | 67.6833 | 72.9 | 98.2667 | 94.2667
2015-07-24 17:30 | 67.4333 | 72.15 | 97.7667 | 93.7667
2015-07-24 17:45 | 67.1833 | 71.4 | 97.2667 | 93.2667
2015-07-24 18:00 | 66.8 | 70.65 | 96.65 | 92.65
2015-07-24 18:15 | 66.05 | 69.9 | 95.9 | 91.9
2015-07-24 18:30 | 65.3 | 69.15 | 95.15 | 91.15
2015-07-24 18:45 | 64.55 | 68.4 | 94.4 | 90.4
2015-07-24 19:00 | 63.9333 | 67.7667 | 93.5333 | 89.65
2015-07-24 19:15 | 63.6833 | 67.2667 | 92.5333 | 88.9
2015-07-24 19:30 | 63.4333 | 66.7667 | 91.5333 | 88.15
2015-07-24 19:45 | 63.1833 | 66.2667 | 90.5333 | 87.4
2015-07-24 20:00 | 62.9333 | 65.8833 | 89.65 | 86.7667
2015-07-24 20:15 | 62.6833 | 65.6333 | 88.9 | 86.2667
2015-07-24 20:30 | 62.4333 | 65.3833 | 88.15 | 85.7667
2015-07-24 20:45 | 62.1833 | 65.1333 | 87.4 | 85.2667
2015-07-24 21:00 | 61.9333 | 64.8833 | 86.7667 | 84.5333
2015-07-24 21:15 | 61.6833 | 64.6333 | 86.2667 | 83.5333
2015-07-24 21:30 | 61.4333 | 64.3833 | 85.7667 | 82.5333
2015-07-24 21:45 | 61.1833 | 64.1333 | 85.2667 | 81.5333
2015-07-24 22:00 | 60.8667 | 63.8833 | 84.7667 | 80.7667
2015-07-24 22:15 | 60.3667 | 63.6333 | 84.2667 | 80.2667
2015-07-24 22:30 | 59.8667 | 63.3833 | 83.7667 | 79.7667
2015-07-24 22:45 | 59.3667 | 63.1333 | 83.2667 | 79.2667
2015-07-24 23:00 | 59 | 62.8833 | 82.7667 | 78.65
2015-07-24 23:15 | 59 | 62.6333 | 82.2667 | 77.9
2015-07-24 23:30 | 59 | 62.3833 | 81.7667 | 77.15
2015-07-24 23:45 | 59 | 62.1333 | 81.2667 | 76.4
2015-07-25 | 59 | 61.7667 | 80.8833 | 75.7667
2015-07-25 00:15 | 59 | 61.2667 | 80.6333 | 75.2667
2015-07-25 00:30 | 59 | 60.7667 | 80.3833 | 74.7667
2015-07-25 00:45 | 59 | 60.2667 | 80.1333 | 74.2667
2015-07-25 01:00 | 59 | 59.8833 | 79.8833 | 73.65
2015-07-25 01:15 | 59 | 59.6333 | 79.6333 | 72.9
2015-07-25 01:30 | 59 | 59.3833 | 79.3833 | 72.15
2015-07-25 01:45 | 59 | 59.1333 | 79.1333 | 71.4
2015-07-25 02:00 | 59 | 59.1167 | 78.8833 | 70.7667
2015-07-25 02:15 | 59 | 59.3667 | 78.6333 | 70.2667
2015-07-25 02:30 | 59 | 59.6167 | 78.3833 | 69.7667
2015-07-25 02:45 | 59 | 59.8667 | 78.1333 | 69.2667
2015-07-25 03:00 | 59 | 59.7667 | 77.8833 | 68.7667
2015-07-25 03:15 | 59 | 59.2667 | 77.6333 | 68.2667
2015-07-25 03:30 | 59 | 58.7667 | 77.3833 | 67.7667
2015-07-25 03:45 | 59 | 58.2667 | 77.1333 | 67.2667
2015-07-25 04:00 | 59 | 58 | 76.8833 | 67
2015-07-25 04:15 | 59 | 58 | 76.6333 | 67
2015-07-25 04:30 | 59 | 58 | 76.3833 | 67
2015-07-25 04:45 | 59 | 58 | 76.1333 | 67
2015-07-25 05:00 | 59 | 58.2333 | 75.8833 | 67.1167
2015-07-25 05:15 | 59 | 58.7333 | 75.6333 | 67.3667
2015-07-25 05:30 | 59 | 59.2333 | 75.3833 | 67.6167
2015-07-25 05:45 | 59 | 59.7333 | 75.1333 | 67.8667
2015-07-25 06:00 | 59.0667 | 60.2333 | 75 | 68.5833
2015-07-25 06:15 | 59.3167 | 60.7333 | 75 | 69.8333
2015-07-25 06:30 | 59.5667 | 61.2333 | 75 | 71.0833
2015-07-25 06:45 | 59.8167 | 61.7333 | 75 | 72.3333
2015-07-25 07:00 | 60 | 62.2333 | 75.4667 | 73.4667
2015-07-25 07:15 | 60 | 62.7333 | 76.4667 | 74.4667
2015-07-25 07:30 | 60 | 63.2333 | 77.4667 | 75.4667
2015-07-25 07:45 | 60 | 63.7333 | 78.4667 | 76.4667
2015-07-25 08:00 | 60.1333 | 64.35 | 79.5833 | 77.5833
2015-07-25 08:15 | 60.6333 | 65.1 | 80.8333 | 78.8333
2015-07-25 08:30 | 61.1333 | 65.85 | 82.0833 | 80.0833
2015-07-25 08:45 | 61.6333 | 66.6 | 83.3333 | 81.3333
2015-07-25 09:00 | 62.0667 | 67.2333 | 84.7 | 82.4667
2015-07-25 09:15 | 62.3167 | 67.7333 | 86.2 | 83.4667
2015-07-25 09:30 | 62.5667 | 68.2333 | 87.7 | 84.4667
2015-07-25 09:45 | 62.8167 | 68.7333 | 89.2 | 85.4667
2015-07-25 10:00 | 63.1333 | 69.2333 | 90.35 | 86.35
2015-07-25 10:15 | 63.6333 | 69.7333 | 91.1 | 87.1
2015-07-25 10:30 | 64.1333 | 70.2333 | 91.85 | 87.85
2015-07-25 10:45 | 64.6333 | 70.7333 | 92.6 | 88.6
2015-07-25 11:00 | 65 | 71.35 | 93.2333 | 89.35
2015-07-25 11:15 | 65 | 72.1 | 93.7333 | 90.1
2015-07-25 11:30 | 65 | 72.85 | 94.2333 | 90.85
2015-07-25 11:45 | 65 | 73.6 | 94.7333 | 91.6
2015-07-25 12:00 | 65.0667 | 74 | 95.35 | 92.2333
2015-07-25 12:15 | 65.3167 | 74 | 96.1 | 92.7333
2015-07-25 12:30 | 65.5667 | 74 | 96.85 | 93.2333
2015-07-25 12:45 | 65.8167 | 74 | 97.6 | 93.7333
2015-07-25 13:00 | 66.1333 | 74 | 98 | 94
2015-07-25 13:15 | 66.6333 | 74 | 98 | 94
2015-07-25 13:30 | 67.1333 | 74 | 98 | 94
2015-07-25 13:45 | 67.6333 | 74 | 98 | 94
2015-07-25 14:00 | 67.9333 | 74 | 98.2333 | 94.2333
2015-07-25 14:15 | 67.6833 | 74 | 98.7333 | 94.7333
2015-07-25 14:30 | 67.4333 | 74 | 99.2333 | 95.2333
2015-07-25 14:45 | 67.1833 | 74 | 99.7333 | 95.7333
2015-07-25 15:00 | 66.9333 | 73.7667 | 100 | 95.8833
2015-07-25 15:15 | 66.6833 | 73.2667 | 100 | 95.6333
2015-07-25 15:30 | 66.4333 | 72.7667 | 100 | 95.3833
2015-07-25 15:45 | 66.1833 | 72.2667 | 100 | 95.1333
2015-07-25 16:00 | 65.8 | 71.7667 | 98.0556 | 95
2015-07-25 16:15 | 65.05 | 71.2667 | 93.8889 | 95
2015-07-25 16:30 | 64.3 | 70.7667 | 89.9167 | 95
2015-07-25 16:45 | 63.55 | 70.2667 | 88.6667 | 95
2015-07-25 17:00 | 62.8667 | 69.65 | 88.6176 | 94.7667
2015-07-25 17:15 | 62.3667 | 68.9 | 89.9412 | 94.2667
2015-07-25 17:30 | 61.8667 | 68.15 | 90.8846 | 93.7667
2015-07-25 17:45 | 61.3667 | 67.4 | 90.3077 | 93.2667
2015-07-25 18:00 | 61 | 66.65 | 89.4167 | 92.7667
2015-07-25 18:15 | 61 | 65.9 | 88.1667 | 92.2667
2015-07-25 18:30 | 61 | 65.15 | 86.9167 | 91.7667
2015-07-25 18:45 | 61 | 64.4 | 85.6667 | 91.2667
2015-07-25 19:00 | 60.9333 | 63.6957 | 85.28 | 90.5333
2015-07-25 19:15 | 60.6833 | 63.0435 | 85.88 | 89.5333
2015-07-25 19:30 | 60.4333 | 63 | 87.7143 | 88.5333
2015-07-25 19:45 | 60.1833 | 63 | 89.8571 | 87.5333
2015-07-25 20:00 | 60.0667 | 62 | 90.65 | 86.65
2015-07-25 20:15 | 60.3167 | 62 | 89.9 | 85.9
2015-07-25 20:30 | 60.5667 | 62 | 89.15 | 85.15
2015-07-25 20:45 | 60.8167 | 62 | 88.4 | 84.4
2015-07-25 21:00 | 61 | 62 | 84.5 | 83.5333
2015-07-25 21:15 | 61 | 62 | 81.1667 | 82.5333
2015-07-25 21:30 | 61 | 62 | 79.9167 | 81.5333
2015-07-25 21:45 | 61 | 62 | 78.6667 | 80.5333
2015-07-25 22:00 | 61 | 61.8833 | 78.1167 | 79.65
2015-07-25 22:15 | 61 | 61.6333 | 78.3667 | 78.9
2015-07-25 22:30 | 61 | 61.3833 | 78.6167 | 78.15
2015-07-25 22:45 | 61 | 61.1333 | 78.8667 | 77.4
2015-07-25 23:00 | 61 | 61 | 78.7667 | 76.7667
2015-07-25 23:15 | 61 | 61 | 78.2667 | 76.2667
2015-07-25 23:30 | 61 | 61 | 77.7667 | 75.7667
2015-07-25 23:45 | 61 | 61 | 77.2667 | 75.2667
2015-07-26 | 61 | 61 | 77.1167 | 74.65
2015-07-26 00:15 | 61 | 61 | 77.3667 | 73.9
2015-07-26 00:30 | 61 | 61 | 77.6167 | 73.15
2015-07-26 00:45 | 61 | 61 | 77.8667 | 72.4
2015-07-26 01:00 | 60.9333 | 61 | 78.1167 | 71.8833
2015-07-26 01:15 | 60.6833 | 61 | 78.3667 | 71.6333
2015-07-26 01:30 | 60.4333 | 61 | 78.6167 | 71.3833
2015-07-26 01:45 | 60.1833 | 61 | 78.8667 | 71.1333
2015-07-26 02:00 | 60 | 61 | 79 | 70.7667
2015-07-26 02:15 | 60 | 61 | 79 | 70.2667
2015-07-26 02:30 | 60 | 61 | 79 | 69.7667
2015-07-26 02:45 | 60 | 61 | 79 | 69.2667
2015-07-26 03:00 | 60.069 | 61 | 78.7667 | 69
2015-07-26 03:15 | 60.3276 | 61 | 78.2667 | 69
2015-07-26 03:30 | 60.5862 | 61 | 77.7667 | 69
2015-07-26 03:45 | 60.8448 | 61 | 77.2667 | 69
2015-07-26 04:00 | 59.8182 | 61 | 76.7667 | 68.7667
2015-07-26 04:15 | 59.1364 | 61 | 76.2667 | 68.2667
2015-07-26 04:30 | 59.3158 | 61 | 75.7667 | 67.7667
2015-07-26 04:45 | 59.7105 | 61 | 75.2667 | 67.2667
2015-07-26 05:00 | 59.3333 | 61 | 74.8833 | 67
2015-07-26 05:15 | 59.2407 | 61 | 74.6333 | 67
2015-07-26 05:30 | 59.5185 | 61 | 74.3833 | 67
2015-07-26 05:45 | 59.7963 | 61 | 74.1333 | 67
2015-07-26 06:00 | 60.1333 | 61 | 74 | 67.35
2015-07-26 06:15 | 60.6333 | 61 | 74 | 68.1
2015-07-26 06:30 | 61.1333 | 61.7895 | 74 | 68.85
2015-07-26 06:45 | 61.6333 | 62.5789 | 74 | 69.6
2015-07-26 07:00 | 62.1333 | 63.35 | 74.4667 | 70.5833
2015-07-26 07:15 | 62.6333 | 64.1 | 75.4667 | 71.8333
2015-07-26 07:30 | 63.1333 | 64.85 | 76.4667 | 73.0833
2015-07-26 07:45 | 63.6333 | 65.6 | 77.4667 | 74.3333
2015-07-26 08:00 | 64.1333 | 66.35 | 78.5833 | 75.35
2015-07-26 08:15 | 64.6333 | 67.1 | 79.8333 | 76.1
2015-07-26 08:30 | 65.1333 | 67.85 | 81.0833 | 76.85
2015-07-26 08:45 | 65.6333 | 68.6 | 82.3333 | 77.6
2015-07-26 09:00 | 66.1333 | 69.4667 | 83.5833 | 78.4667
2015-07-26 09:15 | 66.6333 | 70.4667 | 84.8333 | 79.4667
2015-07-26 09:30 | 67.1333 | 71.4667 | 86.0833 | 80.4667
2015-07-26 09:45 | 67.6333 | 72.4667 | 87.3333 | 81.4667
2015-07-26 10:00 | 68.1333 | 73.4667 | 88.5833 | 82.4667
2015-07-26 10:15 | 68.6333 | 74.4667 | 89.8333 | 83.4667
2015-07-26 10:30 | 69.1333 | 75.4667 | 91.0833 | 84.4667
2015-07-26 10:45 | 69.6333 | 76.4667 | 92.3333 | 85.4667
2015-07-26 11:00 | 70.2667 | 77.1167 | 93.35 | 86.35
2015-07-26 11:15 | 71.2667 | 77.3667 | 94.1 | 87.1
2015-07-26 11:30 | 72.2667 | 77.6167 | 94.85 | 87.85
2015-07-26 11:45 | 73.2667 | 77.8667 | 95.6 | 88.6
2015-07-26 12:00 | 73.4286 | 77.8833 | 96 | 89.2333
2015-07-26 12:15 | 71.8679 | 77.6333 | 96 | 89.7333
2015-07-26 12:30 | 70.4528 | 77.3833 | 96 | 90.2333
2015-07-26 12:45 | 69.0377 | 77.1333 | 96 | 90.7333
2015-07-26 13:00 | 68.0667 | 77.1167 | 96.2333 | 91.35
2015-07-26 13:15 | 68.3167 | 77.3667 | 96.7333 | 92.1
2015-07-26 13:30 | 68.5667 | 77.6167 | 97.2333 | 92.85
2015-07-26 13:45 | 68.8167 | 77.8667 | 97.7333 | 93.6
2015-07-26 14:00 | 69.0667 | 77.65 | 98.35 | 94.1167
2015-07-26 14:15 | 69.3167 | 76.9 | 99.1 | 94.3667
2015-07-26 14:30 | 69.5667 | 76.15 | 99.85 | 94.6167
2015-07-26 14:45 | 69.8167 | 75.4 | 100.6 | 94.8667
2015-07-26 15:00 | 69.8667 | 75.1167 | 101.1167 | 95
2015-07-26 15:15 | 69.3667 | 75.3667 | 101.3667 | 95
2015-07-26 15:30 | 68.8667 | 75.6167 | 101.6167 | 95
2015-07-26 15:45 | 68.3667 | 75.8667 | 101.8667 | 95
2015-07-26 16:00 | 67.9333 | 75.7667 | 101.8833 | 94.8833
2015-07-26 16:15 | 67.6833 | 75.2667 | 101.6333 | 94.6333
2015-07-26 16:30 | 67.4333 | 74.7667 | 101.3833 | 94.3833
2015-07-26 16:45 | 67.1833 | 74.2667 | 101.1333 | 94.1333
2015-07-26 17:00 | 66.9333 | 73.7667 | 100.65 | 93.8833
2015-07-26 17:15 | 66.6833 | 73.2667 | 99.9 | 93.6333
2015-07-26 17:30 | 66.4333 | 72.7667 | 99.15 | 93.3833
2015-07-26 17:45 | 66.1833 | 72.2667 | 98.4 | 93.1333
2015-07-26 18:00 | 65.8667 | 71.7667 | 97.8833 | 92.5333
2015-07-26 18:15 | 65.3667 | 71.2667 | 97.6333 | 91.5333
2015-07-26 18:30 | 64.8667 | 70.7667 | 97.3833 | 90.5333
2015-07-26 18:45 | 64.3667 | 70.2667 | 97.1333 | 89.5333
2015-07-26 19:00 | 63.9333 | 69.7667 | 96.6667 | 88.65
2015-07-26 19:15 | 63.6833 | 69.2667 | 95.9333 | 87.9
2015-07-26 19:30 | 63.4333 | 68.7667 | 94.9167 | 87.15
2015-07-26 19:45 | 63.1833 | 68.2667 | 93.6667 | 86.4
2015-07-26 20:00 | 62.9333 | 67.8833 | 92.7667 | 85.4167
2015-07-26 20:15 | 62.6833 | 67.6333 | 92.2667 | 84.1667
2015-07-26 20:30 | 62.4333 | 67.3833 | 91.7667 | 82.9167
2015-07-26 20:45 | 62.1833 | 67.1333 | 91.2667 | 81.6667
2015-07-26 21:00 | 61.8667 | 66.8833 | 90.65 | 80.5333
2015-07-26 21:15 | 61.3667 | 66.6333 | 89.9 | 79.5333
2015-07-26 21:30 | 60.8667 | 66.3833 | 89.15 | 78.5333
2015-07-26 21:45 | 60.3667 | 66.1333 | 88.4 | 77.5333
2015-07-26 22:00 | 60 | 65.7667 | 87.8833 | 76.7667
2015-07-26 22:15 | 60 | 65.2667 | 87.6333 | 76.2667
2015-07-26 22:30 | 60 | 64.7667 | 87.3833 | 75.7667
2015-07-26 22:45 | 60 | 64.2667 | 87.1333 | 75.2667
2015-07-26 23:00 | 59.9333 | 64.1167 | 86.7667 | 75
2015-07-26 23:15 | 59.6833 | 64.3667 | 86.2667 | 75
2015-07-26 23:30 | 59.4333 | 64.6167 | 85.7667 | 75
2015-07-26 23:45 | 59.1833 | 64.8667 | 85.2667 | 75
2015-07-27 | 59 | 64.5333 | 84.8833 | 74.5333
2015-07-27 00:15 | 59 | 63.5333 | 84.6333 | 73.5333
2015-07-27 00:30 | 59 | 62.5333 | 84.3833 | 72.5333
2015-07-27 00:45 | 59 | 61.5333 | 84.1333 | 71.5333
2015-07-27 01:00 | 58.9333 | 60.8833 | 83.8833 | 70.7667
2015-07-27 01:15 | 58.6833 | 60.6333 | 83.6333 | 70.2667
2015-07-27 01:30 | 58.4333 | 60.3833 | 83.3833 | 69.7667
2015-07-27 01:45 | 58.1833 | 60.1333 | 83.1333 | 69.2667
2015-07-27 02:00 | 58 | 59.8833 | 82.7667 | 68.8833
2015-07-27 02:15 | 58 | 59.6333 | 82.2667 | 68.6333
2015-07-27 02:30 | 58 | 59.3833 | 81.7667 | 68.3833
2015-07-27 02:45 | 58 | 59.1333 | 81.2667 | 68.1333
2015-07-27 03:00 | 57.9333 | 59 | 80.8833 | 67.8833
2015-07-27 03:15 | 57.6833 | 59 | 80.6333 | 67.6333
2015-07-27 03:30 | 57.4333 | 59 | 80.3833 | 67.3833
2015-07-27 03:45 | 57.1833 | 59 | 80.1333 | 67.1333
2015-07-27 04:00 | 57 | 59 | 79.8833 | 66.8833
2015-07-27 04:15 | 57 | 59 | 79.6333 | 66.6333
2015-07-27 04:30 | 57 | 59 | 79.3833 | 66.3833
2015-07-27 04:45 | 57 | 59 | 79.1333 | 66.1333
2015-07-27 05:00 | 57.0667 | 59 | 78.7667 | 66.1167
2015-07-27 05:15 | 57.3167 | 59 | 78.2667 | 66.3667
2015-07-27 05:30 | 57.5667 | 59 | 77.7667 | 66.6167
2015-07-27 05:45 | 57.8167 | 59 | 77.2667 | 66.8667
2015-07-27 06:00 | 58.2667 | 59.35 | 77 | 67.2333
2015-07-27 06:15 | 59.2667 | 60.1 | 77 | 67.7333
2015-07-27 06:30 | 60.2667 | 60.85 | 77 | 68.2333
2015-07-27 06:45 | 61.2667 | 61.6 | 77 | 68.7333
2015-07-27 07:00 | 62.2667 | 62.35 | 77.4667 | 69.5833
2015-07-27 07:15 | 63.2667 | 63.1 | 78.4667 | 70.8333
2015-07-27 07:30 | 64.2667 | 63.85 | 79.4667 | 72.0833
2015-07-27 07:45 | 65.2667 | 64.6 | 80.4667 | 73.3333
2015-07-27 08:00 | 66.1333 | 65.7 | 81.4667 | 74.7
2015-07-27 08:15 | 66.6333 | 67.2 | 82.4667 | 76.2
2015-07-27 08:30 | 67.1333 | 68.7 | 83.4667 | 77.7
2015-07-27 08:45 | 67.6333 | 70.2 | 84.4667 | 79.2
2015-07-27 09:00 | 68.2 | 71.5833 | 85.5833 | 80.35
2015-07-27 09:15 | 68.95 | 72.8333 | 86.8333 | 81.1
2015-07-27 09:30 | 69.7 | 74.0833 | 88.0833 | 81.85
2015-07-27 09:45 | 70.45 | 75.3333 | 89.3333 | 82.6
2015-07-27 10:00 | 71.5333 | 76.2333 | 90.4667 | 83.35
2015-07-27 10:15 | 73.5333 | 76.7333 | 91.4667 | 84.1
2015-07-27 10:30 | 75.5333 | 77.2333 | 92.4667 | 84.85
2015-07-27 10:45 | 77.5333 | 77.7333 | 93.4667 | 85.6
2015-07-27 11:00 | 79.0667 | 78.5833 | 94.2333 | 86.2333
2015-07-27 11:15 | 79.3167 | 79.8333 | 94.7333 | 86.7333
2015-07-27 11:30 | 79.5667 | 81.0833 | 95.2333 | 87.2333
2015-07-27 11:45 | 79.8167 | 82.3333 | 95.7333 | 87.7333
2015-07-27 12:00 | 79.9333 | 83.1167 | 96.4884 | 88.2333
2015-07-27 12:15 | 79.6833 | 83.3667 | 97.5349 | 88.7333
2015-07-27 12:30 | 79.4333 | 83.6167 | 98.5814 | 89.2333
2015-07-27 12:45 | 79.1833 | 83.8667 | 97.7143 | 89.7333
2015-07-27 13:00 | 78.8 | 84.1167 | 91.3333 | 90.35
2015-07-27 13:15 | 78.05 | 84.3667 | 85.3333 | 91.1
2015-07-27 13:30 | 77.3 | 84.6167 | 84.8333 | 91.85
2015-07-27 13:45 | 76.55 | 84.8667 | 86.8571 | 92.6
2015-07-27 14:00 | 75.9333 | 85 | 87.4167 | 93.2333
2015-07-27 14:15 | 75.6833 | 85 | 86.1667 | 93.7333
2015-07-27 14:30 | 75.4333 | 85 | 84.9167 | 94.2333
2015-07-27 14:45 | 75.1833 | 85 | 83.6667 | 94.7333
2015-07-27 15:00 | 74.8667 | 84.8833 | 84.05 | 95
2015-07-27 15:15 | 74.3667 | 84.6333 | 86.3 | 95
2015-07-27 15:30 | 73.8667 | 84.3833 | 88.55 | 95
2015-07-27 15:45 | 73.3667 | 84.1333 | 90.8 | 95
2015-07-27 16:00 | 72.9333 | 83.65 | 92.5833 | 94.8833
2015-07-27 16:15 | 72.6833 | 82.9 | 93.8333 | 94.6333
2015-07-27 16:30 | 72.4333 | 82.15 | 95.0833 | 94.3833
2015-07-27 16:45 | 72.1833 | 81.4 | 96.3333 | 94.1333
2015-07-27 17:00 | 71.7333 | 80.65 | 97 | 93.8833
2015-07-27 17:15 | 70.7333 | 79.9 | 97 | 93.6333
2015-07-27 17:30 | 69.7333 | 79.15 | 97 | 93.3833
2015-07-27 17:45 | 68.7333 | 78.4 | 97 | 93.1333
2015-07-27 18:00 | 67.7333 | 77.65 | 96.86 | 92.65
2015-07-27 18:15 | 66.7333 | 76.9 | 96.56 | 91.9
2015-07-27 18:30 | 65.7333 | 76.15 | 96.26 | 91.15
2015-07-27 18:45 | 64.7333 | 75.4 | 95.8 | 90.4
2015-07-27 19:00 | 63.8 | 74.65 | 94.5333 | 89.65
2015-07-27 19:15 | 63.05 | 73.9 | 93.5333 | 88.9
2015-07-27 19:30 | 62.3 | 73.15 | 92.5333 | 88.15
2015-07-27 19:45 | 61.55 | 72.4 | 91.5333 | 87.4
2015-07-27 20:00 | 61 | 71.7667 | 90.7667 | 86.7667
2015-07-27 20:15 | 61 | 71.2667 | 90.2667 | 86.2667
2015-07-27 20:30 | 61 | 70.7667 | 89.7667 | 85.7667
2015-07-27 20:45 | 61 | 70.2667 | 89.2667 | 85.2667
2015-07-27 21:00 | 61 | 69.65 | 88.65 | 84.7667
2015-07-27 21:15 | 61 | 68.9 | 87.9 | 84.2667
2015-07-27 21:30 | 61 | 68.15 | 87.15 | 83.7667
2015-07-27 21:45 | 61 | 67.4 | 86.4 | 83.2667
2015-07-27 22:00 | 60.9333 | 66.8833 | 85.8833 | 82.5333
2015-07-27 22:15 | 60.6833 | 66.6333 | 85.6333 | 81.5333
2015-07-27 22:30 | 60.4333 | 66.3833 | 85.3833 | 80.5333
2015-07-27 22:45 | 60.1833 | 66.1333 | 85.1333 | 79.5333
2015-07-27 23:00 | 60 | 65.8833 | 84.7667 | 78.8833
2015-07-27 23:15 | 60 | 65.6333 | 84.2667 | 78.6333
2015-07-27 23:30 | 60 | 65.3833 | 83.7667 | 78.3833
2015-07-27 23:45 | 60 | 65.1333 | 83.2667 | 78.1333
2015-07-28 | 60 | 65 | 82.8833 | 77.65
2015-07-28 00:15 | 60 | 65 | 82.6333 | 76.9
2015-07-28 00:30 | 60 | 65 | 82.3833 | 76.15
2015-07-28 00:45 | 60 | 65 | 82.1333 | 75.4
2015-07-28 01:00 | 59.9333 | 64.7667 | 81.8833 | 74.7667
2015-07-28 01:15 | 59.6833 | 64.2667 | 81.6333 | 74.2667
2015-07-28 01:30 | 59.4333 | 63.7667 | 81.3833 | 73.7667
2015-07-28 01:45 | 59.1833 | 63.2667 | 81.1333 | 73.2667
2015-07-28 02:00 | 58.9333 | 63 | 80.8833 | 72.7667
2015-07-28 02:15 | 58.6833 | 63 | 80.6333 | 72.2667
2015-07-28 02:30 | 58.4333 | 63 | 80.3833 | 71.7667
2015-07-28 02:45 | 58.1833 | 63 | 80.1333 | 71.2667
2015-07-28 03:00 | 58 | 62.8833 | 79.65 | 71
2015-07-28 03:15 | 58 | 62.6333 | 78.9 | 71
2015-07-28 03:30 | 58 | 62.3833 | 78.15 | 71
2015-07-28 03:45 | 58 | 62.1333 | 77.4 | 71
2015-07-28 04:00 | 58 | 61.7667 | 76.7667 | 70.8833
2015-07-28 04:15 | 58 | 61.2667 | 76.2667 | 70.6333
2015-07-28 04:30 | 58 | 60.7667 | 75.7667 | 70.3833
2015-07-28 04:45 | 58 | 60.2667 | 75.2667 | 70.1333
2015-07-28 05:00 | 58.1333 | 60.2333 | 74.8833 | 70
2015-07-28 05:15 | 58.6333 | 60.7333 | 74.6333 | 70
2015-07-28 05:30 | 59.1333 | 61.2333 | 74.3833 | 70
2015-07-28 05:45 | 59.6333 | 61.7333 | 74.1333 | 70
2015-07-28 06:00 | 60.3333 | 62.35 | 74.1167 | 70.5833
2015-07-28 06:15 | 61.5833 | 63.1 | 74.3667 | 71.8333
2015-07-28 06:30 | 62.8333 | 63.85 | 74.6167 | 73.0833
2015-07-28 06:45 | 64.0833 | 64.6 | 74.8667 | 74.3333
2015-07-28 07:00 | 65.1333 | 65.5833 | 75.5833 | 75.4667
2015-07-28 07:15 | 65.6333 | 66.8333 | 76.8333 | 76.4667
2015-07-28 07:30 | 66.1333 | 68.0833 | 78.0833 | 77.4667
2015-07-28 07:45 | 66.6333 | 69.3333 | 79.3333 | 78.4667
2015-07-28 08:00 | 67.1333 | 70.7 | 80.5833 | 79.4667
2015-07-28 08:15 | 67.6333 | 72.2 | 81.8333 | 80.4667
2015-07-28 08:30 | 68.1333 | 73.7 | 83.0833 | 81.4667
2015-07-28 08:45 | 68.6333 | 75.2 | 84.3333 | 82.4667
2015-07-28 09:00 | 69.2 | 76.5833 | 85.5833 | 83.4667
2015-07-28 09:15 | 69.95 | 77.8333 | 86.8333 | 84.4667
2015-07-28 09:30 | 70.7 | 79.0833 | 88.0833 | 85.4667
2015-07-28 09:45 | 71.45 | 80.3333 | 89.3333 | 86.4667
2015-07-28 10:00 | 72.1333 | 81.4667 | 90.35 | 87.4667
2015-07-28 10:15 | 72.6333 | 82.4667 | 91.1 | 88.4667
2015-07-28 10:30 | 73.1333 | 83.4667 | 91.85 | 89.4667
2015-07-28 10:45 | 73.6333 | 84.4667 | 92.6 | 90.4667
2015-07-28 11:00 | 74.8 | 85.4667 | 93.2333 | 91.2333
2015-07-28 11:15 | 77.8 | 86.4667 | 93.7333 | 91.7333
2015-07-28 11:30 | 80.8 | 87.4667 | 94.2333 | 92.2333
2015-07-28 11:45 | 83.8 | 88.4667 | 94.7333 | 92.7333
2015-07-28 12:00 | 86.0667 | 89.2333 | 95.1167 | 93.35
2015-07-28 12:15 | 86.3167 | 89.7333 | 95.3667 | 94.1
2015-07-28 12:30 | 86.5667 | 90.2333 | 95.6167 | 94.85
2015-07-28 12:45 | 86.8167 | 90.7333 | 95.8667 | 95.6
2015-07-28 13:00 | 86.7333 | 91.2333 | 96.35 | 96.2333
2015-07-28 13:15 | 85.7333 | 91.7333 | 97.1 | 96.7333
2015-07-28 13:30 | 84.7333 | 92.2333 | 97.85 | 97.2333
2015-07-28 13:45 | 83.7333 | 92.7333 | 98.6 | 97.7333
2015-07-28 14:00 | 83.1333 | 93 | 99 | 98
2015-07-28 14:15 | 83.6333 | 93 | 99 | 98
2015-07-28 14:30 | 84.1333 | 93 | 99 | 98
2015-07-28 14:45 | 84.6333 | 93 | 99 | 98
2015-07-28 15:00 | 84.8 | 92.5333 | 98.7667 | 98.35
2015-07-28 15:15 | 84.05 | 91.5333 | 98.2667 | 99.1
2015-07-28 15:30 | 83.3 | 90.5333 | 97.7667 | 99.85
2015-07-28 15:45 | 82.55 | 89.5333 | 97.2667 | 100.6
2015-07-28 16:00 | 81.9333 | 89 | 96.65 | 100.8833
2015-07-28 16:15 | 81.6833 | 89 | 95.9 | 100.6333
2015-07-28 16:30 | 81.4333 | 89 | 95.15 | 100.3833
2015-07-28 16:45 | 81.1833 | 89 | 94.4 | 100.1333
2015-07-28 17:00 | 80.8667 | 88.7667 | 94.1167 | 99.8833
2015-07-28 17:15 | 80.3667 | 88.2667 | 94.3667 | 99.6333
2015-07-28 17:30 | 79.8667 | 87.7667 | 94.6167 | 99.3833
2015-07-28 17:45 | 79.3667 | 87.2667 | 94.8667 | 99.1333
2015-07-28 18:00 | 78.5333 | 86.5333 | 94.7667 | 98.65
2015-07-28 18:15 | 76.7833 | 85.5333 | 94.2667 | 97.9
2015-07-28 18:30 | 75.0333 | 84.5333 | 93.7667 | 97.15
2015-07-28 18:45 | 73.2833 | 83.5333 | 93.2667 | 96.4
2015-07-28 19:00 | 71.8 | 82.4167 | 92.65 | 95.5333
2015-07-28 19:15 | 71.05 | 81.1667 | 91.9 | 94.5333
2015-07-28 19:30 | 70.3 | 79.9167 | 91.15 | 93.5333
2015-07-28 19:45 | 69.55 | 78.6667 | 90.4 | 92.5333
2015-07-28 20:00 | 69.1333 | 77.7667 | 89.7667 | 91.5333
2015-07-28 20:15 | 69.6333 | 77.2667 | 89.2667 | 90.5333
2015-07-28 20:30 | 70.1333 | 76.7667 | 88.7667 | 89.5333
2015-07-28 20:45 | 70.6333 | 76.2667 | 88.2667 | 88.5333
2015-07-28 21:00 | 70.8667 | 75.8833 | 87.7667 | 87.7667
2015-07-28 21:15 | 70.3667 | 75.6333 | 87.2667 | 87.2667
2015-07-28 21:30 | 69.8667 | 75.3833 | 86.7667 | 86.7667
2015-07-28 21:45 | 69.3667 | 75.1333 | 86.2667 | 86.2667
2015-07-28 22:00 | 68.8 | 74.8833 | 85.7667 | 85.7667
2015-07-28 22:15 | 68.05 | 74.6333 | 85.2667 | 85.2667
2015-07-28 22:30 | 67.3 | 74.3833 | 84.7667 | 84.7667
2015-07-28 22:45 | 66.55 | 74.1333 | 84.2667 | 84.2667
2015-07-28 23:00 | 65.8667 | 73.4167 | 83.7667 | 83.7667
2015-07-28 23:15 | 65.3667 | 72.1667 | 83.2667 | 83.2667
2015-07-28 23:30 | 64.8667 | 70.9167 | 82.7667 | 82.7667
2015-07-28 23:45 | 64.3667 | 69.6667 | 82.2667 | 82.2667
2015-07-29 | 63.9333 | 68.7667 | 81.8833 | 81.7667
2015-07-29 00:15 | 63.6833 | 68.2667 | 81.6333 | 81.2667
2015-07-29 00:30 | 63.4333 | 67.7667 | 81.3833 | 80.7667
2015-07-29 00:45 | 63.1833 | 67.2667 | 81.1333 | 80.2667
2015-07-29 01:00 | 62.9333 | 67 | 80.8833 | 79.7667
2015-07-29 01:15 | 62.6833 | 67 | 80.6333 | 79.2667
2015-07-29 01:30 | 62.4333 | 67 | 80.3833 | 78.7667
2015-07-29 01:45 | 62.1833 | 67 | 80.1333 | 78.2667
2015-07-29 02:00 | 61.8667 | 66.8833 | 79.8833 | 77.7667
2015-07-29 02:15 | 61.3667 | 66.6333 | 79.6333 | 77.2667
2015-07-29 02:30 | 60.8667 | 66.3833 | 79.3833 | 76.7667
2015-07-29 02:45 | 60.3667 | 66.1333 | 79.1333 | 76.2667
2015-07-29 03:00 | 60 | 65.7667 | 78.8833 | 75.65
2015-07-29 03:15 | 60 | 65.2667 | 78.6333 | 74.9
2015-07-29 03:30 | 60 | 64.7667 | 78.3833 | 74.15
2015-07-29 03:45 | 60 | 64.2667 | 78.1333 | 73.4
2015-07-29 04:00 | 59.8667 | 64 | 77.7667 | 73
2015-07-29 04:15 | 59.3667 | 64 | 77.2667 | 73
2015-07-29 04:30 | 58.8667 | 64 | 76.7667 | 73
2015-07-29 04:45 | 58.3667 | 64 | 76.2667 | 73
2015-07-29 05:00 | 58 | 64.1167 | 75.5333 | 73
2015-07-29 05:15 | 58 | 64.3667 | 74.5333 | 73
2015-07-29 05:30 | 58 | 64.6167 | 73.5333 | 73
2015-07-29 05:45 | 58 | 64.8667 | 72.5333 | 73
2015-07-29 06:00 | 58.2 | 65.4667 | 72 | 73.2333
2015-07-29 06:15 | 58.95 | 66.4667 | 72 | 73.7333
2015-07-29 06:30 | 59.7 | 67.4667 | 72 | 74.2333
2015-07-29 06:45 | 60.45 | 68.4667 | 72 | 74.7333
2015-07-29 07:00 | 61.3333 | 69.4667 | 72.5833 | 75.7
2015-07-29 07:15 | 62.5833 | 70.4667 | 73.8333 | 77.2
2015-07-29 07:30 | 63.8333 | 71.4667 | 75.0833 | 78.7
2015-07-29 07:45 | 65.0833 | 72.4667 | 76.3333 | 80.2
2015-07-29 08:00 | 66.1333 | 73.4667 | 77.35 | 81.7
2015-07-29 08:15 | 66.6333 | 74.4667 | 78.1 | 83.2
2015-07-29 08:30 | 67.1333 | 75.4667 | 78.85 | 84.7
2015-07-29 08:45 | 67.6333 | 76.4667 | 79.6 | 86.2
2015-07-29 09:00 | 68.2 | 77.4667 | 80.4667 | 87.4667
2015-07-29 09:15 | 68.95 | 78.4667 | 81.4667 | 88.4667
2015-07-29 09:30 | 69.7 | 79.4667 | 82.4667 | 89.4667
2015-07-29 09:45 | 70.45 | 80.4667 | 83.4667 | 90.4667
2015-07-29 10:00 | 71.3333 | 81.2333 | 84.35 | 91.5833
2015-07-29 10:15 | 72.5833 | 81.7333 | 85.1 | 92.8333
2015-07-29 10:30 | 73.8333 | 82.2333 | 85.85 | 94.0833
2015-07-29 10:45 | 75.0833 | 82.7333 | 86.6 | 95.3333
2015-07-29 11:00 | 76.0667 | 83.2333 | 87.35 | 96.35
2015-07-29 11:15 | 76.3167 | 83.7333 | 88.1 | 97.1
2015-07-29 11:30 | 76.5667 | 84.2333 | 88.85 | 97.85
2015-07-29 11:45 | 76.8167 | 84.7333 | 89.6 | 98.6
2015-07-29 12:00 | 77 | 85.4667 | 90.2333 | 99.35
2015-07-29 12:15 | 77 | 86.4667 | 90.7333 | 100.1
2015-07-29 12:30 | 77 | 87.4667 | 91.2333 | 100.85
2015-07-29 12:45 | 77 | 88.4667 | 91.7333 | 101.6
2015-07-29 13:00 | 77.0667 | 88.8833 | 92.4667 | 102.2333
2015-07-29 13:15 | 77.3167 | 88.6333 | 93.4667 | 102.7333
2015-07-29 13:30 | 77.5667 | 88.3833 | 94.4667 | 103.2333
2015-07-29 13:45 | 77.8167 | 88.1333 | 95.4667 | 103.7333
2015-07-29 14:00 | 77.9333 | 87.8833 | 96.1167 | 104.1167
2015-07-29 14:15 | 77.6833 | 87.6333 | 96.3667 | 104.3667
2015-07-29 14:30 | 77.4333 | 87.3833 | 96.6167 | 104.6167
2015-07-29 14:45 | 77.1833 | 87.1333 | 96.8667 | 104.8667
2015-07-29 15:00 | 76.8 | 86.7667 | 97.1167 | 105.1167
2015-07-29 15:15 | 76.05 | 86.2667 | 97.3667 | 105.3667
2015-07-29 15:30 | 75.3 | 85.7667 | 97.6167 | 105.6167
2015-07-29 15:45 | 74.55 | 85.2667 | 97.8667 | 105.8667
2015-07-29 16:00 | 73.7333 | 84.65 | 97.8833 | 106.1167
2015-07-29 16:15 | 72.7333 | 83.9 | 97.6333 | 106.3667
2015-07-29 16:30 | 71.7333 | 83.15 | 97.3833 | 106.6167
2015-07-29 16:45 | 70.7333 | 82.4 | 97.1333 | 106.8667
2015-07-29 17:00 | 69.8 | 81.65 | 96.8833 | 106.7667
2015-07-29 17:15 | 69.05 | 80.9 | 96.6333 | 106.2667
2015-07-29 17:30 | 68.3 | 80.15 | 96.3833 | 105.7667
2015-07-29 17:45 | 67.55 | 79.4 | 96.1333 | 105.2667
2015-07-29 18:00 | 66.8 | 78.4167 | 95.65 | 104.5333
2015-07-29 18:15 | 66.05 | 77.1667 | 94.9 | 103.5333
2015-07-29 18:30 | 65.3 | 75.9167 | 94.15 | 102.5333
2015-07-29 18:45 | 64.55 | 74.6667 | 93.4 | 101.5333
2015-07-29 19:00 | 63.8667 | 73.5333 | 92.65 | 100.4167
2015-07-29 19:15 | 63.3667 | 72.5333 | 91.9 | 99.1667
2015-07-29 19:30 | 62.8667 | 71.5333 | 91.15 | 97.9167
2015-07-29 19:45 | 62.3667 | 70.5333 | 90.4 | 96.6667
2015-07-29 20:00 | 62 | 69.8833 | 89.65 | 95.7667
2015-07-29 20:15 | 62 | 69.6333 | 88.9 | 95.2667
2015-07-29 20:30 | 62 | 69.3833 | 88.15 | 94.7667
2015-07-29 20:45 | 62 | 69.1333 | 87.4 | 94.2667
2015-07-29 21:00 | 62 | 68.7667 | 86.5333 | 93.65
2015-07-29 21:15 | 62 | 68.2667 | 85.5333 | 92.9
2015-07-29 21:30 | 62 | 67.7667 | 84.5333 | 92.15
2015-07-29 21:45 | 62 | 67.2667 | 83.5333 | 91.4
2015-07-29 22:00 | 61.9333 | 66.8833 | 82.8833 | 90.5333
2015-07-29 22:15 | 61.6833 | 66.6333 | 82.6333 | 89.5333
2015-07-29 22:30 | 61.4333 | 66.3833 | 82.3833 | 88.5333
2015-07-29 22:45 | 61.1833 | 66.1333 | 82.1333 | 87.5333
2015-07-29 23:00 | 61 | 66 | 81.7667 | 86.7667
2015-07-29 23:15 | 61 | 66 | 81.2667 | 86.2667
2015-07-29 23:30 | 61 | 66 | 80.7667 | 85.7667
2015-07-29 23:45 | 61 | 66 | 80.2667 | 85.2667
2015-07-30 | 61 | 65.8833 | 79.8833 | 84.5333
2015-07-30 00:15 | 61 | 65.6333 | 79.6333 | 83.5333
2015-07-30 00:30 | 61 | 65.3833 | 79.3833 | 82.5333
2015-07-30 00:45 | 61 | 65.1333 | 79.1333 | 81.5333
2015-07-30 01:00 | 60.9333 | 64.8833 | 78.8833 | 80.7667
2015-07-30 01:15 | 60.6833 | 64.6333 | 78.6333 | 80.2667
2015-07-30 01:30 | 60.4333 | 64.3833 | 78.3833 | 79.7667
2015-07-30 01:45 | 60.1833 | 64.1333 | 78.1333 | 79.2667
2015-07-30 02:00 | 60.0755 | 63.8833 | 77.7667 | 78.8833
2015-07-30 02:15 | 60.3585 | 63.6333 | 77.2667 | 78.6333
2015-07-30 02:30 | 60.6415 | 63.3833 | 76.7667 | 78.3833
2015-07-30 02:45 | 60.9245 | 63.1333 | 76.2667 | 78.1333
2015-07-30 03:00 | 60.087 | 63 | 76 | 77.8833
2015-07-30 03:15 | 60.413 | 63 | 76 | 77.6333
2015-07-30 03:30 | 60.7391 | 63 | 76 | 77.3833
2015-07-30 03:45 | 61 | 63 | 76 | 77.1333
2015-07-30 04:00 | 60 | 63 | 75.7667 | 76.7667
2015-07-30 04:15 | 60 | 63 | 75.2667 | 76.2667
2015-07-30 04:30 | 60 | 63 | 74.7667 | 75.7667
2015-07-30 04:45 | 60 | 63 | 74.2667 | 75.2667
2015-07-30 05:00 | 60.069 | 63.1167 | 73.7667 | 75.2333
2015-07-30 05:15 | 60.3276 | 63.3667 | 73.2667 | 75.7333
2015-07-30 05:30 | 60.5862 | 63.6167 | 72.7667 | 76.2333
2015-07-30 05:45 | 60.8448 | 63.8667 | 72.2667 | 76.7333
2015-07-30 06:00 | 61.0667 | 64.2333 | 72.1167 | 77.2333
2015-07-30 06:15 | 61.3167 | 64.7333 | 72.3667 | 77.7333
2015-07-30 06:30 | 61.5667 | 65.2333 | 72.6167 | 78.2333
2015-07-30 06:45 | 61.8167 | 65.7333 | 72.8667 | 78.7333
2015-07-30 07:00 | 62.1333 | 66.28 | 73.5833 | 79.35
2015-07-30 07:15 | 62.6333 | 66.88 | 74.8333 | 80.1
2015-07-30 07:30 | 63.1333 | 67.48 | 76.0833 | 80.85
2015-07-30 07:45 | 63.6333 | 68.2 | 77.3333 | 81.6
2015-07-30 08:00 | 64.3077 | 69.2333 | 78.7 | 82.4667
2015-07-30 08:15 | 65.4615 | 69.7333 | 80.2 | 83.4667
2015-07-30 08:30 | 66.2353 | 70.2333 | 81.7 | 84.4667
2015-07-30 08:45 | 66.6765 | 70.7333 | 83.2 | 85.4667
2015-07-30 09:00 | 67.1333 | 71.2333 | 84.4667 | 86.35
2015-07-30 09:15 | 67.6333 | 71.7333 | 85.4667 | 87.1
2015-07-30 09:30 | 68.1333 | 72.2333 | 86.4667 | 87.85
2015-07-30 09:45 | 68.6333 | 72.7333 | 87.4667 | 88.6
2015-07-30 10:00 | 69.0667 | 73.35 | 88.35 | 89.4667
2015-07-30 10:15 | 69.3167 | 74.1 | 89.1 | 90.4667
2015-07-30 10:30 | 69.5667 | 74.85 | 89.85 | 91.4667
2015-07-30 10:45 | 69.8167 | 75.6 | 90.6 | 92.4667
2015-07-30 11:00 | 70 | 76.35 | 91.4667 | 93.7
2015-07-30 11:15 | 70 | 77.1 | 92.4667 | 95.2
2015-07-30 11:30 | 70 | 77.85 | 93.4667 | 96.7
2015-07-30 11:45 | 70 | 78.6 | 94.4667 | 98.2
2015-07-30 12:00 | 70.0667 | 79 | 95.1167 | 99.35
2015-07-30 12:15 | 70.3167 | 79 | 95.3667 | 100.1
2015-07-30 12:30 | 70.5667 | 79 | 95.6167 | 100.85
2015-07-30 12:45 | 70.8167 | 79 | 95.8667 | 101.6
2015-07-30 13:00 | 71.0667 | 79.1167 | 95.7667 | 102
2015-07-30 13:15 | 71.3167 | 79.3667 | 95.2667 | 102
2015-07-30 13:30 | 71.5667 | 79.6167 | 94.7667 | 102
2015-07-30 13:45 | 71.8167 | 79.8667 | 94.2667 | 102
2015-07-30 14:00 | 71.9333 | 80.1167 | 94.1167 | 102
2015-07-30 14:15 | 71.6833 | 80.3667 | 94.3667 | 102
2015-07-30 14:30 | 71.4333 | 80.6167 | 94.6167 | 102
2015-07-30 14:45 | 71.1833 | 80.8667 | 94.8667 | 102
2015-07-30 15:00 | 70.9333 | 81 | 95.2333 | 101.7667
2015-07-30 15:15 | 70.6833 | 81 | 95.7333 | 101.2667
2015-07-30 15:30 | 70.4333 | 81 | 96.2333 | 100.7667
2015-07-30 15:45 | 70.1833 | 81 | 96.7333 | 100.2667
2015-07-30 16:00 | 69.8667 | 80.65 | 96.8833 | 99.8833
2015-07-30 16:15 | 69.3667 | 79.9 | 96.6333 | 99.6333
2015-07-30 16:30 | 68.8667 | 79.15 | 96.3833 | 99.3833
2015-07-30 16:45 | 68.3667 | 78.4 | 96.1333 | 99.1333
2015-07-30 17:00 | 67.8667 | 77.5333 | 95.8833 | 98.7667
2015-07-30 17:15 | 67.3667 | 76.5333 | 95.6333 | 98.2667
2015-07-30 17:30 | 66.8667 | 75.5333 | 95.3833 | 97.7667
2015-07-30 17:45 | 66.3667 | 74.5333 | 95.1333 | 97.2667
2015-07-30 18:00 | 65.8667 | 73.7667 | 94.7667 | 96.5333
2015-07-30 18:15 | 65.3667 | 73.2667 | 94.2667 | 95.5333
2015-07-30 18:30 | 64.8667 | 72.7667 | 93.7667 | 94.5333
2015-07-30 18:45 | 64.3667 | 72.2667 | 93.2667 | 93.5333
2015-07-30 19:00 | 63.8667 | 71.65 | 92.65 | 93
2015-07-30 19:15 | 63.3667 | 70.9 | 91.9 | 93
2015-07-30 19:30 | 62.8667 | 70.15 | 91.15 | 93
2015-07-30 19:45 | 62.3667 | 69.4 | 90.4 | 93
2015-07-30 20:00 | 62 | 68.65 | 89.4167 | 92.7667
2015-07-30 20:15 | 62 | 67.9 | 88.1667 | 92.2667
2015-07-30 20:30 | 62 | 67.15 | 86.9167 | 91.7667
2015-07-30 20:45 | 62 | 66.4 | 85.6667 | 91.2667
2015-07-30 21:00 | 61.9333 | 66 | 84.65 | 90.7667
2015-07-30 21:15 | 61.6833 | 66 | 83.9 | 90.2667
2015-07-30 21:30 | 61.4333 | 66 | 83.15 | 89.7667
2015-07-30 21:45 | 61.1833 | 66 | 82.4 | 89.2667
2015-07-30 22:00 | 61 | 65.8833 | 81.8833 | 89
2015-07-30 22:15 | 61 | 65.6333 | 81.6333 | 89
2015-07-30 22:30 | 61 | 65.3833 | 81.3833 | 89
2015-07-30 22:45 | 61 | 65.1333 | 81.1333 | 89
2015-07-30 23:00 | 60.9333 | 64.8833 | 80.8833 | 88.7667
2015-07-30 23:15 | 60.6833 | 64.6333 | 80.6333 | 88.2667
2015-07-30 23:30 | 60.4333 | 64.3833 | 80.3833 | 87.7667
2015-07-30 23:45 | 60.1833 | 64.1333 | 80.1333 | 87.2667
2015-07-31 | 60 | 64 | 79.8833 | 87
2015-07-31 00:15 | 60 | 64 | 79.6333 | 87
2015-07-31 00:30 | 60 | 64 | 79.3833 | 87
2015-07-31 00:45 | 60 | 64 | 79.1333 | 87
2015-07-31 01:00 | 60 | 64 | 78.7667 | 86.65
2015-07-31 01:15 | 60 | 64 | 78.2667 | 85.9
2015-07-31 01:30 | 60 | 64 | 77.7667 | 85.15
2015-07-31 01:45 | 60 | 64 | 77.2667 | 84.4
2015-07-31 02:00 | 60 | 64 | 76.8833 | 83.7667
2015-07-31 02:15 | 60 | 64 | 76.6333 | 83.2667
2015-07-31 02:30 | 60 | 64 | 76.3833 | 82.7667
2015-07-31 02:45 | 60 | 64 | 76.1333 | 82.2667
2015-07-31 03:00 | 60.2667 | 64 | 75.65 | 81.8833
2015-07-31 03:15 | 60.9111 | 64 | 74.9 | 81.6333
2015-07-31 03:30 | 60.5778 | 64 | 74.15 | 81.3833
2015-07-31 03:45 | 60.2444 | 64 | 73.4 | 81.1333
2015-07-31 04:00 | 60.125 | 64 | 73 | 80.8833
2015-07-31 04:15 | 60.5938 | 64 | 73 | 80.6333
2015-07-31 04:30 | 60.9286 | 64 | 73 | 80.3833
2015-07-31 04:45 | 60.3929 | 64 | 73 | 80.1333
2015-07-31 05:00 | 60.0667 | 64.1167 | 73 | 79.8833
2015-07-31 05:15 | 60.3167 | 64.3667 | 73 | 79.6333
2015-07-31 05:30 | 60.5667 | 64.6167 | 73 | 79.3833
2015-07-31 05:45 | 60.8167 | 64.8667 | 73 | 79.1333
2015-07-31 06:00 | 61.0667 | 64.86 | 73 | 79.2333
2015-07-31 06:15 | 61.3167 | 64.56 | 73 | 79.7333
2015-07-31 06:30 | 61.5667 | 64.26 | 73 | 80.2333
2015-07-31 06:45 | 61.8167 | 64.2 | 73 | 80.7333
2015-07-31 07:00 | 62.2 | 65.2333 | 73.8167 | 81.5833
2015-07-31 07:15 | 62.95 | 65.7333 | 75.5667 | 82.8333
2015-07-31 07:30 | 63.7 | 66.2333 | 77.3167 | 84.0833
2015-07-31 07:45 | 64.45 | 66.7333 | 79.0667 | 85.3333
2015-07-31 08:00 | 65.1333 | 66.8833 | 80.35 | 86.35
2015-07-31 08:15 | 65.6333 | 66.6333 | 81.1 | 87.1
2015-07-31 08:30 | 66.1333 | 66.3833 | 81.85 | 87.85
2015-07-31 08:45 | 66.6333 | 66.1333 | 82.6 | 88.6
2015-07-31 09:00 | 66.8667 | 66.5833 | 83.5833 | 89.4667
2015-07-31 09:15 | 66.3667 | 67.8333 | 84.8333 | 90.4667
2015-07-31 09:30 | 65.8667 | 69.0833 | 86.0833 | 91.4667
2015-07-31 09:45 | 65.3667 | 70.3333 | 87.3333 | 92.4667
2015-07-31 10:00 | 65 | 71.35 | 88.2333 | 93.35
2015-07-31 10:15 | 65 | 72.1 | 88.7333 | 94.1
2015-07-31 10:30 | 65 | 72.85 | 89.2333 | 94.85
2015-07-31 10:45 | 65 | 73.6 | 89.7333 | 95.6
2015-07-31 11:00 | 65.2667 | 73.7667 | 90.4667 | 96.35
2015-07-31 11:15 | 66.2667 | 73.2667 | 91.4667 | 97.1
2015-07-31 11:30 | 67.2667 | 72.7667 | 92.4667 | 97.85
2015-07-31 11:45 | 68.2667 | 72.2667 | 93.4667 | 98.6
2015-07-31 12:00 | 69.1333 | 72.5833 | 94 | 99.2333
2015-07-31 12:15 | 69.6333 | 73.8333 | 94 | 99.7333
2015-07-31 12:30 | 70.1333 | 75.0833 | 94 | 100.2333
2015-07-31 12:45 | 70.6333 | 76.3333 | 94 | 100.7333
2015-07-31 13:00 | 71.0667 | 77.1167 | 94.2333 | 101.2333
2015-07-31 13:15 | 71.3167 | 77.3667 | 94.7333 | 101.7333
2015-07-31 13:30 | 71.5667 | 77.6167 | 95.2333 | 102.2333
2015-07-31 13:45 | 71.8167 | 77.8667 | 95.7333 | 102.7333
2015-07-31 14:00 | 71.9333 | 77.8833 | 95.8833 | 103.1167
2015-07-31 14:15 | 71.6833 | 77.6333 | 95.6333 | 103.3667
2015-07-31 14:30 | 71.4333 | 77.3833 | 95.3833 | 103.6167
2015-07-31 14:45 | 71.1833 | 77.1333 | 95.1333 | 103.8667
2015-07-31 15:00 | 70.9333 | 76.8833 | 95.2333 | 103.8833
2015-07-31 15:15 | 70.6833 | 76.6333 | 95.7333 | 103.6333
2015-07-31 15:30 | 70.4333 | 76.3833 | 96.2333 | 103.3833
2015-07-31 15:45 | 70.1833 | 76.1333 | 96.7333 | 103.1333
2015-07-31 16:00 | 69.8667 | 75.8833 | 96.8833 | 102.8833
2015-07-31 16:15 | 69.3667 | 75.6333 | 96.6333 | 102.6333
2015-07-31 16:30 | 68.8667 | 75.3833 | 96.3833 | 102.3833
2015-07-31 16:45 | 68.3667 | 75.1333 | 96.1333 | 102.1333
2015-07-31 17:00 | 67.8 | 74.65 | 96 | 101.7667
2015-07-31 17:15 | 67.05 | 73.9 | 96 | 101.2667
2015-07-31 17:30 | 66.3 | 73.15 | 96 | 100.7667
2015-07-31 17:45 | 65.55 | 72.4 | 96 | 100.2667
2015-07-31 18:00 | 64.8974 | 71.5333 | 95.65 | 99.4167
2015-07-31 18:15 | 64.5128 | 70.5333 | 94.9 | 98.1667
2015-07-31 18:30 | 64.1282 | 69.5333 | 94.15 | 96.9167
2015-07-31 18:45 | 64.4762 | 68.5333 | 93.4 | 95.6667
2015-07-31 19:00 | 64.7333 | 67.65 | 92.7667 | 94.5333
2015-07-31 19:15 | 64 | 66.9 | 92.2667 | 93.5333
2015-07-31 19:30 | 64 | 66.15 | 91.7667 | 92.5333
2015-07-31 19:45 | 64 | 65.4 | 91.2667 | 91.5333
2015-07-31 20:00 | 64 | 65 | 90.65 | 90.65
2015-07-31 20:15 | 64 | 65 | 89.9 | 89.9
2015-07-31 20:30 | 64 | 65 | 89.15 | 89.15
2015-07-31 20:45 | 64 | 65 | 88.4 | 88.4
2015-07-31 21:00 | 64 | 64.8833 | 87.65 | 87.4167
2015-07-31 21:15 | 64 | 64.6333 | 86.9 | 86.1667
2015-07-31 21:30 | 64 | 64.3833 | 86.15 | 84.9167
2015-07-31 21:45 | 64 | 64.1333 | 85.4 | 83.6667
2015-07-31 22:00 | 63.913 | 64 | 84.5333 | 82.65
2015-07-31 22:15 | 63.587 | 64 | 83.5333 | 81.9
2015-07-31 22:30 | 63.2609 | 64 | 82.5333 | 81.15
2015-07-31 22:45 | 63 | 64 | 81.5333 | 80.4
2015-07-31 23:00 | 63 | 64 | 80.8833 | 79.8833
2015-07-31 23:15 | 63 | 64 | 80.6333 | 79.6333
2015-07-31 23:30 | 63 | 64 | 80.3833 | 79.3833
2015-07-31 23:45 | 63 | 64 | 80.1333 | 79.1333
2015-08-01 | 63 | 64 | 80.1167 | 78.8833
2015-08-01 00:15 | 63 | 64 | 80.3667 | 78.6333
2015-08-01 00:30 | 63 | 64 | 80.6167 | 78.3833
2015-08-01 00:45 | 63 | 64 | 80.8667 | 78.1333
2015-08-01 01:00 | 63 | 64 | 80.7667 | 77.7667
2015-08-01 01:15 | 63 | 64 | 80.2667 | 77.2667
2015-08-01 01:30 | 63 | 64 | 79.7667 | 76.7667
2015-08-01 01:45 | 63 | 64 | 79.2667 | 76.2667
2015-08-01 02:00 | 62.9333 | 64 | 78.8833 | 75.8833
2015-08-01 02:15 | 62.6833 | 64 | 78.6333 | 75.6333
2015-08-01 02:30 | 62.4333 | 64 | 78.3833 | 75.3833
2015-08-01 02:45 | 62.1833 | 64 | 78.1333 | 75.1333
2015-08-01 03:00 | 62.0816 | 63 | 77.8833 | 74.8833
2015-08-01 03:15 | 62.3878 | 63 | 77.6333 | 74.6333
2015-08-01 03:30 | 62.6939 | 63 | 77.3833 | 74.3833
2015-08-01 03:45 | 63 | 63 | 77.1333 | 74.1333
2015-08-01 04:00 | 62.125 | 63 | 76.65 | 73.8833
2015-08-01 04:15 | 62.5938 | 63 | 75.9 | 73.6333
2015-08-01 04:30 | 62.9286 | 63 | 75.15 | 73.3833
2015-08-01 04:45 | 62.3929 | 63 | 74.4 | 73.1333
2015-08-01 05:00 | 62.0667 | 62.8833 | 73.8833 | 73.1167
2015-08-01 05:15 | 62.3167 | 62.6333 | 73.6333 | 73.3667
2015-08-01 05:30 | 62.5667 | 62.3833 | 73.3833 | 73.6167
2015-08-01 05:45 | 62.8167 | 62.1333 | 73.1333 | 73.8667
2015-08-01 06:00 | 63.1333 | 62.3684 | 73.1167 | 74.2333
2015-08-01 06:15 | 63.6333 | 63.0732 | 73.3667 | 74.7333
2015-08-01 06:30 | 64.1333 | 63.439 | 73.6167 | 75.2333
2015-08-01 06:45 | 64.6333 | 63.8049 | 73.8667 | 75.7333
2015-08-01 07:00 | 65.1333 | 64.1167 | 74.4667 | 76.5833
2015-08-01 07:15 | 65.6333 | 64.3667 | 75.4667 | 77.8333
2015-08-01 07:30 | 66.1333 | 64.6167 | 76.4667 | 79.0833
2015-08-01 07:45 | 66.6333 | 64.8667 | 77.4667 | 80.3333
2015-08-01 08:00 | 67.1333 | 65.1207 | 78.7 | 81.35
2015-08-01 08:15 | 67.6333 | 65.3793 | 80.2 | 82.1
2015-08-01 08:30 | 68.1333 | 65.6379 | 81.7 | 82.85
2015-08-01 08:45 | 68.6333 | 65.8966 | 83.2 | 83.6
2015-08-01 09:00 | 69.0667 | 67.8077 | 84.4667 | 84.4667
2015-08-01 09:15 | 69.3167 | 69.5385 | 85.4667 | 85.4667
2015-08-01 09:30 | 69.5667 | 70.6471 | 86.4667 | 86.4667
2015-08-01 09:45 | 69.8167 | 71.5294 | 87.4667 | 87.4667
2015-08-01 10:00 | 70.1333 | 72.2333 | 88.35 | 88.2333
2015-08-01 10:15 | 70.6333 | 72.7333 | 89.1 | 88.7333
2015-08-01 10:30 | 71.1333 | 73.2333 | 89.85 | 89.2333
2015-08-01 10:45 | 71.6333 | 73.7333 | 90.6 | 89.7333
2015-08-01 11:00 | 72.0667 | 74.35 | 91.1167 | 90.4667
2015-08-01 11:15 | 72.3167 | 75.1 | 91.3667 | 91.4667
2015-08-01 11:30 | 72.5667 | 75.85 | 91.6167 | 92.4667
2015-08-01 11:45 | 72.8167 | 76.6 | 91.8667 | 93.4667
2015-08-01 12:00 | 73 | 77 | 92.35 | 94.2333
2015-08-01 12:15 | 73 | 77 | 93.1 | 94.7333
2015-08-01 12:30 | 73 | 77 | 93.85 | 95.2333
2015-08-01 12:45 | 73 | 77 | 94.6 | 95.7333
2015-08-01 13:00 | 73.1333 | 77.1167 | 95.1167 | 96.2333
2015-08-01 13:15 | 73.6333 | 77.3667 | 95.3667 | 96.7333
2015-08-01 13:30 | 74.1333 | 77.6167 | 95.6167 | 97.2333
2015-08-01 13:45 | 74.6333 | 77.8667 | 95.8667 | 97.7333
2015-08-01 14:00 | 74.8667 | 78.2333 | 96.1167 | 98.1167
2015-08-01 14:15 | 74.3667 | 78.7333 | 96.3667 | 98.3667
2015-08-01 14:30 | 73.8667 | 79.2333 | 96.6167 | 98.6167
2015-08-01 14:45 | 73.3667 | 79.7333 | 96.8667 | 98.8667
2015-08-01 15:00 | 73 | 79.8833 | 96.7667 | 99
2015-08-01 15:15 | 73 | 79.6333 | 96.2667 | 99
2015-08-01 15:30 | 73 | 79.3833 | 95.7667 | 99
2015-08-01 15:45 | 73 | 79.1333 | 95.2667 | 99
2015-08-01 16:00 | 72.8667 | 78.8833 | 95.1167 | 98.8833
2015-08-01 16:15 | 72.3667 | 78.6333 | 95.3667 | 98.6333
2015-08-01 16:30 | 71.8667 | 78.3833 | 95.6167 | 98.3833
2015-08-01 16:45 | 71.3667 | 78.1333 | 95.8667 | 98.1333
2015-08-01 17:00 | 70.9333 | 77.65 | 95.8833 | 97.8833
2015-08-01 17:15 | 70.6833 | 76.9 | 95.6333 | 97.6333
2015-08-01 17:30 | 70.4333 | 76.15 | 95.3833 | 97.3833
2015-08-01 17:45 | 70.1833 | 75.4 | 95.1333 | 97.1333
2015-08-01 18:00 | 69.8 | 74.5333 | 93.95 | 96.5333
2015-08-01 18:15 | 69.05 | 73.5333 | 91.7 | 95.5333
2015-08-01 18:30 | 68.3 | 72.5333 | 89.45 | 94.5333
2015-08-01 18:45 | 67.55 | 71.5333 | 87.2 | 93.5333
2015-08-01 19:00 | 66.9333 | 70.7667 | 86 | 92.5333
2015-08-01 19:15 | 66.6833 | 70.2667 | 86 | 91.5333
2015-08-01 19:30 | 66.4333 | 69.7667 | 86 | 90.5333
2015-08-01 19:45 | 66.1833 | 69.2667 | 86 | 89.5333
2015-08-01 20:00 | 66 | 68.7667 | 85.8833 | 88.65
2015-08-01 20:15 | 66 | 68.2667 | 85.6333 | 87.9
2015-08-01 20:30 | 66 | 67.7667 | 85.3833 | 87.15
2015-08-01 20:45 | 66 | 67.2667 | 85.1333 | 86.4
2015-08-01 21:00 | 65.8667 | 66.8833 | 84.65 | 85.7667
2015-08-01 21:15 | 65.3667 | 66.6333 | 83.9 | 85.2667
2015-08-01 21:30 | 64.8667 | 66.3833 | 83.15 | 84.7667
2015-08-01 21:45 | 64.3667 | 66.1333 | 82.4 | 84.2667
2015-08-01 22:00 | 64 | 65.8833 | 81.7667 | 83.65
2015-08-01 22:15 | 64 | 65.6333 | 81.2667 | 82.9
2015-08-01 22:30 | 64 | 65.3833 | 80.7667 | 82.15
2015-08-01 22:45 | 64 | 65.1333 | 80.2667 | 81.4
2015-08-01 23:00 | 63.9333 | 65 | 79.8833 | 80.65
2015-08-01 23:15 | 63.6833 | 65 | 79.6333 | 79.9
2015-08-01 23:30 | 63.4333 | 65 | 79.3833 | 79.15
2015-08-01 23:45 | 63.1833 | 65 | 79.1333 | 78.4
2015-08-02 | 63 | 64.8478 | 78.8833 | 77.7667
2015-08-02 00:15 | 63 | 64.5217 | 78.6333 | 77.2667
2015-08-02 00:30 | 63 | 64.1957 | 78.3833 | 76.7667
2015-08-02 00:45 | 63 | 64 | 78.1333 | 76.2667
2015-08-02 01:00 | 63 | 64 | 77.8833 | 75.65
2015-08-02 01:15 | 63 | 64 | 77.6333 | 74.9
2015-08-02 01:30 | 63 | 64 | 77.3833 | 74.15
2015-08-02 01:45 | 63 | 64 | 77.1333 | 73.4
2015-08-02 02:00 | 63 | 64 | 77 | 72.8833
2015-08-02 02:15 | 63 | 64 | 77 | 72.6333
2015-08-02 02:30 | 63 | 64 | 77 | 72.3833
2015-08-02 02:45 | 63 | 64 | 77 | 72.1333
2015-08-02 03:00 | 62.9333 | 64 | 77 | 72
2015-08-02 03:15 | 62.6833 | 64 | 77 | 72
2015-08-02 03:30 | 62.4333 | 64 | 77 | 72
2015-08-02 03:45 | 62.1833 | 64 | 77 | 72
2015-08-02 04:00 | 62 | 64 | 76.7667 | 71.7667
2015-08-02 04:15 | 62 | 64 | 76.2667 | 71.2667
2015-08-02 04:30 | 62 | 64 | 75.7667 | 70.7667
2015-08-02 04:45 | 62 | 64 | 75.2667 | 70.2667
2015-08-02 05:00 | 62 | 64 | 74.8833 | 70
2015-08-02 05:15 | 62 | 64 | 74.6333 | 70
2015-08-02 05:30 | 62 | 64 | 74.3833 | 70
2015-08-02 05:45 | 62 | 64 | 74.1333 | 70
2015-08-02 06:00 | 62 | 64.1167 | 74 | 70.2333
2015-08-02 06:15 | 62 | 64.3667 | 74 | 70.7333
2015-08-02 06:30 | 62 | 64.6167 | 74 | 71.2333
2015-08-02 06:45 | 62 | 64.8667 | 74 | 71.7333
2015-08-02 07:00 | 62.0667 | 65 | 74.4667 | 72.35
2015-08-02 07:15 | 62.3167 | 65 | 75.4667 | 73.1
2015-08-02 07:30 | 62.5667 | 65 | 76.4667 | 73.85
2015-08-02 07:45 | 62.8167 | 65 | 77.4667 | 74.6
2015-08-02 08:00 | 63 | 65.2333 | 78.7 | 75.5833
2015-08-02 08:15 | 63 | 65.7333 | 80.2 | 76.8333
2015-08-02 08:30 | 63 | 66.2333 | 81.7 | 78.0833
2015-08-02 08:45 | 63 | 66.7333 | 83.2 | 79.3333
2015-08-02 09:00 | 63.1333 | 67.1707 | 84.4667 | 80.4667
2015-08-02 09:15 | 63.6333 | 67.5366 | 85.4667 | 81.4667
2015-08-02 09:30 | 64.1333 | 67.9024 | 86.4667 | 82.4667
2015-08-02 09:45 | 64.6333 | 69.1579 | 87.4667 | 83.4667
2015-08-02 10:00 | 65.2 | 70.2333 | 88.2333 | 84.5833
2015-08-02 10:15 | 65.95 | 70.7333 | 88.7333 | 85.8333
2015-08-02 10:30 | 66.7 | 71.2333 | 89.2333 | 87.0833
2015-08-02 10:45 | 67.45 | 71.7333 | 89.7333 | 88.3333
2015-08-02 11:00 | 68 | 72.1167 | 90.4667 | 89.35
2015-08-02 11:15 | 68 | 72.3667 | 91.4667 | 90.1
2015-08-02 11:30 | 68 | 72.6167 | 92.4667 | 90.85
2015-08-02 11:45 | 68 | 72.8667 | 93.4667 | 91.6
2015-08-02 12:00 | 68.1333 | 73.2333 | 94.2333 | 92.2333
2015-08-02 12:15 | 68.6333 | 73.7333 | 94.7333 | 92.7333
2015-08-02 12:30 | 69.1333 | 74.2333 | 95.2333 | 93.2333
2015-08-02 12:45 | 69.6333 | 74.7333 | 95.7333 | 93.7333
2015-08-02 13:00 | 70.0667 | 75 | 96.1167 | 94.2333
2015-08-02 13:15 | 70.3167 | 75 | 96.3667 | 94.7333
2015-08-02 13:30 | 70.5667 | 75 | 96.6167 | 95.2333
2015-08-02 13:45 | 70.8167 | 75 | 96.8667 | 95.7333
2015-08-02 14:00 | 70.9333 | 75 | 97 | 96.35
2015-08-02 14:15 | 70.6833 | 75 | 97 | 97.1
2015-08-02 14:30 | 70.4333 | 75 | 97 | 97.85
2015-08-02 14:45 | 70.1833 | 75 | 97 | 98.6
2015-08-02 15:00 | 70 | 75.1167 | 97.2333 | 98.8833
2015-08-02 15:15 | 70 | 75.3667 | 97.7333 | 98.6333
2015-08-02 15:30 | 70 | 75.6167 | 98.2333 | 98.3833
2015-08-02 15:45 | 70 | 75.8667 | 98.7333 | 98.1333
2015-08-02 16:00 | 69.9333 | 75.8833 | 98.8833 | 97.8833
2015-08-02 16:15 | 69.6833 | 75.6333 | 98.6333 | 97.6333
2015-08-02 16:30 | 69.4333 | 75.3833 | 98.3833 | 97.3833
2015-08-02 16:45 | 69.1833 | 75.1333 | 98.1333 | 97.1333
2015-08-02 17:00 | 68.8667 | 74.5333 | 97.7667 | 96.65
2015-08-02 17:15 | 68.3667 | 73.5333 | 97.2667 | 95.9
2015-08-02 17:30 | 67.8667 | 72.5333 | 96.7667 | 95.15
2015-08-02 17:45 | 67.3667 | 71.5333 | 96.2667 | 94.4
2015-08-02 18:00 | 66.9333 | 70.7667 | 95.7667 | 93.5333
2015-08-02 18:15 | 66.6833 | 70.2667 | 95.2667 | 92.5333
2015-08-02 18:30 | 66.4333 | 69.7667 | 94.7667 | 91.5333
2015-08-02 18:45 | 66.1833 | 69.2667 | 94.2667 | 90.5333
2015-08-02 19:00 | 65.9333 | 68.7667 | 93.5333 | 89.65
2015-08-02 19:15 | 65.6833 | 68.2667 | 92.5333 | 88.9
2015-08-02 19:30 | 65.4333 | 67.7667 | 91.5333 | 88.15
2015-08-02 19:45 | 65.1833 | 67.2667 | 90.5333 | 87.4
2015-08-02 20:00 | 64.9333 | 66.8833 | 89.7667 | 86.65
2015-08-02 20:15 | 64.6833 | 66.6333 | 89.2667 | 85.9
2015-08-02 20:30 | 64.4333 | 66.3833 | 88.7667 | 85.15
2015-08-02 20:45 | 64.1833 | 66.1333 | 88.2667 | 84.4
2015-08-02 21:00 | 63.9333 | 65.8833 | 87.7667 | 83.7667
2015-08-02 21:15 | 63.6833 | 65.6333 | 87.2667 | 83.2667
2015-08-02 21:30 | 63.4333 | 65.3833 | 86.7667 | 82.7667
2015-08-02 21:45 | 63.1833 | 65.1333 | 86.2667 | 82.2667
2015-08-02 22:00 | 63 | 64.8833 | 85.7667 | 81.65
2015-08-02 22:15 | 63 | 64.6333 | 85.2667 | 80.9
2015-08-02 22:30 | 63 | 64.3833 | 84.7667 | 80.15
2015-08-02 22:45 | 63 | 64.1333 | 84.2667 | 79.4
2015-08-02 23:00 | 63 | 64 | 83.7667 | 78.65
2015-08-02 23:15 | 63 | 64 | 83.2667 | 77.9
2015-08-02 23:30 | 63 | 64 | 82.7667 | 77.15
2015-08-02 23:45 | 63 | 64 | 82.2667 | 76.4
2015-08-03 | 63 | 63.8833 | 81.8833 | 75.7667
2015-08-03 00:15 | 63 | 63.6333 | 81.6333 | 75.2667
2015-08-03 00:30 | 63 | 63.3833 | 81.3833 | 74.7667
2015-08-03 00:45 | 63 | 63.1333 | 81.1333 | 74.2667
2015-08-03 01:00 | 64 | 63 | 80.8833 | 73.65
2015-08-03 01:15 | 64 | 63 | 80.6333 | 72.9
2015-08-03 01:30 | 64 | 63 | 80.3833 | 72.15
2015-08-03 01:45 | 64 | 63 | 80.1333 | 71.4
2015-08-03 02:00 | 64 | 62.8833 | 79.7667 | 70.8833
2015-08-03 02:15 | 64 | 62.6333 | 79.2667 | 70.6333
2015-08-03 02:30 | 64 | 62.3833 | 78.7667 | 70.3833
2015-08-03 02:45 | 64 | 62.1333 | 78.2667 | 70.1333
2015-08-03 03:00 | 63.9333 | 62.125 | 77.8833 | 69.8833
2015-08-03 03:15 | 63.6833 | 62.3929 | 77.6333 | 69.6333
2015-08-03 03:30 | 63.4333 | 62.6607 | 77.3833 | 69.3833
2015-08-03 03:45 | 63.1833 | 62.9286 | 77.1333 | 69.1333
2015-08-03 04:00 | 63.0667 | 62.1167 | 77.1167 | 68.8833
2015-08-03 04:15 | 63.3167 | 62.3667 | 77.3667 | 68.6333
2015-08-03 04:30 | 63.5667 | 62.6167 | 77.6167 | 68.3833
2015-08-03 04:45 | 63.8167 | 62.8667 | 77.8667 | 68.1333
2015-08-03 05:00 | 64 | 63 | 77.7667 | 68
2015-08-03 05:15 | 64 | 63 | 77.2667 | 68
2015-08-03 05:30 | 64 | 63 | 76.7667 | 68
2015-08-03 05:45 | 64 | 63 | 76.2667 | 68
2015-08-03 06:00 | 64 | 63 | 76 | 68.2333
2015-08-03 06:15 | 64 | 63 | 76 | 68.7333
2015-08-03 06:30 | 64 | 63 | 76 | 69.2333
2015-08-03 06:45 | 64 | 63 | 76 | 69.7333
2015-08-03 07:00 | 64.0667 | 63.1167 | 76.35 | 70.35
2015-08-03 07:15 | 64.3167 | 63.3667 | 77.1 | 71.1
2015-08-03 07:30 | 64.5667 | 63.6167 | 77.85 | 71.85
2015-08-03 07:45 | 64.8167 | 63.8667 | 78.6 | 72.6
2015-08-03 08:00 | 65.1176 | 64.35 | 79.5833 | 73.4667
2015-08-03 08:15 | 65.5588 | 65.1 | 80.8333 | 74.4667
2015-08-03 08:30 | 66 | 65.85 | 82.0833 | 75.4667
2015-08-03 08:45 | 67.1538 | 66.6 | 83.3333 | 76.4667
2015-08-03 09:00 | 68.0667 | 66.6957 | 84.2333 | 77.35
2015-08-03 09:15 | 68.3167 | 66.0435 | 84.7333 | 78.1
2015-08-03 09:30 | 68.5667 | 67.1351 | 85.2333 | 78.85
2015-08-03 09:45 | 68.8167 | 68.3514 | 85.7333 | 79.6
2015-08-03 10:00 | 69 | 69.35 | 86.7 | 80.35
2015-08-03 10:15 | 69 | 70.1 | 88.2 | 81.1
2015-08-03 10:30 | 69 | 70.85 | 89.7 | 81.85
2015-08-03 10:45 | 69 | 71.6 | 91.2 | 82.6
2015-08-03 11:00 | 69.1333 | 72.2333 | 92.35 | 83.4667
2015-08-03 11:15 | 69.6333 | 72.7333 | 93.1 | 84.4667
2015-08-03 11:30 | 70.1333 | 73.2333 | 93.85 | 85.4667
2015-08-03 11:45 | 70.6333 | 73.7333 | 94.6 | 86.4667
2015-08-03 12:00 | 71.0667 | 74.1167 | 95.2333 | 87.5833
2015-08-03 12:15 | 71.3167 | 74.3667 | 95.7333 | 88.8333
2015-08-03 12:30 | 71.5667 | 74.6167 | 96.2333 | 90.0833
2015-08-03 12:45 | 71.8167 | 74.8667 | 96.7333 | 91.3333
2015-08-03 13:00 | 72.0667 | 75.1167 | 97.1167 | 92
2015-08-03 13:15 | 72.3167 | 75.3667 | 97.3667 | 92
2015-08-03 13:30 | 72.5667 | 75.6167 | 97.6167 | 92
2015-08-03 13:45 | 72.8167 | 75.8667 | 97.8667 | 92
2015-08-03 14:00 | 72.9333 | 76 | 98.2333 | 92.2333
2015-08-03 14:15 | 72.6833 | 76 | 98.7333 | 92.7333
2015-08-03 14:30 | 72.4333 | 76 | 99.2333 | 93.2333
2015-08-03 14:45 | 72.1833 | 76 | 99.7333 | 93.7333
2015-08-03 15:00 | 72 | 76 | 99.7667 | 94
2015-08-03 15:15 | 72 | 76 | 99.2667 | 94
2015-08-03 15:30 | 72 | 76 | 98.7667 | 94
2015-08-03 15:45 | 72 | 76 | 98.2667 | 94
2015-08-03 16:00 | 71.8667 | 75.7667 | 97.8833 | 94
2015-08-03 16:15 | 71.3667 | 75.2667 | 97.6333 | 94
2015-08-03 16:30 | 70.8667 | 74.7667 | 97.3833 | 94
2015-08-03 16:45 | 70.3667 | 74.2667 | 97.1333 | 94
2015-08-03 17:00 | 69.9333 | 73.7667 | 96.65 | 93.7667
2015-08-03 17:15 | 69.6833 | 73.2667 | 95.9 | 93.2667
2015-08-03 17:30 | 69.4333 | 72.7667 | 95.15 | 92.7667
2015-08-03 17:45 | 69.1833 | 72.2667 | 94.4 | 92.2667
2015-08-03 18:00 | 68.8667 | 71.65 | 93.7667 | 91.5333
2015-08-03 18:15 | 68.3667 | 70.9 | 93.2667 | 90.5333
2015-08-03 18:30 | 67.8667 | 70.15 | 92.7667 | 89.5333
2015-08-03 18:45 | 67.3667 | 69.4 | 92.2667 | 88.5333
2015-08-03 19:00 | 66.9333 | 68.65 | 92 | 87.65
2015-08-03 19:15 | 66.6833 | 67.9 | 91.1892 | 86.9
2015-08-03 19:30 | 66.4333 | 67.15 | 89.1622 | 86.15
2015-08-03 19:45 | 66.1833 | 66.4 | 87.1351 | 85.4
2015-08-03 20:00 | 65.9333 | 65.8833 | 89.52 | 84.5333
2015-08-03 20:15 | 65.6833 | 65.6333 | 85.92 | 83.5333
2015-08-03 20:30 | 65.4333 | 65.3833 | 81 | 82.5333
2015-08-03 20:45 | 65.1833 | 65.1333 | 78.5333 | 81.5333
2015-08-03 21:00 | 65 | 64.8833 | 77.7667 | 80.65
2015-08-03 21:15 | 65 | 64.6333 | 77.2667 | 79.9
2015-08-03 21:30 | 65 | 64.3833 | 76.7667 | 79.15
2015-08-03 21:45 | 65 | 64.1333 | 76.2667 | 78.4
2015-08-03 22:00 | 65 | 63.7667 | 75.8833 | 77.5333
2015-08-03 22:15 | 65 | 63.2667 | 75.6333 | 76.5333
2015-08-03 22:30 | 65 | 62.7667 | 75.3833 | 75.5333
2015-08-03 22:45 | 65 | 62.2667 | 75.1333 | 74.5333
2015-08-03 23:00 | 64.9333 | 62.2333 | 75.1167 | 73.65
2015-08-03 23:15 | 64.6833 | 62.7333 | 75.3667 | 72.9
2015-08-03 23:30 | 64.4333 | 63.2333 | 75.6167 | 72.15
2015-08-03 23:45 | 64.1833 | 63.7333 | 75.8667 | 71.4
2015-08-04 | 64 | 63.8833 | 76 | 70.7667
2015-08-04 00:15 | 64 | 63.6333 | 76 | 70.2667
2015-08-04 00:30 | 64 | 63.3833 | 76 | 69.7667
2015-08-04 00:45 | 64 | 63.1333 | 76 | 69.2667
2015-08-04 01:00 | 63.9333 | 62.8833 | 75.8833 | 68.8833
2015-08-04 01:15 | 63.6833 | 62.6333 | 75.6333 | 68.6333
2015-08-04 01:30 | 63.4333 | 62.3833 | 75.3833 | 68.3833
2015-08-04 01:45 | 63.1833 | 62.1333 | 75.1333 | 68.1333
2015-08-04 02:00 | 63 | 61.7667 | 74.7667 | 67.8833
2015-08-04 02:15 | 63 | 61.2667 | 74.2667 | 67.6333
2015-08-04 02:30 | 63 | 60.7667 | 73.7667 | 67.3833
2015-08-04 02:45 | 63 | 60.2667 | 73.2667 | 67.1333
2015-08-04 03:00 | 62.9333 | 60 | 73 | 66.7667
2015-08-04 03:15 | 62.6833 | 60 | 73 | 66.2667
2015-08-04 03:30 | 62.4333 | 60 | 73 | 65.7667
2015-08-04 03:45 | 62.1833 | 60 | 73 | 65.2667
2015-08-04 04:00 | 61.9333 | 59.7667 | 72.8833 | 65
2015-08-04 04:15 | 61.6833 | 59.2667 | 72.6333 | 65
2015-08-04 04:30 | 61.4333 | 58.7667 | 72.3833 | 65
2015-08-04 04:45 | 61.1833 | 58.2667 | 72.1333 | 65
2015-08-04 05:00 | 61.0667 | 58.1167 | 72 | 65
2015-08-04 05:15 | 61.3167 | 58.3667 | 72 | 65
2015-08-04 05:30 | 61.5667 | 58.6167 | 72 | 65
2015-08-04 05:45 | 61.8167 | 58.8667 | 72 | 65
2015-08-04 06:00 | 62.0667 | 59.4667 | 72.2333 | 65.2333
2015-08-04 06:15 | 62.3167 | 60.4667 | 72.7333 | 65.7333
2015-08-04 06:30 | 62.5667 | 61.4667 | 73.2333 | 66.2333
2015-08-04 06:45 | 62.8167 | 62.4667 | 73.7333 | 66.7333
2015-08-04 07:00 | 63.2 | 63.35 | 74.1167 | 67.35
2015-08-04 07:15 | 63.95 | 64.1 | 74.3667 | 68.1
2015-08-04 07:30 | 64.7 | 64.85 | 74.6167 | 68.85
2015-08-04 07:45 | 65.45 | 65.6 | 74.8667 | 69.6
2015-08-04 08:00 | 66 | 66.2333 | 75.4667 | 70.4667
2015-08-04 08:15 | 66 | 66.7333 | 76.4667 | 71.4667
2015-08-04 08:30 | 66 | 67.2333 | 77.4667 | 72.4667
2015-08-04 08:45 | 66 | 67.7333 | 78.4667 | 73.4667
2015-08-04 09:00 | 66.1333 | 68.1167 | 79.7 | 74.2333
2015-08-04 09:15 | 66.6333 | 68.3667 | 81.2 | 74.7333
2015-08-04 09:30 | 67.1333 | 68.6167 | 82.7 | 75.2333
2015-08-04 09:45 | 67.6333 | 68.8667 | 84.2 | 75.7333
2015-08-04 10:00 | 68 | 69.35 | 85.5833 | 76.2333
2015-08-04 10:15 | 68 | 70.1 | 86.8333 | 76.7333
2015-08-04 10:30 | 68 | 70.85 | 88.0833 | 77.2333
2015-08-04 10:45 | 68 | 71.6 | 89.3333 | 77.7333
2015-08-04 11:00 | 68.0667 | 72.1167 | 90.35 | 78.1167
2015-08-04 11:15 | 68.3167 | 72.3667 | 91.1 | 78.3667
2015-08-04 11:30 | 68.5667 | 72.6167 | 91.85 | 78.6167
2015-08-04 11:45 | 68.8167 | 72.8667 | 92.6 | 78.8667
2015-08-04 12:00 | 69.0667 | 72.7667 | 93.35 | 79.1167
2015-08-04 12:15 | 69.3167 | 72.2667 | 94.1 | 79.3667
2015-08-04 12:30 | 69.5667 | 71.7667 | 94.85 | 79.6167
2015-08-04 12:45 | 69.8167 | 71.2667 | 95.6 | 79.8667
2015-08-04 13:00 | 70.0667 | 71.1167 | 96.1167 | 80.1167
2015-08-04 13:15 | 70.3167 | 71.3667 | 96.3667 | 80.3667
2015-08-04 13:30 | 70.5667 | 71.6167 | 96.6167 | 80.6167
2015-08-04 13:45 | 70.8167 | 71.8667 | 96.8667 | 80.8667
2015-08-04 14:00 | 71 | 72.1167 | 97.35 | 81.1167
2015-08-04 14:15 | 71 | 72.3667 | 98.1 | 81.3667
2015-08-04 14:30 | 71 | 72.6167 | 98.85 | 81.6167
2015-08-04 14:45 | 71 | 72.8667 | 99.6 | 81.8667
2015-08-04 15:00 | 71.0667 | 73.2333 | 99.8833 | 82.1167
2015-08-04 15:15 | 71.3167 | 73.7333 | 99.6333 | 82.3667
2015-08-04 15:30 | 71.5667 | 74.2333 | 99.3833 | 82.6167
2015-08-04 15:45 | 71.8167 | 74.7333 | 99.1333 | 82.8667
2015-08-04 16:00 | 72 | 74.8833 | 98.8833 | 83
2015-08-04 16:15 | 72 | 74.6333 | 98.6333 | 83
2015-08-04 16:30 | 72 | 74.3833 | 98.3833 | 83
2015-08-04 16:45 | 72 | 74.1333 | 98.1333 | 83
2015-08-04 17:00 | 71.8667 | 73.7667 | 98.1167 | 82.7667
2015-08-04 17:15 | 71.3667 | 73.2667 | 98.3667 | 82.2667
2015-08-04 17:30 | 70.8667 | 72.7667 | 98.6167 | 81.7667
2015-08-04 17:45 | 70.3667 | 72.2667 | 98.8667 | 81.2667
2015-08-04 18:00 | 69.8667 | 71.7667 | 97.6667 | 80.7667
2015-08-04 18:15 | 69.3667 | 71.2667 | 94.9487 | 80.2667
2015-08-04 18:30 | 68.8667 | 70.7667 | 94.1795 | 79.7667
2015-08-04 18:45 | 68.3667 | 70.2667 | 93.4103 | 79.2667
2015-08-04 19:00 | 67.8667 | 69.7667 | 92.7667 | 78.7667
2015-08-04 19:15 | 67.3667 | 69.2667 | 92.2667 | 78.2667
2015-08-04 19:30 | 66.8667 | 68.7667 | 91.7667 | 77.7667
2015-08-04 19:45 | 66.3667 | 68.2667 | 91.2667 | 77.2667
2015-08-04 20:00 | 65.9333 | 67.7667 | 90.7667 | 76.8833
2015-08-04 20:15 | 65.6833 | 67.2667 | 90.2667 | 76.6333
2015-08-04 20:30 | 65.4333 | 66.7667 | 89.7667 | 76.3833
2015-08-04 20:45 | 65.1833 | 66.2667 | 89.2667 | 76.1333
2015-08-04 21:00 | 64.9333 | 65.8833 | 88.7667 | 75.65
2015-08-04 21:15 | 64.6833 | 65.6333 | 88.2667 | 74.9
2015-08-04 21:30 | 64.4333 | 65.3833 | 87.7667 | 74.15
2015-08-04 21:45 | 64.1833 | 65.1333 | 87.2667 | 73.4
2015-08-04 22:00 | 64 | 64.8833 | 86.7667 | 72.7667
2015-08-04 22:15 | 64 | 64.6333 | 86.2667 | 72.2667
2015-08-04 22:30 | 64 | 64.3833 | 85.7667 | 71.7667
2015-08-04 22:45 | 64 | 64.1333 | 85.2667 | 71.2667
2015-08-04 23:00 | 63.9333 | 64 | 84.825 | 70.7667
2015-08-04 23:15 | 63.6833 | 64 | 84.45 | 70.2667
2015-08-04 23:30 | 63.4333 | 64 | 84.075 | 69.7667
2015-08-04 23:45 | 63.1833 | 64 | 83.7 | 69.2667
2015-08-05 | 62.9333 | 64 | 83.325 | 68.7667
2015-08-05 00:15 | 62.6833 | 64 | 82.95 | 68.2667
2015-08-05 00:30 | 62.4333 | 64 | 82.575 | 67.7667
2015-08-05 00:45 | 62.1833 | 64 | 82.2 | 67.2667
2015-08-05 01:00 | 61.9333 | 63.8679 | 81.8833 | 66.8833
2015-08-05 01:15 | 61.6833 | 63.5849 | 81.6333 | 66.6333
2015-08-05 01:30 | 61.4333 | 63.3019 | 81.3833 | 66.3833
2015-08-05 01:45 | 61.1833 | 63.0189 | 81.1333 | 66.1333
2015-08-05 02:00 | 61 | 63.8571 | 80.8833 | 65.8833
2015-08-05 02:15 | 61 | 63.551 | 80.6333 | 65.6333
2015-08-05 02:30 | 61 | 63.2449 | 80.3833 | 65.3833
2015-08-05 02:45 | 61 | 62.7273 | 80.1333 | 65.1333
2015-08-05 03:00 | 60.9333 | 61.7667 | 79.7667 | 64.8833
2015-08-05 03:15 | 60.6833 | 61.2667 | 79.2667 | 64.6333
2015-08-05 03:30 | 60.4333 | 60.7667 | 78.7667 | 64.3833
2015-08-05 03:45 | 60.1833 | 60.2667 | 78.2667 | 64.1333
2015-08-05 04:00 | 60.069 | 59.8833 | 77.7667 | 63.8833
2015-08-05 04:15 | 60.3276 | 59.6333 | 77.2667 | 63.6333
2015-08-05 04:30 | 60.5862 | 59.3833 | 76.7667 | 63.3833
2015-08-05 04:45 | 60.8448 | 59.1333 | 76.2667 | 63.1333
2015-08-05 05:00 | 60.0667 | 59.1167 | 76 | 62.8833
2015-08-05 05:15 | 60.3167 | 59.3667 | 76 | 62.6333
2015-08-05 05:30 | 60.5667 | 59.6167 | 76 | 62.3833
2015-08-05 05:45 | 60.8167 | 59.8667 | 76 | 62.1333
2015-08-05 06:00 | 61.1333 | 60.35 | 76 | 62.35
2015-08-05 06:15 | 61.6333 | 61.1 | 76 | 63.1
2015-08-05 06:30 | 62.1333 | 61.85 | 76 | 63.85
2015-08-05 06:45 | 62.6333 | 62.6 | 76 | 64.6
2015-08-05 07:00 | 63.069 | 63.35 | 76.4667 | 65.35
2015-08-05 07:15 | 63.3276 | 64.1 | 77.4667 | 66.1
2015-08-05 07:30 | 63.5862 | 64.85 | 78.4667 | 66.85
2015-08-05 07:45 | 63.8448 | 65.6 | 79.4667 | 67.6
2015-08-05 08:00 | 65 | 66.1167 | 80.7 | 68.5833
2015-08-05 08:15 | 65 | 66.3667 | 82.2 | 69.8333
2015-08-05 08:30 | 65 | 66.6167 | 83.7 | 71.0833
2015-08-05 08:45 | 65 | 66.8667 | 85.2 | 72.3333
2015-08-05 09:00 | 65.1333 | 67.35 | 86.7 | 73.4667
2015-08-05 09:15 | 65.6333 | 68.1 | 88.2 | 74.4667
2015-08-05 09:30 | 66.1333 | 68.85 | 89.7 | 75.4667
2015-08-05 09:45 | 66.6333 | 69.6 | 91.2 | 76.4667
2015-08-05 10:00 | 67.125 | 70.2333 | 92.35 | 77.35
2015-08-05 10:15 | 67.5938 | 70.7333 | 93.1 | 78.1
2015-08-05 10:30 | 68.0714 | 71.2333 | 93.85 | 78.85
2015-08-05 10:45 | 68.6071 | 71.7333 | 94.6 | 79.6
2015-08-05 11:00 | 69.2 | 72.35 | 95.35 | 80.35
2015-08-05 11:15 | 69.95 | 73.1 | 96.1 | 81.1
2015-08-05 11:30 | 70.7 | 73.85 | 96.85 | 81.85
2015-08-05 11:45 | 71.45 | 74.6 | 97.6 | 82.6
2015-08-05 12:00 | 72.0667 | 75.35 | 98.1167 | 83.2333
2015-08-05 12:15 | 72.3167 | 76.1 | 98.3667 | 83.7333
2015-08-05 12:30 | 72.5667 | 76.85 | 98.6167 | 84.2333
2015-08-05 12:45 | 72.8167 | 77.6 | 98.8667 | 84.7333
2015-08-05 13:00 | 72.9333 | 78 | 99.1167 | 85.1167
2015-08-05 13:15 | 72.6833 | 78 | 99.3667 | 85.3667
2015-08-05 13:30 | 72.4333 | 78 | 99.6167 | 85.6167
2015-08-05 13:45 | 72.1833 | 78 | 99.8667 | 85.8667
2015-08-05 14:00 | 71.9333 | 78.1167 | 100.2333 | 86.2333
2015-08-05 14:15 | 71.6833 | 78.3667 | 100.7333 | 86.7333
2015-08-05 14:30 | 71.4333 | 78.6167 | 101.2333 | 87.2333
2015-08-05 14:45 | 71.1833 | 78.8667 | 101.7333 | 87.7333
2015-08-05 15:00 | 70.8667 | 78.7667 | 101.8833 | 87.7667
2015-08-05 15:15 | 70.3667 | 78.2667 | 101.6333 | 87.2667
2015-08-05 15:30 | 69.8667 | 77.7667 | 101.3833 | 86.7667
2015-08-05 15:45 | 69.3667 | 77.2667 | 101.1333 | 86.2667
2015-08-05 16:00 | 68.8667 | 76.8833 | 101 | 86
2015-08-05 16:15 | 68.3667 | 76.6333 | 101 | 86
2015-08-05 16:30 | 67.8667 | 76.3833 | 101 | 86
2015-08-05 16:45 | 67.3667 | 76.1333 | 101 | 86
2015-08-05 17:00 | 66.9333 | 75.8833 | 100.8833 | 85.8833
2015-08-05 17:15 | 66.6833 | 75.6333 | 100.6333 | 85.6333
2015-08-05 17:30 | 66.4333 | 75.3833 | 100.3833 | 85.3833
2015-08-05 17:45 | 66.1833 | 75.1333 | 100.1333 | 85.1333
2015-08-05 18:00 | 65.8667 | 74.5333 | 99.65 | 84.8833
2015-08-05 18:15 | 65.3667 | 73.5333 | 98.9 | 84.6333
2015-08-05 18:30 | 64.8667 | 72.5333 | 98.15 | 84.3833
2015-08-05 18:45 | 64.3667 | 71.5333 | 97.4 | 84.1333
2015-08-05 19:00 | 63.9333 | 70.65 | 96.65 | 83.8833
2015-08-05 19:15 | 63.6833 | 69.9 | 95.9 | 83.6333
2015-08-05 19:30 | 63.4333 | 69.15 | 95.15 | 83.3833
2015-08-05 19:45 | 63.1833 | 68.4 | 94.4 | 83.1333
2015-08-05 20:00 | 62.9333 | 67.8833 | 93.65 | 82.7667
2015-08-05 20:15 | 62.6833 | 67.6333 | 92.9 | 82.2667
2015-08-05 20:30 | 62.4333 | 67.3833 | 92.15 | 81.7667
2015-08-05 20:45 | 62.1833 | 67.1333 | 91.4 | 81.2667
2015-08-05 21:00 | 62 | 66.8833 | 90.65 | 80.8833
2015-08-05 21:15 | 62 | 66.6333 | 89.9 | 80.6333
2015-08-05 21:30 | 62 | 66.3833 | 89.15 | 80.3833
2015-08-05 21:45 | 62 | 66.1333 | 88.4 | 80.1333
2015-08-05 22:00 | 62 | 66 | 87.65 | 79.65
2015-08-05 22:15 | 62 | 66 | 86.9 | 78.9
2015-08-05 22:30 | 62 | 66 | 86.15 | 78.15
2015-08-05 22:45 | 62 | 66 | 85.4 | 77.4
2015-08-05 23:00 | 61.9333 | 66 | 84.7667 | 76.7667
2015-08-05 23:15 | 61.6833 | 66 | 84.2667 | 76.2667
2015-08-05 23:30 | 61.4333 | 66 | 83.7667 | 75.7667
2015-08-05 23:45 | 61.1833 | 66 | 83.2667 | 75.2667
2015-08-06 | 61 | 65.7667 | 82.8833 | 75
2015-08-06 00:15 | 61 | 65.2667 | 82.6333 | 75
2015-08-06 00:30 | 61 | 64.7667 | 82.3833 | 75
2015-08-06 00:45 | 61 | 64.2667 | 82.1333 | 75
2015-08-06 01:00 | 61 | 64 | 81.8833 | 74.8833
2015-08-06 01:15 | 61 | 64 | 81.6333 | 74.6333
2015-08-06 01:30 | 61 | 64 | 81.3833 | 74.3833
2015-08-06 01:45 | 61 | 64 | 81.1333 | 74.1333
2015-08-06 02:00 | 60.9333 | 64 | 80.7667 | 74
2015-08-06 02:15 | 60.6833 | 64 | 80.2667 | 74
2015-08-06 02:30 | 60.4333 | 64 | 79.7667 | 74
2015-08-06 02:45 | 60.1833 | 64 | 79.2667 | 74
2015-08-06 03:00 | 59.9333 | 63.65 | 78.7667 | 73.8833
2015-08-06 03:15 | 59.6833 | 62.9 | 78.2667 | 73.6333
2015-08-06 03:30 | 59.4333 | 62.15 | 77.7667 | 73.3833
2015-08-06 03:45 | 59.1833 | 61.4 | 77.2667 | 73.1333
2015-08-06 04:00 | 59 | 61.2333 | 76.7667 | 73
2015-08-06 04:15 | 59 | 61.7333 | 76.2667 | 73
2015-08-06 04:30 | 59 | 62.2333 | 75.7667 | 73
2015-08-06 04:45 | 59 | 62.7333 | 75.2667 | 73
2015-08-06 05:00 | 59 | 63 | 74.8833 | 73.1167
2015-08-06 05:15 | 59 | 63 | 74.6333 | 73.3667
2015-08-06 05:30 | 59 | 63 | 74.3833 | 73.6167
2015-08-06 05:45 | 59 | 63 | 74.1333 | 73.8667
2015-08-06 06:00 | 60.0667 | 63.1167 | 74 | 74.1167
2015-08-06 06:15 | 60.3167 | 63.3667 | 74 | 74.3667
2015-08-06 06:30 | 60.5667 | 63.6167 | 74 | 74.6167
2015-08-06 06:45 | 60.8167 | 63.8667 | 74 | 74.8667
2015-08-06 07:00 | 61.0667 | 64.35 | 74.5833 | 75.35
2015-08-06 07:15 | 61.3167 | 65.1 | 75.8333 | 76.1
2015-08-06 07:30 | 61.5667 | 65.85 | 77.0833 | 76.85
2015-08-06 07:45 | 61.8167 | 66.6 | 78.3333 | 77.6
2015-08-06 08:00 | 62.1333 | 67.1167 | 79.7 | 78.35
2015-08-06 08:15 | 62.6333 | 67.3667 | 81.2 | 79.1
2015-08-06 08:30 | 63.1333 | 67.6167 | 82.7 | 79.85
2015-08-06 08:45 | 63.6333 | 67.8667 | 84.2 | 80.6
2015-08-06 09:00 | 64.1333 | 68.2333 | 85.7 | 81.35
2015-08-06 09:15 | 64.6333 | 68.7333 | 87.2 | 82.1
2015-08-06 09:30 | 65.1333 | 69.2333 | 88.7 | 82.85
2015-08-06 09:45 | 65.6333 | 69.7333 | 90.2 | 83.6
2015-08-06 10:00 | 66 | 70.1167 | 91.4667 | 84.35
2015-08-06 10:15 | 66 | 70.3667 | 92.4667 | 85.1
2015-08-06 10:30 | 66 | 70.6167 | 93.4667 | 85.85
2015-08-06 10:45 | 66 | 70.8667 | 94.4667 | 86.6
2015-08-06 11:00 | 66.2 | 71.2333 | 95.35 | 87.2333
2015-08-06 11:15 | 66.95 | 71.7333 | 96.1 | 87.7333
2015-08-06 11:30 | 67.7 | 72.2333 | 96.85 | 88.2333
2015-08-06 11:45 | 68.45 | 72.7333 | 97.6 | 88.7333
2015-08-06 12:00 | 68.931 | 73.1167 | 98.1167 | 89.35
2015-08-06 12:15 | 68.6724 | 73.3667 | 98.3667 | 90.1
2015-08-06 12:30 | 68.4138 | 73.6167 | 98.6167 | 90.85
2015-08-06 12:45 | 68.1552 | 73.8667 | 98.8667 | 91.6
2015-08-06 13:00 | 67.9333 | 74.1167 | 99.2333 | 91.8833
2015-08-06 13:15 | 67.6833 | 74.3667 | 99.7333 | 91.6333
2015-08-06 13:30 | 67.4333 | 74.6167 | 100.2333 | 91.3833
2015-08-06 13:45 | 67.1833 | 74.8667 | 100.7333 | 91.1333
2015-08-06 14:00 | 67.1333 | 75.2333 | 101 | 90.8833
2015-08-06 14:15 | 67.6333 | 75.7333 | 101 | 90.6333
2015-08-06 14:30 | 68.1333 | 76.2333 | 101 | 90.3833
2015-08-06 14:45 | 68.6333 | 76.7333 | 101 | 90.1333
2015-08-06 15:00 | 69 | 76.8833 | 101.1167 | 90
2015-08-06 15:15 | 69 | 76.6333 | 101.3667 | 90
2015-08-06 15:30 | 69 | 76.3833 | 101.6167 | 90
2015-08-06 15:45 | 69 | 76.1333 | 101.8667 | 90
2015-08-06 16:00 | 68.8667 | 76.1167 | 102 | 89.8833
2015-08-06 16:15 | 68.3667 | 76.3667 | 102 | 89.6333
2015-08-06 16:30 | 67.8667 | 76.6167 | 102 | 89.3833
2015-08-06 16:45 | 67.3667 | 76.8667 | 102 | 89.1333
2015-08-06 17:00 | 66.8 | 76.7667 | 101.7667 | 88.7667
2015-08-06 17:15 | 66.05 | 76.2667 | 101.2667 | 88.2667
2015-08-06 17:30 | 65.3 | 75.7667 | 100.7667 | 87.7667
2015-08-06 17:45 | 64.55 | 75.2667 | 100.2667 | 87.2667
2015-08-06 18:00 | 63.9333 | 74.3 | 99.65 | 86.7667
2015-08-06 18:15 | 63.6833 | 72.8 | 98.9 | 86.2667
2015-08-06 18:30 | 63.4333 | 71.3 | 98.15 | 85.7667
2015-08-06 18:45 | 63.1833 | 69.8 | 97.4 | 85.2667
2015-08-06 19:00 | 62.9333 | 68.7667 | 96.5333 | 84.7667
2015-08-06 19:15 | 62.6833 | 68.2667 | 95.5333 | 84.2667
2015-08-06 19:30 | 62.4333 | 67.7667 | 94.5333 | 83.7667
2015-08-06 19:45 | 62.1833 | 67.2667 | 93.5333 | 83.2667
2015-08-06 20:00 | 61.9333 | 66.8158 | 92.5333 | 82.8833
2015-08-06 20:15 | 61.6833 | 66.4211 | 91.5333 | 82.6333
2015-08-06 20:30 | 61.4333 | 66.0263 | 90.5333 | 82.3833
2015-08-06 20:45 | 61.1833 | 65.3636 | 89.5333 | 82.1333
2015-08-06 21:00 | 61.0667 | 64.6111 | 88.7667 | 81.7667
2015-08-06 21:15 | 61.3167 | 64.0952 | 88.2667 | 81.2667
2015-08-06 21:30 | 61.5667 | 64.4524 | 87.7667 | 80.7667
2015-08-06 21:45 | 61.8167 | 64.8095 | 87.2667 | 80.2667
2015-08-06 22:00 | 62.087 | 64.8542 | 86.65 | 79.7667
2015-08-06 22:15 | 62.413 | 64.5417 | 85.9 | 79.2667
2015-08-06 22:30 | 62.7391 | 64.2292 | 85.15 | 78.7667
2015-08-06 22:45 | 63 | 64 | 84.4 | 78.2667
2015-08-06 23:00 | 63 | 65 | 83.7667 | 77.8833
2015-08-06 23:15 | 63 | 65 | 83.2667 | 77.6333
2015-08-06 23:30 | 62.8387 | 65 | 82.7667 | 77.3833
2015-08-06 23:45 | 62.3548 | 65 | 82.2667 | 77.1333
2015-08-07 | 61.9333 | 65 | 81.7667 | 76.65
2015-08-07 00:15 | 61.6833 | 65 | 81.2667 | 75.9
2015-08-07 00:30 | 61.4333 | 65 | 80.7667 | 75.15
2015-08-07 00:45 | 61.1833 | 65 | 80.2667 | 74.4
2015-08-07 01:00 | 61 | 64.7667 | 79.8833 | 74
2015-08-07 01:15 | 61 | 64.2667 | 79.6333 | 74
2015-08-07 01:30 | 61 | 63.7667 | 79.3833 | 74
2015-08-07 01:45 | 61 | 63.2667 | 79.1333 | 74
2015-08-07 02:00 | 61 | 62.8833 | 78.8833 | 73.7667
2015-08-07 02:15 | 61 | 62.6333 | 78.6333 | 73.2667
2015-08-07 02:30 | 61 | 62.3833 | 78.3833 | 72.7667
2015-08-07 02:45 | 61 | 62.1333 | 78.1333 | 72.2667
2015-08-07 03:00 | 60.9333 | 61.8833 | 77.8833 | 71.7667
2015-08-07 03:15 | 60.6833 | 61.6333 | 77.6333 | 71.2667
2015-08-07 03:30 | 60.4333 | 61.3833 | 77.3833 | 70.7667
2015-08-07 03:45 | 60.1833 | 61.1333 | 77.1333 | 70.2667
2015-08-07 04:00 | 59.8667 | 60.8833 | 76.8833 | 69.8833
2015-08-07 04:15 | 59.3667 | 60.6333 | 76.6333 | 69.6333
2015-08-07 04:30 | 58.8667 | 60.3833 | 76.3833 | 69.3833
2015-08-07 04:45 | 58.3667 | 60.1333 | 76.1333 | 69.1333
2015-08-07 05:00 | 58.0667 | 60 | 75.7667 | 69.1167
2015-08-07 05:15 | 58.3167 | 60 | 75.2667 | 69.3667
2015-08-07 05:30 | 58.5667 | 60 | 74.7667 | 69.6167
2015-08-07 05:45 | 58.8167 | 60 | 74.2667 | 69.8667
2015-08-07 06:00 | 59.2 | 60.2333 | 74 | 70.2333
2015-08-07 06:15 | 59.95 | 60.7333 | 74 | 70.7333
2015-08-07 06:30 | 60.7 | 61.2333 | 74 | 71.2333
2015-08-07 06:45 | 61.45 | 61.7333 | 74 | 71.7333
2015-08-07 07:00 | 62.2 | 62.35 | 74.7 | 72.4667
2015-08-07 07:15 | 62.95 | 63.1 | 76.2 | 73.4667
2015-08-07 07:30 | 63.7 | 63.85 | 77.7 | 74.4667
2015-08-07 07:45 | 64.45 | 64.6 | 79.2 | 75.4667
2015-08-07 08:00 | 65.2 | 65.2333 | 80.4667 | 76.4667
2015-08-07 08:15 | 65.95 | 65.7333 | 81.4667 | 77.4667
2015-08-07 08:30 | 66.7 | 66.2333 | 82.4667 | 78.4667
2015-08-07 08:45 | 67.45 | 66.7333 | 83.4667 | 79.4667
2015-08-07 09:00 | 68.0667 | 67.4667 | 84.7 | 80.35
2015-08-07 09:15 | 68.3167 | 68.4667 | 86.2 | 81.1
2015-08-07 09:30 | 68.5667 | 69.4667 | 87.7 | 81.85
2015-08-07 09:45 | 68.8167 | 70.4667 | 89.2 | 82.6
2015-08-07 10:00 | 69.2 | 71.4667 | 90.35 | 83.2333
2015-08-07 10:15 | 69.95 | 72.4667 | 91.1 | 83.7333
2015-08-07 10:30 | 70.7 | 73.4667 | 91.85 | 84.2333
2015-08-07 10:45 | 71.45 | 74.4667 | 92.6 | 84.7333
2015-08-07 11:00 | 72 | 75.35 | 93.35 | 85.4667
2015-08-07 11:15 | 72 | 76.1 | 94.1 | 86.4667
2015-08-07 11:30 | 72 | 76.85 | 94.85 | 87.4667
2015-08-07 11:45 | 72 | 77.6 | 95.6 | 88.4667
2015-08-07 12:00 | 72.2 | 78.4667 | 96.1167 | 89.2333
2015-08-07 12:15 | 72.95 | 79.4667 | 96.3667 | 89.7333
2015-08-07 12:30 | 73.7 | 80.4667 | 96.6167 | 90.2333
2015-08-07 12:45 | 74.45 | 81.4667 | 96.8667 | 90.7333
2015-08-07 13:00 | 75 | 81.8833 | 97.5833 | 91.2333
2015-08-07 13:15 | 75 | 81.6333 | 98.8333 | 91.7333
2015-08-07 13:30 | 75 | 81.3833 | 100.0833 | 92.2333
2015-08-07 13:45 | 75 | 81.1333 | 101.3333 | 92.7333
2015-08-07 14:00 | 75 | 80.7667 | 101.7667 | 92.8833
2015-08-07 14:15 | 75 | 80.2667 | 101.2667 | 92.6333
2015-08-07 14:30 | 75 | 79.7667 | 100.7667 | 92.3833
2015-08-07 14:45 | 75 | 79.2667 | 100.2667 | 92.1333
2015-08-07 15:00 | 74.9333 | 78.8833 | 100.35 | 92.1167
2015-08-07 15:15 | 74.6833 | 78.6333 | 101.1 | 92.3667
2015-08-07 15:30 | 74.4333 | 78.3833 | 101.85 | 92.6167
2015-08-07 15:45 | 74.1833 | 78.1333 | 102.6 | 92.8667
2015-08-07 16:00 | 73.9333 | 77.7667 | 102.7667 | 93
2015-08-07 16:15 | 73.6833 | 77.2667 | 102.2667 | 93
2015-08-07 16:30 | 73.4333 | 76.7667 | 101.7667 | 93
2015-08-07 16:45 | 73.1833 | 76.2667 | 101.2667 | 93
2015-08-07 17:00 | 72.8667 | 75.8833 | 100.65 | 92.7667
2015-08-07 17:15 | 72.3667 | 75.6333 | 99.9 | 92.2667
2015-08-07 17:30 | 71.8667 | 75.3833 | 99.15 | 91.7667
2015-08-07 17:45 | 71.3667 | 75.1333 | 98.4 | 91.2667
2015-08-07 18:00 | 70.8 | 74.4167 | 97.7667 | 90.65
2015-08-07 18:15 | 70.05 | 73.1667 | 97.2667 | 89.9
2015-08-07 18:30 | 69.3 | 71.9167 | 96.7667 | 89.15
2015-08-07 18:45 | 68.55 | 70.6667 | 96.2667 | 88.4
2015-08-07 19:00 | 67.8667 | 69.7667 | 95.5333 | 87.65
2015-08-07 19:15 | 67.3667 | 69.2667 | 94.5333 | 86.9
2015-08-07 19:30 | 66.8667 | 68.7667 | 93.5333 | 86.15
2015-08-07 19:45 | 66.3667 | 68.2667 | 92.5333 | 85.4
2015-08-07 20:00 | 65.8667 | 67.8833 | 91.65 | 84.65
2015-08-07 20:15 | 65.3667 | 67.6333 | 90.9 | 83.9
2015-08-07 20:30 | 64.8667 | 67.3833 | 90.15 | 83.15
2015-08-07 20:45 | 64.3667 | 67.1333 | 89.4 | 82.4
2015-08-07 21:00 | 63.9333 | 66.7667 | 88.8833 | 81.5333
2015-08-07 21:15 | 63.6833 | 66.2667 | 88.6333 | 80.5333
2015-08-07 21:30 | 63.4333 | 65.7667 | 88.3833 | 79.5333
2015-08-07 21:45 | 63.1833 | 65.2667 | 88.1333 | 78.5333
2015-08-07 22:00 | 63 | 64.8833 | 87.8833 | 77.65
2015-08-07 22:15 | 63 | 64.6333 | 87.6333 | 76.9
2015-08-07 22:30 | 63 | 64.3833 | 87.3833 | 76.15
2015-08-07 22:45 | 63 | 64.1333 | 87.1333 | 75.4
2015-08-07 23:00 | 62.9333 | 63.8833 | 86.7667 | 74.8833
2015-08-07 23:15 | 62.6833 | 63.6333 | 86.2667 | 74.6333
2015-08-07 23:30 | 62.4333 | 63.3833 | 85.7667 | 74.3833
2015-08-07 23:45 | 62.1833 | 63.1333 | 85.2667 | 74.1333
2015-08-08 | 62 | 63 | 84.8833 | 73.65
2015-08-08 00:15 | 62 | 63 | 84.6333 | 72.9
2015-08-08 00:30 | 62 | 63 | 84.3833 | 72.15
2015-08-08 00:45 | 62 | 63 | 84.1333 | 71.4
2015-08-08 01:00 | 61.9333 | 63 | 83.8833 | 70.8833
2015-08-08 01:15 | 61.6833 | 63 | 83.6333 | 70.6333
2015-08-08 01:30 | 61.4333 | 63 | 83.3833 | 70.3833
2015-08-08 01:45 | 61.1833 | 63 | 83.1333 | 70.1333
2015-08-08 02:00 | 61.1429 | 63 | 82.7667 | 69.7667
2015-08-08 02:15 | 61.6786 | 63 | 82.2667 | 69.2667
2015-08-08 02:30 | 62.2143 | 63 | 81.7667 | 68.7667
2015-08-08 02:45 | 62.75 | 63 | 81.2667 | 68.2667
2015-08-08 03:00 | 61.9333 | 62.6667 | 80.8833 | 67.7667
2015-08-08 03:15 | 61.6833 | 61.9524 | 80.6333 | 67.2667
2015-08-08 03:30 | 61.4333 | 61.2381 | 80.3833 | 66.7667
2015-08-08 03:45 | 61.1833 | 61 | 80.1333 | 66.2667
2015-08-08 04:00 | 61 | 61 | 79.8833 | 65.8833
2015-08-08 04:15 | 61 | 61 | 79.6333 | 65.6333
2015-08-08 04:30 | 61 | 61 | 79.3833 | 65.3833
2015-08-08 04:45 | 61 | 61 | 79.1333 | 65.1333
2015-08-08 05:00 | 61 | 60.25 | 78.7667 | 65
2015-08-08 05:15 | 61 | 60.7857 | 78.2667 | 65
2015-08-08 05:30 | 61 | 60.7188 | 77.7667 | 65
2015-08-08 05:45 | 61 | 60.25 | 77.2667 | 65
2015-08-08 06:00 | 61.0667 | 60.2333 | 77 | 65.4667
2015-08-08 06:15 | 61.3167 | 60.7333 | 77 | 66.4667
2015-08-08 06:30 | 61.5667 | 61.2333 | 77 | 67.4667
2015-08-08 06:45 | 61.8167 | 61.7333 | 77 | 68.4667
2015-08-08 07:00 | 62.1333 | 62.4375 | 77.4667 | 69.5833
2015-08-08 07:15 | 62.6333 | 63.2727 | 78.4667 | 70.8333
2015-08-08 07:30 | 63.1333 | 63.9545 | 79.4667 | 72.0833
2015-08-08 07:45 | 63.6333 | 64.6364 | 80.4667 | 73.3333
2015-08-08 08:00 | 64.1333 | 65.1707 | 81.8167 | 74.35
2015-08-08 08:15 | 64.6333 | 65.5366 | 83.5667 | 75.1
2015-08-08 08:30 | 65.1333 | 65.9024 | 85.3167 | 75.85
2015-08-08 08:45 | 65.6333 | 66.5789 | 87.0667 | 76.6
2015-08-08 09:00 | 66 | 67.4667 | 88.7 | 77.4667
2015-08-08 09:15 | 66.0465 | 68.4667 | 90.2 | 78.4667
2015-08-08 09:30 | 66.3953 | 69.4667 | 91.7 | 79.4667
2015-08-08 09:45 | 66.7442 | 70.4667 | 93.2 | 80.4667
2015-08-08 10:00 | 67.1333 | 71.35 | 94.2333 | 81.35
2015-08-08 10:15 | 67.6333 | 72.1 | 94.7333 | 82.1
2015-08-08 10:30 | 68.1333 | 72.85 | 95.2333 | 82.85
2015-08-08 10:45 | 68.6333 | 73.6 | 95.7333 | 83.6
2015-08-08 11:00 | 69 | 74.4667 | 96.35 | 84.35
2015-08-08 11:15 | 69 | 75.4667 | 97.1 | 85.1
2015-08-08 11:30 | 69 | 76.4667 | 97.85 | 85.85
2015-08-08 11:45 | 69 | 77.4667 | 98.6 | 86.6
2015-08-08 12:00 | 69.1333 | 77.7667 | 99 | 87.35
2015-08-08 12:15 | 69.6333 | 77.2667 | 99 | 88.1
2015-08-08 12:30 | 70.1333 | 76.7667 | 99 | 88.85
2015-08-08 12:45 | 70.6333 | 76.2667 | 99 | 89.6
2015-08-08 13:00 | 70.8667 | 75.8833 | 99.4667 | 90.4667
2015-08-08 13:15 | 70.3667 | 75.6333 | 100.4667 | 91.4667
2015-08-08 13:30 | 69.8667 | 75.3833 | 101.4667 | 92.4667
2015-08-08 13:45 | 69.3667 | 75.1333 | 102.4667 | 93.4667
2015-08-08 14:00 | 68.9333 | 75 | 103 | 94
2015-08-08 14:15 | 68.6833 | 75 | 103 | 94
2015-08-08 14:30 | 68.4333 | 75 | 103 | 94
2015-08-08 14:45 | 68.1833 | 75 | 103 | 94
2015-08-08 15:00 | 67.9333 | 74.7667 | 102.8833 | 94
2015-08-08 15:15 | 67.6833 | 74.2667 | 102.6333 | 94
2015-08-08 15:30 | 67.4333 | 73.7667 | 102.3833 | 94
2015-08-08 15:45 | 67.1833 | 73.2667 | 102.1333 | 94
2015-08-08 16:00 | 66.8667 | 72.7667 | 101.3 | 94
2015-08-08 16:15 | 66.3667 | 72.2667 | 99.0645 | 94
2015-08-08 16:30 | 65.8667 | 71.7667 | 96.6452 | 94
2015-08-08 16:45 | 65.3667 | 71.2667 | 92.4 | 94
2015-08-08 17:00 | 65 | 70.7667 | 91.9091 | 93.7667
2015-08-08 17:15 | 65 | 70.2667 | 93.2619 | 93.2667
2015-08-08 17:30 | 65 | 69.7667 | 93.619 | 92.7667
2015-08-08 17:45 | 65 | 69.2667 | 93.9762 | 92.2667
2015-08-08 18:00 | 64.8667 | 68.7667 | 90 | 91.65
2015-08-08 18:15 | 64.3667 | 68.2667 | 83.6364 | 90.9
2015-08-08 18:30 | 63.8667 | 67.7667 | 83.619 | 90.15
2015-08-08 18:45 | 63.3667 | 67.2667 | 82.1905 | 89.4
2015-08-08 19:00 | 63 | 66.7667 | 82.7385 | 88.65
2015-08-08 19:15 | 63 | 66.2667 | 83.6615 | 87.9
2015-08-08 19:30 | 63 | 65.7667 | 84.5846 | 87.15
2015-08-08 19:45 | 63 | 65.2667 | 85.5077 | 86.4
2015-08-08 20:00 | 63 | 65 | 86.2333 | 85.4167
2015-08-08 20:15 | 63 | 65 | 86.7333 | 84.1667
2015-08-08 20:30 | 63 | 65 | 87.2333 | 82.9167
2015-08-08 20:45 | 63 | 65 | 87.7333 | 81.6667
2015-08-08 21:00 | 63 | 64.8833 | 87.7667 | 80.7667
2015-08-08 21:15 | 63 | 64.6333 | 87.2667 | 80.2667
2015-08-08 21:30 | 63 | 64.3833 | 86.7667 | 79.7667
2015-08-08 21:45 | 63 | 64.1333 | 86.2667 | 79.2667
2015-08-08 22:00 | 63 | 63.8833 | 85.8833 | 78.7667
2015-08-08 22:15 | 63 | 63.6333 | 85.6333 | 78.2667
2015-08-08 22:30 | 63 | 63.3833 | 85.3833 | 77.7667
2015-08-08 22:45 | 63 | 63.1333 | 85.1333 | 77.2667
2015-08-08 23:00 | 62.9333 | 63 | 84.8833 | 76.5333
2015-08-08 23:15 | 62.6833 | 63 | 84.6333 | 75.5333
2015-08-08 23:30 | 62.4333 | 63 | 84.3833 | 74.5333
2015-08-08 23:45 | 62.1833 | 63 | 84.1333 | 73.5333
2015-08-09 | 62.08 | 62.7667 | 83.8833 | 72.8833
2015-08-09 00:15 | 62.38 | 62.2667 | 83.6333 | 72.6333
2015-08-09 00:30 | 62.68 | 61.7667 | 83.3833 | 72.3833
2015-08-09 00:45 | 62.98 | 61.2667 | 83.1333 | 72.1333
2015-08-09 01:00 | 61.9245 | 60.8833 | 82.8833 | 71.65
2015-08-09 01:15 | 61.6415 | 60.6333 | 82.6333 | 70.9
2015-08-09 01:30 | 61.3585 | 60.3833 | 82.3833 | 70.15
2015-08-09 01:45 | 61.0755 | 60.1333 | 82.1333 | 69.4
2015-08-09 02:00 | 61 | 59.8833 | 81.8833 | 68.8833
2015-08-09 02:15 | 61 | 59.6333 | 81.6333 | 68.6333
2015-08-09 02:30 | 60.7027 | 59.3833 | 81.3833 | 68.3833
2015-08-09 02:45 | 60.2973 | 59.1333 | 81.1333 | 68.1333
2015-08-09 03:00 | 60.2105 | 59 | 80.8833 | 67.8833
2015-08-09 03:15 | 61 | 59 | 80.6333 | 67.6333
2015-08-09 03:30 | 60.6341 | 59 | 80.3833 | 67.3833
2015-08-09 03:45 | 60.2683 | 59 | 80.1333 | 67.1333
2015-08-09 04:00 | 60 | 58.8833 | 79.7667 | 66.8833
2015-08-09 04:15 | 60 | 58.6333 | 79.2667 | 66.6333
2015-08-09 04:30 | 60 | 58.3833 | 78.7667 | 66.3833
2015-08-09 04:45 | 60 | 58.1333 | 78.2667 | 66.1333
2015-08-09 05:00 | 60 | 57.8833 | 77.8833 | 66.1167
2015-08-09 05:15 | 60 | 57.6333 | 77.6333 | 66.3667
2015-08-09 05:30 | 60 | 57.3833 | 77.3833 | 66.6167
2015-08-09 05:45 | 60 | 57.1333 | 77.1333 | 66.8667
2015-08-09 06:00 | 60 | 57.35 | 76.8833 | 67.35
2015-08-09 06:15 | 60 | 58.1 | 76.6333 | 68.1
2015-08-09 06:30 | 60 | 58.85 | 76.3833 | 68.85
2015-08-09 06:45 | 60 | 59.6 | 76.1333 | 69.6
2015-08-09 07:00 | 60.2353 | 60.35 | 76.2333 | 70.4667
2015-08-09 07:15 | 61.1176 | 61.1 | 76.7333 | 71.4667
2015-08-09 07:30 | 62 | 61.85 | 77.2333 | 72.4667
2015-08-09 07:45 | 62.8824 | 62.6 | 77.7333 | 73.4667
2015-08-09 08:00 | 62.1818 | 63.5833 | 78.5833 | 74.5833
2015-08-09 08:15 | 62.8636 | 64.8333 | 79.8333 | 75.8333
2015-08-09 08:30 | 63.3158 | 66.0833 | 81.0833 | 77.0833
2015-08-09 08:45 | 63.7105 | 67.3333 | 82.3333 | 78.3333
2015-08-09 09:00 | 64.1333 | 68.4667 | 83.7 | 79.5833
2015-08-09 09:15 | 64.6333 | 69.4667 | 85.2 | 80.8333
2015-08-09 09:30 | 65.1333 | 70.4667 | 86.7 | 82.0833
2015-08-09 09:45 | 65.6333 | 71.4667 | 88.2 | 83.3333
2015-08-09 10:00 | 66.1333 | 72.5833 | 89.2333 | 84.35
2015-08-09 10:15 | 66.6333 | 73.8333 | 89.7333 | 85.1
2015-08-09 10:30 | 67.1333 | 75.0833 | 90.2333 | 85.85
2015-08-09 10:45 | 67.6333 | 76.3333 | 90.7333 | 86.6
2015-08-09 11:00 | 68.0667 | 77.1167 | 91.35 | 87.4667
2015-08-09 11:15 | 68.3167 | 77.3667 | 92.1 | 88.4667
2015-08-09 11:30 | 68.5667 | 77.6167 | 92.85 | 89.4667
2015-08-09 11:45 | 68.8167 | 77.8667 | 93.6 | 90.4667
2015-08-09 12:00 | 69 | 77.8833 | 94.35 | 91.35
2015-08-09 12:15 | 69 | 77.6333 | 95.1 | 92.1
2015-08-09 12:30 | 69 | 77.3833 | 95.85 | 92.85
2015-08-09 12:45 | 69 | 77.1333 | 96.6 | 93.6
2015-08-09 13:00 | 69.0667 | 77 | 97.2333 | 94.1167
2015-08-09 13:15 | 69.3167 | 77 | 97.7333 | 94.3667
2015-08-09 13:30 | 69.5667 | 77 | 98.2333 | 94.6167
2015-08-09 13:45 | 69.8167 | 77 | 98.7333 | 94.8667
2015-08-09 14:00 | 70 | 77 | 99.1167 | 95
2015-08-09 14:15 | 70 | 77 | 99.3667 | 95
2015-08-09 14:30 | 70 | 77 | 99.6167 | 95
2015-08-09 14:45 | 70 | 77 | 99.8667 | 95
2015-08-09 15:00 | 69.9333 | 76.8833 | 100.2333 | 95.1167
2015-08-09 15:15 | 69.6833 | 76.6333 | 100.7333 | 95.3667
2015-08-09 15:30 | 69.4333 | 76.3833 | 101.2333 | 95.6167
2015-08-09 15:45 | 69.1833 | 76.1333 | 101.7333 | 95.8667
2015-08-09 16:00 | 68.8 | 75.65 | 102 | 96.1167
2015-08-09 16:15 | 68.05 | 74.9 | 102 | 96.3667
2015-08-09 16:30 | 67.3 | 74.15 | 102 | 96.6167
2015-08-09 16:45 | 66.55 | 73.4 | 100.5333 | 96.8667
2015-08-09 17:00 | 65.9333 | 72.7667 | 100.1515 | 96.7667
2015-08-09 17:15 | 65.6833 | 72.2667 | 98.3333 | 96.2667
2015-08-09 17:30 | 65.4333 | 71.7667 | 97.1481 | 95.7667
2015-08-09 17:45 | 65.1833 | 71.2667 | 97.7037 | 95.2667
2015-08-09 18:00 | 64.8667 | 70.65 | 97.7667 | 94.65
2015-08-09 18:15 | 64.3667 | 69.9 | 97.2667 | 93.9
2015-08-09 18:30 | 63.8667 | 69.15 | 96.7667 | 93.15
2015-08-09 18:45 | 63.3667 | 68.4 | 96.2667 | 92.4
2015-08-09 19:00 | 62.9333 | 67.8833 | 95.65 | 91.4167
2015-08-09 19:15 | 62.6833 | 67.6333 | 94.9 | 90.1667
2015-08-09 19:30 | 62.4333 | 67.3833 | 94.15 | 88.9167
2015-08-09 19:45 | 62.1833 | 67.1333 | 93.4 | 87.6667
2015-08-09 20:00 | 62 | 67 | 92.5333 | 86.7667
2015-08-09 20:15 | 62 | 67 | 91.5333 | 86.2667
2015-08-09 20:30 | 62 | 67 | 90.5333 | 85.7667
2015-08-09 20:45 | 62 | 67 | 89.5333 | 85.2667
2015-08-09 21:00 | 62 | 66.8833 | 88.7667 | 84.5333
2015-08-09 21:15 | 62 | 66.6333 | 88.2667 | 83.5333
2015-08-09 21:30 | 62 | 66.3833 | 87.7667 | 82.5333
2015-08-09 21:45 | 62 | 66.1333 | 87.2667 | 81.5333
2015-08-09 22:00 | 62 | 65.8833 | 86.65 | 80.7667
2015-08-09 22:15 | 62 | 65.6333 | 85.9 | 80.2667
2015-08-09 22:30 | 62 | 65.3833 | 85.15 | 79.7667
2015-08-09 22:45 | 62 | 65.1333 | 84.4 | 79.2667
2015-08-09 23:00 | 62.0667 | 64.8833 | 83.8833 | 78.65
2015-08-09 23:15 | 62.3167 | 64.6333 | 83.6333 | 77.9
2015-08-09 23:30 | 62.5667 | 64.3833 | 83.3833 | 77.15
2015-08-09 23:45 | 62.8167 | 64.1333 | 83.1333 | 76.4
2015-08-10 | 62.9333 | 63.7667 | 82.7667 | 75.7667
2015-08-10 00:15 | 62.6833 | 63.2667 | 82.2667 | 75.2667
2015-08-10 00:30 | 62.4333 | 62.7667 | 81.7667 | 74.7667
2015-08-10 00:45 | 62.1833 | 62.2667 | 81.2667 | 74.2667
2015-08-10 01:00 | 61.9333 | 62.1167 | 80.8833 | 73.8833
2015-08-10 01:15 | 61.6833 | 62.3667 | 80.6333 | 73.6333
2015-08-10 01:30 | 61.4333 | 62.6167 | 80.3833 | 73.3833
2015-08-10 01:45 | 61.1833 | 62.8667 | 80.1333 | 73.1333
2015-08-10 02:00 | 60.9333 | 62.65 | 79.7667 | 72.7667
2015-08-10 02:15 | 60.6833 | 61.9 | 79.2667 | 72.2667
2015-08-10 02:30 | 60.4333 | 61.15 | 78.7667 | 71.7667
2015-08-10 02:45 | 60.1833 | 60.4 | 78.2667 | 71.2667
2015-08-10 03:00 | 60 | 60 | 77.65 | 70.8833
2015-08-10 03:15 | 60 | 60 | 76.9 | 70.6333
2015-08-10 03:30 | 60 | 60 | 76.15 | 70.3833
2015-08-10 03:45 | 60 | 60 | 75.4 | 70.1333
2015-08-10 04:00 | 60 | 60.1346 | 75 | 69.8833
2015-08-10 04:15 | 60 | 60.4231 | 75 | 69.6333
2015-08-10 04:30 | 60 | 60.7115 | 75 | 69.3833
2015-08-10 04:45 | 60 | 61 | 75 | 69.1333
2015-08-10 05:00 | 60 | 60 | 75 | 69.1167
2015-08-10 05:15 | 60 | 60 | 75 | 69.3667
2015-08-10 05:30 | 60 | 60 | 75 | 69.6167
2015-08-10 05:45 | 60 | 60 | 75 | 69.8667
2015-08-10 06:00 | 60.0667 | 60.35 | 74.8833 | 70.2333
2015-08-10 06:15 | 60.3167 | 61.1 | 74.6333 | 70.7333
2015-08-10 06:30 | 60.5667 | 61.85 | 74.3833 | 71.2333
2015-08-10 06:45 | 60.8167 | 62.6 | 74.1333 | 71.7333
2015-08-10 07:00 | 61.2 | 63.35 | 74.7 | 72.2333
2015-08-10 07:15 | 61.95 | 64.1 | 76.2 | 72.7333
2015-08-10 07:30 | 62.7 | 64.85 | 77.7 | 73.2333
2015-08-10 07:45 | 63.45 | 65.6 | 79.2 | 73.7333
2015-08-10 08:00 | 64 | 66.35 | 80.5833 | 74.4667
2015-08-10 08:15 | 64 | 67.1 | 81.8333 | 75.4667
2015-08-10 08:30 | 64 | 67.85 | 83.0833 | 76.4667
2015-08-10 08:45 | 64.5769 | 68.6 | 84.3333 | 77.4667
2015-08-10 09:00 | 65.2 | 69.4667 | 85.4667 | 78.5833
2015-08-10 09:15 | 65.95 | 70.4667 | 86.4667 | 79.8333
2015-08-10 09:30 | 66.7 | 71.4667 | 87.4667 | 81.0833
2015-08-10 09:45 | 67.45 | 72.4667 | 88.4667 | 82.3333
2015-08-10 10:00 | 68.2667 | 73.35 | 89.5833 | 83.35
2015-08-10 10:15 | 69.2667 | 74.1 | 90.8333 | 84.1
2015-08-10 10:30 | 70.2667 | 74.85 | 92.0833 | 84.85
2015-08-10 10:45 | 71.2667 | 75.6 | 93.3333 | 85.6
2015-08-10 11:00 | 72 | 76.1167 | 94.2333 | 86.4667
2015-08-10 11:15 | 72 | 76.3667 | 94.7333 | 87.4667
2015-08-10 11:30 | 72 | 76.6167 | 95.2333 | 88.4667
2015-08-10 11:45 | 72 | 76.8667 | 95.7333 | 89.4667
2015-08-10 12:00 | 71.8667 | 77.1167 | 96 | 90.2333
2015-08-10 12:15 | 71.3667 | 77.3667 | 96 | 90.7333
2015-08-10 12:30 | 70.8667 | 77.6167 | 96 | 91.2333
2015-08-10 12:45 | 70.3667 | 77.8667 | 96 | 91.7333
2015-08-10 13:00 | 70 | 78 | 96.2333 | 92.1167
2015-08-10 13:15 | 70 | 78 | 96.7333 | 92.3667
2015-08-10 13:30 | 70 | 78 | 97.2333 | 92.6167
2015-08-10 13:45 | 70 | 78 | 97.7333 | 92.8667
2015-08-10 14:00 | 69.9333 | 77.7667 | 98.35 | 93.1167
2015-08-10 14:15 | 69.6833 | 77.2667 | 99.1 | 93.3667
2015-08-10 14:30 | 69.4333 | 76.7667 | 99.85 | 93.6167
2015-08-10 14:45 | 69.1833 | 76.2667 | 100.6 | 93.8667
2015-08-10 15:00 | 69 | 75.7667 | 100.8833 | 94.2333
2015-08-10 15:15 | 69 | 75.2667 | 100.6333 | 94.7333
2015-08-10 15:30 | 69 | 74.7667 | 100.3833 | 95.2333
2015-08-10 15:45 | 69 | 74.2667 | 100.1333 | 95.7333
2015-08-10 16:00 | 68.8 | 73.7667 | 100 | 95.7667
2015-08-10 16:15 | 68.05 | 73.2667 | 100 | 95.2667
2015-08-10 16:30 | 67.3 | 72.7667 | 100 | 94.7667
2015-08-10 16:45 | 66.55 | 72.2667 | 100 | 94.2667
2015-08-10 17:00 | 66 | 71.7667 | 99.7667 | 93.7667
2015-08-10 17:15 | 66 | 71.2667 | 99.2667 | 93.2667
2015-08-10 17:30 | 66 | 70.7667 | 98.7667 | 92.7667
2015-08-10 17:45 | 66 | 70.2667 | 98.2667 | 92.2667
2015-08-10 18:00 | 66 | 69.65 | 97.65 | 91.5333
2015-08-10 18:15 | 66 | 68.9 | 96.9 | 90.5333
2015-08-10 18:30 | 66 | 68.15 | 96.15 | 89.5333
2015-08-10 18:45 | 66 | 67.4 | 95.4 | 88.5333
2015-08-10 19:00 | 65.8667 | 66.8833 | 94.7667 | 87.5333
2015-08-10 19:15 | 65.3667 | 66.6333 | 94.2667 | 86.5333
2015-08-10 19:30 | 64.8667 | 66.3833 | 93.7667 | 85.5333
2015-08-10 19:45 | 64.3667 | 66.1333 | 93.2667 | 84.5333
2015-08-10 20:00 | 63.9273 | 65.8833 | 92.5333 | 83.65
2015-08-10 20:15 | 63.6545 | 65.6333 | 91.5333 | 82.9
2015-08-10 20:30 | 63.3818 | 65.3833 | 90.5333 | 82.15
2015-08-10 20:45 | 63.1091 | 65.1333 | 89.5333 | 81.4
2015-08-10 21:00 | 62.9333 | 65 | 88.65 | 80.5333
2015-08-10 21:15 | 62.6833 | 65 | 87.9 | 79.5333
2015-08-10 21:30 | 62.4333 | 65 | 87.15 | 78.5333
2015-08-10 21:45 | 62.1833 | 65 | 86.4 | 77.5333
2015-08-10 22:00 | 62 | 64.8654 | 85.65 | 76.65
2015-08-10 22:15 | 62 | 64.5769 | 84.9 | 75.9
2015-08-10 22:30 | 62 | 64.2885 | 84.15 | 75.15
2015-08-10 22:45 | 62 | 64 | 83.4 | 74.4
2015-08-10 23:00 | 61.9333 | 64 | 82.65 | 73.7667
2015-08-10 23:15 | 61.6833 | 64 | 81.9 | 73.2667
2015-08-10 23:30 | 61.4333 | 64 | 81.15 | 72.7667
2015-08-10 23:45 | 61.1833 | 64 | 80.4 | 72.2667
2015-08-11 | 61 | 64 | 79.8833 | 71.7667
2015-08-11 00:15 | 61 | 63.8636 | 79.6333 | 71.2667
2015-08-11 00:30 | 61 | 63.5227 | 79.3833 | 70.7667
2015-08-11 00:45 | 60.5 | 63.1818 | 79.1333 | 70.2667
2015-08-11 01:00 | 60 | 62.8833 | 78.65 | 69.8833
2015-08-11 01:15 | 60 | 62.6333 | 77.9 | 69.6333
2015-08-11 01:30 | 60 | 62.3833 | 77.15 | 69.3833
2015-08-11 01:45 | 60 | 62.1333 | 76.4 | 69.1333
2015-08-11 02:00 | 60 | 61.8793 | 76.1167 | 68.7667
2015-08-11 02:15 | 60 | 61.6207 | 76.3667 | 68.2667
2015-08-11 02:30 | 60 | 61.3621 | 76.6167 | 67.7667
2015-08-11 02:45 | 60 | 61.1034 | 76.8667 | 67.2667
2015-08-11 03:00 | 60 | 62.1167 | 76.65 | 66.8833
2015-08-11 03:15 | 60 | 62.3667 | 75.9 | 66.6333
2015-08-11 03:30 | 60 | 62.6167 | 75.15 | 66.3833
2015-08-11 03:45 | 60 | 62.8667 | 74.4 | 66.1333
2015-08-11 04:00 | 60.2857 | 63 | 73.8833 | 65.7667
2015-08-11 04:15 | 60.8913 | 63 | 73.6333 | 65.2667
2015-08-11 04:30 | 60.5652 | 63 | 73.3833 | 64.7667
2015-08-11 04:45 | 60.2391 | 62.0667 | 73.1333 | 64.2667
2015-08-11 05:00 | 60 | 61 | 73 | 64
2015-08-11 05:15 | 60 | 61 | 73 | 64
2015-08-11 05:30 | 60 | 61 | 73 | 64
2015-08-11 05:45 | 60 | 61 | 73 | 64
2015-08-11 06:00 | 60.1333 | 61.2333 | 73 | 64.35
2015-08-11 06:15 | 60.6333 | 61.7333 | 73 | 65.1
2015-08-11 06:30 | 61.1333 | 62.2333 | 73 | 65.85
2015-08-11 06:45 | 61.6333 | 62.7333 | 73 | 66.6
2015-08-11 07:00 | 62.0667 | 63.1429 | 73.4667 | 67.35
2015-08-11 07:15 | 62.3167 | 63.449 | 74.4667 | 68.1
2015-08-11 07:30 | 62.5667 | 63.7551 | 75.4667 | 68.85
2015-08-11 07:45 | 62.8167 | 64.2727 | 76.4667 | 69.6
2015-08-11 08:00 | 63.2 | 65.2333 | 77.7 | 70.5833
2015-08-11 08:15 | 63.95 | 65.7333 | 79.2 | 71.8333
2015-08-11 08:30 | 64.7 | 66.2333 | 80.7 | 73.0833
2015-08-11 08:45 | 65.45 | 66.7333 | 82.2 | 74.3333
2015-08-11 09:00 | 66.1333 | 67.35 | 83.1167 | 75.4667
2015-08-11 09:15 | 66.6333 | 68.1 | 83.3667 | 76.4667
2015-08-11 09:30 | 67.1333 | 68.85 | 83.6167 | 77.4667
2015-08-11 09:45 | 67.6333 | 69.6 | 83.8667 | 78.4667
2015-08-11 10:00 | 68.0667 | 70.4667 | 84.5833 | 79.4667
2015-08-11 10:15 | 68.3167 | 71.4667 | 85.8333 | 80.4667
2015-08-11 10:30 | 68.5667 | 72.4667 | 87.0833 | 81.4667
2015-08-11 10:45 | 68.8167 | 73.4667 | 88.3333 | 82.4667
2015-08-11 11:00 | 69.0667 | 74.4667 | 89.4667 | 83.4667
2015-08-11 11:15 | 69.3167 | 75.4667 | 90.4667 | 84.4667
2015-08-11 11:30 | 69.5667 | 76.4667 | 91.4667 | 85.4667
2015-08-11 11:45 | 69.8167 | 77.4667 | 92.4667 | 86.4667
2015-08-11 12:00 | 70.1333 | 78.4667 | 93.2333 | 87.2333
2015-08-11 12:15 | 70.6333 | 79.4667 | 93.7333 | 87.7333
2015-08-11 12:30 | 71.1333 | 80.4667 | 94.2333 | 88.2333
2015-08-11 12:45 | 71.6333 | 81.4667 | 94.7333 | 88.7333
2015-08-11 13:00 | 71.8667 | 81.65 | 95.2333 | 89.2333
2015-08-11 13:15 | 71.3667 | 80.9 | 95.7333 | 89.7333
2015-08-11 13:30 | 70.8667 | 80.15 | 96.2333 | 90.2333
2015-08-11 13:45 | 70.3667 | 79.4 | 96.7333 | 90.7333
2015-08-11 14:00 | 69.9333 | 78.8833 | 97.2333 | 91.1167
2015-08-11 14:15 | 69.6833 | 78.6333 | 97.7333 | 91.3667
2015-08-11 14:30 | 69.4333 | 78.3833 | 98.2333 | 91.6167
2015-08-11 14:45 | 69.1833 | 78.1333 | 98.7333 | 91.8667
2015-08-11 15:00 | 69 | 77.8833 | 99 | 92.1167
2015-08-11 15:15 | 69 | 77.6333 | 99 | 92.3667
2015-08-11 15:30 | 69 | 77.3833 | 99 | 92.6167
2015-08-11 15:45 | 69 | 77.1333 | 99 | 92.8667
2015-08-11 16:00 | 68.9333 | 76.65 | 98.8833 | 93
2015-08-11 16:15 | 68.6833 | 75.9 | 98.6333 | 93
2015-08-11 16:30 | 68.4333 | 75.15 | 98.3833 | 93
2015-08-11 16:45 | 68.1833 | 74.4 | 98.1333 | 93
2015-08-11 17:00 | 67.8667 | 73.7667 | 97.7667 | 92.7667
2015-08-11 17:15 | 67.3667 | 73.2667 | 97.2667 | 92.2667
2015-08-11 17:30 | 66.8667 | 72.7667 | 96.7667 | 91.7667
2015-08-11 17:45 | 66.3667 | 72.2667 | 96.2667 | 91.2667
2015-08-11 18:00 | 65.8 | 71.5333 | 95.8833 | 90.7667
2015-08-11 18:15 | 65.05 | 70.5333 | 95.6333 | 90.2667
2015-08-11 18:30 | 64.3 | 69.5333 | 95.3833 | 89.7667
2015-08-11 18:45 | 63.55 | 68.5333 | 95.1333 | 89.2667
2015-08-11 19:00 | 62.9333 | 67.7667 | 94.65 | 88.65
2015-08-11 19:15 | 62.6833 | 67.2667 | 93.9 | 87.9
2015-08-11 19:30 | 62.4333 | 66.7667 | 93.15 | 87.15
2015-08-11 19:45 | 62.1833 | 66.2667 | 92.4 | 86.4
2015-08-11 20:00 | 62 | 65.8833 | 91.65 | 85.5333
2015-08-11 20:15 | 62 | 65.6333 | 90.9 | 84.5333
2015-08-11 20:30 | 62 | 65.3833 | 90.15 | 83.5333
2015-08-11 20:45 | 62 | 65.1333 | 89.4 | 82.5333
2015-08-11 21:00 | 62 | 64.8833 | 88.4167 | 81.5333
2015-08-11 21:15 | 62 | 64.6333 | 87.1667 | 80.5333
2015-08-11 21:30 | 62 | 64.3833 | 85.9167 | 79.5333
2015-08-11 21:45 | 62 | 64.1333 | 84.6667 | 78.5333
2015-08-11 22:00 | 62 | 63.8833 | 83.65 | 77.7667
2015-08-11 22:15 | 62 | 63.6333 | 82.9 | 77.2667
2015-08-11 22:30 | 62 | 63.3833 | 82.15 | 76.7667
2015-08-11 22:45 | 62 | 63.1333 | 81.4 | 76.2667
2015-08-11 23:00 | 61.9333 | 62.8833 | 80.8833 | 75.5333
2015-08-11 23:15 | 61.6833 | 62.6333 | 80.6333 | 74.5333
2015-08-11 23:30 | 61.4333 | 62.3833 | 80.3833 | 73.5333
2015-08-11 23:45 | 61.1833 | 62.1333 | 80.1333 | 72.5333
2015-08-12 | 60.9333 | 62 | 79.5333 | 71.7667
2015-08-12 00:15 | 60.6833 | 62 | 78.5333 | 71.2667
2015-08-12 00:30 | 60.4333 | 62 | 77.5333 | 70.7667
2015-08-12 00:45 | 60.1833 | 62 | 76.5333 | 70.2667
2015-08-12 01:00 | 60 | 62 | 75.7667 | 69.8833
2015-08-12 01:15 | 60 | 62 | 75.2667 | 69.6333
2015-08-12 01:30 | 60 | 62 | 74.7667 | 69.3833
2015-08-12 01:45 | 60 | 62 | 74.2667 | 69.1333
2015-08-12 02:00 | 59.9333 | 61.8833 | 74 | 68.8833
2015-08-12 02:15 | 59.6833 | 61.6333 | 74 | 68.6333
2015-08-12 02:30 | 59.4333 | 61.3833 | 74 | 68.3833
2015-08-12 02:45 | 59.1833 | 61.1333 | 74 | 68.1333
2015-08-12 03:00 | 59 | 60.7667 | 73.8833 | 67.7667
2015-08-12 03:15 | 59 | 60.2667 | 73.6333 | 67.2667
2015-08-12 03:30 | 59 | 59.7667 | 73.3833 | 66.7667
2015-08-12 03:45 | 59 | 59.2667 | 73.1333 | 66.2667
2015-08-12 04:00 | 59 | 59 | 72.8833 | 66
2015-08-12 04:15 | 59 | 59 | 72.6333 | 66
2015-08-12 04:30 | 59 | 59 | 72.3833 | 66
2015-08-12 04:45 | 59 | 59 | 72.1333 | 66
2015-08-12 05:00 | 59 | 59 | 71.8833 | 65.8833
2015-08-12 05:15 | 59 | 59 | 71.6333 | 65.6333
2015-08-12 05:30 | 59 | 59 | 71.3833 | 65.3833
2015-08-12 05:45 | 59 | 59 | 71.1333 | 65.1333
2015-08-12 06:00 | 59.2 | 59.35 | 71.4667 | 65.2333
2015-08-12 06:15 | 59.95 | 60.1 | 72.4667 | 65.7333
2015-08-12 06:30 | 60.7 | 60.85 | 73.4667 | 66.2333
2015-08-12 06:45 | 61.45 | 61.6 | 74.4667 | 66.7333
2015-08-12 07:00 | 62.2 | 62.4667 | 75.5833 | 67.5833
2015-08-12 07:15 | 62.95 | 63.4667 | 76.8333 | 68.8333
2015-08-12 07:30 | 63.7 | 64.4667 | 78.0833 | 70.0833
2015-08-12 07:45 | 64.45 | 65.4667 | 79.3333 | 71.3333
2015-08-12 08:00 | 65.1333 | 66.35 | 80.7 | 72.4667
2015-08-12 08:15 | 65.6333 | 67.1 | 82.2 | 73.4667
2015-08-12 08:30 | 66.1333 | 67.85 | 83.7 | 74.4667
2015-08-12 08:45 | 66.6333 | 68.6 | 85.2 | 75.4667
2015-08-12 09:00 | 67.1333 | 69.5833 | 86.4667 | 76.4667
2015-08-12 09:15 | 67.6333 | 70.8333 | 87.4667 | 77.4667
2015-08-12 09:30 | 68.1333 | 72.0833 | 88.4667 | 78.4667
2015-08-12 09:45 | 68.6333 | 73.3333 | 89.4667 | 79.4667
2015-08-12 10:00 | 69.1333 | 74.2333 | 90.2333 | 80.2333
2015-08-12 10:15 | 69.6333 | 74.7333 | 90.7333 | 80.7333
2015-08-12 10:30 | 70.1333 | 75.2333 | 91.2333 | 81.2333
2015-08-12 10:45 | 70.6333 | 75.7333 | 91.7333 | 81.7333
2015-08-12 11:00 | 71.4 | 76.2333 | 92.35 | 82.5833
2015-08-12 11:15 | 72.9 | 76.7333 | 93.1 | 83.8333
2015-08-12 11:30 | 74.4 | 77.2333 | 93.85 | 85.0833
2015-08-12 11:45 | 75.9 | 77.7333 | 94.6 | 86.3333
2015-08-12 12:00 | 76.8667 | 78.1167 | 95.2333 | 87.2333
2015-08-12 12:15 | 76.3667 | 78.3667 | 95.7333 | 87.7333
2015-08-12 12:30 | 75.8667 | 78.6167 | 96.2333 | 88.2333
2015-08-12 12:45 | 75.3667 | 78.8667 | 96.7333 | 88.7333
2015-08-12 13:00 | 74.9333 | 79.1167 | 97.1167 | 89.2333
2015-08-12 13:15 | 74.6833 | 79.3667 | 97.3667 | 89.7333
2015-08-12 13:30 | 74.4333 | 79.6167 | 97.6167 | 90.2333
2015-08-12 13:45 | 74.1833 | 79.8667 | 97.8667 | 90.7333
2015-08-12 14:00 | 74.0667 | 80.1167 | 98 | 91.2333
2015-08-12 14:15 | 74.3167 | 80.3667 | 98 | 91.7333
2015-08-12 14:30 | 74.5667 | 80.6167 | 98 | 92.2333
2015-08-12 14:45 | 74.8167 | 80.8667 | 98 | 92.7333
2015-08-12 15:00 | 75.0667 | 80.7667 | 97.8833 | 93.2333
2015-08-12 15:15 | 75.3167 | 80.2667 | 97.6333 | 93.7333
2015-08-12 15:30 | 75.5667 | 79.7667 | 97.3833 | 94.2333
2015-08-12 15:45 | 75.8167 | 79.2667 | 97.1333 | 94.7333
2015-08-12 16:00 | 75.9333 | 78.8833 | 96.4167 | 95
2015-08-12 16:15 | 75.6833 | 78.6333 | 95.1667 | 95
2015-08-12 16:30 | 75.4333 | 78.3833 | 93.9167 | 95
2015-08-12 16:45 | 75.1833 | 78.1333 | 92.6667 | 95
2015-08-12 17:00 | 74.8 | 77.7667 | 92 | 94.7667
2015-08-12 17:15 | 74.05 | 77.2667 | 92 | 94.2667
2015-08-12 17:30 | 73.3 | 76.7667 | 92 | 93.7667
2015-08-12 17:45 | 72.55 | 76.2667 | 92 | 93.2667
2015-08-12 18:00 | 71.7333 | 75.5333 | 91.8833 | 92.65
2015-08-12 18:15 | 70.7333 | 74.5333 | 91.6333 | 91.9
2015-08-12 18:30 | 69.7333 | 73.5333 | 91.3833 | 91.15
2015-08-12 18:45 | 68.7333 | 72.5333 | 91.1333 | 90.4
2015-08-12 19:00 | 67.9333 | 71.7667 | 90.3 | 89.5333
2015-08-12 19:15 | 67.6833 | 71.2667 | 88.8 | 88.5333
2015-08-12 19:30 | 67.4333 | 70.7667 | 87.3 | 87.5333
2015-08-12 19:45 | 67.1833 | 70.2667 | 85.8 | 86.5333
2015-08-12 20:00 | 67 | 69.7667 | 84.65 | 85.65
2015-08-12 20:15 | 67 | 69.2667 | 83.9 | 84.9
2015-08-12 20:30 | 67 | 68.7667 | 83.15 | 84.15
2015-08-12 20:45 | 67 | 68.2667 | 82.4 | 83.4
2015-08-12 21:00 | 66.9333 | 67.8833 | 82 | 82.65
2015-08-12 21:15 | 66.6833 | 67.6333 | 82 | 81.9
2015-08-12 21:30 | 66.4333 | 67.3833 | 82 | 81.15
2015-08-12 21:45 | 66.1833 | 67.1333 | 82 | 80.4
2015-08-12 22:00 | 66 | 66.8833 | 82 | 79.65
2015-08-12 22:15 | 66 | 66.6333 | 82 | 78.9
2015-08-12 22:30 | 66 | 66.3833 | 82 | 78.15
2015-08-12 22:45 | 66 | 66.1333 | 82 | 77.4
2015-08-12 23:00 | 66.92 | 66 | 81.65 | 76.7667
2015-08-12 23:15 | 66.62 | 66 | 80.9 | 76.2667
2015-08-12 23:30 | 66.32 | 66.2069 | 80.15 | 75.7667
2015-08-12 23:45 | 66.02 | 66.7241 | 79.4 | 75.2667
2015-08-13 | 66 | 67 | 78.65 | 74.65
2015-08-13 00:15 | 66 | 67 | 77.9 | 73.9
2015-08-13 00:30 | 66 | 67 | 77.15 | 73.15
2015-08-13 00:45 | 66 | 67 | 76.4 | 72.4
2015-08-13 01:00 | 65.9333 | 67 | 76.2333 | 71.7667
2015-08-13 01:15 | 65.6833 | 67 | 76.7333 | 71.2667
2015-08-13 01:30 | 65.4333 | 67 | 77.2333 | 70.7667
2015-08-13 01:45 | 65.1833 | 67 | 77.7333 | 70.2667
2015-08-13 02:00 | 64.931 | 66.8833 | 77.7667 | 69.7667
2015-08-13 02:15 | 64.6724 | 66.6333 | 77.2667 | 69.2667
2015-08-13 02:30 | 64.4138 | 66.3833 | 76.7667 | 68.7667
2015-08-13 02:45 | 64.1552 | 66.1333 | 76.2667 | 68.2667
2015-08-13 03:00 | 64.9333 | 66 | 76 | 67.8833
2015-08-13 03:15 | 64.6833 | 66 | 76 | 67.6333
2015-08-13 03:30 | 64.4333 | 66 | 76 | 67.3833
2015-08-13 03:45 | 64.1833 | 66 | 76 | 67.1333
2015-08-13 04:00 | 63.9245 | 65.4615 | 76 | 66.8833
2015-08-13 04:15 | 63.6415 | 64.3077 | 76 | 66.6333
2015-08-13 04:30 | 63.3585 | 64 | 76 | 66.3833
2015-08-13 04:45 | 63.0755 | 64.5556 | 76 | 66.1333
2015-08-13 05:00 | 63 | 64.8409 | 75.7667 | 66
2015-08-13 05:15 | 63 | 64.5 | 75.2667 | 66
2015-08-13 05:30 | 63 | 64.1591 | 74.7667 | 66
2015-08-13 05:45 | 63 | 64 | 74.2667 | 66
2015-08-13 06:00 | 63 | 64.1167 | 74.1167 | 66.35
2015-08-13 06:15 | 63 | 64.3667 | 74.3667 | 67.1
2015-08-13 06:30 | 63 | 64.6167 | 74.6167 | 67.85
2015-08-13 06:45 | 63 | 64.8667 | 74.8667 | 68.6
2015-08-13 07:00 | 63.0667 | 65.2333 | 75.7 | 69.35
2015-08-13 07:15 | 63.3167 | 65.7333 | 77.2 | 70.1
2015-08-13 07:30 | 63.5667 | 66.2333 | 78.7 | 70.85
2015-08-13 07:45 | 63.8167 | 66.7333 | 80.2 | 71.6
2015-08-13 08:00 | 64.4211 | 67.4667 | 81.7 | 72.5833
2015-08-13 08:15 | 66 | 68.4667 | 83.2 | 73.8333
2015-08-13 08:30 | 66.7317 | 69.4667 | 84.7 | 75.0833
2015-08-13 08:45 | 67.4634 | 70.4667 | 86.2 | 76.3333
2015-08-13 09:00 | 68 | 71.2333 | 87.35 | 77.4667
2015-08-13 09:15 | 68 | 71.7333 | 88.1 | 78.4667
2015-08-13 09:30 | 68 | 72.2333 | 88.85 | 79.4667
2015-08-13 09:45 | 68 | 72.7333 | 89.6 | 80.4667
2015-08-13 10:00 | 68.2667 | 73.2333 | 90.2333 | 81.4667
2015-08-13 10:15 | 69.2667 | 73.7333 | 90.7333 | 82.4667
2015-08-13 10:30 | 70.2667 | 74.2333 | 91.2333 | 83.4667
2015-08-13 10:45 | 71.2667 | 74.7333 | 91.7333 | 84.4667
2015-08-13 11:00 | 72 | 75.1167 | 92.2333 | 85.4667
2015-08-13 11:15 | 72 | 75.3667 | 92.7333 | 86.4667
2015-08-13 11:30 | 72 | 75.6167 | 93.2333 | 87.4667
2015-08-13 11:45 | 72 | 75.8667 | 93.7333 | 88.4667
2015-08-13 12:00 | 72 | 76.1167 | 94.35 | 89.2333
2015-08-13 12:15 | 72 | 76.3667 | 95.1 | 89.7333
2015-08-13 12:30 | 72 | 76.6167 | 95.85 | 90.2333
2015-08-13 12:45 | 72 | 76.8667 | 96.6 | 90.7333
2015-08-13 13:00 | 72.0667 | 77 | 97.35 | 91.35
2015-08-13 13:15 | 72.3167 | 77 | 98.1 | 92.1
2015-08-13 13:30 | 72.5667 | 77 | 98.85 | 92.85
2015-08-13 13:45 | 72.8167 | 77 | 99.6 | 93.6
2015-08-13 14:00 | 73.0667 | 77.2333 | 99.8833 | 94.1167
2015-08-13 14:15 | 73.3167 | 77.7333 | 99.6333 | 94.3667
2015-08-13 14:30 | 73.5667 | 78.2333 | 99.3833 | 94.6167
2015-08-13 14:45 | 73.8167 | 78.7333 | 99.1333 | 94.8667
2015-08-13 15:00 | 73.9333 | 78.8833 | 99.1167 | 95.2333
2015-08-13 15:15 | 73.6833 | 78.6333 | 99.3667 | 95.7333
2015-08-13 15:30 | 73.4333 | 78.3833 | 99.6167 | 96.2333
2015-08-13 15:45 | 73.1833 | 78.1333 | 99.8667 | 96.7333
2015-08-13 16:00 | 72.8667 | 77.8833 | 99.8833 | 97
2015-08-13 16:15 | 72.3667 | 77.6333 | 99.6333 | 97
2015-08-13 16:30 | 71.8667 | 77.3833 | 99.3833 | 97
2015-08-13 16:45 | 71.3667 | 77.1333 | 99.1333 | 97
2015-08-13 17:00 | 70.8667 | 76.5333 | 98.8833 | 96.7667
2015-08-13 17:15 | 70.3667 | 75.5333 | 98.6333 | 96.2667
2015-08-13 17:30 | 69.8667 | 74.5333 | 98.3833 | 95.7667
2015-08-13 17:45 | 69.3667 | 73.5333 | 98.1333 | 95.2667
2015-08-13 18:00 | 68.8667 | 72.65 | 97.7667 | 94.5333
2015-08-13 18:15 | 68.3667 | 71.9 | 97.2667 | 93.5333
2015-08-13 18:30 | 67.8667 | 71.15 | 96.7667 | 92.5333
2015-08-13 18:45 | 67.3667 | 70.4 | 96.2667 | 91.5333
2015-08-13 19:00 | 66.8667 | 69.7667 | 95.5333 | 90.65
2015-08-13 19:15 | 66.3667 | 69.2667 | 94.5333 | 89.9
2015-08-13 19:30 | 65.8667 | 68.7667 | 93.5333 | 89.15
2015-08-13 19:45 | 65.3667 | 68.2667 | 92.5333 | 88.4
2015-08-13 20:00 | 64.7838 | 67.8833 | 91.7667 | 87.4167
2015-08-13 20:15 | 63.973 | 67.6333 | 91.2667 | 86.1667
2015-08-13 20:30 | 63.1622 | 67.3833 | 90.7667 | 84.9167
2015-08-13 20:45 | 63 | 67.1333 | 90.2667 | 83.6667
2015-08-13 21:00 | 63 | 66.8833 | 89.7667 | 82.65
2015-08-13 21:15 | 63 | 66.6333 | 89.2667 | 81.9
2015-08-13 21:30 | 63 | 66.3833 | 88.7667 | 81.15
2015-08-13 21:45 | 63 | 66.1333 | 88.2667 | 80.4
2015-08-13 22:00 | 63 | 65.8833 | 87.7667 | 79.65
2015-08-13 22:15 | 63 | 65.6333 | 87.2667 | 78.9
2015-08-13 22:30 | 63 | 65.3833 | 86.7667 | 78.15
2015-08-13 22:45 | 63 | 65.1333 | 86.2667 | 77.4
2015-08-13 23:00 | 62.9333 | 64.4615 | 85.7667 | 76.7667
2015-08-13 23:15 | 62.6833 | 64 | 85.2667 | 76.2667
2015-08-13 23:30 | 62.4333 | 64 | 84.7667 | 75.7667
2015-08-13 23:45 | 62.1833 | 64.619 | 84.2667 | 75.2667
2015-08-14 | 62 | 65 | 83.7667 | 74.7667
2015-08-14 00:15 | 62 | 65 | 83.2667 | 74.2667
2015-08-14 00:30 | 62 | 65 | 82.7667 | 73.7667
2015-08-14 00:45 | 62 | 65 | 82.2667 | 73.2667
2015-08-14 01:00 | 62 | 65 | 81.7667 | 72.7667
2015-08-14 01:15 | 62 | 65 | 81.2667 | 72.2667
2015-08-14 01:30 | 62 | 65 | 80.7667 | 71.7667
2015-08-14 01:45 | 62 | 65 | 80.2667 | 71.2667
2015-08-14 02:00 | 62 | 64.8333 | 80 | 70.7667
2015-08-14 02:15 | 62 | 64.4762 | 80 | 70.2667
2015-08-14 02:30 | 62 | 64.119 | 80 | 69.7667
2015-08-14 02:45 | 62 | 64.2727 | 80 | 69.2667
2015-08-14 03:00 | 62.1 | 64.8833 | 79.8833 | 69
2015-08-14 03:15 | 62.475 | 64.6333 | 79.6333 | 69
2015-08-14 03:30 | 62.85 | 64.3833 | 79.3833 | 69
2015-08-14 03:45 | 63 | 64.1333 | 79.1333 | 69
2015-08-14 04:00 | 62.9333 | 64 | 78.8833 | 68.8833
2015-08-14 04:15 | 62.6833 | 64 | 78.6333 | 68.6333
2015-08-14 04:30 | 62.4333 | 64 | 78.3833 | 68.3833
2015-08-14 04:45 | 62.1833 | 64 | 78.1333 | 68.1333
2015-08-14 05:00 | 62 | 64 | 77.7667 | 67.7667
2015-08-14 05:15 | 62 | 64 | 77.2667 | 67.2667
2015-08-14 05:30 | 62 | 64 | 76.7667 | 66.7667
2015-08-14 05:45 | 62 | 64 | 76.2667 | 66.2667
2015-08-14 06:00 | 62.3636 | 64.1167 | 76 | 66.2333
2015-08-14 06:15 | 63.1633 | 64.3667 | 76 | 66.7333
2015-08-14 06:30 | 63.4694 | 64.6167 | 76 | 67.2333
2015-08-14 06:45 | 63.7755 | 64.8667 | 76 | 67.7333
2015-08-14 07:00 | 64 | 65.1167 | 77.05 | 68.35
2015-08-14 07:15 | 64 | 65.3667 | 79.3 | 69.1
2015-08-14 07:30 | 64 | 65.6167 | 81.55 | 69.85
2015-08-14 07:45 | 64 | 65.8667 | 83.8 | 70.6
2015-08-14 08:00 | 65.1333 | 66.1167 | 85.4667 | 71.35
2015-08-14 08:15 | 65.6333 | 66.3667 | 86.4667 | 72.1
2015-08-14 08:30 | 66.1333 | 66.6167 | 87.4667 | 72.85
2015-08-14 08:45 | 66.6333 | 66.8667 | 88.4667 | 73.6
2015-08-14 09:00 | 67 | 67.3818 | 89.35 | 74.4667
2015-08-14 09:15 | 67 | 68.2 | 90.1 | 75.4667
2015-08-14 09:30 | 67 | 69.0182 | 90.85 | 76.4667
2015-08-14 09:45 | 67 | 69.8364 | 91.6 | 77.4667
2015-08-14 10:00 | 67.1333 | 69.35 | 92.4667 | 78.4667
2015-08-14 10:15 | 67.6333 | 70.1 | 93.4667 | 79.4667
2015-08-14 10:30 | 68.1333 | 70.85 | 94.4667 | 80.4667
2015-08-14 10:45 | 68.6333 | 71.6 | 95.4667 | 81.4667
2015-08-14 11:00 | 69.2 | 72.4667 | 96 | 82.4667
2015-08-14 11:15 | 69.95 | 73.4667 | 96 | 83.4667
2015-08-14 11:30 | 70.7 | 74.4667 | 96 | 84.4667
2015-08-14 11:45 | 71.45 | 75.4667 | 96 | 85.4667
2015-08-14 12:00 | 71.9333 | 76.1167 | 96.35 | 86.2333
2015-08-14 12:15 | 71.6833 | 76.3667 | 97.1 | 86.7333
2015-08-14 12:30 | 71.4333 | 76.6167 | 97.85 | 87.2333
2015-08-14 12:45 | 71.1833 | 76.8667 | 98.6 | 87.7333
2015-08-14 13:00 | 71.1333 | 77.1167 | 98.8833 | 88.2333
2015-08-14 13:15 | 71.6333 | 77.3667 | 98.6333 | 88.7333
2015-08-14 13:30 | 72.1333 | 77.6167 | 98.3833 | 89.2333
2015-08-14 13:45 | 72.6333 | 77.8667 | 98.1333 | 89.7333
2015-08-14 14:00 | 72.9333 | 78 | 98.2333 | 90.4667
2015-08-14 14:15 | 72.6833 | 78 | 98.7333 | 91.4667
2015-08-14 14:30 | 72.4333 | 78 | 99.2333 | 92.4667
2015-08-14 14:45 | 72.1833 | 78 | 99.7333 | 93.4667
2015-08-14 15:00 | 71.9333 | 78 | 100 | 93.8833
2015-08-14 15:15 | 71.6833 | 78 | 100 | 93.6333
2015-08-14 15:30 | 71.4333 | 78 | 100 | 93.3833
2015-08-14 15:45 | 71.1833 | 78 | 100 | 93.1333
2015-08-14 16:00 | 71 | 77.8833 | 99.8833 | 93
2015-08-14 16:15 | 71 | 77.6333 | 99.6333 | 93
2015-08-14 16:30 | 71 | 77.3833 | 99.3833 | 93
2015-08-14 16:45 | 71 | 77.1333 | 99.1333 | 93
2015-08-14 17:00 | 70.8 | 76.5333 | 99 | 92.7667
2015-08-14 17:15 | 70.05 | 75.5333 | 95.6452 | 92.2667
2015-08-14 17:30 | 69.3 | 74.5333 | 91.7742 | 91.7667
2015-08-14 17:45 | 68.55 | 73.5333 | 78.0769 | 91.2667
2015-08-14 18:00 | 67.8 | 72.65 | 77 | 90.65
2015-08-14 18:15 | 67.05 | 71.9 | 78.875 | 89.9
2015-08-14 18:30 | 66.3 | 71.15 | 76.36 | 89.15
2015-08-14 18:45 | 65.55 | 70.4 | 73.96 | 88.4
2015-08-14 19:00 | 64.9333 | 69.7667 | 74.875 | 87.7667
2015-08-14 19:15 | 64.6833 | 69.2667 | 75.5652 | 87.2667
2015-08-14 19:30 | 64.4333 | 68.7667 | 74.2609 | 86.7667
2015-08-14 19:45 | 64.1833 | 68.2667 | 75.2 | 86.2667
2015-08-14 20:00 | 63.9333 | 67.7667 | 76.1167 | 85.65
2015-08-14 20:15 | 63.6833 | 67.2667 | 76.3667 | 84.9
2015-08-14 20:30 | 63.4333 | 66.7667 | 76.6167 | 84.15
2015-08-14 20:45 | 63.1833 | 66.2667 | 76.8667 | 83.4
2015-08-14 21:00 | 63 | 65.8833 | 77.1167 | 82.65
2015-08-14 21:15 | 63 | 65.6333 | 77.3667 | 81.9
2015-08-14 21:30 | 63 | 65.3833 | 77.6167 | 81.15
2015-08-14 21:45 | 63 | 65.1333 | 77.8667 | 80.4
2015-08-14 22:00 | 63.0667 | 65 | 77.5333 | 79.7667
2015-08-14 22:15 | 63.3167 | 65 | 76.5333 | 79.2667
2015-08-14 22:30 | 63.5667 | 65 | 75.5333 | 78.7667
2015-08-14 22:45 | 63.8167 | 65 | 74.5333 | 78.2667
2015-08-14 23:00 | 63.9333 | 65 | 73.65 | 77.7667
2015-08-14 23:15 | 63.6833 | 65 | 72.9 | 77.2667
2015-08-14 23:30 | 63.4333 | 65 | 72.15 | 76.7667
2015-08-14 23:45 | 63.1833 | 65 | 71.4 | 76.2667
2015-08-15 | 62.8667 | 64.8833 | 71.2333 | 75.65
2015-08-15 00:15 | 62.3667 | 64.6333 | 71.7333 | 74.9
2015-08-15 00:30 | 61.8667 | 64.3833 | 72.2333 | 74.15
2015-08-15 00:45 | 61.3667 | 64.1333 | 72.7333 | 73.4
2015-08-15 01:00 | 61 | 63.8833 | 73 | 72.8833
2015-08-15 01:15 | 61 | 63.6333 | 73 | 72.6333
2015-08-15 01:30 | 61 | 63.3833 | 73 | 72.3833
2015-08-15 01:45 | 61 | 63.1333 | 73 | 72.1333
2015-08-15 02:00 | 61.0667 | 62.8833 | 72.7667 | 71.7667
2015-08-15 02:15 | 61.3167 | 62.6333 | 72.2667 | 71.2667
2015-08-15 02:30 | 61.5667 | 62.3833 | 71.7667 | 70.7667
2015-08-15 02:45 | 61.8167 | 62.1333 | 71.2667 | 70.2667
2015-08-15 03:00 | 62 | 61.8833 | 70.7667 | 69.8833
2015-08-15 03:15 | 62 | 61.6333 | 70.2667 | 69.6333
2015-08-15 03:30 | 62 | 61.3833 | 69.7667 | 69.3833
2015-08-15 03:45 | 62 | 61.1333 | 69.2667 | 69.1333
2015-08-15 04:00 | 61.9333 | 60.7667 | 69 | 68.8833
2015-08-15 04:15 | 61.6833 | 60.2667 | 69 | 68.6333
2015-08-15 04:30 | 61.4333 | 59.7667 | 69 | 68.3833
2015-08-15 04:45 | 61.1833 | 59.2667 | 69 | 68.1333
2015-08-15 05:00 | 61 | 59.2333 | 68.8833 | 68
2015-08-15 05:15 | 61 | 59.7333 | 68.6333 | 68
2015-08-15 05:30 | 61 | 60.2333 | 68.3833 | 68
2015-08-15 05:45 | 61 | 60.7333 | 68.1333 | 68
2015-08-15 06:00 | 61.3333 | 61.35 | 68.1167 | 68.2333
2015-08-15 06:15 | 62.5833 | 62.1 | 68.3667 | 68.7333
2015-08-15 06:30 | 63.8333 | 62.85 | 68.6167 | 69.2333
2015-08-15 06:45 | 65.0833 | 63.6 | 68.8667 | 69.7333
2015-08-15 07:00 | 66.2 | 64.4667 | 69.5833 | 70.5833
2015-08-15 07:15 | 66.95 | 65.4667 | 70.8333 | 71.8333
2015-08-15 07:30 | 67.7 | 66.4667 | 72.0833 | 73.0833
2015-08-15 07:45 | 68.45 | 67.4667 | 73.3333 | 74.3333
2015-08-15 08:00 | 69.0667 | 68.5833 | 74.2333 | 75.5833
2015-08-15 08:15 | 69.3167 | 69.8333 | 74.7333 | 76.8333
2015-08-15 08:30 | 69.5667 | 71.0833 | 75.2333 | 78.0833
2015-08-15 08:45 | 69.8167 | 72.3333 | 75.7333 | 79.3333
2015-08-15 09:00 | 70.1333 | 73.7 | 76.4667 | 80.4667
2015-08-15 09:15 | 70.6333 | 75.2 | 77.4667 | 81.4667
2015-08-15 09:30 | 71.1333 | 76.7 | 78.4667 | 82.4667
2015-08-15 09:45 | 71.6333 | 78.2 | 79.4667 | 83.4667
2015-08-15 10:00 | 72.2 | 79.4667 | 80.35 | 84.5833
2015-08-15 10:15 | 72.95 | 80.4667 | 81.1 | 85.8333
2015-08-15 10:30 | 73.7 | 81.4667 | 81.85 | 87.0833
2015-08-15 10:45 | 74.45 | 82.4667 | 82.6 | 88.3333
2015-08-15 11:00 | 75.2 | 83.2333 | 83.4667 | 89.35
2015-08-15 11:15 | 75.95 | 83.7333 | 84.4667 | 90.1
2015-08-15 11:30 | 76.7 | 84.2333 | 85.4667 | 90.85
2015-08-15 11:45 | 77.45 | 84.7333 | 86.4667 | 91.6
2015-08-15 12:00 | 78.3333 | 85.8167 | 87.4667 | 92.35
2015-08-15 12:15 | 79.5833 | 87.5667 | 88.4667 | 93.1
2015-08-15 12:30 | 80.8333 | 89.3167 | 89.4667 | 93.85
2015-08-15 12:45 | 82.0833 | 91.0667 | 90.4667 | 94.6
2015-08-15 13:00 | 83.6 | 92.1167 | 91.35 | 95.35
2015-08-15 13:15 | 85.85 | 92.3667 | 92.1 | 96.1
2015-08-15 13:30 | 88.1 | 92.6167 | 92.85 | 96.85
2015-08-15 13:45 | 90.35 | 92.8667 | 93.6 | 97.6
2015-08-15 14:00 | 91.8 | 93 | 94.1167 | 98.1167
2015-08-15 14:15 | 91.05 | 93 | 94.3667 | 98.3667
2015-08-15 14:30 | 90.3 | 93 | 94.6167 | 98.6167
2015-08-15 14:45 | 89.55 | 93 | 94.8667 | 98.8667
2015-08-15 15:00 | 88.5333 | 92.8833 | 95 | 98.8833
2015-08-15 15:15 | 86.7833 | 92.6333 | 95 | 98.6333
2015-08-15 15:30 | 85.0333 | 92.3833 | 95 | 98.3833
2015-08-15 15:45 | 83.2833 | 92.1333 | 95 | 98.1333
2015-08-15 16:00 | 81.8 | 91.65 | 95 | 97.8833
2015-08-15 16:15 | 81.05 | 90.9 | 95 | 97.6333
2015-08-15 16:30 | 80.3 | 90.15 | 95 | 97.3833
2015-08-15 16:45 | 79.55 | 89.4 | 95 | 97.1333
2015-08-15 17:00 | 78.6667 | 88.5333 | 94.8833 | 96.8833
2015-08-15 17:15 | 77.4167 | 87.5333 | 94.6333 | 96.6333
2015-08-15 17:30 | 76.1667 | 86.5333 | 94.3833 | 96.3833
2015-08-15 17:45 | 74.9167 | 85.5333 | 94.1333 | 96.1333
2015-08-15 18:00 | 73.8 | 84.4167 | 93.7667 | 95.7667
2015-08-15 18:15 | 73.05 | 83.1667 | 93.2667 | 95.2667
2015-08-15 18:30 | 72.3 | 81.9167 | 92.7667 | 94.7667
2015-08-15 18:45 | 71.55 | 80.6667 | 92.2667 | 94.2667
2015-08-15 19:00 | 70.6667 | 79.7667 | 91.4167 | 93.5333
2015-08-15 19:15 | 69.4167 | 79.2667 | 90.1667 | 92.5333
2015-08-15 19:30 | 68.1667 | 78.7667 | 88.9167 | 91.5333
2015-08-15 19:45 | 66.9167 | 78.2667 | 87.6667 | 90.5333
2015-08-15 20:00 | 65.8667 | 77.7667 | 86.5333 | 89.7667
2015-08-15 20:15 | 65.3667 | 77.2667 | 85.5333 | 89.2667
2015-08-15 20:30 | 64.8667 | 76.7667 | 84.5333 | 88.7667
2015-08-15 20:45 | 64.3667 | 76.2667 | 83.5333 | 88.2667
2015-08-15 21:00 | 64 | 75.8833 | 82.8833 | 87.65
2015-08-15 21:15 | 64 | 75.6333 | 82.6333 | 86.9
2015-08-15 21:30 | 64 | 75.3833 | 82.3833 | 86.15
2015-08-15 21:45 | 64 | 75.1333 | 82.1333 | 85.4
2015-08-15 22:00 | 63.9333 | 74.65 | 81.8833 | 84.65
2015-08-15 22:15 | 63.6833 | 73.9 | 81.6333 | 83.9
2015-08-15 22:30 | 63.4333 | 73.15 | 81.3833 | 83.15
2015-08-15 22:45 | 63.1833 | 72.4 | 81.1333 | 82.4
2015-08-15 23:00 | 62.9333 | 72.5 | 80.8833 | 81.8833
2015-08-15 23:15 | 62.6833 | 72.6522 | 80.6333 | 81.6333
2015-08-15 23:30 | 62.4333 | 72 | 80.3833 | 81.3833
2015-08-15 23:45 | 62.1833 | 71.3478 | 80.1333 | 81.1333
2015-08-16 | 62 | 71.2414 | 80 | 80.7667
2015-08-16 00:15 | 62 | 71.7586 | 80 | 80.2667
2015-08-16 00:30 | 62 | 71.7419 | 80 | 79.7667
2015-08-16 00:45 | 62 | 71.2581 | 80 | 79.2667
2015-08-16 01:00 | 62 | 70.8833 | 79.7667 | 78.7667
2015-08-16 01:15 | 62 | 70.6333 | 79.2667 | 78.2667
2015-08-16 01:30 | 62 | 70.3833 | 78.7667 | 77.7667
2015-08-16 01:45 | 62 | 70.1333 | 78.2667 | 77.2667
2015-08-16 02:00 | 62 | 69.8833 | 78 | 76.8833
2015-08-16 02:15 | 62 | 69.6333 | 78 | 76.6333
2015-08-16 02:30 | 62 | 69.3833 | 78 | 76.3833
2015-08-16 02:45 | 62 | 69.1333 | 78 | 76.1333
2015-08-16 03:00 | 62 | 68.8833 | 77.8833 | 75.8833
2015-08-16 03:15 | 62 | 68.6333 | 77.6333 | 75.6333
2015-08-16 03:30 | 62 | 68.3833 | 77.3833 | 75.3833
2015-08-16 03:45 | 62 | 68.1333 | 77.1333 | 75.1333
2015-08-16 04:00 | 62 | 67.8833 | 76.8833 | 74.7667
2015-08-16 04:15 | 62 | 67.6333 | 76.6333 | 74.2667
2015-08-16 04:30 | 62 | 67.3833 | 76.3833 | 73.7667
2015-08-16 04:45 | 62 | 67.1333 | 76.1333 | 73.2667
2015-08-16 05:00 | 62 | 66.8833 | 75.8833 | 73.1167
2015-08-16 05:15 | 62 | 66.6333 | 75.6333 | 73.3667
2015-08-16 05:30 | 62 | 66.3833 | 75.3833 | 73.6167
2015-08-16 05:45 | 62 | 66.1333 | 75.1333 | 73.8667
2015-08-16 06:00 | 62.3333 | 66.35 | 75 | 74.4667
2015-08-16 06:15 | 63.5833 | 67.1 | 75 | 75.4667
2015-08-16 06:30 | 64.8333 | 67.85 | 75 | 76.4667
2015-08-16 06:45 | 66.0833 | 68.6 | 75 | 77.4667
2015-08-16 07:00 | 67.1333 | 69.1167 | 75.35 | 78.4667
2015-08-16 07:15 | 67.6333 | 69.3667 | 76.1 | 79.4667
2015-08-16 07:30 | 68.1333 | 69.6167 | 76.85 | 80.4667
2015-08-16 07:45 | 68.6333 | 69.8667 | 77.6 | 81.4667
2015-08-16 08:00 | 69.1333 | 70.7 | 78.5833 | 82.5833
2015-08-16 08:15 | 69.6333 | 72.2 | 79.8333 | 83.8333
2015-08-16 08:30 | 70.1333 | 73.7 | 81.0833 | 85.0833
2015-08-16 08:45 | 70.6333 | 75.2 | 82.3333 | 86.3333
2015-08-16 09:00 | 71.2667 | 76.7 | 83.2333 | 87.35
2015-08-16 09:15 | 72.2667 | 78.2 | 83.7333 | 88.1
2015-08-16 09:30 | 73.2667 | 79.7 | 84.2333 | 88.85
2015-08-16 09:45 | 74.2667 | 81.2 | 84.7333 | 89.6
2015-08-16 10:00 | 75.1333 | 82.5833 | 85.35 | 90.7
2015-08-16 10:15 | 75.6333 | 83.8333 | 86.1 | 92.2
2015-08-16 10:30 | 76.1333 | 85.0833 | 86.85 | 93.7
2015-08-16 10:45 | 76.6333 | 86.3333 | 87.6 | 95.2
2015-08-16 11:00 | 77.0667 | 87.4667 | 88.2333 | 96.2333
2015-08-16 11:15 | 77.3167 | 88.4667 | 88.7333 | 96.7333
2015-08-16 11:30 | 77.5667 | 89.4667 | 89.2333 | 97.2333
2015-08-16 11:45 | 77.8167 | 90.4667 | 89.7333 | 97.7333
2015-08-16 12:00 | 78.1333 | 91.35 | 89.8409 | 98.4667
2015-08-16 12:15 | 78.6333 | 92.1 | 89.5 | 99.4667
2015-08-16 12:30 | 79.1333 | 92.85 | 89.1591 | 100.4667
2015-08-16 12:45 | 79.6333 | 93.6 | 90.5 | 101.4667
2015-08-16 13:00 | 80.6667 | 94.35 | 92.2333 | 102.1167
2015-08-16 13:15 | 83.1667 | 95.1 | 92.7333 | 102.3667
2015-08-16 13:30 | 85.6667 | 95.85 | 93.2333 | 102.6167
2015-08-16 13:45 | 88.1667 | 96.6 | 93.7333 | 102.8667
2015-08-16 14:00 | 89.7333 | 97 | 94.2333 | 103
2015-08-16 14:15 | 88.7333 | 97 | 94.7333 | 103
2015-08-16 14:30 | 87.7333 | 97 | 95.2333 | 103
2015-08-16 14:45 | 86.7333 | 97 | 95.7333 | 103
2015-08-16 15:00 | 85.9333 | 96.7667 | 96 | 103
2015-08-16 15:15 | 85.6833 | 96.2667 | 96 | 103
2015-08-16 15:30 | 85.4333 | 95.7667 | 96 | 103
2015-08-16 15:45 | 85.1833 | 95.2667 | 96 | 103
2015-08-16 16:00 | 84.8667 | 94.5333 | 95.7667 | 103
2015-08-16 16:15 | 84.3667 | 93.5333 | 95.2667 | 103
2015-08-16 16:30 | 83.8667 | 92.5333 | 94.7667 | 103
2015-08-16 16:45 | 83.3667 | 91.5333 | 94.2667 | 103
2015-08-16 17:00 | 82.9333 | 90.65 | 93.7667 | 102.8833
2015-08-16 17:15 | 82.6833 | 89.9 | 93.2667 | 102.6333
2015-08-16 17:30 | 82.4333 | 89.15 | 92.7667 | 102.3833
2015-08-16 17:45 | 82.1833 | 88.4 | 92.2667 | 102.1333
2015-08-16 18:00 | 81.7333 | 87.5333 | 90.0556 | 101.4167
2015-08-16 18:15 | 80.7333 | 86.5333 | 85.8889 | 100.1667
2015-08-16 18:30 | 79.7333 | 85.5333 | 81.9583 | 98.9167
2015-08-16 18:45 | 78.7333 | 84.5333 | 81.3333 | 97.6667
2015-08-16 19:00 | 77.6667 | 83.65 | 80.65 | 96.65
2015-08-16 19:15 | 76.4167 | 82.9 | 79.9 | 95.9
2015-08-16 19:30 | 75.1667 | 82.15 | 79.15 | 95.15
2015-08-16 19:45 | 73.9167 | 81.4 | 78.4 | 94.4
2015-08-16 20:00 | 73 | 80.65 | 77.7667 | 93.65
2015-08-16 20:15 | 73 | 79.9 | 77.2667 | 92.9
2015-08-16 20:30 | 73 | 79.15 | 76.7667 | 92.15
2015-08-16 20:45 | 73 | 78.4 | 76.2667 | 91.4
2015-08-16 21:00 | 72.6667 | 78 | 75.8833 | 90.7667
2015-08-16 21:15 | 71.4167 | 78 | 75.6333 | 90.2667
2015-08-16 21:30 | 70.1667 | 78 | 75.3833 | 89.7667
2015-08-16 21:45 | 68.9167 | 78 | 75.1333 | 89.2667
2015-08-16 22:00 | 67.8667 | 77.7667 | 74.8833 | 88.4167
2015-08-16 22:15 | 67.3667 | 77.2667 | 74.6333 | 87.1667
2015-08-16 22:30 | 66.8667 | 76.7667 | 74.3833 | 85.9167
2015-08-16 22:45 | 66.3667 | 76.2667 | 74.1333 | 84.6667
2015-08-16 23:00 | 65.8667 | 75.7667 | 74 | 83.8833
2015-08-16 23:15 | 65.3667 | 75.2667 | 74 | 83.6333
2015-08-16 23:30 | 64.8667 | 74.7667 | 74 | 83.3833
2015-08-16 23:45 | 64.3667 | 74.2667 | 74 | 83.1333
2015-08-17 | 63.8667 | 73.7667 | 73.8833 | 82.8833
2015-08-17 00:15 | 63.3667 | 73.2667 | 73.6333 | 82.6333
2015-08-17 00:30 | 62.8667 | 72.7667 | 73.3833 | 82.3833
2015-08-17 00:45 | 62.3667 | 72.2667 | 73.1333 | 82.1333
2015-08-17 01:00 | 62 | 72 | 73.35 | 81.5333
2015-08-17 01:15 | 62 | 72 | 74.1 | 80.5333
2015-08-17 01:30 | 62 | 72 | 74.85 | 79.5333
2015-08-17 01:45 | 62 | 72 | 75.6 | 78.5333
2015-08-17 02:00 | 61.9333 | 71.5333 | 75.8833 | 78
2015-08-17 02:15 | 61.6833 | 70.5333 | 75.6333 | 78
2015-08-17 02:30 | 61.4333 | 69.5333 | 75.3833 | 78
2015-08-17 02:45 | 61.1833 | 68.5333 | 75.1333 | 78
2015-08-17 03:00 | 61 | 67.8833 | 74.7667 | 77.7667
2015-08-17 03:15 | 61 | 67.6333 | 74.2667 | 77.2667
2015-08-17 03:30 | 61 | 67.3833 | 73.7667 | 76.7667
2015-08-17 03:45 | 61 | 67.1333 | 73.2667 | 76.2667
2015-08-17 04:00 | 60.9333 | 67 | 72.8833 | 75.7667
2015-08-17 04:15 | 60.6833 | 67 | 72.6333 | 75.2667
2015-08-17 04:30 | 60.4333 | 67 | 72.3833 | 74.7667
2015-08-17 04:45 | 60.1833 | 67 | 72.1333 | 74.2667
2015-08-17 05:00 | 60.2105 | 66.8833 | 71.8833 | 74.1167
2015-08-17 05:15 | 61 | 66.6333 | 71.6333 | 74.3667
2015-08-17 05:30 | 61 | 66.3833 | 71.3833 | 74.6167
2015-08-17 05:45 | 61 | 66.1333 | 71.1333 | 74.8667
2015-08-17 06:00 | 61.1333 | 66.2333 | 71 | 75.35
2015-08-17 06:15 | 61.6333 | 66.7333 | 71 | 76.1
2015-08-17 06:30 | 62.1333 | 67.2333 | 71 | 76.85
2015-08-17 06:45 | 62.6333 | 67.7333 | 71 | 77.6
2015-08-17 07:00 | 63.2667 | 68.5833 | 71.5833 | 78.5833
2015-08-17 07:15 | 64.2667 | 69.8333 | 72.8333 | 79.8333
2015-08-17 07:30 | 65.2667 | 71.0833 | 74.0833 | 81.0833
2015-08-17 07:45 | 66.2667 | 72.3333 | 75.3333 | 82.3333
2015-08-17 08:00 | 67.1333 | 73.4667 | 76.7 | 83.4667
2015-08-17 08:15 | 67.6333 | 74.4667 | 78.2 | 84.4667
2015-08-17 08:30 | 68.1333 | 75.4667 | 79.7 | 85.4667
2015-08-17 08:45 | 68.6333 | 76.4667 | 81.2 | 86.4667
2015-08-17 09:00 | 69 | 77.5833 | 82.4667 | 87.4667
2015-08-17 09:15 | 69 | 78.8333 | 83.4667 | 88.4667
2015-08-17 09:30 | 69 | 80.0833 | 84.4667 | 89.4667
2015-08-17 09:45 | 69 | 81.3333 | 85.4667 | 90.4667
2015-08-17 10:00 | 69.1333 | 82.1167 | 86.5833 | 91.4667
2015-08-17 10:15 | 69.6333 | 82.3667 | 87.8333 | 92.4667
2015-08-17 10:30 | 70.1333 | 82.6167 | 89.0833 | 93.4667
2015-08-17 10:45 | 70.6333 | 82.8667 | 90.3333 | 94.4667
2015-08-17 11:00 | 71.3333 | 83.35 | 91.1167 | 95.5833
2015-08-17 11:15 | 72.5833 | 84.1 | 91.3667 | 96.8333
2015-08-17 11:30 | 73.8333 | 84.85 | 91.6167 | 98.0833
2015-08-17 11:45 | 75.0833 | 85.6 | 91.8667 | 99.3333
2015-08-17 12:00 | 76 | 86.2333 | 92.35 | 100.4667
2015-08-17 12:15 | 76 | 86.7333 | 93.1 | 101.4667
2015-08-17 12:30 | 76 | 87.2333 | 93.85 | 102.4667
2015-08-17 12:45 | 76 | 87.7333 | 94.6 | 103.4667
2015-08-17 13:00 | 75.8667 | 88.35 | 95 | 104.2333
2015-08-17 13:15 | 75.3667 | 89.1 | 95 | 104.7333
2015-08-17 13:30 | 74.8667 | 89.85 | 95 | 105.2333
2015-08-17 13:45 | 74.3667 | 90.6 | 95 | 105.7333
2015-08-17 14:00 | 73.8667 | 90.7667 | 95 | 106
2015-08-17 14:15 | 73.3667 | 90.2667 | 95 | 106
2015-08-17 14:30 | 72.8667 | 89.7667 | 95 | 106
2015-08-17 14:45 | 72.3667 | 89.2667 | 95 | 106
2015-08-17 15:00 | 71.9333 | 88.7667 | 94.8833 | 106.1167
2015-08-17 15:15 | 71.6833 | 88.2667 | 94.6333 | 106.3667
2015-08-17 15:30 | 71.4333 | 87.7667 | 94.3833 | 106.6167
2015-08-17 15:45 | 71.1833 | 87.2667 | 94.1333 | 106.8667
2015-08-17 16:00 | 70.8 | 86.65 | 94 | 106.8833
2015-08-17 16:15 | 70.05 | 85.9 | 94 | 106.6333
2015-08-17 16:30 | 69.3 | 85.15 | 94 | 106.3833
2015-08-17 16:45 | 68.55 | 84.4 | 94 | 106.1333
2015-08-17 17:00 | 67.8 | 83.5333 | 93.8833 | 105.7667
2015-08-17 17:15 | 67.05 | 82.5333 | 93.6333 | 105.2667
2015-08-17 17:30 | 66.3 | 81.5333 | 93.3833 | 104.7667
2015-08-17 17:45 | 65.55 | 80.5333 | 93.1333 | 104.2667
2015-08-17 18:00 | 64.8 | 79.1833 | 92.65 | 103.5333
2015-08-17 18:15 | 64.05 | 77.4333 | 91.9 | 102.5333
2015-08-17 18:30 | 63.3 | 75.6833 | 91.15 | 101.5333
2015-08-17 18:45 | 62.55 | 73.9333 | 90.4 | 100.5333
2015-08-17 19:00 | 61.9333 | 72.65 | 89.7667 | 99.3
2015-08-17 19:15 | 61.6833 | 71.9 | 89.2667 | 97.8
2015-08-17 19:30 | 61.4333 | 71.15 | 88.7667 | 96.3
2015-08-17 19:45 | 61.1833 | 70.4 | 88.2667 | 94.8
2015-08-17 20:00 | 61 | 69.65 | 87.65 | 93.65
2015-08-17 20:15 | 61 | 68.9 | 86.9 | 92.9
2015-08-17 20:30 | 61 | 68.15 | 86.15 | 92.15
2015-08-17 20:45 | 61 | 67.4 | 85.4 | 91.4
2015-08-17 21:00 | 61 | 66.65 | 84.7667 | 90.5333
2015-08-17 21:15 | 61 | 65.9 | 84.2667 | 89.5333
2015-08-17 21:30 | 61 | 65.15 | 83.7667 | 88.5333
2015-08-17 21:45 | 61 | 64.4 | 83.2667 | 87.5333
2015-08-17 22:00 | 60.9333 | 64 | 82.8833 | 86.7667
2015-08-17 22:15 | 60.6833 | 64 | 82.6333 | 86.2667
2015-08-17 22:30 | 60.4333 | 64 | 82.3833 | 85.7667
2015-08-17 22:45 | 60.1833 | 64 | 82.1333 | 85.2667
2015-08-17 23:00 | 60 | 64 | 81.8833 | 84.5333
2015-08-17 23:15 | 60 | 64 | 81.6333 | 83.5333
2015-08-17 23:30 | 60 | 64 | 81.3833 | 82.5333
2015-08-17 23:45 | 60 | 64 | 81.1333 | 81.5333
2015-08-18 | 59.9333 | 63.65 | 81 | 80.7667
2015-08-18 00:15 | 59.6833 | 62.9 | 81 | 80.2667
2015-08-18 00:30 | 59.4333 | 62.15 | 81 | 79.7667
2015-08-18 00:45 | 59.1833 | 61.4 | 81 | 79.2667
2015-08-18 01:00 | 59 | 61 | 80.8833 | 78.8833
2015-08-18 01:15 | 59 | 61 | 80.6333 | 78.6333
2015-08-18 01:30 | 59 | 61 | 80.3833 | 78.3833
2015-08-18 01:45 | 59 | 61 | 80.1333 | 78.1333
2015-08-18 02:00 | 59 | 61 | 79.8833 | 77.7667
2015-08-18 02:15 | 59 | 61 | 79.6333 | 77.2667
2015-08-18 02:30 | 59 | 61 | 79.3833 | 76.7667
2015-08-18 02:45 | 59 | 61 | 79.1333 | 76.2667
2015-08-18 03:00 | 59.0667 | 60.8833 | 78.8833 | 75.8833
2015-08-18 03:15 | 59.3167 | 60.6333 | 78.6333 | 75.6333
2015-08-18 03:30 | 59.5667 | 60.3833 | 78.3833 | 75.3833
2015-08-18 03:45 | 59.8167 | 60.1333 | 78.1333 | 75.1333
2015-08-18 04:00 | 59.9333 | 59.825 | 78 | 75
2015-08-18 04:15 | 59.6833 | 59.45 | 78 | 75
2015-08-18 04:30 | 59.4333 | 59.075 | 78 | 75
2015-08-18 04:45 | 59.1833 | 59 | 78 | 75
2015-08-18 05:00 | 59.0667 | 59 | 77.8833 | 74.8833
2015-08-18 05:15 | 59.3167 | 59 | 77.6333 | 74.6333
2015-08-18 05:30 | 59.5667 | 59 | 77.3833 | 74.3833
2015-08-18 05:45 | 59.8167 | 59 | 77.1333 | 74.1333
2015-08-18 06:00 | 60.0667 | 59.1167 | 76.8833 | 74.1167
2015-08-18 06:15 | 60.3167 | 59.3667 | 76.6333 | 74.3667
2015-08-18 06:30 | 60.5667 | 59.6167 | 76.3833 | 74.6167
2015-08-18 06:45 | 60.8167 | 59.8667 | 76.1333 | 74.8667
2015-08-18 07:00 | 61.1333 | 60.35 | 76.4667 | 75.4667
2015-08-18 07:15 | 61.6333 | 61.1 | 77.4667 | 76.4667
2015-08-18 07:30 | 62.1333 | 61.85 | 78.4667 | 77.4667
2015-08-18 07:45 | 62.6333 | 62.6 | 79.4667 | 78.4667
2015-08-18 08:00 | 63.1905 | 63.4667 | 80.7 | 79.4667
2015-08-18 08:15 | 63.9048 | 64.4667 | 82.2 | 80.4667
2015-08-18 08:30 | 64.6667 | 65.4667 | 83.7 | 81.4667
2015-08-18 08:45 | 65.4359 | 66.4667 | 85.2 | 82.4667
2015-08-18 09:00 | 66.1333 | 67.4667 | 86.35 | 83.4667
2015-08-18 09:15 | 66.6333 | 68.4667 | 87.1 | 84.4667
2015-08-18 09:30 | 67.1333 | 69.4667 | 87.85 | 85.4667
2015-08-18 09:45 | 67.6333 | 70.4667 | 88.6 | 86.4667
2015-08-18 10:00 | 68.0667 | 71.5833 | 89.549 | 87.35
2015-08-18 10:15 | 68.3167 | 72.8333 | 90.7255 | 88.1
2015-08-18 10:30 | 68.5667 | 74.0833 | 91.902 | 88.85
2015-08-18 10:45 | 68.8167 | 75.3333 | 93 | 89.6
2015-08-18 11:00 | 69.2 | 76.2333 | 90.3077 | 90.5833
2015-08-18 11:15 | 69.95 | 76.7333 | 84.6842 | 91.8333
2015-08-18 11:30 | 70.7 | 77.2333 | 81.7143 | 93.0833
2015-08-18 11:45 | 71.45 | 77.7333 | 83.8571 | 94.3333
2015-08-18 12:00 | 72.1333 | 78.1167 | 86.1667 | 95.35
2015-08-18 12:15 | 72.6333 | 78.3667 | 88.6667 | 96.1
2015-08-18 12:30 | 73.1333 | 78.6167 | 91.1667 | 96.85
2015-08-18 12:45 | 73.6333 | 78.8667 | 93.6667 | 97.6
2015-08-18 13:00 | 74.0667 | 79.1167 | 95.35 | 98.35
2015-08-18 13:15 | 74.3167 | 79.3667 | 96.1 | 99.1
2015-08-18 13:30 | 74.5667 | 79.6167 | 96.85 | 99.85
2015-08-18 13:45 | 74.8167 | 79.8667 | 97.6 | 100.6
2015-08-18 14:00 | 75 | 79.8833 | 98.1167 | 101.1167
2015-08-18 14:15 | 75 | 79.6333 | 98.3667 | 101.3667
2015-08-18 14:30 | 75 | 79.3833 | 98.6167 | 101.6167
2015-08-18 14:45 | 75 | 79.1333 | 98.8667 | 101.8667
2015-08-18 15:00 | 74.8667 | 78.8833 | 99.1167 | 102.1167
2015-08-18 15:15 | 74.3667 | 78.6333 | 99.3667 | 102.3667
2015-08-18 15:30 | 73.8667 | 78.3833 | 99.6167 | 102.6167
2015-08-18 15:45 | 73.3667 | 78.1333 | 99.8667 | 102.8667
2015-08-18 16:00 | 72.8 | 77.8833 | 100 | 102.7667
2015-08-18 16:15 | 72.05 | 77.6333 | 100 | 102.2667
2015-08-18 16:30 | 71.3 | 77.3833 | 100 | 101.7667
2015-08-18 16:45 | 70.55 | 77.1333 | 100 | 101.2667
2015-08-18 17:00 | 69.8667 | 76.65 | 99.8833 | 100.65
2015-08-18 17:15 | 69.3667 | 75.9 | 99.6333 | 99.9
2015-08-18 17:30 | 68.8667 | 75.15 | 99.3833 | 99.15
2015-08-18 17:45 | 68.3667 | 74.4 | 99.1333 | 98.4
2015-08-18 18:00 | 67.8 | 73.5333 | 98.65 | 97.5333
2015-08-18 18:15 | 67.05 | 72.5333 | 97.9 | 96.5333
2015-08-18 18:30 | 66.3 | 71.5333 | 97.15 | 95.5333
2015-08-18 18:45 | 65.55 | 70.5333 | 96.4 | 94.5333
2015-08-18 19:00 | 64.9333 | 69.65 | 95.5333 | 93.5333
2015-08-18 19:15 | 64.6833 | 68.9 | 94.5333 | 92.5333
2015-08-18 19:30 | 64.4333 | 68.15 | 93.5333 | 91.5333
2015-08-18 19:45 | 64.1833 | 67.4 | 92.5333 | 90.5333
2015-08-18 20:00 | 63.9333 | 66.7667 | 91.7667 | 89.5333
2015-08-18 20:15 | 63.6833 | 66.2667 | 91.2667 | 88.5333
2015-08-18 20:30 | 63.4333 | 65.7667 | 90.7667 | 87.5333
2015-08-18 20:45 | 63.1833 | 65.2667 | 90.2667 | 86.5333
2015-08-18 21:00 | 63 | 64.7667 | 89.65 | 85.7667
2015-08-18 21:15 | 63 | 64.2667 | 88.9 | 85.2667
2015-08-18 21:30 | 63 | 63.7667 | 88.15 | 84.7667
2015-08-18 21:45 | 63 | 63.2667 | 87.4 | 84.2667
2015-08-18 22:00 | 62.9333 | 63 | 86.8833 | 83.7667
2015-08-18 22:15 | 62.6833 | 63 | 86.6333 | 83.2667
2015-08-18 22:30 | 62.4333 | 63 | 86.3833 | 82.7667
2015-08-18 22:45 | 62.1833 | 63 | 86.1333 | 82.2667
2015-08-18 23:00 | 62 | 63 | 85.65 | 81.5333
2015-08-18 23:15 | 62 | 63 | 84.9 | 80.5333
2015-08-18 23:30 | 62 | 63 | 84.15 | 79.5333
2015-08-18 23:45 | 62 | 63 | 83.4 | 78.5333
2015-08-19 | 62.1111 | 63 | 82.8833 | 77.65
2015-08-19 00:15 | 62.5278 | 63 | 82.6333 | 76.9
2015-08-19 00:30 | 62.9444 | 63 | 82.3833 | 76.15
2015-08-19 00:45 | 62.4583 | 63 | 82.1333 | 75.4
2015-08-19 01:00 | 62.25 | 63 | 81.65 | 74.65
2015-08-19 01:15 | 62.8636 | 63 | 80.9 | 73.9
2015-08-19 01:30 | 62.1818 | 63 | 80.15 | 73.15
2015-08-19 01:45 | 61.5 | 63 | 79.4 | 72.4
2015-08-19 02:00 | 61 | 63 | 79 | 71.7667
2015-08-19 02:15 | 61 | 63 | 79 | 71.2667
2015-08-19 02:30 | 61 | 63 | 79 | 70.7667
2015-08-19 02:45 | 61 | 63 | 79 | 70.2667
2015-08-19 03:00 | 60.9333 | 63 | 78.65 | 69.7667
2015-08-19 03:15 | 60.6833 | 63 | 77.9 | 69.2667
2015-08-19 03:30 | 60.4333 | 63 | 77.15 | 68.7667
2015-08-19 03:45 | 60.1833 | 63 | 76.4 | 68.2667
2015-08-19 04:00 | 60 | 62.8833 | 75.8833 | 67.8833
2015-08-19 04:15 | 60 | 62.6333 | 75.6333 | 67.6333
2015-08-19 04:30 | 60 | 62.3833 | 75.3833 | 67.3833
2015-08-19 04:45 | 60 | 62.1333 | 75.1333 | 67.1333
2015-08-19 05:00 | 60.0667 | 61.8833 | 74.7667 | 67
2015-08-19 05:15 | 60.3167 | 61.6333 | 74.2667 | 67
2015-08-19 05:30 | 60.5667 | 61.3833 | 73.7667 | 67
2015-08-19 05:45 | 60.8167 | 61.1333 | 73.2667 | 67
2015-08-19 06:00 | 61.0667 | 61 | 73 | 67.35
2015-08-19 06:15 | 61.3167 | 61 | 73 | 68.1
2015-08-19 06:30 | 61.5667 | 61 | 73 | 68.85
2015-08-19 06:45 | 61.8167 | 61 | 73 | 69.6
2015-08-19 07:00 | 62.1026 | 61.1167 | 73.8167 | 70.5833
2015-08-19 07:15 | 62.4872 | 61.3667 | 75.5667 | 71.8333
2015-08-19 07:30 | 62.8718 | 61.6167 | 77.3167 | 73.0833
2015-08-19 07:45 | 63.4762 | 61.8667 | 79.0667 | 74.3333
2015-08-19 08:00 | 64 | 62.5385 | 80.8167 | 75.5833
2015-08-19 08:15 | 64 | 63.25 | 82.5667 | 76.8333
2015-08-19 08:30 | 64 | 63.6667 | 84.3167 | 78.0833
2015-08-19 08:45 | 64 | 64.2727 | 86.0667 | 79.3333
2015-08-19 09:00 | 64.2759 | 65.4667 | 87.1167 | 80.4667
2015-08-19 09:15 | 65.3103 | 66.4667 | 87.3667 | 81.4667
2015-08-19 09:30 | 66.3448 | 67.4667 | 87.6167 | 82.4667
2015-08-19 09:45 | 67.3793 | 68.4667 | 87.8667 | 83.4667
2015-08-19 10:00 | 68.2 | 69.4667 | 88 | 84.7
2015-08-19 10:15 | 68.95 | 70.4667 | 88 | 86.2
2015-08-19 10:30 | 69.7 | 71.4667 | 88 | 87.7
2015-08-19 10:45 | 70.45 | 72.4667 | 88 | 89.2
2015-08-19 11:00 | 71.1333 | 73.2333 | 88.2333 | 90.2333
2015-08-19 11:15 | 71.6333 | 73.7333 | 88.7333 | 90.7333
2015-08-19 11:30 | 72.1333 | 74.2333 | 89.2333 | 91.2333
2015-08-19 11:45 | 72.6333 | 74.7333 | 89.7333 | 91.7333
2015-08-19 12:00 | 73 | 75.1167 | 90.1167 | 92.35
2015-08-19 12:15 | 73 | 75.3667 | 90.3667 | 93.1
2015-08-19 12:30 | 73 | 75.6167 | 90.6167 | 93.85
2015-08-19 12:45 | 73 | 75.8667 | 90.8667 | 94.6
2015-08-19 13:00 | 73 | 76 | 91.35 | 95.35
2015-08-19 13:15 | 73 | 76 | 92.1 | 96.1
2015-08-19 13:30 | 73 | 76 | 92.85 | 96.85
2015-08-19 13:45 | 73 | 76 | 93.6 | 97.6
2015-08-19 14:00 | 73 | 76 | 94.1167 | 98.1167
2015-08-19 14:15 | 73 | 76 | 94.3667 | 98.3667
2015-08-19 14:30 | 73 | 76 | 94.6167 | 98.6167
2015-08-19 14:45 | 73 | 76 | 94.8667 | 98.8667
2015-08-19 15:00 | 72.9333 | 76 | 95.1167 | 99
2015-08-19 15:15 | 72.6833 | 76 | 95.3667 | 99
2015-08-19 15:30 | 72.4333 | 76 | 95.6167 | 99
2015-08-19 15:45 | 72.1833 | 76 | 95.8667 | 99
2015-08-19 16:00 | 71.8 | 75.7667 | 95.4167 | 98.8833
2015-08-19 16:15 | 71.05 | 75.2667 | 94.1667 | 98.6333
2015-08-19 16:30 | 70.3 | 74.7667 | 92.9167 | 98.3833
2015-08-19 16:45 | 69.55 | 74.2667 | 91.6667 | 98.1333
2015-08-19 17:00 | 68.8667 | 73.65 | 90.4167 | 97.7667
2015-08-19 17:15 | 68.3667 | 72.9 | 89.1667 | 97.2667
2015-08-19 17:30 | 67.8667 | 72.15 | 87.9167 | 96.7667
2015-08-19 17:45 | 67.3667 | 71.4 | 86.6667 | 96.2667
2015-08-19 18:00 | 66.8667 | 70.65 | 85.5333 | 95.4167
2015-08-19 18:15 | 66.3667 | 69.9 | 84.5333 | 94.1667
2015-08-19 18:30 | 65.8667 | 69.15 | 83.5333 | 92.9167
2015-08-19 18:45 | 65.3667 | 68.4 | 82.5333 | 91.6667
2015-08-19 19:00 | 65 | 67.7667 | 81.65 | 90.5333
2015-08-19 19:15 | 65 | 67.2667 | 80.9 | 89.5333
2015-08-19 19:30 | 65 | 66.7667 | 80.15 | 88.5333
2015-08-19 19:45 | 65 | 66.2667 | 79.4 | 87.5333
2015-08-19 20:00 | 65 | 65.8833 | 78.65 | 86.65
2015-08-19 20:15 | 65 | 65.6333 | 77.9 | 85.9
2015-08-19 20:30 | 65 | 65.3833 | 77.15 | 85.15
2015-08-19 20:45 | 65 | 65.1333 | 76.4 | 84.4
2015-08-19 21:00 | 64.931 | 64.8627 | 75.4167 | 83.65
2015-08-19 21:15 | 64.6724 | 64.5686 | 74.1667 | 82.9
2015-08-19 21:30 | 64.4138 | 64.2745 | 72.9167 | 82.15
2015-08-19 21:45 | 64.1552 | 64 | 71.6667 | 81.4
2015-08-19 22:00 | 65 | 64.1167 | 70.7667 | 80.65
2015-08-19 22:15 | 65 | 64.3667 | 70.2667 | 79.9
2015-08-19 22:30 | 65 | 64.6167 | 69.7667 | 79.15
2015-08-19 22:45 | 65 | 64.8667 | 69.2667 | 78.4
2015-08-19 23:00 | 64.9333 | 65 | 68.7667 | 77.5333
2015-08-19 23:15 | 64.6833 | 65 | 68.2667 | 76.5333
2015-08-19 23:30 | 64.4333 | 65 | 67.7667 | 75.5333
2015-08-19 23:45 | 64.1833 | 65 | 67.2667 | 74.5333
2015-08-20 | 64 | 65 | 66.8833 | 73.65
2015-08-20 00:15 | 64 | 65 | 66.6333 | 72.9
2015-08-20 00:30 | 64 | 65 | 66.3833 | 72.15
2015-08-20 00:45 | 64 | 65 | 66.1333 | 71.4
2015-08-20 01:00 | 64 | 65 | 65.8833 | 70.7667
2015-08-20 01:15 | 64 | 65 | 65.6333 | 70.2667
2015-08-20 01:30 | 64 | 65 | 65.3833 | 69.7667
2015-08-20 01:45 | 64 | 65 | 65.1333 | 69.2667
2015-08-20 02:00 | 63.9333 | 65 | 64.86 | 68.7667
2015-08-20 02:15 | 63.6833 | 65 | 64.56 | 68.2667
2015-08-20 02:30 | 63.4333 | 65 | 64.26 | 67.7667
2015-08-20 02:45 | 63.1833 | 65 | 64 | 67.2667
2015-08-20 03:00 | 63 | 65 | 64.1167 | 66.8833
2015-08-20 03:15 | 63 | 65 | 64.3667 | 66.6333
2015-08-20 03:30 | 63 | 65 | 64.6167 | 66.3833
2015-08-20 03:45 | 63 | 65 | 64.8667 | 66.1333
2015-08-20 04:00 | 62.9333 | 65 | 65 | 65.7667
2015-08-20 04:15 | 62.6833 | 65 | 65 | 65.2667
2015-08-20 04:30 | 62.4333 | 65 | 65 | 64.7667
2015-08-20 04:45 | 62.1833 | 65 | 65 | 64.2667
2015-08-20 05:00 | 62 | 65 | 65 | 64.1167
2015-08-20 05:15 | 62 | 65 | 65 | 64.3667
2015-08-20 05:30 | 62 | 65 | 65 | 64.6167
2015-08-20 05:45 | 62 | 65 | 65 | 64.8667
2015-08-20 06:00 | 62 | 65 | 64.8833 | 65.2333
2015-08-20 06:15 | 62 | 65 | 64.6333 | 65.7333
2015-08-20 06:30 | 62 | 65 | 64.3833 | 66.2333
2015-08-20 06:45 | 62 | 65 | 64.1333 | 66.7333
2015-08-20 07:00 | 62.0667 | 65.1167 | 64.1167 | 67.4667
2015-08-20 07:15 | 62.3167 | 65.3667 | 64.3667 | 68.4667
2015-08-20 07:30 | 62.5667 | 65.6167 | 64.6167 | 69.4667
2015-08-20 07:45 | 62.8167 | 65.8667 | 64.8667 | 70.4667
2015-08-20 08:00 | 63 | 66.1167 | 65.2333 | 71.4667
2015-08-20 08:15 | 63 | 66.3667 | 65.7333 | 72.4667
2015-08-20 08:30 | 63 | 66.6167 | 66.2333 | 73.4667
2015-08-20 08:45 | 63 | 66.8667 | 66.7333 | 74.4667
2015-08-20 09:00 | 63 | 67.4286 | 67.5833 | 75.4667
2015-08-20 09:15 | 63 | 68.3469 | 68.8333 | 76.4667
2015-08-20 09:30 | 63 | 69.2653 | 70.0833 | 77.4667
2015-08-20 09:45 | 63 | 70 | 71.3333 | 78.4667
2015-08-20 10:00 | 63.2667 | 70.1167 | 72.4667 | 79.4667
2015-08-20 10:15 | 64.2667 | 70.3667 | 73.4667 | 80.4667
2015-08-20 10:30 | 65.2667 | 70.6167 | 74.4667 | 81.4667
2015-08-20 10:45 | 66.2667 | 70.8667 | 75.4667 | 82.4667
2015-08-20 11:00 | 67.0667 | 71.35 | 76.5833 | 83.4667
2015-08-20 11:15 | 67.3167 | 72.1 | 77.8333 | 84.4667
2015-08-20 11:30 | 67.5667 | 72.85 | 79.0833 | 85.4667
2015-08-20 11:45 | 67.8167 | 73.6 | 80.3333 | 86.4667
2015-08-20 12:00 | 68 | 74 | 81.4667 | 87.35
2015-08-20 12:15 | 68 | 74 | 82.4667 | 88.1
2015-08-20 12:30 | 68 | 74 | 83.4667 | 88.85
2015-08-20 12:45 | 68 | 74 | 84.4667 | 89.6
2015-08-20 13:00 | 68.0667 | 73.8833 | 85.35 | 90.2333
2015-08-20 13:15 | 68.3167 | 73.6333 | 86.1 | 90.7333
2015-08-20 13:30 | 68.5667 | 73.3833 | 86.85 | 91.2333
2015-08-20 13:45 | 68.8167 | 73.1333 | 87.6 | 91.7333
2015-08-20 14:00 | 68.9333 | 73.1167 | 88.5833 | 92.2333
2015-08-20 14:15 | 68.6833 | 73.3667 | 89.8333 | 92.7333
2015-08-20 14:30 | 68.4333 | 73.6167 | 91.0833 | 93.2333
2015-08-20 14:45 | 68.1833 | 73.8667 | 92.3333 | 93.7333
2015-08-20 15:00 | 68 | 73.8833 | 93.2333 | 94.1167
2015-08-20 15:15 | 68 | 73.6333 | 93.7333 | 94.3667
2015-08-20 15:30 | 68 | 73.3833 | 94.2333 | 94.6167
2015-08-20 15:45 | 68 | 73.1333 | 94.7333 | 94.8667
2015-08-20 16:00 | 67.9333 | 72.7667 | 95 | 94.8833
2015-08-20 16:15 | 67.6833 | 72.2667 | 95 | 94.6333
2015-08-20 16:30 | 67.4333 | 71.7667 | 95 | 94.3833
2015-08-20 16:45 | 67.1833 | 71.2667 | 95 | 94.1333
2015-08-20 17:00 | 66.8667 | 70.7667 | 95 | 93.7667
2015-08-20 17:15 | 66.3667 | 70.2667 | 94.8919 | 93.2667
2015-08-20 17:30 | 65.8667 | 69.7667 | 94.0811 | 92.7667
2015-08-20 17:45 | 65.3667 | 69.2667 | 93.2703 | 92.2667
2015-08-20 18:00 | 64.8667 | 68.65 | 92.65 | 91.5333
2015-08-20 18:15 | 64.3667 | 67.9 | 91.9 | 90.5333
2015-08-20 18:30 | 63.8667 | 67.15 | 91.15 | 89.5333
2015-08-20 18:45 | 63.3667 | 66.4 | 90.4 | 88.5333
2015-08-20 19:00 | 63 | 65.7667 | 89.65 | 87.65
2015-08-20 19:15 | 63 | 65.2667 | 88.9 | 86.9
2015-08-20 19:30 | 63 | 64.7667 | 88.15 | 86.15
2015-08-20 19:45 | 63 | 64.2667 | 87.4 | 85.4
2015-08-20 20:00 | 63 | 64 | 86.4167 | 84.7667
2015-08-20 20:15 | 63 | 64 | 85.1667 | 84.2667
2015-08-20 20:30 | 63 | 64 | 83.9167 | 83.7667
2015-08-20 20:45 | 63 | 64 | 82.6667 | 83.2667
2015-08-20 21:00 | 63 | 63.8833 | 81.5333 | 82.5333
2015-08-20 21:15 | 63 | 63.6333 | 80.5333 | 81.5333
2015-08-20 21:30 | 63 | 63.3833 | 79.5333 | 80.5333
2015-08-20 21:45 | 62.44 | 63.1333 | 78.5333 | 79.5333
2015-08-20 22:00 | 61.9333 | 62.8833 | 77.8833 | 78.65
2015-08-20 22:15 | 61.6833 | 62.6333 | 77.6333 | 77.9
2015-08-20 22:30 | 61.4333 | 62.3833 | 77.3833 | 77.15
2015-08-20 22:45 | 61.1833 | 62.1333 | 77.1333 | 76.4
2015-08-20 23:00 | 61.1905 | 62.2258 | 77 | 75.65
2015-08-20 23:15 | 61.9048 | 62.7097 | 77 | 74.9
2015-08-20 23:30 | 62.619 | 63 | 77 | 74.15
2015-08-20 23:45 | 62.2222 | 63 | 77 | 73.4
2015-08-21 | 61 | 62.7586 | 76.8833 | 72.7667
2015-08-21 00:15 | 61 | 62.2414 | 76.6333 | 72.2667
2015-08-21 00:30 | 61 | 61.7241 | 76.3833 | 71.7667
2015-08-21 00:45 | 61 | 61.2069 | 76.1333 | 71.2667
2015-08-21 01:00 | 60.8667 | 61 | 75.8833 | 70.7667
2015-08-21 01:15 | 60.3667 | 61 | 75.6333 | 70.2667
2015-08-21 01:30 | 59.8667 | 61 | 75.3833 | 69.7667
2015-08-21 01:45 | 59.3667 | 61 | 75.1333 | 69.2667
2015-08-21 02:00 | 59 | 60.8833 | 75.35 | 68.7667
2015-08-21 02:15 | 59 | 60.6333 | 76.1 | 68.2667
2015-08-21 02:30 | 59 | 60.3833 | 76.85 | 67.7667
2015-08-21 02:45 | 59 | 60.1333 | 77.6 | 67.2667
2015-08-21 03:00 | 59 | 60 | 77 | 66.8833
2015-08-21 03:15 | 59 | 60 | 74.9487 | 66.6333
2015-08-21 03:30 | 59 | 60 | 74.1795 | 66.3833
2015-08-21 03:45 | 59 | 60 | 73.4103 | 66.1333
2015-08-21 04:00 | 59 | 60.1842 | 72.65 | 65.8833
2015-08-21 04:15 | 59 | 60.5789 | 71.9 | 65.6333
2015-08-21 04:30 | 59 | 60.9737 | 71.15 | 65.3833
2015-08-21 04:45 | 59 | 61 | 70.4 | 65.1333
2015-08-21 05:00 | 59.0667 | 61 | 70 | 65
2015-08-21 05:15 | 59.3167 | 61 | 70 | 65
2015-08-21 05:30 | 59.5667 | 61 | 70 | 65
2015-08-21 05:45 | 59.8167 | 61 | 70 | 65
2015-08-21 06:00 | 60.0667 | 61.1167 | 70.1167 | 65.35
2015-08-21 06:15 | 60.3167 | 61.3667 | 70.3667 | 66.1
2015-08-21 06:30 | 60.5667 | 61.6167 | 70.6167 | 66.85
2015-08-21 06:45 | 60.8167 | 61.8667 | 70.8667 | 67.6
2015-08-21 07:00 | 61.2581 | 62.1842 | 71.5833 | 68.35
2015-08-21 07:15 | 62.2258 | 62.5789 | 72.8333 | 69.1
2015-08-21 07:30 | 63.1034 | 62.9737 | 74.0833 | 69.85
2015-08-21 07:45 | 63.6207 | 63.6364 | 75.3333 | 70.6
2015-08-21 08:00 | 64 | 64.4667 | 76.35 | 71.7
2015-08-21 08:15 | 64 | 65.4667 | 77.1 | 73.2
2015-08-21 08:30 | 64 | 66.4667 | 77.85 | 74.7
2015-08-21 08:45 | 64 | 67.4667 | 78.6 | 76.2
2015-08-21 09:00 | 64.2667 | 68.35 | 79.8167 | 77.4667
2015-08-21 09:15 | 65.2667 | 69.1 | 81.5667 | 78.4667
2015-08-21 09:30 | 66.2667 | 69.85 | 83.3167 | 79.4667
2015-08-21 09:45 | 67.2667 | 70.6 | 85.0667 | 80.4667
2015-08-21 10:00 | 68.2 | 71.35 | 86.4667 | 81.4667
2015-08-21 10:15 | 68.95 | 72.1 | 87.4667 | 82.4667
2015-08-21 10:30 | 69.7 | 72.85 | 88.4667 | 83.4667
2015-08-21 10:45 | 70.45 | 73.6 | 89.4667 | 84.4667
2015-08-21 11:00 | 70.8667 | 74.35 | 90.35 | 85.35
2015-08-21 11:15 | 70.3667 | 75.1 | 91.1 | 86.1
2015-08-21 11:30 | 69.8667 | 75.85 | 91.85 | 86.85
2015-08-21 11:45 | 69.3667 | 76.6 | 92.6 | 87.6
2015-08-21 12:00 | 69 | 77 | 93.35 | 88.35
2015-08-21 12:15 | 69 | 77 | 94.1 | 89.1
2015-08-21 12:30 | 69 | 77 | 94.85 | 89.85
2015-08-21 12:45 | 69 | 77 | 95.6 | 90.6
2015-08-21 13:00 | 69 | 76.8833 | 96.1167 | 91.2333
2015-08-21 13:15 | 69 | 76.6333 | 96.3667 | 91.7333
2015-08-21 13:30 | 69 | 76.3833 | 96.6167 | 92.2333
2015-08-21 13:45 | 69 | 76.1333 | 96.8667 | 92.7333
2015-08-21 14:00 | 68.9333 | 75.7667 | 97 | 93.2333
2015-08-21 14:15 | 68.6833 | 75.2667 | 97 | 93.7333
2015-08-21 14:30 | 68.4333 | 74.7667 | 97 | 94.2333
2015-08-21 14:45 | 68.1833 | 74.2667 | 97 | 94.7333
2015-08-21 15:00 | 68 | 74 | 96.3 | 95
2015-08-21 15:15 | 68 | 74 | 94.8 | 95
2015-08-21 15:30 | 68 | 74 | 93.3 | 95
2015-08-21 15:45 | 68 | 74 | 90.6 | 95
2015-08-21 16:00 | 67.8667 | 73.7667 | 88.3 | 94.7667
2015-08-21 16:15 | 67.3667 | 73.2667 | 87.04 | 94.2667
2015-08-21 16:30 | 66.8667 | 72.7667 | 85.84 | 93.7667
2015-08-21 16:45 | 66.3667 | 72.2667 | 84.64 | 93.2667
2015-08-21 17:00 | 65.9333 | 71.5333 | 84.2333 | 92.7667
2015-08-21 17:15 | 65.6833 | 70.5333 | 84.7333 | 92.2667
2015-08-21 17:30 | 65.4333 | 69.5333 | 85.2333 | 91.7667
2015-08-21 17:45 | 65.1833 | 68.5333 | 85.7333 | 91.2667
2015-08-21 18:00 | 64.8 | 67.7667 | 86.1167 | 90.5333
2015-08-21 18:15 | 64.05 | 67.2667 | 86.3667 | 89.5333
2015-08-21 18:30 | 63.3 | 66.7667 | 86.6167 | 88.5333
2015-08-21 18:45 | 62.55 | 66.2667 | 86.8667 | 87.5333
2015-08-21 19:00 | 62 | 65.7667 | 86.65 | 86.65
2015-08-21 19:15 | 62 | 65.2667 | 85.9 | 85.9
2015-08-21 19:30 | 62 | 64.7667 | 85.15 | 85.15
2015-08-21 19:45 | 62 | 64.2667 | 84.4 | 84.4
2015-08-21 20:00 | 62 | 63.8833 | 83.5333 | 83.8833
2015-08-21 20:15 | 62 | 63.6333 | 82.5333 | 83.6333
2015-08-21 20:30 | 62 | 63.3833 | 81.5333 | 83.3833
2015-08-21 20:45 | 62 | 63.1333 | 80.5333 | 83.1333
2015-08-21 21:00 | 62 | 62.8833 | 79.8833 | 82.4167
2015-08-21 21:15 | 62 | 62.6333 | 79.6333 | 81.1667
2015-08-21 21:30 | 62 | 62.3833 | 79.3833 | 79.9167
2015-08-21 21:45 | 62 | 62.1333 | 79.1333 | 78.6667
2015-08-21 22:00 | 61.9333 | 62 | 79.2333 | 77.65
2015-08-21 22:15 | 61.6833 | 62 | 79.7333 | 76.9
2015-08-21 22:30 | 61.4333 | 62 | 80.2333 | 76.15
2015-08-21 22:45 | 61.1833 | 62 | 80.7333 | 75.4
2015-08-21 23:00 | 61 | 61.8833 | 80.8833 | 74.65
2015-08-21 23:15 | 61 | 61.6333 | 80.6333 | 73.9
2015-08-21 23:30 | 61 | 61.3833 | 80.3833 | 73.15
2015-08-21 23:45 | 61 | 61.1333 | 80.1333 | 72.4
2015-08-22 | 60.9333 | 60.8833 | 79.8833 | 71.7667
2015-08-22 00:15 | 60.6833 | 60.6333 | 79.6333 | 71.2667
2015-08-22 00:30 | 60.4333 | 60.3833 | 79.3833 | 70.7667
2015-08-22 00:45 | 60.1833 | 60.1333 | 79.1333 | 70.2667
2015-08-22 01:00 | 60.0714 | 60 | 78.8833 | 69.7667
2015-08-22 01:15 | 60.3393 | 60 | 78.6333 | 69.2667
2015-08-22 01:30 | 60.6071 | 60 | 78.3833 | 68.7667
2015-08-22 01:45 | 60.875 | 60 | 78.1333 | 68.2667
2015-08-22 02:00 | 60.0952 | 59.8108 | 78.1167 | 67.8833
2015-08-22 02:15 | 60.4524 | 59.4054 | 78.3667 | 67.6333
2015-08-22 02:30 | 60.8095 | 59 | 78.6167 | 67.3833
2015-08-22 02:45 | 60.6111 | 59 | 78.8667 | 67.1333
2015-08-22 03:00 | 59.9333 | 60.5556 | 78.8833 | 66.8833
2015-08-22 03:15 | 59.6833 | 60.2973 | 78.6333 | 66.6333
2015-08-22 03:30 | 59.4333 | 59.4865 | 78.3833 | 66.3833
2015-08-22 03:45 | 59.1833 | 61 | 78.1333 | 66.1333
2015-08-22 04:00 | 59.3077 | 60 | 77.65 | 65.8833
2015-08-22 04:15 | 60.4615 | 60 | 76.9 | 65.6333
2015-08-22 04:30 | 61 | 60 | 76.15 | 65.3833
2015-08-22 04:45 | 61 | 60 | 75.4 | 65.1333
2015-08-22 05:00 | 61 | 60 | 74.65 | 64.8833
2015-08-22 05:15 | 61 | 60 | 73.9 | 64.6333
2015-08-22 05:30 | 61 | 60 | 73.15 | 64.3833
2015-08-22 05:45 | 61 | 60 | 72.4 | 64.1333
2015-08-22 06:00 | 61.0667 | 60.1167 | 72.1167 | 64.35
2015-08-22 06:15 | 61.3167 | 60.3667 | 72.3667 | 65.1
2015-08-22 06:30 | 61.5667 | 60.6167 | 72.6167 | 65.85
2015-08-22 06:45 | 61.8167 | 60.8667 | 72.8667 | 66.6
2015-08-22 07:00 | 62.0667 | 61.1167 | 73.4667 | 67.4667
2015-08-22 07:15 | 62.3167 | 61.3667 | 74.4667 | 68.4667
2015-08-22 07:30 | 62.5667 | 61.6167 | 75.4667 | 69.4667
2015-08-22 07:45 | 62.8167 | 61.8667 | 76.4667 | 70.4667
2015-08-22 08:00 | 63.1333 | 62.1667 | 77.7 | 71.5833
2015-08-22 08:15 | 63.6333 | 62.5238 | 79.2 | 72.8333
2015-08-22 08:30 | 64.1333 | 62.881 | 80.7 | 74.0833
2015-08-22 08:45 | 64.6333 | 63.5556 | 82.2 | 75.3333
2015-08-22 09:00 | 65.2 | 64.4667 | 83.4667 | 76.35
2015-08-22 09:15 | 65.95 | 65.4667 | 84.4667 | 77.1
2015-08-22 09:30 | 66.7 | 66.4667 | 85.4667 | 77.85
2015-08-22 09:45 | 67.45 | 67.4667 | 86.4667 | 78.6
2015-08-22 10:00 | 68.0667 | 68.4667 | 87.4667 | 79.5833
2015-08-22 10:15 | 68.3167 | 69.4667 | 88.4667 | 80.8333
2015-08-22 10:30 | 68.5667 | 70.4667 | 89.4667 | 82.0833
2015-08-22 10:45 | 68.8167 | 71.4667 | 90.4667 | 83.3333
2015-08-22 11:00 | 69.0667 | 72.4667 | 91.2333 | 84.4667
2015-08-22 11:15 | 69.3167 | 73.4667 | 91.7333 | 85.4667
2015-08-22 11:30 | 69.5667 | 74.4667 | 92.2333 | 86.4667
2015-08-22 11:45 | 69.8167 | 75.4667 | 92.7333 | 87.4667
2015-08-22 12:00 | 70.1333 | 76.35 | 93.1167 | 88.4667
2015-08-22 12:15 | 70.6333 | 77.1 | 93.3667 | 89.4667
2015-08-22 12:30 | 71.1333 | 77.85 | 93.6167 | 90.4667
2015-08-22 12:45 | 71.6333 | 78.6 | 93.8667 | 91.4667
2015-08-22 13:00 | 72 | 79.1167 | 94.2333 | 92.35
2015-08-22 13:15 | 72 | 79.3667 | 94.7333 | 93.1
2015-08-22 13:30 | 72 | 79.6167 | 95.2333 | 93.85
2015-08-22 13:45 | 72 | 79.8667 | 95.7333 | 94.6
2015-08-22 14:00 | 72 | 79.7667 | 96.4667 | 95
2015-08-22 14:15 | 72 | 79.2667 | 97.4667 | 95
2015-08-22 14:30 | 72 | 78.7667 | 98.4667 | 95
2015-08-22 14:45 | 72 | 78.2667 | 99.4667 | 95
2015-08-22 15:00 | 71.9333 | 77.8833 | 99.7667 | 95.1167
2015-08-22 15:15 | 71.6833 | 77.6333 | 99.2667 | 95.3667
2015-08-22 15:30 | 71.4333 | 77.3833 | 98.7667 | 95.6167
2015-08-22 15:45 | 71.1833 | 77.1333 | 98.2667 | 95.8667
2015-08-22 16:00 | 70.8667 | 76.65 | 97.1765 | 96
2015-08-22 16:15 | 70.3667 | 75.9 | 96 | 96
2015-08-22 16:30 | 69.8667 | 75.15 | 96 | 96
2015-08-22 16:45 | 69.3667 | 74.4 | 96 | 96
2015-08-22 17:00 | 68.8 | 73.65 | 95.5333 | 95.7667
2015-08-22 17:15 | 68.05 | 72.9 | 94.5333 | 95.2667
2015-08-22 17:30 | 67.3 | 72.15 | 93.5333 | 94.7667
2015-08-22 17:45 | 66.55 | 71.4 | 92.5333 | 94.2667
2015-08-22 18:00 | 65.7333 | 70.5333 | 91.8833 | 93.5333
2015-08-22 18:15 | 64.7333 | 69.5333 | 91.6333 | 92.5333
2015-08-22 18:30 | 63.7333 | 68.5333 | 91.3833 | 91.5333
2015-08-22 18:45 | 62.7333 | 67.5333 | 91.1333 | 90.5333
2015-08-22 19:00 | 62 | 66.65 | 90.7667 | 89.5333
2015-08-22 19:15 | 62 | 65.9 | 90.2667 | 88.5333
2015-08-22 19:30 | 62 | 65.15 | 89.7667 | 87.5333
2015-08-22 19:45 | 62 | 64.4 | 89.2667 | 86.5333
2015-08-22 20:00 | 62 | 63.8833 | 88.5333 | 85.7667
2015-08-22 20:15 | 62 | 63.6333 | 87.5333 | 85.2667
2015-08-22 20:30 | 62 | 63.3833 | 86.5333 | 84.7667
2015-08-22 20:45 | 62 | 63.1333 | 85.5333 | 84.2667
2015-08-22 21:00 | 61.9333 | 62.8833 | 84.7667 | 83.5333
2015-08-22 21:15 | 61.6833 | 62.6333 | 84.2667 | 82.5333
2015-08-22 21:30 | 61.4333 | 62.3833 | 83.7667 | 81.5333
2015-08-22 21:45 | 61.1833 | 62.1333 | 83.2667 | 80.5333
2015-08-22 22:00 | 61 | 61.8833 | 82.8833 | 79.5333
2015-08-22 22:15 | 61 | 61.6333 | 82.6333 | 78.5333
2015-08-22 22:30 | 61 | 61.3833 | 82.3833 | 77.5333
2015-08-22 22:45 | 61 | 61.1333 | 82.1333 | 76.5333
2015-08-22 23:00 | 61 | 61 | 82 | 75.7667
2015-08-22 23:15 | 61 | 61 | 82 | 75.2667
2015-08-22 23:30 | 61 | 61 | 82 | 74.7667
2015-08-22 23:45 | 61 | 61 | 82 | 74.2667
2015-08-23 | 61 | 61.1167 | 81.8833 | 73.7667
2015-08-23 00:15 | 61 | 61.3667 | 81.6333 | 73.2667
2015-08-23 00:30 | 61 | 61.6167 | 81.3833 | 72.7667
2015-08-23 00:45 | 61 | 61.8667 | 81.1333 | 72.2667
2015-08-23 01:00 | 61 | 62 | 80.65 | 71.7667
2015-08-23 01:15 | 60.9762 | 62 | 79.9 | 71.2667
2015-08-23 01:30 | 60.619 | 62 | 79.15 | 70.7667
2015-08-23 01:45 | 60.2619 | 62 | 78.4 | 70.2667
2015-08-23 02:00 | 60 | 62 | 78.1167 | 69.8833
2015-08-23 02:15 | 60 | 62 | 78.3667 | 69.6333
2015-08-23 02:30 | 60 | 62 | 78.6167 | 69.3833
2015-08-23 02:45 | 60 | 62 | 78.8667 | 69.1333
2015-08-23 03:00 | 60.1176 | 62 | 78.8833 | 68.7667
2015-08-23 03:15 | 60.5588 | 62 | 78.6333 | 68.2667
2015-08-23 03:30 | 61 | 62 | 78.3833 | 67.7667
2015-08-23 03:45 | 60.4231 | 62 | 78.1333 | 67.2667
2015-08-23 04:00 | 60.0667 | 62.25 | 77.8833 | 67
2015-08-23 04:15 | 60.3167 | 62.7857 | 77.6333 | 67
2015-08-23 04:30 | 60.5667 | 62.7188 | 77.3833 | 67
2015-08-23 04:45 | 60.8167 | 62.25 | 77.1333 | 67
2015-08-23 05:00 | 61 | 61.8833 | 76.7667 | 66.8833
2015-08-23 05:15 | 61 | 61.6333 | 76.2667 | 66.6333
2015-08-23 05:30 | 61 | 61.3833 | 75.7667 | 66.3833
2015-08-23 05:45 | 61 | 61.1333 | 75.2667 | 66.1333
2015-08-23 06:00 | 61.0667 | 60.8833 | 74.8833 | 66.1167
2015-08-23 06:15 | 61.3167 | 60.6333 | 74.6333 | 66.3667
2015-08-23 06:30 | 61.5667 | 60.3833 | 74.3833 | 66.6167
2015-08-23 06:45 | 61.8167 | 60.1333 | 74.1333 | 66.8667
2015-08-23 07:00 | 62.0667 | 60 | 74.4667 | 67.4667
2015-08-23 07:15 | 62.3167 | 60 | 75.4667 | 68.4667
2015-08-23 07:30 | 62.5667 | 60 | 76.4667 | 69.4667
2015-08-23 07:45 | 62.8167 | 60 | 77.4667 | 70.4667
2015-08-23 08:00 | 63.0889 | 60.35 | 78.7 | 71.7
2015-08-23 08:15 | 63.4222 | 61.1 | 80.2 | 73.2
2015-08-23 08:30 | 63.7556 | 61.85 | 81.7 | 74.7
2015-08-23 08:45 | 64.2667 | 62.6 | 83.2 | 76.2
2015-08-23 09:00 | 65.2 | 63.525 | 84.5833 | 77.35
2015-08-23 09:15 | 65.95 | 64.65 | 85.8333 | 78.1
2015-08-23 09:30 | 66.7 | 65.775 | 87.0833 | 78.85
2015-08-23 09:45 | 67.45 | 66.6 | 88.3333 | 79.6
2015-08-23 10:00 | 68.2 | 67.5833 | 89.35 | 80.5833
2015-08-23 10:15 | 68.95 | 68.8333 | 90.1 | 81.8333
2015-08-23 10:30 | 69.7 | 70.0833 | 90.85 | 83.0833
2015-08-23 10:45 | 70.45 | 71.3333 | 91.6 | 84.3333
2015-08-23 11:00 | 71.2 | 72.35 | 92.4667 | 85.5833
2015-08-23 11:15 | 71.95 | 73.1 | 93.4667 | 86.8333
2015-08-23 11:30 | 72.7 | 73.85 | 94.4667 | 88.0833
2015-08-23 11:45 | 73.45 | 74.6 | 95.4667 | 89.3333
2015-08-23 12:00 | 73.9333 | 75.1167 | 96.1167 | 90.1167
2015-08-23 12:15 | 73.6833 | 75.3667 | 96.3667 | 90.3667
2015-08-23 12:30 | 73.4333 | 75.6167 | 96.6167 | 90.6167
2015-08-23 12:45 | 73.1833 | 75.8667 | 96.8667 | 90.8667
2015-08-23 13:00 | 72.7333 | 76.1167 | 97.1321 | 91.4667
2015-08-23 13:15 | 71.7333 | 76.3667 | 97.4151 | 92.4667
2015-08-23 13:30 | 70.7333 | 76.6167 | 97.6981 | 93.4667
2015-08-23 13:45 | 69.7333 | 76.8667 | 97.9811 | 94.4667
2015-08-23 14:00 | 69.0667 | 76.7667 | 97 | 95.1167
2015-08-23 14:15 | 69.3167 | 76.2667 | 95.32 | 95.3667
2015-08-23 14:30 | 69.5667 | 75.7667 | 93.5 | 95.6167
2015-08-23 14:45 | 69.8167 | 75.2667 | 91.625 | 95.8667
2015-08-23 15:00 | 69.9333 | 74.8833 | 90.95 | 96.1167
2015-08-23 15:15 | 69.6833 | 74.6333 | 88.7 | 96.3667
2015-08-23 15:30 | 69.4333 | 74.3833 | 86.45 | 96.6167
2015-08-23 15:45 | 69.1833 | 74.1333 | 84.2 | 96.8667
2015-08-23 16:00 | 68.8667 | 73.7667 | 83.35 | 96.8833
2015-08-23 16:15 | 68.3667 | 73.2667 | 84.1 | 96.6333
2015-08-23 16:30 | 67.8667 | 72.7667 | 84.85 | 96.3833
2015-08-23 16:45 | 67.3667 | 72.2667 | 85.6 | 96.1333
2015-08-23 17:00 | 66.9333 | 71.7667 | 85.3 | 95.7667
2015-08-23 17:15 | 66.6833 | 71.2667 | 83.8 | 95.2667
2015-08-23 17:30 | 66.4333 | 70.7667 | 82.3 | 94.7667
2015-08-23 17:45 | 66.1833 | 70.2667 | 80.8 | 94.2667
2015-08-23 18:00 | 65.8 | 69.5333 | 79.8833 | 93.5333
2015-08-23 18:15 | 65.05 | 68.5333 | 79.6333 | 92.5333
2015-08-23 18:30 | 64.3 | 67.5333 | 79.3833 | 91.5333
2015-08-23 18:45 | 63.55 | 66.5333 | 79.1333 | 90.5333
2015-08-23 19:00 | 63 | 65.8833 | 78.5333 | 89.65
2015-08-23 19:15 | 63 | 65.6333 | 77.5333 | 88.9
2015-08-23 19:30 | 63 | 65.3833 | 76.5333 | 88.15
2015-08-23 19:45 | 63 | 65.1333 | 75.5333 | 87.4
2015-08-23 20:00 | 63 | 64.8833 | 74.8833 | 86.7667
2015-08-23 20:15 | 63 | 64.6333 | 74.6333 | 86.2667
2015-08-23 20:30 | 63 | 64.3833 | 74.3833 | 85.7667
2015-08-23 20:45 | 63 | 64.1333 | 74.1333 | 85.2667
2015-08-23 21:00 | 63 | 63.8833 | 74.1167 | 84.5333
2015-08-23 21:15 | 63 | 63.6333 | 74.3667 | 83.5333
2015-08-23 21:30 | 63 | 63.3833 | 74.6167 | 82.5333
2015-08-23 21:45 | 63 | 63.1333 | 74.8667 | 81.5333
2015-08-23 22:00 | 62.9333 | 62.8833 | 75 | 80.65
2015-08-23 22:15 | 62.6833 | 62.6333 | 75 | 79.9
2015-08-23 22:30 | 62.4333 | 62.3833 | 75 | 79.15
2015-08-23 22:45 | 62.1833 | 62.1333 | 75 | 78.4
2015-08-23 23:00 | 62.0755 | 62 | 74.5333 | 77.65
2015-08-23 23:15 | 62.3585 | 62 | 73.5333 | 76.9
2015-08-23 23:30 | 62.6415 | 62 | 72.5333 | 76.15
2015-08-23 23:45 | 62.9245 | 62 | 71.5333 | 75.4
2015-08-24 | 62 | 62.1167 | 71.2333 | 74.8833
2015-08-24 00:15 | 62 | 62.3667 | 71.7333 | 74.6333
2015-08-24 00:30 | 62 | 62.6167 | 72.2333 | 74.3833
2015-08-24 00:45 | 62 | 62.8667 | 72.7333 | 74.1333
2015-08-24 01:00 | 62 | 63 | 73.1167 | 73.7667
2015-08-24 01:15 | 62 | 63 | 73.3667 | 73.2667
2015-08-24 01:30 | 62 | 63 | 73.6167 | 72.7667
2015-08-24 01:45 | 62 | 63 | 73.8667 | 72.2667
2015-08-24 02:00 | 62 | 63 | 73.65 | 71.7667
2015-08-24 02:15 | 62 | 63 | 72.9 | 71.2667
2015-08-24 02:30 | 62 | 63 | 72.15 | 70.7667
2015-08-24 02:45 | 62 | 63 | 71.4 | 70.2667
2015-08-24 03:00 | 61.9333 | 62.8833 | 70.8833 | 69.7667
2015-08-24 03:15 | 61.6833 | 62.6333 | 70.6333 | 69.2667
2015-08-24 03:30 | 61.4333 | 62.3833 | 70.3833 | 68.7667
2015-08-24 03:45 | 61.1833 | 62.1333 | 70.1333 | 68.2667
2015-08-24 04:00 | 61 | 62.14 | 70 | 67.8833
2015-08-24 04:15 | 61 | 62.44 | 70 | 67.6333
2015-08-24 04:30 | 61 | 62.74 | 70 | 67.3833
2015-08-24 04:45 | 61 | 63 | 70 | 67.1333
2015-08-24 05:00 | 61 | 63 | 69.65 | 67
2015-08-24 05:15 | 61 | 63 | 68.9 | 67
2015-08-24 05:30 | 61 | 63 | 68.15 | 67
2015-08-24 05:45 | 61 | 63 | 67.4 | 67
2015-08-24 06:00 | 61.0667 | 63 | 67.2593 | 67.2333
2015-08-24 06:15 | 61.3167 | 63 | 67.8148 | 67.7333
2015-08-24 06:30 | 61.5667 | 63 | 68.303 | 68.2333
2015-08-24 06:45 | 61.8167 | 63 | 68.7576 | 68.7333
2015-08-24 07:00 | 62.0667 | 63.1167 | 69.2333 | 69.5833
2015-08-24 07:15 | 62.3167 | 63.3667 | 69.7333 | 70.8333
2015-08-24 07:30 | 62.5667 | 63.6167 | 70.2333 | 72.0833
2015-08-24 07:45 | 62.8167 | 63.8667 | 70.7333 | 73.3333
2015-08-24 08:00 | 63.1333 | 64.4242 | 71.4667 | 74.7
2015-08-24 08:15 | 63.6333 | 65.3333 | 72.4667 | 76.2
2015-08-24 08:30 | 64.1333 | 66 | 73.4667 | 77.7
2015-08-24 08:45 | 64.6333 | 66 | 74.4667 | 79.2
2015-08-24 09:00 | 65.069 | 66.35 | 75.4773 | 80.4667
2015-08-24 09:15 | 65.3276 | 67.1 | 76.5 | 81.4667
2015-08-24 09:30 | 65.5862 | 67.85 | 77.5227 | 82.4667
2015-08-24 09:45 | 65.8448 | 68.6 | 78.5 | 83.4667
2015-08-24 10:00 | 67.0667 | 69.35 | 79.4667 | 84.5833
2015-08-24 10:15 | 67.3167 | 70.1 | 80.4667 | 85.8333
2015-08-24 10:30 | 67.5667 | 70.85 | 81.4667 | 87.0833
2015-08-24 10:45 | 67.8167 | 71.6 | 82.4667 | 88.3333
2015-08-24 11:00 | 68.0667 | 72.1167 | 83.35 | 89.2333
2015-08-24 11:15 | 68.3167 | 72.3667 | 84.1 | 89.7333
2015-08-24 11:30 | 68.5667 | 72.6167 | 84.85 | 90.2333
2015-08-24 11:45 | 68.8167 | 72.8667 | 85.6 | 90.7333
2015-08-24 12:00 | 69.1333 | 73 | 86.35 | 91.4667
2015-08-24 12:15 | 69.6333 | 73 | 87.1 | 92.4667
2015-08-24 12:30 | 70.1333 | 73 | 87.85 | 93.4667
2015-08-24 12:45 | 70.6333 | 73.6522 | 88.6 | 94.4667
2015-08-24 13:00 | 71 | 74.1167 | 89.1167 | 95.35
2015-08-24 13:15 | 71 | 74.3667 | 89.3667 | 96.1
2015-08-24 13:30 | 71 | 74.6167 | 89.6167 | 96.85
2015-08-24 13:45 | 71 | 74.8667 | 89.8667 | 97.6
2015-08-24 14:00 | 71 | 75.2333 | 90.5833 | 98
2015-08-24 14:15 | 71 | 75.7333 | 91.8333 | 98
2015-08-24 14:30 | 71 | 76.2333 | 93.0833 | 98
2015-08-24 14:45 | 71 | 76.7333 | 94.3333 | 98
2015-08-24 15:00 | 70.9333 | 77 | 95.1167 | 98.1167
2015-08-24 15:15 | 70.6833 | 77 | 95.3667 | 98.3667
2015-08-24 15:30 | 70.4333 | 77 | 95.6167 | 98.6167
2015-08-24 15:45 | 70.1833 | 77 | 95.8667 | 98.8667
2015-08-24 16:00 | 69.8667 | 76.7667 | 95.5333 | 98.8833
2015-08-24 16:15 | 69.3667 | 76.2667 | 94.5333 | 98.6333
2015-08-24 16:30 | 68.8667 | 75.7667 | 93.5333 | 98.3833
2015-08-24 16:45 | 68.3667 | 75.2667 | 92.5333 | 98.1333
2015-08-24 17:00 | 67.8667 | 74.65 | 91.8833 | 97.7667
2015-08-24 17:15 | 67.3667 | 73.9 | 91.6333 | 97.2667
2015-08-24 17:30 | 66.8667 | 73.15 | 91.3833 | 96.7667
2015-08-24 17:45 | 66.3667 | 72.4 | 91.1333 | 96.2667
2015-08-24 18:00 | 65.8667 | 71.65 | 90.8833 | 95.4167
2015-08-24 18:15 | 65.3667 | 70.9 | 90.6333 | 94.1667
2015-08-24 18:30 | 64.8667 | 70.15 | 90.3833 | 92.9167
2015-08-24 18:45 | 64.3667 | 69.4 | 90.1333 | 91.6667
2015-08-24 19:00 | 63.9333 | 68.7667 | 89.65 | 90.65
2015-08-24 19:15 | 63.6833 | 68.2667 | 88.9 | 89.9
2015-08-24 19:30 | 63.4333 | 67.7667 | 88.15 | 89.15
2015-08-24 19:45 | 63.1833 | 67.2667 | 87.4 | 88.4
2015-08-24 20:00 | 62.9333 | 66.7667 | 86.65 | 87.65
2015-08-24 20:15 | 62.6833 | 66.2667 | 85.9 | 86.9
2015-08-24 20:30 | 62.4333 | 65.7667 | 85.15 | 86.15
2015-08-24 20:45 | 62.1833 | 65.2667 | 84.4 | 85.4
2015-08-24 21:00 | 62 | 64.8833 | 83.65 | 84.65
2015-08-24 21:15 | 62 | 64.6333 | 82.9 | 83.9
2015-08-24 21:30 | 62 | 64.3833 | 82.15 | 83.15
2015-08-24 21:45 | 62 | 64.1333 | 81.4 | 82.4
2015-08-24 22:00 | 61.9333 | 63.8833 | 80.65 | 81.65
2015-08-24 22:15 | 61.6833 | 63.6333 | 79.9 | 80.9
2015-08-24 22:30 | 61.4333 | 63.3833 | 79.15 | 80.15
2015-08-24 22:45 | 61.1833 | 63.1333 | 78.4 | 79.4
2015-08-24 23:00 | 60.9333 | 62.8833 | 77.65 | 78.7667
2015-08-24 23:15 | 60.6833 | 62.6333 | 76.9 | 78.2667
2015-08-24 23:30 | 60.4333 | 62.3833 | 76.15 | 77.7667
2015-08-24 23:45 | 60.1833 | 62.1333 | 75.4 | 77.2667
2015-08-25 | 60 | 62 | 75 | 76.65
2015-08-25 00:15 | 60 | 62 | 75 | 75.9
2015-08-25 00:30 | 60 | 62 | 75 | 75.15
2015-08-25 00:45 | 60 | 62 | 75 | 74.4
2015-08-25 01:00 | 59.9333 | 61.7667 | 74.8833 | 73.7667
2015-08-25 01:15 | 59.6833 | 61.2667 | 74.6333 | 73.2667
2015-08-25 01:30 | 59.4333 | 60.7667 | 74.3833 | 72.7667
2015-08-25 01:45 | 59.1833 | 60.2667 | 74.1333 | 72.2667
2015-08-25 02:00 | 59 | 60.1207 | 73.8833 | 71.7667
2015-08-25 02:15 | 59 | 60.3793 | 73.6333 | 71.2667
2015-08-25 02:30 | 59 | 60.6379 | 73.3833 | 70.7667
2015-08-25 02:45 | 59 | 60.8966 | 73.1333 | 70.2667
2015-08-25 03:00 | 59 | 61.1167 | 72.8833 | 69.8833
2015-08-25 03:15 | 59 | 61.3667 | 72.6333 | 69.6333
2015-08-25 03:30 | 59 | 61.6167 | 72.3833 | 69.3833
2015-08-25 03:45 | 59 | 61.8667 | 72.1333 | 69.1333
2015-08-25 04:00 | 58.9333 | 62.1556 | 71.7667 | 68.8833
2015-08-25 04:15 | 58.6833 | 62.4889 | 71.2667 | 68.6333
2015-08-25 04:30 | 58.4333 | 62.8222 | 70.7667 | 68.3833
2015-08-25 04:45 | 58.1833 | 62.5333 | 70.2667 | 68.1333
2015-08-25 05:00 | 58.0667 | 62 | 69.8833 | 68
2015-08-25 05:15 | 58.3167 | 62 | 69.6333 | 68
2015-08-25 05:30 | 58.5667 | 62 | 69.3833 | 68
2015-08-25 05:45 | 58.8167 | 62 | 69.1333 | 68
2015-08-25 06:00 | 59.0667 | 62 | 69.1167 | 68.4667
2015-08-25 06:15 | 59.3167 | 62 | 69.3667 | 69.4667
2015-08-25 06:30 | 59.5667 | 62 | 69.6167 | 70.4667
2015-08-25 06:45 | 59.8167 | 62 | 69.8667 | 71.4667
2015-08-25 07:00 | 60.1333 | 62.1321 | 70.8167 | 72.7
2015-08-25 07:15 | 60.6333 | 62.4151 | 72.5667 | 74.2
2015-08-25 07:30 | 61.1333 | 62.6981 | 74.3167 | 75.7
2015-08-25 07:45 | 61.6333 | 62.9811 | 76.0667 | 77.2
2015-08-25 08:00 | 62.125 | 63.35 | 77.5833 | 78.5833
2015-08-25 08:15 | 62.5938 | 64.1 | 78.8333 | 79.8333
2015-08-25 08:30 | 63.0714 | 64.85 | 80.0833 | 81.0833
2015-08-25 08:45 | 63.6071 | 65.6 | 81.3333 | 82.3333
2015-08-25 09:00 | 64.0667 | 66.35 | 82.7 | 83.4667
2015-08-25 09:15 | 64.3167 | 67.1 | 84.2 | 84.4667
2015-08-25 09:30 | 64.5667 | 67.85 | 85.7 | 85.4667
2015-08-25 09:45 | 64.8167 | 68.6 | 87.2 | 86.4667
2015-08-25 10:00 | 65.1333 | 69.2333 | 88.4667 | 87.2333
2015-08-25 10:15 | 65.6333 | 69.7333 | 89.4667 | 87.7333
2015-08-25 10:30 | 66.1333 | 70.2333 | 90.4667 | 88.2333
2015-08-25 10:45 | 66.6333 | 70.7333 | 91.4667 | 88.7333
2015-08-25 11:00 | 67.2 | 71.35 | 92.1167 | 89.35
2015-08-25 11:15 | 67.95 | 72.1 | 92.3667 | 90.1
2015-08-25 11:30 | 68.7 | 72.85 | 92.6167 | 90.85
2015-08-25 11:45 | 69.45 | 73.6 | 92.8667 | 91.6
2015-08-25 12:00 | 69.9333 | 74.2333 | 93.2333 | 92.5833
2015-08-25 12:15 | 69.6833 | 74.7333 | 93.7333 | 93.8333
2015-08-25 12:30 | 69.4333 | 75.2333 | 94.2333 | 95.0833
2015-08-25 12:45 | 69.1833 | 75.7333 | 94.7333 | 96.3333
2015-08-25 13:00 | 69 | 76.35 | 95 | 97.2333
2015-08-25 13:15 | 69 | 77.1 | 95 | 97.7333
2015-08-25 13:30 | 69 | 77.85 | 95 | 98.2333
2015-08-25 13:45 | 69 | 78.6 | 95 | 98.7333
2015-08-25 14:00 | 69 | 79 | 95 | 99.2333
2015-08-25 14:15 | 69 | 79 | 95 | 99.7333
2015-08-25 14:30 | 69 | 79 | 95 | 100.2333
2015-08-25 14:45 | 69 | 79 | 95 | 100.7333
2015-08-25 15:00 | 68.8667 | 78.65 | 95.2333 | 101
2015-08-25 15:15 | 68.3667 | 77.9 | 95.7333 | 101
2015-08-25 15:30 | 67.8667 | 77.15 | 96.2333 | 101
2015-08-25 15:45 | 67.3667 | 76.4 | 96.7333 | 101
2015-08-25 16:00 | 66.9333 | 75.7667 | 96.8833 | 101
2015-08-25 16:15 | 66.6833 | 75.2667 | 96.6333 | 101
2015-08-25 16:30 | 66.4333 | 74.7667 | 96.3833 | 101
2015-08-25 16:45 | 66.1833 | 74.2667 | 96.1333 | 101
2015-08-25 17:00 | 65.7333 | 73.7667 | 95.5333 | 100.65
2015-08-25 17:15 | 64.7333 | 73.2667 | 94.5333 | 99.9
2015-08-25 17:30 | 63.7333 | 72.7667 | 93.5333 | 99.15
2015-08-25 17:45 | 62.7333 | 72.2667 | 92.5333 | 98.4
2015-08-25 18:00 | 61.8667 | 71.5333 | 91.125 | 97.65
2015-08-25 18:15 | 61.3667 | 70.5333 | 90.4615 | 96.9
2015-08-25 18:30 | 60.8667 | 69.5333 | 89.8846 | 96.15
2015-08-25 18:45 | 60.3667 | 68.5333 | 89.3077 | 95.4
2015-08-25 19:00 | 59.9333 | 67.7667 | 88.4167 | 94.5333
2015-08-25 19:15 | 59.6833 | 67.2667 | 87.1667 | 93.5333
2015-08-25 19:30 | 59.4333 | 66.7667 | 85.9167 | 92.5333
2015-08-25 19:45 | 59.1833 | 66.2667 | 84.6667 | 91.5333
2015-08-25 20:00 | 59 | 65.7667 | 83.7667 | 90.7667
2015-08-25 20:15 | 59 | 65.2667 | 83.2667 | 90.2667
2015-08-25 20:30 | 59 | 64.7667 | 82.7667 | 89.7667
2015-08-25 20:45 | 59 | 64.2667 | 82.2667 | 89.2667
2015-08-25 21:00 | 59 | 63.8833 | 82.2333 | 88.5333
2015-08-25 21:15 | 59 | 63.6333 | 82.7333 | 87.5333
2015-08-25 21:30 | 59 | 63.3833 | 83.2333 | 86.5333
2015-08-25 21:45 | 59 | 63.1333 | 83.7333 | 85.5333
2015-08-25 22:00 | 59 | 62.8833 | 83.7667 | 84.7667
2015-08-25 22:15 | 59 | 62.6333 | 83.2667 | 84.2667
2015-08-25 22:30 | 59 | 62.3833 | 82.7667 | 83.7667
2015-08-25 22:45 | 59 | 62.1333 | 82.2667 | 83.2667
2015-08-25 23:00 | 59 | 62 | 81.8833 | 82.5333
2015-08-25 23:15 | 59 | 62 | 81.6333 | 81.5333
2015-08-25 23:30 | 59 | 62 | 81.3833 | 80.5333
2015-08-25 23:45 | 59 | 62 | 81.1333 | 79.5333
2015-08-26 | 59 | 62 | 80.8833 | 78.8833
2015-08-26 00:15 | 59 | 62 | 80.6333 | 78.6333
2015-08-26 00:30 | 59 | 62 | 80.3833 | 78.3833
2015-08-26 00:45 | 59 | 62 | 80.1333 | 78.1333
2015-08-26 01:00 | 58.9333 | 61.8833 | 79.7667 | 77.7667
2015-08-26 01:15 | 58.6833 | 61.6333 | 79.2667 | 77.2667
2015-08-26 01:30 | 58.4333 | 61.3833 | 78.7667 | 76.7667
2015-08-26 01:45 | 58.1833 | 61.1333 | 78.2667 | 76.2667
2015-08-26 02:00 | 58 | 61 | 77.7667 | 75.8833
2015-08-26 02:15 | 58 | 61 | 77.2667 | 75.6333
2015-08-26 02:30 | 58 | 61 | 76.7667 | 75.3833
2015-08-26 02:45 | 58 | 61 | 76.2667 | 75.1333
2015-08-26 03:00 | 58 | 61 | 75.7667 | 74.8833
2015-08-26 03:15 | 58 | 61 | 75.2667 | 74.6333
2015-08-26 03:30 | 58 | 61 | 74.7667 | 74.3833
2015-08-26 03:45 | 58 | 61 | 74.2667 | 74.1333
2015-08-26 04:00 | 58 | 61 | 73.65 | 73.8833
2015-08-26 04:15 | 58 | 61 | 72.9 | 73.6333
2015-08-26 04:30 | 58 | 61 | 72.15 | 73.3833
2015-08-26 04:45 | 58 | 60.6154 | 71.4 | 73.1333
2015-08-26 05:00 | 58.0667 | 60 | 70.8833 | 72.8833
2015-08-26 05:15 | 58.3167 | 60 | 70.6333 | 72.6333
2015-08-26 05:30 | 58.5667 | 60 | 70.3833 | 72.3833
2015-08-26 05:45 | 58.8167 | 60 | 70.1333 | 72.1333
2015-08-26 06:00 | 59 | 60.2333 | 70.1167 | 72.1167
2015-08-26 06:15 | 59 | 60.7333 | 70.3667 | 72.3667
2015-08-26 06:30 | 59 | 61.2333 | 70.6167 | 72.6167
2015-08-26 06:45 | 59 | 61.7333 | 70.8667 | 72.8667
2015-08-26 07:00 | 59.2667 | 62.35 | 71.5833 | 73.5833
2015-08-26 07:15 | 60.2667 | 63.1 | 72.8333 | 74.8333
2015-08-26 07:30 | 61.2667 | 63.85 | 74.0833 | 76.0833
2015-08-26 07:45 | 62.2667 | 64.6 | 75.3333 | 77.3333
2015-08-26 08:00 | 63.2 | 65.35 | 76.7 | 78.5833
2015-08-26 08:15 | 63.95 | 66.1 | 78.2 | 79.8333
2015-08-26 08:30 | 64.7 | 66.85 | 79.7 | 81.0833
2015-08-26 08:45 | 65.45 | 67.6 | 81.2 | 82.3333
2015-08-26 09:00 | 66.1333 | 68.2333 | 82.5833 | 83.5833
2015-08-26 09:15 | 66.6333 | 68.7333 | 83.8333 | 84.8333
2015-08-26 09:30 | 67.1333 | 69.2333 | 85.0833 | 86.0833
2015-08-26 09:45 | 67.6333 | 69.7333 | 86.3333 | 87.3333
2015-08-26 10:00 | 68.2667 | 70.5833 | 87.35 | 88.35
2015-08-26 10:15 | 69.2667 | 71.8333 | 88.1 | 89.1
2015-08-26 10:30 | 70.2667 | 73.0833 | 88.85 | 89.85
2015-08-26 10:45 | 71.2667 | 74.3333 | 89.6 | 90.6
2015-08-26 11:00 | 72.1333 | 75.4667 | 90.35 | 91.4667
2015-08-26 11:15 | 72.6333 | 76.4667 | 91.1 | 92.4667
2015-08-26 11:30 | 73.1333 | 77.4667 | 91.85 | 93.4667
2015-08-26 11:45 | 73.6333 | 78.4667 | 92.6 | 94.4667
2015-08-26 12:00 | 74.1333 | 79.35 | 93.2333 | 95.35
2015-08-26 12:15 | 74.6333 | 80.1 | 93.7333 | 96.1
2015-08-26 12:30 | 75.1333 | 80.85 | 94.2333 | 96.85
2015-08-26 12:45 | 75.6333 | 81.6 | 94.7333 | 97.6
2015-08-26 13:00 | 75.9333 | 82.35 | 95 | 98.2333
2015-08-26 13:15 | 75.6833 | 83.1 | 95 | 98.7333
2015-08-26 13:30 | 75.4333 | 83.85 | 95 | 99.2333
2015-08-26 13:45 | 75.1833 | 84.6 | 95 | 99.7333
2015-08-26 14:00 | 74.7333 | 84.8833 | 95.1167 | 100.1167
2015-08-26 14:15 | 73.7333 | 84.6333 | 95.3667 | 100.3667
2015-08-26 14:30 | 72.7333 | 84.3833 | 95.6167 | 100.6167
2015-08-26 14:45 | 71.7333 | 84.1333 | 95.8667 | 100.8667
2015-08-26 15:00 | 71 | 83.5333 | 96 | 101
2015-08-26 15:15 | 71 | 82.5333 | 96 | 101
2015-08-26 15:30 | 71 | 81.5333 | 96 | 101
2015-08-26 15:45 | 71 | 80.5333 | 96 | 101
2015-08-26 16:00 | 71.1333 | 79.7667 | 95.8833 | 100.8833
2015-08-26 16:15 | 71.6333 | 79.2667 | 95.6333 | 100.6333
2015-08-26 16:30 | 72.1333 | 78.7667 | 95.3833 | 100.3833
2015-08-26 16:45 | 72.6333 | 78.2667 | 95.1333 | 100.1333
2015-08-26 17:00 | 72.7333 | 78 | 94.7667 | 99.65
2015-08-26 17:15 | 71.7333 | 78 | 94.2667 | 98.9
2015-08-26 17:30 | 70.7333 | 78 | 93.7667 | 98.15
2015-08-26 17:45 | 69.7333 | 78 | 93.2667 | 97.4
2015-08-26 18:00 | 68.8 | 77.5333 | 92.8833 | 96.5333
2015-08-26 18:15 | 68.05 | 76.5333 | 92.6333 | 95.5333
2015-08-26 18:30 | 67.3 | 75.5333 | 92.3833 | 94.5333
2015-08-26 18:45 | 66.55 | 74.5333 | 92.1333 | 93.5333
2015-08-26 19:00 | 65.8667 | 73.65 | 90.0167 | 92.8833
2015-08-26 19:15 | 65.3667 | 72.9 | 85.7667 | 92.6333
2015-08-26 19:30 | 64.8667 | 72.15 | 81.5167 | 92.3833
2015-08-26 19:45 | 64.3667 | 71.4 | 77.2667 | 92.1333
2015-08-26 20:00 | 64 | 70.7667 | 75.1556 | 91.4167
2015-08-26 20:15 | 64 | 70.2667 | 75.4889 | 90.1667
2015-08-26 20:30 | 64 | 69.7667 | 75.8222 | 88.9167
2015-08-26 20:45 | 64 | 69.2667 | 76 | 87.6667
2015-08-26 21:00 | 64 | 69 | 76.5 | 86.8833
2015-08-26 21:15 | 64 | 69 | 77.3478 | 86.6333
2015-08-26 21:30 | 64 | 69 | 78 | 86.3833
2015-08-26 21:45 | 64 | 69 | 78.6522 | 86.1333
2015-08-26 22:00 | 64 | 68.8833 | 78.8833 | 85.65
2015-08-26 22:15 | 64 | 68.6333 | 78.6333 | 84.9
2015-08-26 22:30 | 64 | 68.3833 | 78.3833 | 84.15
2015-08-26 22:45 | 64 | 68.1333 | 78.1333 | 83.4
2015-08-26 23:00 | 63.9333 | 67.8833 | 77.65 | 82.65
2015-08-26 23:15 | 63.6833 | 67.6333 | 76.9 | 81.9
2015-08-26 23:30 | 63.4333 | 67.3833 | 76.15 | 81.15
2015-08-26 23:45 | 63.1833 | 67.1333 | 75.4 | 80.4
2015-08-27 | 62.9333 | 66.8833 | 75 | 79.65
2015-08-27 00:15 | 62.6833 | 66.6333 | 75 | 78.9
2015-08-27 00:30 | 62.4333 | 66.3833 | 75 | 78.15
2015-08-27 00:45 | 62.1833 | 66.1333 | 75 | 77.4
2015-08-27 01:00 | 62 | 66.1167 | 74.8833 | 76.8833
2015-08-27 01:15 | 62 | 66.3667 | 74.6333 | 76.6333
2015-08-27 01:30 | 62 | 66.6167 | 74.3833 | 76.3833
2015-08-27 01:45 | 62 | 66.8667 | 74.1333 | 76.1333
2015-08-27 02:00 | 62 | 66.7667 | 73.7667 | 75.65
2015-08-27 02:15 | 62 | 66.2667 | 73.2667 | 74.9
2015-08-27 02:30 | 62 | 65.7667 | 72.7667 | 74.15
2015-08-27 02:45 | 62 | 65.2667 | 72.2667 | 73.4
2015-08-27 03:00 | 61.9333 | 65 | 71.8833 | 73
2015-08-27 03:15 | 61.6833 | 65 | 71.6333 | 73
2015-08-27 03:30 | 61.4333 | 65 | 71.3833 | 73
2015-08-27 03:45 | 61.1833 | 65 | 71.1333 | 73
2015-08-27 04:00 | 61 | 64.8833 | 71 | 72.8833
2015-08-27 04:15 | 61 | 64.6333 | 71 | 72.6333
2015-08-27 04:30 | 61 | 64.3833 | 71 | 72.3833
2015-08-27 04:45 | 61 | 64.1333 | 71 | 72.1333
2015-08-27 05:00 | 61 | 64.1167 | 70.8833 | 72
2015-08-27 05:15 | 61 | 64.3667 | 70.6333 | 72
2015-08-27 05:30 | 61 | 64.6167 | 70.3833 | 72
2015-08-27 05:45 | 61 | 64.8667 | 70.1333 | 72
2015-08-27 06:00 | 61.2 | 65.2333 | 70.1167 | 72.35
2015-08-27 06:15 | 61.95 | 65.7333 | 70.3667 | 73.1
2015-08-27 06:30 | 62.7 | 66.2333 | 70.6167 | 73.85
2015-08-27 06:45 | 63.45 | 66.7333 | 70.8667 | 74.6
2015-08-27 07:00 | 64.2 | 67.35 | 71.4667 | 75.5833
2015-08-27 07:15 | 64.95 | 68.1 | 72.4667 | 76.8333
2015-08-27 07:30 | 65.7 | 68.85 | 73.4667 | 78.0833
2015-08-27 07:45 | 66.45 | 69.6 | 74.4667 | 79.3333
2015-08-27 08:00 | 67.2 | 70.5833 | 76.05 | 80.4667
2015-08-27 08:15 | 67.95 | 71.8333 | 78.3 | 81.4667
2015-08-27 08:30 | 68.7 | 73.0833 | 80.55 | 82.4667
2015-08-27 08:45 | 69.45 | 74.3333 | 82.8 | 83.4667
2015-08-27 09:00 | 70.1333 | 75.5833 | 84.4667 | 84.4667
2015-08-27 09:15 | 70.6333 | 76.8333 | 85.4667 | 85.4667
2015-08-27 09:30 | 71.1333 | 78.0833 | 86.4667 | 86.4667
2015-08-27 09:45 | 71.6333 | 79.3333 | 87.4667 | 87.4667
2015-08-27 10:00 | 72.1333 | 80.5833 | 88.35 | 88.2333
2015-08-27 10:15 | 72.6333 | 81.8333 | 89.1 | 88.7333
2015-08-27 10:30 | 73.1333 | 83.0833 | 89.85 | 89.2333
2015-08-27 10:45 | 73.6333 | 84.3333 | 90.6 | 89.7333
2015-08-27 11:00 | 74.7333 | 85.2333 | 91.1167 | 90.4667
2015-08-27 11:15 | 77.4833 | 85.7333 | 91.3667 | 91.4667
2015-08-27 11:30 | 80.2333 | 86.2333 | 91.6167 | 92.4667
2015-08-27 11:45 | 82.9833 | 86.7333 | 91.8667 | 93.4667
2015-08-27 12:00 | 84.9333 | 87.35 | 92.35 | 94.5833
2015-08-27 12:15 | 84.6833 | 88.1 | 93.1 | 95.8333
2015-08-27 12:30 | 84.4333 | 88.85 | 93.85 | 97.0833
2015-08-27 12:45 | 84.1833 | 89.6 | 94.6 | 98.3333
2015-08-27 13:00 | 83.7333 | 90.1167 | 95.2333 | 99.2333
2015-08-27 13:15 | 82.7333 | 90.3667 | 95.7333 | 99.7333
2015-08-27 13:30 | 81.7333 | 90.6167 | 96.2333 | 100.2333
2015-08-27 13:45 | 80.7333 | 90.8667 | 96.7333 | 100.7333
2015-08-27 14:00 | 79.9333 | 90.65 | 97 | 101
2015-08-27 14:15 | 79.6833 | 89.9 | 97 | 101
2015-08-27 14:30 | 79.4333 | 89.15 | 97 | 101
2015-08-27 14:45 | 79.1833 | 88.4 | 97 | 101
2015-08-27 15:00 | 78.8667 | 87.7667 | 97 | 101.1167
2015-08-27 15:15 | 78.3667 | 87.2667 | 97 | 101.3667
2015-08-27 15:30 | 77.8667 | 86.7667 | 97 | 101.6167
2015-08-27 15:45 | 77.3667 | 86.2667 | 97 | 101.8667
2015-08-27 16:00 | 77 | 85.5333 | 96.8833 | 102
2015-08-27 16:15 | 77 | 84.5333 | 96.6333 | 102
2015-08-27 16:30 | 77 | 83.5333 | 96.3833 | 102
2015-08-27 16:45 | 77 | 82.5333 | 96.1333 | 102
2015-08-27 17:00 | 76.7333 | 81.5333 | 95.8833 | 101.65
2015-08-27 17:15 | 75.7333 | 80.5333 | 95.6333 | 100.9
2015-08-27 17:30 | 74.7333 | 79.5333 | 95.3833 | 100.15
2015-08-27 17:45 | 73.7333 | 78.5333 | 95.1333 | 99.4
2015-08-27 18:00 | 72.8667 | 77.7667 | 94.65 | 98.4167
2015-08-27 18:15 | 72.3667 | 77.2667 | 93.9 | 97.1667
2015-08-27 18:30 | 71.8667 | 76.7667 | 93.15 | 95.9167
2015-08-27 18:45 | 71.3667 | 76.2667 | 92.4 | 94.6667
2015-08-27 19:00 | 70.8667 | 75.7667 | 91.5333 | 93.8833
2015-08-27 19:15 | 70.3667 | 75.2667 | 90.5333 | 93.6333
2015-08-27 19:30 | 69.8667 | 74.7667 | 89.5333 | 93.3833
2015-08-27 19:45 | 69.3667 | 74.2667 | 88.5333 | 93.1333
2015-08-27 20:00 | 69.0667 | 74 | 87.7667 | 92.5333
2015-08-27 20:15 | 69.3167 | 74 | 87.2667 | 91.5333
2015-08-27 20:30 | 69.5667 | 74 | 86.7667 | 90.5333
2015-08-27 20:45 | 69.8167 | 74 | 86.2667 | 89.5333
2015-08-27 21:00 | 69.8667 | 73.8833 | 85.7667 | 88.7667
2015-08-27 21:15 | 69.3667 | 73.6333 | 85.2667 | 88.2667
2015-08-27 21:30 | 68.8667 | 73.3833 | 84.7667 | 87.7667
2015-08-27 21:45 | 68.3667 | 73.1333 | 84.2667 | 87.2667
2015-08-27 22:00 | 67.9333 | 72.8833 | 83.7667 | 86.65
2015-08-27 22:15 | 67.6833 | 72.6333 | 83.2667 | 85.9
2015-08-27 22:30 | 67.4333 | 72.3833 | 82.7667 | 85.15
2015-08-27 22:45 | 67.1833 | 72.1333 | 82.2667 | 84.4
2015-08-27 23:00 | 67 | 71.8833 | 81.7667 | 83.65
2015-08-27 23:15 | 67 | 71.6333 | 81.2667 | 82.9
2015-08-27 23:30 | 67 | 71.3833 | 80.7667 | 82.15
2015-08-27 23:45 | 67 | 71.1333 | 80.2667 | 81.4
2015-08-28 | 67 | 70.8833 | 79.8833 | 80.8833
2015-08-28 00:15 | 67 | 70.6333 | 79.6333 | 80.6333
2015-08-28 00:30 | 67 | 70.3833 | 79.3833 | 80.3833
2015-08-28 00:45 | 67 | 70.1333 | 79.1333 | 80.1333
2015-08-28 01:00 | 66.9333 | 69.8833 | 78.7667 | 79.7667
2015-08-28 01:15 | 66.6833 | 69.6333 | 78.2667 | 79.2667
2015-08-28 01:30 | 66.4333 | 69.3833 | 77.7667 | 78.7667
2015-08-28 01:45 | 66.1833 | 69.1333 | 77.2667 | 78.2667
2015-08-28 02:00 | 65.9333 | 68.7667 | 76.8833 | 77.65
2015-08-28 02:15 | 65.6833 | 68.2667 | 76.6333 | 76.9
2015-08-28 02:30 | 65.4333 | 67.7667 | 76.3833 | 76.15
2015-08-28 02:45 | 65.1833 | 67.2667 | 76.1333 | 75.4
2015-08-28 03:00 | 65 | 66.8833 | 75.8833 | 75
2015-08-28 03:15 | 65 | 66.6333 | 75.6333 | 75
2015-08-28 03:30 | 65 | 66.3833 | 75.3833 | 75
2015-08-28 03:45 | 65 | 66.1333 | 75.1333 | 75
2015-08-28 04:00 | 65 | 66 | 74.7667 | 74.7667
2015-08-28 04:15 | 65 | 66 | 74.2667 | 74.2667
2015-08-28 04:30 | 65 | 66 | 73.7667 | 73.7667
2015-08-28 04:45 | 65 | 66 | 73.2667 | 73.2667
2015-08-28 05:00 | 65.0667 | 66.1167 | 72.8833 | 73
2015-08-28 05:15 | 65.3167 | 66.3667 | 72.6333 | 73
2015-08-28 05:30 | 65.5667 | 66.6167 | 72.3833 | 73
2015-08-28 05:45 | 65.8167 | 66.8667 | 72.1333 | 73
2015-08-28 06:00 | 66.1333 | 67.5833 | 71.8833 | 73.5833
2015-08-28 06:15 | 66.6333 | 68.8333 | 71.6333 | 74.8333
2015-08-28 06:30 | 67.1333 | 70.0833 | 71.3833 | 76.0833
2015-08-28 06:45 | 67.6333 | 71.3333 | 71.1333 | 77.3333
2015-08-28 07:00 | 68.1333 | 72.7 | 71.5833 | 78.4667
2015-08-28 07:15 | 68.6333 | 74.2 | 72.8333 | 79.4667
2015-08-28 07:30 | 69.1333 | 75.7 | 74.0833 | 80.4667
2015-08-28 07:45 | 69.6333 | 77.2 | 75.3333 | 81.4667
2015-08-28 08:00 | 70.3333 | 78.5833 | 76.9333 | 82.5833
2015-08-28 08:15 | 71.5833 | 79.8333 | 78.9333 | 83.8333
2015-08-28 08:30 | 72.8333 | 81.0833 | 80.9333 | 85.0833
2015-08-28 08:45 | 74.0833 | 82.3333 | 82.9333 | 86.3333
2015-08-28 09:00 | 74.9333 | 83 | 84.7 | 87.35
2015-08-28 09:15 | 74.6833 | 83 | 86.2 | 88.1
2015-08-28 09:30 | 74.4333 | 83 | 87.7 | 88.85
2015-08-28 09:45 | 74.1833 | 83 | 89.2 | 89.6
2015-08-28 10:00 | 74.2 | 83.7 | 90.35 | 90.35
2015-08-28 10:15 | 74.95 | 85.2 | 91.1 | 91.1
2015-08-28 10:30 | 75.7 | 86.7 | 91.85 | 91.85
2015-08-28 10:45 | 76.45 | 88.2 | 92.6 | 92.6
2015-08-28 11:00 | 77.2 | 89.35 | 93.2333 | 93.35
2015-08-28 11:15 | 77.95 | 90.1 | 93.7333 | 94.1
2015-08-28 11:30 | 78.7 | 90.85 | 94.2333 | 94.85
2015-08-28 11:45 | 79.45 | 91.6 | 94.7333 | 95.6
2015-08-28 12:00 | 80.5714 | 92 | 95.4667 | 96.35
2015-08-28 12:15 | 82.7143 | 92 | 96.4667 | 97.1
2015-08-28 12:30 | 85.5 | 92 | 97.4667 | 97.85
2015-08-28 12:45 | 89.25 | 92 | 98.4667 | 98.6
2015-08-28 13:00 | 91.5333 | 92.2333 | 98.8833 | 99.5833
2015-08-28 13:15 | 89.7833 | 92.7333 | 98.6333 | 100.8333
2015-08-28 13:30 | 88.0333 | 93.2333 | 98.3833 | 102.0833
2015-08-28 13:45 | 86.2833 | 93.7333 | 98.1333 | 103.3333
2015-08-28 14:00 | 84.7333 | 94 | 98 | 103.8833
2015-08-28 14:15 | 83.7333 | 94 | 98 | 103.6333
2015-08-28 14:30 | 82.7333 | 94 | 98 | 103.3833
2015-08-28 14:45 | 81.7333 | 94 | 98 | 103.1333
2015-08-28 15:00 | 80.4667 | 93.65 | 98 | 103.2333
2015-08-28 15:15 | 78.4667 | 92.9 | 98 | 103.7333
2015-08-28 15:30 | 76.4667 | 92.15 | 98 | 104.2333
2015-08-28 15:45 | 74.4667 | 91.4 | 98 | 104.7333
2015-08-28 16:00 | 72.6667 | 90.4167 | 98 | 105
2015-08-28 16:15 | 71.4167 | 89.1667 | 98 | 105
2015-08-28 16:30 | 70.1667 | 87.9167 | 98 | 105
2015-08-28 16:45 | 68.9167 | 86.6667 | 98 | 105
2015-08-28 17:00 | 67.9333 | 85.1833 | 97.65 | 104.65
2015-08-28 17:15 | 67.6833 | 83.4333 | 96.9 | 103.9
2015-08-28 17:30 | 67.4333 | 81.6833 | 96.15 | 103.15
2015-08-28 17:45 | 67.1833 | 79.9333 | 95.4 | 102.4
2015-08-28 18:00 | 66.9333 | 78.5333 | 94.65 | 101.5333
2015-08-28 18:15 | 66.6833 | 77.5333 | 93.9 | 100.5333
2015-08-28 18:30 | 66.4333 | 76.5333 | 93.15 | 99.5333
2015-08-28 18:45 | 66.1833 | 75.5333 | 92.4 | 98.5333
2015-08-28 19:00 | 65.9333 | 74.65 | 91.65 | 96.6
2015-08-28 19:15 | 65.6833 | 73.9 | 90.9 | 93.9
2015-08-28 19:30 | 65.4333 | 73.15 | 90.15 | 93.15
2015-08-28 19:45 | 65.1833 | 72.4 | 89.4 | 92.4
2015-08-28 20:00 | 65.1111 | 71.65 | 87.6538 | 91.65
2015-08-28 20:15 | 65.5278 | 70.9 | 84.7692 | 90.9
2015-08-28 20:30 | 65.9444 | 70.15 | 82.3824 | 90.15
2015-08-28 20:45 | 66 | 69.4 | 80.1765 | 89.4
2015-08-28 21:00 | 66 | 68.8833 | 78.8833 | 88.65
2015-08-28 21:15 | 66 | 68.6333 | 78.6333 | 87.9
2015-08-28 21:30 | 66 | 68.3833 | 78.3833 | 87.15
2015-08-28 21:45 | 66 | 68.1333 | 78.1333 | 86.4
2015-08-28 22:00 | 65.75 | 67.8833 | 78 | 85.7667
2015-08-28 22:15 | 64.8125 | 67.6333 | 78 | 85.2667
2015-08-28 22:30 | 64.0714 | 67.3833 | 78 | 84.7667
2015-08-28 22:45 | 64.6071 | 67.1333 | 78 | 84.2667
2015-08-28 23:00 | 65 | 67 | 78.1167 | 83.65
2015-08-28 23:15 | 65 | 67 | 78.3667 | 82.9
2015-08-28 23:30 | 65 | 67 | 78.6167 | 82.15
2015-08-28 23:45 | 65 | 67 | 78.8667 | 81.4
2015-08-29 | 65.0667 | 66.65 | 79 | 80.7667
2015-08-29 00:15 | 65.3167 | 66 | 79 | 80.2667
2015-08-29 00:30 | 65.5667 | 66 | 79 | 79.7667
2015-08-29 00:45 | 65.8167 | 66.5789 | 79 | 79.2667
2015-08-29 01:00 | 66.0667 | 66.6957 | 79 | 78.8833
2015-08-29 01:15 | 66.3167 | 66.0435 | 79 | 78.6333
2015-08-29 01:30 | 66.5667 | 66 | 79 | 78.3833
2015-08-29 01:45 | 66.8167 | 66.5789 | 79 | 78.1333
2015-08-29 02:00 | 67 | 66.3 | 78.8833 | 77.7667
2015-08-29 02:15 | 67 | 66.24 | 78.6333 | 77.2667
2015-08-29 02:30 | 67 | 66.54 | 78.3833 | 76.7667
2015-08-29 02:45 | 67 | 66.84 | 78.1333 | 76.2667
2015-08-29 03:00 | 67 | 66 | 77.65 | 75.8833
2015-08-29 03:15 | 67 | 66.283 | 76.9 | 75.6333
2015-08-29 03:30 | 67 | 66.566 | 76.15 | 75.3833
2015-08-29 03:45 | 67 | 66.8491 | 75.4 | 75.1333
2015-08-29 04:00 | 66.8519 | 67 | 75 | 74.7667
2015-08-29 04:15 | 66.2963 | 67 | 75 | 74.2667
2015-08-29 04:30 | 66.2121 | 67 | 75 | 73.7667
2015-08-29 04:45 | 66.6667 | 67 | 75 | 73.2667
2015-08-29 05:00 | 66.913 | 66.75 | 75 | 72.8833
2015-08-29 05:15 | 66.587 | 66.2143 | 75 | 72.6333
2015-08-29 05:30 | 66.2609 | 66.5625 | 75 | 72.3833
2015-08-29 05:45 | 66 | 67.5 | 75 | 72.1333
2015-08-29 06:00 | 66.0667 | 68 | 74.7667 | 72.35
2015-08-29 06:15 | 66.3167 | 68 | 74.2667 | 73.1
2015-08-29 06:30 | 66.5667 | 68 | 73.7667 | 73.85
2015-08-29 06:45 | 66.8167 | 68 | 73.2667 | 74.6
2015-08-29 07:00 | 67.1333 | 68.35 | 73 | 75.4667
2015-08-29 07:15 | 67.6333 | 69.1 | 73 | 76.4667
2015-08-29 07:30 | 68.1333 | 69.85 | 73 | 77.4667
2015-08-29 07:45 | 68.6333 | 70.6 | 73 | 78.4667
2015-08-29 08:00 | 69 | 71.2745 | 73.1167 | 79.4667
2015-08-29 08:15 | 69 | 71.8627 | 73.3667 | 80.4667
2015-08-29 08:30 | 69 | 72.451 | 73.6167 | 81.4667
2015-08-29 08:45 | 69 | 73 | 73.8667 | 82.4667
2015-08-29 09:00 | 69.25 | 73.35 | 74 | 83.35
2015-08-29 09:15 | 70 | 74.1 | 74 | 84.1
2015-08-29 09:30 | 70.037 | 74.85 | 74 | 84.85
2015-08-29 09:45 | 70.5926 | 75.6 | 74 | 85.6
2015-08-29 10:00 | 70.8667 | 76.1167 | 74 | 86.35
2015-08-29 10:15 | 70.3667 | 76.3667 | 74 | 87.1
2015-08-29 10:30 | 69.8667 | 76.6167 | 74 | 87.85
2015-08-29 10:45 | 69.3667 | 76.8667 | 74 | 88.6
2015-08-29 11:00 | 69.5714 | 77.2333 | 74.1167 | 89.2333
2015-08-29 11:15 | 71.7143 | 77.7333 | 74.3667 | 89.7333
2015-08-29 11:30 | 72.3333 | 78.2333 | 74.6167 | 90.2333
2015-08-29 11:45 | 72.7179 | 78.7333 | 74.8667 | 90.7333
2015-08-29 12:00 | 73.0667 | 78.7667 | 75.35 | 91.1167
2015-08-29 12:15 | 73.3167 | 78.2667 | 76.1 | 91.3667
2015-08-29 12:30 | 73.5667 | 77.7667 | 76.85 | 91.6167
2015-08-29 12:45 | 73.8167 | 77.2667 | 77.6 | 91.8667
2015-08-29 13:00 | 73.9333 | 77.2333 | 78.4667 | 92.2333
2015-08-29 13:15 | 73.6833 | 77.7333 | 79.4667 | 92.7333
2015-08-29 13:30 | 73.4333 | 78.2333 | 80.4667 | 93.2333
2015-08-29 13:45 | 73.1833 | 78.7333 | 81.4667 | 93.7333
2015-08-29 14:00 | 73.0667 | 78.7667 | 82.2333 | 94
2015-08-29 14:15 | 73.3167 | 78.2667 | 82.7333 | 94
2015-08-29 14:30 | 73.5667 | 77.7667 | 83.2333 | 94
2015-08-29 14:45 | 73.8167 | 77.2667 | 83.7333 | 94
2015-08-29 15:00 | 73.8667 | 77 | 83.7667 | 94
2015-08-29 15:15 | 73.3667 | 77 | 83.2667 | 94
2015-08-29 15:30 | 72.8667 | 77 | 82.7667 | 94
2015-08-29 15:45 | 72.3667 | 77 | 82.2667 | 94
2015-08-29 16:00 | 71.8667 | 77 | 82 | 93.7667
2015-08-29 16:15 | 71.3667 | 77 | 82 | 93.2667
2015-08-29 16:30 | 70.8667 | 77 | 82 | 92.7667
2015-08-29 16:45 | 70.3667 | 77 | 82 | 92.2667
2015-08-29 17:00 | 69.9333 | 76.65 | 82 | 91.8833
2015-08-29 17:15 | 69.6833 | 75.9 | 82 | 91.6333
2015-08-29 17:30 | 69.4333 | 75.15 | 82 | 91.3833
2015-08-29 17:45 | 69.1833 | 74.4 | 82 | 91.1333
2015-08-29 18:00 | 68.8 | 73.5333 | 81.8833 | 90.5333
2015-08-29 18:15 | 68.05 | 72.5333 | 81.6333 | 89.5333
2015-08-29 18:30 | 67.3 | 71.5333 | 81.3833 | 88.5333
2015-08-29 18:45 | 66.55 | 70.5333 | 81.1333 | 87.5333
2015-08-29 19:00 | 65.9333 | 69.7667 | 80.65 | 86.5333
2015-08-29 19:15 | 65.6833 | 69.2667 | 79.9 | 85.5333
2015-08-29 19:30 | 65.4333 | 68.7667 | 79.15 | 84.5333
2015-08-29 19:45 | 65.1833 | 68.2667 | 78.4 | 83.5333
2015-08-29 20:00 | 65 | 67.7667 | 77.65 | 82.65
2015-08-29 20:15 | 65 | 67.2667 | 76.9 | 81.9
2015-08-29 20:30 | 65 | 66.7667 | 76.15 | 81.15
2015-08-29 20:45 | 65 | 66.2667 | 75.4 | 80.4
2015-08-29 21:00 | 64.8571 | 65.8833 | 74.7667 | 79.7667
2015-08-29 21:15 | 64.3214 | 65.6333 | 74.2667 | 79.2667
2015-08-29 21:30 | 64.1875 | 65.3833 | 73.7667 | 78.7667
2015-08-29 21:45 | 64.6562 | 65.1333 | 73.2667 | 78.2667
2015-08-29 22:00 | 65.069 | 64.8833 | 72.8833 | 77.7667
2015-08-29 22:15 | 65.3276 | 64.6333 | 72.6333 | 77.2667
2015-08-29 22:30 | 65.5862 | 64.3833 | 72.3833 | 76.7667
2015-08-29 22:45 | 65.8448 | 64.1333 | 72.1333 | 76.2667
2015-08-29 23:00 | 65.9333 | 64 | 72 | 75.7667
2015-08-29 23:15 | 65.6833 | 64 | 72 | 75.2667
2015-08-29 23:30 | 65.4333 | 64 | 72 | 74.7667
2015-08-29 23:45 | 65.1833 | 64 | 72 | 74.2667
2015-08-30 | 65 | 64 | 71.65 | 73.65
2015-08-30 00:15 | 65 | 64 | 70.9 | 72.9
2015-08-30 00:30 | 65 | 64.7895 | 70.15 | 72.15
2015-08-30 00:45 | 65 | 65.5789 | 69.4 | 71.4
2015-08-30 01:00 | 64.8621 | 65.7544 | 69 | 70.8833
2015-08-30 01:15 | 64.3448 | 65.2281 | 69 | 70.6333
2015-08-30 01:30 | 63.8276 | 64.7018 | 69 | 70.3833
2015-08-30 01:45 | 63.3103 | 64.1754 | 69 | 70.1333
2015-08-30 02:00 | 63.1905 | 63.8833 | 68.8833 | 69.8833
2015-08-30 02:15 | 63.9048 | 63.6333 | 68.6333 | 69.6333
2015-08-30 02:30 | 63.6486 | 63.3833 | 68.3833 | 69.3833
2015-08-30 02:45 | 63.2432 | 63.1333 | 68.1333 | 69.1333
2015-08-30 03:00 | 63 | 63 | 68.1167 | 68.8833
2015-08-30 03:15 | 63 | 63 | 68.3667 | 68.6333
2015-08-30 03:30 | 63 | 63 | 68.6167 | 68.3833
2015-08-30 03:45 | 63 | 63 | 68.8667 | 68.1333
2015-08-30 04:00 | 63.0667 | 63 | 68.7667 | 67.8833
2015-08-30 04:15 | 63.3167 | 63.2245 | 68.2667 | 67.6333
2015-08-30 04:30 | 63.5667 | 63.5306 | 67.7667 | 67.3833
2015-08-30 04:45 | 63.8167 | 63.8367 | 67.2667 | 67.1333
2015-08-30 05:00 | 63.9024 | 64 | 67.1167 | 66.8833
2015-08-30 05:15 | 63.5366 | 64 | 67.3667 | 66.6333
2015-08-30 05:30 | 63.1707 | 64 | 67.6167 | 66.3833
2015-08-30 05:45 | 63 | 64 | 67.8667 | 66.1333
2015-08-30 06:00 | 63 | 64 | 67.7667 | 66.2333
2015-08-30 06:15 | 63.0682 | 64 | 67.2667 | 66.7333
2015-08-30 06:30 | 63.4091 | 64 | 66.7667 | 67.2333
2015-08-30 06:45 | 63.75 | 64 | 66.2667 | 67.7333
2015-08-30 07:00 | 64 | 64.4828 | 66.5833 | 68.35
2015-08-30 07:15 | 64 | 65.5172 | 67.8333 | 69.1
2015-08-30 07:30 | 64 | 66.2581 | 69.0833 | 69.85
2015-08-30 07:45 | 64 | 66.7419 | 70.3333 | 70.6
2015-08-30 08:00 | 64.2667 | 67.2333 | 71.5833 | 71.4667
2015-08-30 08:15 | 65.2667 | 67.7333 | 72.8333 | 72.4667
2015-08-30 08:30 | 66.2667 | 68.2333 | 74.0833 | 73.4667
2015-08-30 08:45 | 67.2667 | 68.7333 | 75.3333 | 74.4667
2015-08-30 09:00 | 68.1333 | 69.35 | 76.4667 | 75.35
2015-08-30 09:15 | 68.6333 | 70.1 | 77.4667 | 76.1
2015-08-30 09:30 | 69.1333 | 70.85 | 78.4667 | 76.85
2015-08-30 09:45 | 69.6333 | 71.6 | 79.4667 | 77.6
2015-08-30 10:00 | 70.0667 | 72.2333 | 80.2333 | 78.35
2015-08-30 10:15 | 70.3167 | 72.7333 | 80.7333 | 79.1
2015-08-30 10:30 | 70.5667 | 73.2333 | 81.2333 | 79.85
2015-08-30 10:45 | 70.8167 | 73.7333 | 81.7333 | 80.6
2015-08-30 11:00 | 71.1333 | 74.1167 | 82.5833 | 81.2333
2015-08-30 11:15 | 71.6333 | 74.3667 | 83.8333 | 81.7333
2015-08-30 11:30 | 72.1333 | 74.6167 | 85.0833 | 82.2333
2015-08-30 11:45 | 72.6333 | 74.8667 | 86.3333 | 82.7333
2015-08-30 12:00 | 73.0667 | 75.2333 | 87.35 | 83.35
2015-08-30 12:15 | 73.3167 | 75.7333 | 88.1 | 84.1
2015-08-30 12:30 | 73.5667 | 76.2333 | 88.85 | 84.85
2015-08-30 12:45 | 73.8167 | 76.7333 | 89.6 | 85.6
2015-08-30 13:00 | 73.9333 | 77 | 90.1167 | 86.1167
2015-08-30 13:15 | 73.6833 | 77 | 90.3667 | 86.3667
2015-08-30 13:30 | 73.4333 | 77 | 90.6167 | 86.6167
2015-08-30 13:45 | 73.1833 | 77 | 90.8667 | 86.8667
2015-08-30 14:00 | 72.9333 | 77 | 91.1167 | 87.2333
2015-08-30 14:15 | 72.6833 | 77 | 91.3667 | 87.7333
2015-08-30 14:30 | 72.4333 | 77 | 91.6167 | 88.2333
2015-08-30 14:45 | 72.1833 | 77 | 91.8667 | 88.7333
2015-08-30 15:00 | 72 | 77 | 91.7667 | 89
2015-08-30 15:15 | 72 | 77 | 91.2667 | 89
2015-08-30 15:30 | 72 | 77 | 90.7667 | 89
2015-08-30 15:45 | 72 | 77 | 90.2667 | 89
2015-08-30 16:00 | 71.9333 | 76.7667 | 90.1167 | 88.8833
2015-08-30 16:15 | 71.6833 | 76.2667 | 90.3667 | 88.6333
2015-08-30 16:30 | 71.4333 | 75.7667 | 90.6167 | 88.3833
2015-08-30 16:45 | 71.1833 | 75.2667 | 90.8667 | 88.1333
2015-08-30 17:00 | 70.8667 | 74.7667 | 90.7667 | 87.65
2015-08-30 17:15 | 70.3667 | 74.2667 | 90.2667 | 86.9
2015-08-30 17:30 | 69.8667 | 73.7667 | 89.7667 | 86.15
2015-08-30 17:45 | 69.3667 | 73.2667 | 89.2667 | 85.4
2015-08-30 18:00 | 68.8667 | 72.7667 | 88.65 | 84.65
2015-08-30 18:15 | 68.3667 | 72.2667 | 87.9 | 83.9
2015-08-30 18:30 | 67.8667 | 71.7667 | 87.15 | 83.15
2015-08-30 18:45 | 67.3667 | 71.2667 | 86.4 | 82.4
2015-08-30 19:00 | 66.8667 | 70.7667 | 85.65 | 81.65
2015-08-30 19:15 | 66.3667 | 70.2667 | 84.9 | 80.9
2015-08-30 19:30 | 65.8667 | 69.7667 | 84.15 | 80.15
2015-08-30 19:45 | 65.3667 | 69.2667 | 83.4 | 79.4
2015-08-30 20:00 | 64.9333 | 69 | 82.65 | 78.7667
2015-08-30 20:15 | 64.6833 | 69 | 81.9 | 78.2667
2015-08-30 20:30 | 64.4333 | 69 | 81.15 | 77.7667
2015-08-30 20:45 | 64.1833 | 69 | 80.4 | 77.2667
2015-08-30 21:00 | 64.0667 | 68.7667 | 79.7667 | 76.7667
2015-08-30 21:15 | 64.3167 | 68.2667 | 79.2667 | 76.2667
2015-08-30 21:30 | 64.5667 | 67.7667 | 78.7667 | 75.7667
2015-08-30 21:45 | 64.8167 | 67.2667 | 78.2667 | 75.2667
2015-08-30 22:00 | 64.8667 | 66.8833 | 77.7667 | 74.7667
2015-08-30 22:15 | 64.3667 | 66.6333 | 77.2667 | 74.2667
2015-08-30 22:30 | 63.8667 | 66.3833 | 76.7667 | 73.7667
2015-08-30 22:45 | 63.3667 | 66.1333 | 76.2667 | 73.2667
2015-08-30 23:00 | 63 | 66 | 75.7667 | 72.7667
2015-08-30 23:15 | 63 | 66 | 75.2667 | 72.2667
2015-08-30 23:30 | 63 | 66 | 74.7667 | 71.7667
2015-08-30 23:45 | 63 | 66 | 74.2667 | 71.2667
2015-08-31 | 62.9333 | 65.65 | 73.8833 | 70.7667
2015-08-31 00:15 | 62.6833 | 64.9 | 73.6333 | 70.2667
2015-08-31 00:30 | 62.4333 | 64.15 | 73.3833 | 69.7667
2015-08-31 00:45 | 62.1833 | 63.4 | 73.1333 | 69.2667
2015-08-31 01:00 | 61.9333 | 63 | 72.7667 | 68.8833
2015-08-31 01:15 | 61.6833 | 63 | 72.2667 | 68.6333
2015-08-31 01:30 | 61.4333 | 63 | 71.7667 | 68.3833
2015-08-31 01:45 | 61.1833 | 63 | 71.2667 | 68.1333
2015-08-31 02:00 | 60.9333 | 62.8833 | 70.7667 | 67.8833
2015-08-31 02:15 | 60.6833 | 62.6333 | 70.2667 | 67.6333
2015-08-31 02:30 | 60.4333 | 62.3833 | 69.7667 | 67.3833
2015-08-31 02:45 | 60.1833 | 62.1333 | 69.2667 | 67.1333
2015-08-31 03:00 | 60 | 61.7667 | 69 | 66.8833
2015-08-31 03:15 | 60 | 61.2667 | 69 | 66.6333
2015-08-31 03:30 | 60 | 60.7667 | 69 | 66.3833
2015-08-31 03:45 | 60 | 60.2667 | 69 | 66.1333
2015-08-31 04:00 | 60 | 60.1167 | 68.8833 | 65.8833
2015-08-31 04:15 | 60 | 60.3667 | 68.6333 | 65.6333
2015-08-31 04:30 | 60 | 60.6167 | 68.3833 | 65.3833
2015-08-31 04:45 | 60 | 60.8667 | 68.1333 | 65.1333
2015-08-31 05:00 | 60.069 | 61 | 67.7667 | 64.8833
2015-08-31 05:15 | 60.3276 | 61 | 67.2667 | 64.6333
2015-08-31 05:30 | 60.5862 | 61 | 66.7667 | 64.3833
2015-08-31 05:45 | 60.8448 | 61 | 66.2667 | 64.1333
2015-08-31 06:00 | 60.2 | 61.1167 | 65.8833 | 64.2333
2015-08-31 06:15 | 60.95 | 61.3667 | 65.6333 | 64.7333
2015-08-31 06:30 | 61.7 | 61.6167 | 65.3833 | 65.2333
2015-08-31 06:45 | 62.45 | 61.8667 | 65.1333 | 65.7333
2015-08-31 07:00 | 63.2 | 62.35 | 65.5833 | 66.4667
2015-08-31 07:15 | 63.95 | 63.1 | 66.8333 | 67.4667
2015-08-31 07:30 | 64.7 | 63.85 | 68.0833 | 68.4667
2015-08-31 07:45 | 65.45 | 64.6 | 69.3333 | 69.4667
2015-08-31 08:00 | 66.0667 | 65.4667 | 70.7 | 70.5833
2015-08-31 08:15 | 66.3167 | 66.4667 | 72.2 | 71.8333
2015-08-31 08:30 | 66.5667 | 67.4667 | 73.7 | 73.0833
2015-08-31 08:45 | 66.8167 | 68.4667 | 75.2 | 74.3333
2015-08-31 09:00 | 67.2 | 69.4667 | 76.8167 | 75.4667
2015-08-31 09:15 | 67.95 | 70.4667 | 78.5667 | 76.4667
2015-08-31 09:30 | 68.7 | 71.4667 | 80.3167 | 77.4667
2015-08-31 09:45 | 69.45 | 72.4667 | 82.0667 | 78.4667
2015-08-31 10:00 | 70.2667 | 73.5833 | 83.35 | 79.2333
2015-08-31 10:15 | 71.2667 | 74.8333 | 84.1 | 79.7333
2015-08-31 10:30 | 72.2667 | 76.0833 | 84.85 | 80.2333
2015-08-31 10:45 | 73.2667 | 77.3333 | 85.6 | 80.7333
2015-08-31 11:00 | 74 | 78.35 | 86.4667 | 81.5833
2015-08-31 11:15 | 74 | 79.1 | 87.4667 | 82.8333
2015-08-31 11:30 | 74 | 79.85 | 88.4667 | 84.0833
2015-08-31 11:45 | 74 | 80.6 | 89.4667 | 85.3333
2015-08-31 12:00 | 74.0667 | 81.35 | 90.1167 | 86.1167
2015-08-31 12:15 | 74.3167 | 82.1 | 90.3667 | 86.3667
2015-08-31 12:30 | 74.5667 | 82.85 | 90.6167 | 86.6167
2015-08-31 12:45 | 74.8167 | 83.6 | 90.8667 | 86.8667
2015-08-31 13:00 | 75 | 83.8833 | 91.2333 | 87.1167
2015-08-31 13:15 | 75 | 83.6333 | 91.7333 | 87.3667
2015-08-31 13:30 | 75 | 83.3833 | 92.2333 | 87.6167
2015-08-31 13:45 | 75 | 83.1333 | 92.7333 | 87.8667
2015-08-31 14:00 | 74.8 | 82.8833 | 93.2333 | 88.2333
2015-08-31 14:15 | 74.05 | 82.6333 | 93.7333 | 88.7333
2015-08-31 14:30 | 73.3 | 82.3833 | 94.2333 | 89.2333
2015-08-31 14:45 | 72.55 | 82.1333 | 94.7333 | 89.7333
2015-08-31 15:00 | 71.9333 | 81.7667 | 95 | 90.1167
2015-08-31 15:15 | 71.6833 | 81.2667 | 95 | 90.3667
2015-08-31 15:30 | 71.4333 | 80.7667 | 95 | 90.6167
2015-08-31 15:45 | 71.1833 | 80.2667 | 95 | 90.8667
2015-08-31 16:00 | 70.8 | 79.65 | 95 | 91
2015-08-31 16:15 | 70.05 | 78.9 | 95 | 91
2015-08-31 16:30 | 69.3 | 78.15 | 95 | 91
2015-08-31 16:45 | 68.55 | 77.4 | 95 | 91
2015-08-31 17:00 | 67.8 | 76.3 | 94.7667 | 90.7667
2015-08-31 17:15 | 67.05 | 74.8 | 94.2667 | 90.2667
2015-08-31 17:30 | 66.3 | 73.3 | 93.7667 | 89.7667
2015-08-31 17:45 | 65.55 | 71.8 | 93.2667 | 89.2667
2015-08-31 18:00 | 64.9333 | 70.65 | 92.65 | 88.5333
2015-08-31 18:15 | 64.6833 | 69.9 | 91.9 | 87.5333
2015-08-31 18:30 | 64.4333 | 69.15 | 91.15 | 86.5333
2015-08-31 18:45 | 64.1833 | 68.4 | 90.4 | 85.5333
2015-08-31 19:00 | 63.9333 | 67.65 | 89.65 | 84.7667
2015-08-31 19:15 | 63.6833 | 66.9 | 88.9 | 84.2667
2015-08-31 19:30 | 63.4333 | 66.15 | 88.15 | 83.7667
2015-08-31 19:45 | 63.1833 | 65.4 | 87.4 | 83.2667
2015-08-31 20:00 | 63 | 65 | 86.65 | 82.7667
2015-08-31 20:15 | 63 | 65 | 85.9 | 82.2667
2015-08-31 20:30 | 63 | 65 | 85.15 | 81.7667
2015-08-31 20:45 | 63 | 65 | 84.4 | 81.2667
2015-08-31 21:00 | 63 | 64.7667 | 83.7667 | 80.8833
2015-08-31 21:15 | 63 | 64.2667 | 83.2667 | 80.6333
2015-08-31 21:30 | 63 | 63.7667 | 82.7667 | 80.3833
2015-08-31 21:45 | 63 | 63.2667 | 82.2667 | 80.1333
2015-08-31 22:00 | 62.9333 | 62.8833 | 81.7667 | 79.8833
2015-08-31 22:15 | 62.6833 | 62.6333 | 81.2667 | 79.6333
2015-08-31 22:30 | 62.4333 | 62.3833 | 80.7667 | 79.3833
2015-08-31 22:45 | 62.1833 | 62.1333 | 80.2667 | 79.1333
2015-08-31 23:00 | 61.9333 | 62 | 79.8833 | 78.5333
2015-08-31 23:15 | 61.6833 | 62 | 79.6333 | 77.5333
2015-08-31 23:30 | 61.4333 | 62 | 79.3833 | 76.5333
2015-08-31 23:45 | 61.1833 | 62 | 79.1333 | 75.5333
2015-09-01 | 61 | 62 | 78.7667 | 74.7667
2015-09-01 00:15 | 61 | 62 | 78.2667 | 74.2667
2015-09-01 00:30 | 61 | 62 | 77.7667 | 73.7667
2015-09-01 00:45 | 61 | 62 | 77.2667 | 73.2667
2015-09-01 01:00 | 61 | 61.7667 | 76.8833 | 72.8833
2015-09-01 01:15 | 61 | 61.2667 | 76.6333 | 72.6333
2015-09-01 01:30 | 61 | 60.7667 | 76.3833 | 72.3833
2015-09-01 01:45 | 61 | 60.2667 | 76.1333 | 72.1333
2015-09-01 02:00 | 60.9333 | 60.1167 | 75.7667 | 71.65
2015-09-01 02:15 | 60.6833 | 60.3667 | 75.2667 | 70.9
2015-09-01 02:30 | 60.4333 | 60.6167 | 74.7667 | 70.15
2015-09-01 02:45 | 60.1833 | 60.8667 | 74.2667 | 69.4
2015-09-01 03:00 | 60 | 60.8833 | 73.7667 | 68.7667
2015-09-01 03:15 | 60 | 60.6333 | 73.2667 | 68.2667
2015-09-01 03:30 | 60 | 60.3833 | 72.7667 | 67.7667
2015-09-01 03:45 | 60 | 60.1333 | 72.2667 | 67.2667
2015-09-01 04:00 | 60 | 59.8833 | 71.8833 | 66.8833
2015-09-01 04:15 | 60 | 59.6333 | 71.6333 | 66.6333
2015-09-01 04:30 | 60 | 59.3833 | 71.3833 | 66.3833
2015-09-01 04:45 | 60 | 59.1333 | 71.1333 | 66.1333
2015-09-01 05:00 | 60 | 59 | 70.7667 | 66.1167
2015-09-01 05:15 | 60 | 59 | 70.2667 | 66.3667
2015-09-01 05:30 | 60 | 59 | 69.7667 | 66.6167
2015-09-01 05:45 | 60 | 59 | 69.2667 | 66.8667
2015-09-01 06:00 | 60.1333 | 59.2333 | 68.8833 | 67.35
2015-09-01 06:15 | 60.6333 | 59.7333 | 68.6333 | 68.1
2015-09-01 06:30 | 61.1333 | 60.2333 | 68.3833 | 68.85
2015-09-01 06:45 | 61.6333 | 60.7333 | 68.1333 | 69.6
2015-09-01 07:00 | 62.2667 | 61.2333 | 68.4667 | 70.7
2015-09-01 07:15 | 63.2667 | 61.7333 | 69.4667 | 72.2
2015-09-01 07:30 | 64.2667 | 62.2333 | 70.4667 | 73.7
2015-09-01 07:45 | 65.2667 | 62.7333 | 71.4667 | 75.2
2015-09-01 08:00 | 66.1333 | 63.4667 | 72.4667 | 76.5833
2015-09-01 08:15 | 66.6333 | 64.4667 | 73.4667 | 77.8333
2015-09-01 08:30 | 67.1333 | 65.4667 | 74.4667 | 79.0833
2015-09-01 08:45 | 67.6333 | 66.4667 | 75.4667 | 80.3333
2015-09-01 09:00 | 68.2 | 67.5833 | 76.8167 | 81.35
2015-09-01 09:15 | 68.95 | 68.8333 | 78.5667 | 82.1
2015-09-01 09:30 | 69.7 | 70.0833 | 80.3167 | 82.85
2015-09-01 09:45 | 70.45 | 71.3333 | 82.0667 | 83.6
2015-09-01 10:00 | 71.0667 | 72.35 | 83.5833 | 84.4667
2015-09-01 10:15 | 71.3167 | 73.1 | 84.8333 | 85.4667
2015-09-01 10:30 | 71.5667 | 73.85 | 86.0833 | 86.4667
2015-09-01 10:45 | 71.8167 | 74.6 | 87.3333 | 87.4667
2015-09-01 11:00 | 72.1333 | 75.5833 | 88.2333 | 88.35
2015-09-01 11:15 | 72.6333 | 76.8333 | 88.7333 | 89.1
2015-09-01 11:30 | 73.1333 | 78.0833 | 89.2333 | 89.85
2015-09-01 11:45 | 73.6333 | 79.3333 | 89.7333 | 90.6
2015-09-01 12:00 | 74 | 80.2333 | 90.2333 | 91.1167
2015-09-01 12:15 | 74 | 80.7333 | 90.7333 | 91.3667
2015-09-01 12:30 | 74 | 81.2333 | 91.2333 | 91.6167
2015-09-01 12:45 | 74 | 81.7333 | 91.7333 | 91.8667
2015-09-01 13:00 | 74.1333 | 81.65 | 92.1167 | 92.2333
2015-09-01 13:15 | 74.6333 | 80.9 | 92.3667 | 92.7333
2015-09-01 13:30 | 75.1333 | 80.15 | 92.6167 | 93.2333
2015-09-01 13:45 | 75.6333 | 79.4 | 92.8667 | 93.7333
2015-09-01 14:00 | 75.9333 | 79 | 93 | 94
2015-09-01 14:15 | 75.6833 | 79 | 93 | 94
2015-09-01 14:30 | 75.4333 | 79 | 93 | 94
2015-09-01 14:45 | 75.1833 | 79 | 93 | 94
2015-09-01 15:00 | 74.8667 | 79 | 93.1167 | 94.2333
2015-09-01 15:15 | 74.3667 | 79 | 93.3667 | 94.7333
2015-09-01 15:30 | 73.8667 | 79 | 93.6167 | 95.2333
2015-09-01 15:45 | 73.3667 | 79 | 93.8667 | 95.7333
2015-09-01 16:00 | 72.7333 | 78.7667 | 93.8833 | 95.7667
2015-09-01 16:15 | 71.7333 | 78.2667 | 93.6333 | 95.2667
2015-09-01 16:30 | 70.7333 | 77.7667 | 93.3833 | 94.7667
2015-09-01 16:45 | 69.7333 | 77.2667 | 93.1333 | 94.2667
2015-09-01 17:00 | 68.7333 | 76.3 | 92.7667 | 93.7667
2015-09-01 17:15 | 67.7333 | 74.8 | 92.2667 | 93.2667
2015-09-01 17:30 | 66.7333 | 73.3 | 91.7667 | 92.7667
2015-09-01 17:45 | 65.7333 | 71.8 | 91.2667 | 92.2667
2015-09-01 18:00 | 64.9333 | 70.5333 | 90.65 | 91.5333
2015-09-01 18:15 | 64.6833 | 69.5333 | 89.9 | 90.5333
2015-09-01 18:30 | 64.4333 | 68.5333 | 89.15 | 89.5333
2015-09-01 18:45 | 64.1833 | 67.5333 | 88.4 | 88.5333
2015-09-01 19:00 | 63.9333 | 66.65 | 87.65 | 87.7667
2015-09-01 19:15 | 63.6833 | 65.9 | 86.9 | 87.2667
2015-09-01 19:30 | 63.4333 | 65.15 | 86.15 | 86.7667
2015-09-01 19:45 | 63.1833 | 64.4 | 85.4 | 86.2667
2015-09-01 20:00 | 63 | 64 | 84.7667 | 85.4167
2015-09-01 20:15 | 63 | 64 | 84.2667 | 84.1667
2015-09-01 20:30 | 63 | 64 | 83.7667 | 82.9167
2015-09-01 20:45 | 63 | 64 | 83.2667 | 81.6667
2015-09-01 21:00 | 63 | 64 | 82.5333 | 80.65
2015-09-01 21:15 | 63 | 64 | 81.5333 | 79.9
2015-09-01 21:30 | 63 | 64 | 80.5333 | 79.15
2015-09-01 21:45 | 63 | 64 | 79.5333 | 78.4
2015-09-01 22:00 | 63 | 63.8833 | 78.7667 | 77.5333
2015-09-01 22:15 | 63 | 63.6333 | 78.2667 | 76.5333
2015-09-01 22:30 | 63 | 63.3833 | 77.7667 | 75.5333
2015-09-01 22:45 | 63 | 63.1333 | 77.2667 | 74.5333
2015-09-01 23:00 | 63 | 62.8833 | 76.8833 | 73.7667
2015-09-01 23:15 | 63 | 62.6333 | 76.6333 | 73.2667
2015-09-01 23:30 | 63 | 62.3833 | 76.3833 | 72.7667
2015-09-01 23:45 | 63 | 62.1333 | 76.1333 | 72.2667
2015-09-02 | 63 | 61.8833 | 75.7667 | 71.65
2015-09-02 00:15 | 63 | 61.6333 | 75.2667 | 70.9
2015-09-02 00:30 | 63 | 61.3833 | 74.7667 | 70.15
2015-09-02 00:45 | 63 | 61.1333 | 74.2667 | 69.4
2015-09-02 01:00 | 62.9333 | 60.8833 | 73.8833 | 69
2015-09-02 01:15 | 62.6833 | 60.6333 | 73.6333 | 69
2015-09-02 01:30 | 62.4333 | 60.3833 | 73.3833 | 69
2015-09-02 01:45 | 62.1833 | 60.1333 | 73.1333 | 69
2015-09-02 02:00 | 62.0667 | 60 | 72.8833 | 68.7667
2015-09-02 02:15 | 62.3167 | 60 | 72.6333 | 68.2667
2015-09-02 02:30 | 62.5667 | 60 | 72.3833 | 67.7667
2015-09-02 02:45 | 62.8167 | 60 | 72.1333 | 67.2667
2015-09-02 03:00 | 63 | 59.7667 | 71.8833 | 66.8833
2015-09-02 03:15 | 63 | 59.2667 | 71.6333 | 66.6333
2015-09-02 03:30 | 63 | 58.7667 | 71.3833 | 66.3833
2015-09-02 03:45 | 63 | 58.2667 | 71.1333 | 66.1333
2015-09-02 04:00 | 63 | 58 | 70.8833 | 65.7667
2015-09-02 04:15 | 63 | 58 | 70.6333 | 65.2667
2015-09-02 04:30 | 63 | 58 | 70.3833 | 64.7667
2015-09-02 04:45 | 63 | 58 | 70.1333 | 64.2667
2015-09-02 05:00 | 63 | 58 | 69.8833 | 64
2015-09-02 05:15 | 63 | 58 | 69.6333 | 64
2015-09-02 05:30 | 63 | 58 | 69.3833 | 64
2015-09-02 05:45 | 63 | 58 | 69.1333 | 64
2015-09-02 06:00 | 63 | 58.2333 | 69 | 64.2333
2015-09-02 06:15 | 63 | 58.7333 | 69 | 64.7333
2015-09-02 06:30 | 63 | 59.2333 | 69 | 65.2333
2015-09-02 06:45 | 63 | 59.7333 | 69 | 65.7333
2015-09-02 07:00 | 63 | 60.2333 | 69.35 | 66.5833
2015-09-02 07:15 | 63 | 60.7333 | 70.1 | 67.8333
2015-09-02 07:30 | 63 | 61.2333 | 70.85 | 69.0833
2015-09-02 07:45 | 63 | 61.7333 | 71.6 | 70.3333
2015-09-02 08:00 | 63.1333 | 62.35 | 72.5833 | 71.5833
2015-09-02 08:15 | 63.6333 | 63.1 | 73.8333 | 72.8333
2015-09-02 08:30 | 64.1333 | 63.85 | 75.0833 | 74.0833
2015-09-02 08:45 | 64.6333 | 64.6 | 76.3333 | 75.3333
2015-09-02 09:00 | 65.2 | 64.7812 | 77.7 | 76.4667
2015-09-02 09:15 | 65.95 | 64.3125 | 79.2 | 77.4667
2015-09-02 09:30 | 66.7 | 64.7143 | 80.7 | 78.4667
2015-09-02 09:45 | 67.45 | 66.8571 | 82.2 | 79.4667
2015-09-02 10:00 | 66.8571 | 68.35 | 83.35 | 80.35
2015-09-02 10:15 | 66.9057 | 69.1 | 84.1 | 81.1
2015-09-02 10:30 | 68.0377 | 69.85 | 84.85 | 81.85
2015-09-02 10:45 | 69.1698 | 70.6 | 85.6 | 82.6
2015-09-02 11:00 | 69.9333 | 71.35 | 86.2333 | 83.4667
2015-09-02 11:15 | 69.6833 | 72.1 | 86.7333 | 84.4667
2015-09-02 11:30 | 69.4333 | 72.85 | 87.2333 | 85.4667
2015-09-02 11:45 | 69.1833 | 73.6 | 87.7333 | 86.4667
2015-09-02 12:00 | 69.2 | 74.2333 | 88.2333 | 87.2333
2015-09-02 12:15 | 69.95 | 74.7333 | 88.7333 | 87.7333
2015-09-02 12:30 | 70.7 | 75.2333 | 89.2333 | 88.2333
2015-09-02 12:45 | 71.45 | 75.7333 | 89.7333 | 88.7333
2015-09-02 13:00 | 71.8667 | 76 | 90.35 | 89.1167
2015-09-02 13:15 | 71.3667 | 76 | 91.1 | 89.3667
2015-09-02 13:30 | 70.8667 | 76 | 91.85 | 89.6167
2015-09-02 13:45 | 70.3667 | 76 | 92.6 | 89.8667
2015-09-02 14:00 | 70 | 75.7667 | 93 | 90.2333
2015-09-02 14:15 | 70 | 75.2667 | 93 | 90.7333
2015-09-02 14:30 | 70 | 74.7667 | 93 | 91.2333
2015-09-02 14:45 | 70 | 74.2667 | 93 | 91.7333
2015-09-02 15:00 | 68.9333 | 73.8833 | 93.1167 | 91.8833
2015-09-02 15:15 | 68.6833 | 73.6333 | 93.3667 | 91.6333
2015-09-02 15:30 | 68.4333 | 73.3833 | 93.6167 | 91.3833
2015-09-02 15:45 | 68.1833 | 73.1333 | 93.8667 | 91.1333
2015-09-02 16:00 | 67.9333 | 72.7667 | 93.7667 | 90.8833
2015-09-02 16:15 | 67.6833 | 72.2667 | 93.2667 | 90.6333
2015-09-02 16:30 | 67.4333 | 71.7667 | 92.7667 | 90.3833
2015-09-02 16:45 | 67.1833 | 71.2667 | 92.2667 | 90.1333
2015-09-02 17:00 | 66.8667 | 70.7667 | 91.8833 | 89.7667
2015-09-02 17:15 | 66.3667 | 70.2667 | 91.6333 | 89.2667
2015-09-02 17:30 | 65.8667 | 69.7667 | 91.3833 | 88.7667
2015-09-02 17:45 | 65.3667 | 69.2667 | 91.1333 | 88.2667
2015-09-02 18:00 | 64.9333 | 68.7667 | 90.65 | 87.4167
2015-09-02 18:15 | 64.6833 | 68.2667 | 89.9 | 86.1667
2015-09-02 18:30 | 64.4333 | 67.7667 | 89.15 | 84.9167
2015-09-02 18:45 | 64.1833 | 67.2667 | 88.4 | 83.6667
2015-09-02 19:00 | 63.9333 | 66.7667 | 87.5333 | 82.65
2015-09-02 19:15 | 63.6833 | 66.2667 | 86.5333 | 81.9
2015-09-02 19:30 | 63.4333 | 65.7667 | 85.5333 | 81.15
2015-09-02 19:45 | 63.1833 | 65.2667 | 84.5333 | 80.4
2015-09-02 20:00 | 63 | 64.8833 | 83.7667 | 79.5333
2015-09-02 20:15 | 63 | 64.6333 | 83.2667 | 78.5333
2015-09-02 20:30 | 63 | 64.3833 | 82.7667 | 77.5333
2015-09-02 20:45 | 63 | 64.1333 | 82.2667 | 76.5333
2015-09-02 21:00 | 63 | 64.1167 | 81.7667 | 75.7667
2015-09-02 21:15 | 63 | 64.3667 | 81.2667 | 75.2667
2015-09-02 21:30 | 63 | 64.6167 | 80.7667 | 74.7667
2015-09-02 21:45 | 63 | 64.8667 | 80.2667 | 74.2667
2015-09-02 22:00 | 62.9333 | 65 | 79.5333 | 73.65
2015-09-02 22:15 | 62.6833 | 65 | 78.5333 | 72.9
2015-09-02 22:30 | 62.4333 | 65 | 77.5333 | 72.15
2015-09-02 22:45 | 62.1833 | 65 | 76.5333 | 71.4
2015-09-02 23:00 | 62 | 64.7667 | 75.7667 | 70.65
2015-09-02 23:15 | 62 | 64.2667 | 75.2667 | 69.9
2015-09-02 23:30 | 62 | 63.7667 | 74.7667 | 69.15
2015-09-02 23:45 | 62 | 63.2667 | 74.2667 | 68.4
2015-09-03 | 61.9333 | 62.7667 | 73.7667 | 68
2015-09-03 00:15 | 61.6833 | 62.2667 | 73.2667 | 68
2015-09-03 00:30 | 61.4333 | 61.7667 | 72.7667 | 68
2015-09-03 00:45 | 61.1833 | 61.2667 | 72.2667 | 68
2015-09-03 01:00 | 61 | 61 | 71.7667 | 67.8833
2015-09-03 01:15 | 61 | 61 | 71.2667 | 67.6333
2015-09-03 01:30 | 61 | 61 | 70.7667 | 67.3833
2015-09-03 01:45 | 61 | 61 | 70.2667 | 67.1333
2015-09-03 02:00 | 61 | 60.7667 | 70 | 66.8833
2015-09-03 02:15 | 61 | 60.2667 | 70 | 66.6333
2015-09-03 02:30 | 61 | 59.7667 | 70 | 66.3833
2015-09-03 02:45 | 61 | 59.2667 | 70 | 66.1333
2015-09-03 03:00 | 61 | 59 | 70 | 65.7667
2015-09-03 03:15 | 61 | 59 | 70 | 65.2667
2015-09-03 03:30 | 61 | 59 | 70 | 64.7667
2015-09-03 03:45 | 61 | 59 | 70 | 64.2667
2015-09-03 04:00 | 61 | 58.8833 | 70 | 63.8833
2015-09-03 04:15 | 61 | 58.6333 | 70 | 63.6333
2015-09-03 04:30 | 61 | 58.3833 | 70 | 63.3833
2015-09-03 04:45 | 61 | 58.1333 | 70 | 63.1333
2015-09-03 05:00 | 61 | 58.1167 | 70 | 63
2015-09-03 05:15 | 61 | 58.3667 | 70 | 63
2015-09-03 05:30 | 61 | 58.6167 | 70 | 63
2015-09-03 05:45 | 61 | 58.8667 | 70 | 63
2015-09-03 06:00 | 61.0667 | 59.2333 | 70 | 63.2333
2015-09-03 06:15 | 61.3167 | 59.7333 | 70 | 63.7333
2015-09-03 06:30 | 61.5667 | 60.2333 | 70 | 64.2333
2015-09-03 06:45 | 61.8167 | 60.7333 | 70 | 64.7333
2015-09-03 07:00 | 62.0667 | 61.35 | 70.5833 | 65.4667
2015-09-03 07:15 | 62.3167 | 62.1 | 71.8333 | 66.4667
2015-09-03 07:30 | 62.5667 | 62.85 | 73.0833 | 67.4667
2015-09-03 07:45 | 62.8167 | 63.6 | 74.3333 | 68.4667
2015-09-03 08:00 | 63.1333 | 64.35 | 75.4667 | 69.35
2015-09-03 08:15 | 63.6333 | 65.1 | 76.4667 | 70.1
2015-09-03 08:30 | 64.1333 | 65.85 | 77.4667 | 70.85
2015-09-03 08:45 | 64.6333 | 66.6 | 78.4667 | 71.6
2015-09-03 09:00 | 65.1333 | 67.2333 | 79.5833 | 72.5833
2015-09-03 09:15 | 65.6333 | 67.7333 | 80.8333 | 73.8333
2015-09-03 09:30 | 66.1333 | 68.2333 | 82.0833 | 75.0833
2015-09-03 09:45 | 66.6333 | 68.7333 | 83.3333 | 76.3333
2015-09-03 10:00 | 67 | 69.2333 | 84.4667 | 77.1167
2015-09-03 10:15 | 67 | 69.7333 | 85.4667 | 77.3667
2015-09-03 10:30 | 67 | 70.2333 | 86.4667 | 77.6167
2015-09-03 10:45 | 67 | 70.7333 | 87.4667 | 77.8667
2015-09-03 11:00 | 67 | 71.1167 | 88.35 | 78.35
2015-09-03 11:15 | 67 | 71.3667 | 89.1 | 79.1
2015-09-03 11:30 | 67 | 71.6167 | 89.85 | 79.85
2015-09-03 11:45 | 67 | 71.8667 | 90.6 | 80.6
2015-09-03 12:00 | 67 | 72.1167 | 91 | 81.35
2015-09-03 12:15 | 67 | 72.3667 | 91 | 82.1
2015-09-03 12:30 | 67 | 72.6167 | 91 | 82.85
2015-09-03 12:45 | 67 | 72.8667 | 91 | 83.6
2015-09-03 13:00 | 67 | 73.1167 | 91.2333 | 84.1167
2015-09-03 13:15 | 67 | 73.3667 | 91.7333 | 84.3667
2015-09-03 13:30 | 67 | 73.6167 | 92.2333 | 84.6167
2015-09-03 13:45 | 67 | 73.8667 | 92.7333 | 84.8667
2015-09-03 14:00 | 66.9333 | 73.8833 | 93.1167 | 85.2333
2015-09-03 14:15 | 66.6833 | 73.6333 | 93.3667 | 85.7333
2015-09-03 14:30 | 66.4333 | 73.3833 | 93.6167 | 86.2333
2015-09-03 14:45 | 66.1833 | 73.1333 | 93.8667 | 86.7333
2015-09-03 15:00 | 66 | 72.8833 | 94 | 87
2015-09-03 15:15 | 66 | 72.6333 | 94 | 87
2015-09-03 15:30 | 66 | 72.3833 | 94 | 87
2015-09-03 15:45 | 66 | 72.1333 | 94 | 87
2015-09-03 16:00 | 65.8667 | 71.7667 | 93.8833 | 86.8833
2015-09-03 16:15 | 65.3667 | 71.2667 | 93.6333 | 86.6333
2015-09-03 16:30 | 64.8667 | 70.7667 | 93.3833 | 86.3833
2015-09-03 16:45 | 64.3667 | 70.2667 | 93.1333 | 86.1333
2015-09-03 17:00 | 63.8667 | 69.65 | 92.8833 | 85.7667
2015-09-03 17:15 | 63.3667 | 68.9 | 92.6333 | 85.2667
2015-09-03 17:30 | 62.8667 | 68.15 | 92.3833 | 84.7667
2015-09-03 17:45 | 62.3667 | 67.4 | 92.1333 | 84.2667
2015-09-03 18:00 | 61.9333 | 66.5333 | 91.5333 | 83.65
2015-09-03 18:15 | 61.6833 | 65.5333 | 90.5333 | 82.9
2015-09-03 18:30 | 61.4333 | 64.5333 | 89.5333 | 82.15
2015-09-03 18:45 | 61.1833 | 63.5333 | 88.5333 | 81.4
2015-09-03 19:00 | 61 | 62.7667 | 87.7667 | 80.5333
2015-09-03 19:15 | 61 | 62.2667 | 87.2667 | 79.5333
2015-09-03 19:30 | 61 | 61.7667 | 86.7667 | 78.5333
2015-09-03 19:45 | 61 | 61.2667 | 86.2667 | 77.5333
2015-09-03 20:00 | 60.9333 | 61.2333 | 85.65 | 76.65
2015-09-03 20:15 | 60.6833 | 61.7333 | 84.9 | 75.9
2015-09-03 20:30 | 60.4333 | 62.2333 | 84.15 | 75.15
2015-09-03 20:45 | 60.1833 | 62.7333 | 83.4 | 74.4
2015-09-03 21:00 | 60 | 62.8833 | 82.65 | 73.7667
2015-09-03 21:15 | 60 | 62.6333 | 81.9 | 73.2667
2015-09-03 21:30 | 60 | 62.3833 | 81.15 | 72.7667
2015-09-03 21:45 | 60 | 62.1333 | 80.4 | 72.2667
2015-09-03 22:00 | 60 | 61.7667 | 79.65 | 71.7667
2015-09-03 22:15 | 60 | 61.2667 | 78.9 | 71.2667
2015-09-03 22:30 | 60 | 60.7667 | 78.15 | 70.7667
2015-09-03 22:45 | 60 | 60.2667 | 77.4 | 70.2667
2015-09-03 23:00 | 59.9333 | 59.5333 | 76.7667 | 69.65
2015-09-03 23:15 | 59.6833 | 58.5333 | 76.2667 | 68.9
2015-09-03 23:30 | 59.4333 | 57.5333 | 75.7667 | 68.15
2015-09-03 23:45 | 59.1833 | 56.5333 | 75.2667 | 67.4
2015-09-04 | 59 | 56.2333 | 74.7667 | 66.8833
2015-09-04 00:15 | 59 | 56.7333 | 74.2667 | 66.6333
2015-09-04 00:30 | 59 | 57.2333 | 73.7667 | 66.3833
2015-09-04 00:45 | 59 | 57.7333 | 73.2667 | 66.1333
2015-09-04 01:00 | 58.9333 | 57.8833 | 72.8833 | 65.7667
2015-09-04 01:15 | 58.6833 | 57.6333 | 72.6333 | 65.2667
2015-09-04 01:30 | 58.4333 | 57.3833 | 72.3833 | 64.7667
2015-09-04 01:45 | 58.1833 | 57.1333 | 72.1333 | 64.2667
2015-09-04 02:00 | 57.9333 | 57 | 72 | 63.8833
2015-09-04 02:15 | 57.6833 | 57 | 72 | 63.6333
2015-09-04 02:30 | 57.4333 | 57 | 72 | 63.3833
2015-09-04 02:45 | 57.1833 | 57 | 72 | 63.1333
2015-09-04 03:00 | 57 | 56.8833 | 72 | 62.8833
2015-09-04 03:15 | 57 | 56.6333 | 72 | 62.6333
2015-09-04 03:30 | 57 | 56.3833 | 72 | 62.3833
2015-09-04 03:45 | 57 | 56.1333 | 72 | 62.1333
2015-09-04 04:00 | 57 | 56 | 72 | 62
2015-09-04 04:15 | 57 | 56 | 72 | 62
2015-09-04 04:30 | 57 | 56 | 72 | 62
2015-09-04 04:45 | 57 | 56 | 72 | 62
2015-09-04 05:00 | 56.9333 | 55.8833 | 71.7667 | 61.8833
2015-09-04 05:15 | 56.6833 | 55.6333 | 71.2667 | 61.6333
2015-09-04 05:30 | 56.4333 | 55.3833 | 70.7667 | 61.3833
2015-09-04 05:45 | 56.1833 | 55.1333 | 70.2667 | 61.1333
2015-09-04 06:00 | 56.1333 | 55.2333 | 70 | 61.35
2015-09-04 06:15 | 56.6333 | 55.7333 | 70 | 62.1
2015-09-04 06:30 | 57.1333 | 56.2333 | 70 | 62.85
2015-09-04 06:45 | 57.6333 | 56.7333 | 70 | 63.6
2015-09-04 07:00 | 58.1333 | 57.35 | 70.5833 | 64.4667
2015-09-04 07:15 | 58.6333 | 58.1 | 71.8333 | 65.4667
2015-09-04 07:30 | 59.1333 | 58.85 | 73.0833 | 66.4667
2015-09-04 07:45 | 59.6333 | 59.6 | 74.3333 | 67.4667
2015-09-04 08:00 | 60.2 | 60.35 | 75.7 | 68.35
2015-09-04 08:15 | 60.95 | 61.1 | 77.2 | 69.1
2015-09-04 08:30 | 61.7 | 61.85 | 78.7 | 69.85
2015-09-04 08:45 | 62.45 | 62.6 | 80.2 | 70.6
2015-09-04 09:00 | 63.1333 | 63.35 | 81.7 | 71.4667
2015-09-04 09:15 | 63.6333 | 64.1 | 83.2 | 72.4667
2015-09-04 09:30 | 64.1333 | 64.85 | 84.7 | 73.4667
2015-09-04 09:45 | 64.6333 | 65.6 | 86.2 | 74.4667
2015-09-04 10:00 | 65.1333 | 66.5833 | 87.35 | 75.4667
2015-09-04 10:15 | 65.6333 | 67.8333 | 88.1 | 76.4667
2015-09-04 10:30 | 66.1333 | 69.0833 | 88.85 | 77.4667
2015-09-04 10:45 | 66.6333 | 70.3333 | 89.6 | 78.4667
2015-09-04 11:00 | 67 | 71.1167 | 90.1167 | 79.35
2015-09-04 11:15 | 67 | 71.3667 | 90.3667 | 80.1
2015-09-04 11:30 | 67 | 71.6167 | 90.6167 | 80.85
2015-09-04 11:45 | 67 | 71.8667 | 90.8667 | 81.6
2015-09-04 12:00 | 67.0667 | 72.2333 | 91.2333 | 82.2333
2015-09-04 12:15 | 67.3167 | 72.7333 | 91.7333 | 82.7333
2015-09-04 12:30 | 67.5667 | 73.2333 | 92.2333 | 83.2333
2015-09-04 12:45 | 67.8167 | 73.7333 | 92.7333 | 83.7333
2015-09-04 13:00 | 68 | 74.1167 | 93.2333 | 84.2333
2015-09-04 13:15 | 68 | 74.3667 | 93.7333 | 84.7333
2015-09-04 13:30 | 68 | 74.6167 | 94.2333 | 85.2333
2015-09-04 13:45 | 68 | 74.8667 | 94.7333 | 85.7333
2015-09-04 14:00 | 67.8667 | 74.8833 | 95.1167 | 86
2015-09-04 14:15 | 67.3667 | 74.6333 | 95.3667 | 86
2015-09-04 14:30 | 66.8667 | 74.3833 | 95.6167 | 86
2015-09-04 14:45 | 66.3667 | 74.1333 | 95.8667 | 86
2015-09-04 15:00 | 65.9333 | 73.7667 | 95.8833 | 86
2015-09-04 15:15 | 65.6833 | 73.2667 | 95.6333 | 86
2015-09-04 15:30 | 65.4333 | 72.7667 | 95.3833 | 86
2015-09-04 15:45 | 65.1833 | 72.2667 | 95.1333 | 86
2015-09-04 16:00 | 64.8667 | 71.65 | 94.8833 | 85.8833
2015-09-04 16:15 | 64.3667 | 70.9 | 94.6333 | 85.6333
2015-09-04 16:30 | 63.8667 | 70.15 | 94.3833 | 85.3833
2015-09-04 16:45 | 63.3667 | 69.4 | 94.1333 | 85.1333
2015-09-04 17:00 | 62.8667 | 68.5333 | 93.7667 | 84.7667
2015-09-04 17:15 | 62.3667 | 67.5333 | 93.2667 | 84.2667
2015-09-04 17:30 | 61.8667 | 66.5333 | 92.7667 | 83.7667
2015-09-04 17:45 | 61.3667 | 65.5333 | 92.2667 | 83.2667
2015-09-04 18:00 | 60.9333 | 64.7667 | 91.65 | 82.5333
2015-09-04 18:15 | 60.6833 | 64.2667 | 90.9 | 81.5333
2015-09-04 18:30 | 60.4333 | 63.7667 | 90.15 | 80.5333
2015-09-04 18:45 | 60.1833 | 63.2667 | 89.4 | 79.5333
2015-09-04 19:00 | 59.9333 | 62.8833 | 88.65 | 78.4167
2015-09-04 19:15 | 59.6833 | 62.6333 | 87.9 | 77.1667
2015-09-04 19:30 | 59.4333 | 62.3833 | 87.15 | 75.9167
2015-09-04 19:45 | 59.1833 | 62.1333 | 86.4 | 74.6667
2015-09-04 20:00 | 59 | 62 | 85.8833 | 73.5333
2015-09-04 20:15 | 59 | 62 | 85.6333 | 72.5333
2015-09-04 20:30 | 59 | 62 | 85.3833 | 71.5333
2015-09-04 20:45 | 59 | 62 | 85.1333 | 70.5333
2015-09-04 21:00 | 58.9333 | 61.7667 | 84.7667 | 69.65
2015-09-04 21:15 | 58.6833 | 61.2667 | 84.2667 | 68.9
2015-09-04 21:30 | 58.4333 | 60.7667 | 83.7667 | 68.15
2015-09-04 21:45 | 58.1833 | 60.2667 | 83.2667 | 67.4
2015-09-04 22:00 | 58 | 60.1167 | 82.7667 | 66.7667
2015-09-04 22:15 | 58 | 60.3667 | 82.2667 | 66.2667
2015-09-04 22:30 | 58 | 60.6167 | 81.7667 | 65.7667
2015-09-04 22:45 | 58 | 60.8667 | 81.2667 | 65.2667
2015-09-04 23:00 | 57.9333 | 60.7667 | 80.8833 | 64.7667
2015-09-04 23:15 | 57.6833 | 60.2667 | 80.6333 | 64.2667
2015-09-04 23:30 | 57.4333 | 59.7667 | 80.3833 | 63.7667
2015-09-04 23:45 | 57.1833 | 59.2667 | 80.1333 | 63.2667
2015-09-05 | 57.0667 | 58.4167 | 79.8833 | 62.8833
2015-09-05 00:15 | 57.3167 | 57.1667 | 79.6333 | 62.6333
2015-09-05 00:30 | 57.5667 | 55.9167 | 79.3833 | 62.3833
2015-09-05 00:45 | 57.8167 | 54.6667 | 79.1333 | 62.1333
2015-09-05 01:00 | 57.8 | 54.2333 | 78.8833 | 61.7667
2015-09-05 01:15 | 57.05 | 54.7333 | 78.6333 | 61.2667
2015-09-05 01:30 | 56.3 | 55.2333 | 78.3833 | 60.7667
2015-09-05 01:45 | 55.55 | 55.7333 | 78.1333 | 60.2667
2015-09-05 02:00 | 55 | 55.7667 | 77.8833 | 59.8833
2015-09-05 02:15 | 55 | 55.2667 | 77.6333 | 59.6333
2015-09-05 02:30 | 55 | 54.7667 | 77.3833 | 59.3833
2015-09-05 02:45 | 55 | 54.2667 | 77.1333 | 59.1333
2015-09-05 03:00 | 54.9333 | 54 | 76.7667 | 58.8833
2015-09-05 03:15 | 54.6833 | 54 | 76.2667 | 58.6333
2015-09-05 03:30 | 54.4333 | 54 | 75.7667 | 58.3833
2015-09-05 03:45 | 54.1833 | 54 | 75.2667 | 58.1333
2015-09-05 04:00 | 54 | 53.8833 | 74.8833 | 57.8833
2015-09-05 04:15 | 54 | 53.6333 | 74.6333 | 57.6333
2015-09-05 04:30 | 54 | 53.3833 | 74.3833 | 57.3833
2015-09-05 04:45 | 54 | 53.1333 | 74.1333 | 57.1333
2015-09-05 05:00 | 54 | 53 | 73.8833 | 56.8833
2015-09-05 05:15 | 54 | 53 | 73.6333 | 56.6333
2015-09-05 05:30 | 54 | 53 | 73.3833 | 56.3833
2015-09-05 05:45 | 54 | 53 | 73.1333 | 56.1333
2015-09-05 06:00 | 54.2667 | 53.2333 | 73 | 56.2333
2015-09-05 06:15 | 55.2667 | 53.7333 | 73 | 56.7333
2015-09-05 06:30 | 56.2667 | 54.2333 | 73 | 57.2333
2015-09-05 06:45 | 57.2667 | 54.7333 | 73 | 57.7333
2015-09-05 07:00 | 58.2 | 55.4667 | 73.35 | 58.4667
2015-09-05 07:15 | 58.95 | 56.4667 | 74.1 | 59.4667
2015-09-05 07:30 | 59.7 | 57.4667 | 74.85 | 60.4667
2015-09-05 07:45 | 60.45 | 58.4667 | 75.6 | 61.4667
2015-09-05 08:00 | 61.2 | 59.4667 | 76.35 | 62.7
2015-09-05 08:15 | 61.95 | 60.4667 | 77.1 | 64.2
2015-09-05 08:30 | 62.7 | 61.4667 | 77.85 | 65.7
2015-09-05 08:45 | 63.45 | 62.4667 | 78.6 | 67.2
2015-09-05 09:00 | 64.2 | 63.5833 | 79.5833 | 68.35
2015-09-05 09:15 | 64.95 | 64.8333 | 80.8333 | 69.1
2015-09-05 09:30 | 65.7 | 66.0833 | 82.0833 | 69.85
2015-09-05 09:45 | 66.45 | 67.3333 | 83.3333 | 70.6
2015-09-05 10:00 | 67.2 | 68.35 | 84.4667 | 71.35
2015-09-05 10:15 | 67.95 | 69.1 | 85.4667 | 72.1
2015-09-05 10:30 | 68.7 | 69.85 | 86.4667 | 72.85
2015-09-05 10:45 | 69.45 | 70.6 | 87.4667 | 73.6
2015-09-05 11:00 | 70.1333 | 71.35 | 88.35 | 74.4667
2015-09-05 11:15 | 70.6333 | 72.1 | 89.1 | 75.4667
2015-09-05 11:30 | 71.1333 | 72.85 | 89.85 | 76.4667
2015-09-05 11:45 | 71.6333 | 73.6 | 90.6 | 77.4667
2015-09-05 12:00 | 72.2667 | 74.35 | 91.2333 | 78.4667
2015-09-05 12:15 | 73.2667 | 75.1 | 91.7333 | 79.4667
2015-09-05 12:30 | 74.2667 | 75.85 | 92.2333 | 80.4667
2015-09-05 12:45 | 75.2667 | 76.6 | 92.7333 | 81.4667
2015-09-05 13:00 | 76 | 77.1167 | 93.2333 | 82.2333
2015-09-05 13:15 | 76 | 77.3667 | 93.7333 | 82.7333
2015-09-05 13:30 | 76 | 77.6167 | 94.2333 | 83.2333
2015-09-05 13:45 | 76 | 77.8667 | 94.7333 | 83.7333
2015-09-05 14:00 | 75.8 | 78.2333 | 95.1167 | 84.1167
2015-09-05 14:15 | 75.05 | 78.7333 | 95.3667 | 84.3667
2015-09-05 14:30 | 74.3 | 79.2333 | 95.6167 | 84.6167
2015-09-05 14:45 | 73.55 | 79.7333 | 95.8667 | 84.8667
2015-09-05 15:00 | 73 | 79.7667 | 96 | 85
2015-09-05 15:15 | 73 | 79.2667 | 96 | 85
2015-09-05 15:30 | 73 | 78.7667 | 96 | 85
2015-09-05 15:45 | 73 | 78.2667 | 96 | 85
2015-09-05 16:00 | 72.8667 | 77.5333 | 95.8833 | 84.8833
2015-09-05 16:15 | 72.3667 | 76.5333 | 95.6333 | 84.6333
2015-09-05 16:30 | 71.8667 | 75.5333 | 95.3833 | 84.3833
2015-09-05 16:45 | 71.3667 | 74.5333 | 95.1333 | 84.1333
2015-09-05 17:00 | 70.8 | 73.65 | 94.7667 | 83.7667
2015-09-05 17:15 | 70.05 | 72.9 | 94.2667 | 83.2667
2015-09-05 17:30 | 69.3 | 72.15 | 93.7667 | 82.7667
2015-09-05 17:45 | 68.55 | 71.4 | 93.2667 | 82.2667
2015-09-05 18:00 | 67.7333 | 70.7667 | 92.65 | 81.65
2015-09-05 18:15 | 66.7333 | 70.2667 | 91.9 | 80.9
2015-09-05 18:30 | 65.7333 | 69.7667 | 91.15 | 80.15
2015-09-05 18:45 | 64.7333 | 69.2667 | 90.4 | 79.4
2015-09-05 19:00 | 63.8667 | 68.7667 | 89.65 | 78.7667
2015-09-05 19:15 | 63.3667 | 68.2667 | 88.9 | 78.2667
2015-09-05 19:30 | 62.8667 | 67.7667 | 88.15 | 77.7667
2015-09-05 19:45 | 62.3667 | 67.2667 | 87.4 | 77.2667
2015-09-05 20:00 | 62 | 66.8833 | 86.7667 | 76.7667
2015-09-05 20:15 | 62 | 66.6333 | 86.2667 | 76.2667
2015-09-05 20:30 | 62 | 66.3833 | 85.7667 | 75.7667
2015-09-05 20:45 | 62 | 66.1333 | 85.2667 | 75.2667
2015-09-05 21:00 | 62.1333 | 65.8833 | 84.8833 | 74.7667
2015-09-05 21:15 | 62.6333 | 65.6333 | 84.6333 | 74.2667
2015-09-05 21:30 | 63.1333 | 65.3833 | 84.3833 | 73.7667
2015-09-05 21:45 | 63.6333 | 65.1333 | 84.1333 | 73.2667
2015-09-05 22:00 | 63.8667 | 64.8833 | 83.7667 | 72.5333
2015-09-05 22:15 | 63.3667 | 64.6333 | 83.2667 | 71.5333
2015-09-05 22:30 | 62.8667 | 64.3833 | 82.7667 | 70.5333
2015-09-05 22:45 | 62.3667 | 64.1333 | 82.2667 | 69.5333
2015-09-05 23:00 | 62 | 63.4167 | 81.7667 | 68.65
2015-09-05 23:15 | 62 | 62.1667 | 81.2667 | 67.9
2015-09-05 23:30 | 62 | 60.9167 | 80.7667 | 67.15
2015-09-05 23:45 | 62 | 59.6667 | 80.2667 | 66.4
2015-09-06 | 61.8667 | 59 | 79.8833 | 65.7667
2015-09-06 00:15 | 61.3667 | 59 | 79.6333 | 65.2667
2015-09-06 00:30 | 60.8667 | 59 | 79.3833 | 64.7667
2015-09-06 00:45 | 60.3667 | 59 | 79.1333 | 64.2667
2015-09-06 01:00 | 60 | 58.65 | 78.8833 | 63.8833
2015-09-06 01:15 | 60 | 57.9 | 78.6333 | 63.6333
2015-09-06 01:30 | 60 | 57.15 | 78.3833 | 63.3833
2015-09-06 01:45 | 60 | 56.4 | 78.1333 | 63.1333
2015-09-06 02:00 | 59.8 | 56 | 77.8833 | 62.8833
2015-09-06 02:15 | 59.05 | 56 | 77.6333 | 62.6333
2015-09-06 02:30 | 58.3 | 56 | 77.3833 | 62.3833
2015-09-06 02:45 | 57.55 | 56 | 77.1333 | 62.1333
2015-09-06 03:00 | 56.9333 | 55.65 | 76.8833 | 61.8833
2015-09-06 03:15 | 56.6833 | 54.9 | 76.6333 | 61.6333
2015-09-06 03:30 | 56.4333 | 54.15 | 76.3833 | 61.3833
2015-09-06 03:45 | 56.1833 | 53.4 | 76.1333 | 61.1333
2015-09-06 04:00 | 56.0667 | 53 | 75.8833 | 60.65
2015-09-06 04:15 | 56.3167 | 53 | 75.6333 | 59.9
2015-09-06 04:30 | 56.5667 | 53 | 75.3833 | 59.15
2015-09-06 04:45 | 56.8167 | 53 | 75.1333 | 58.4
2015-09-06 05:00 | 57 | 53.1167 | 74.8833 | 58.1167
2015-09-06 05:15 | 57 | 53.3667 | 74.6333 | 58.3667
2015-09-06 05:30 | 57 | 53.6167 | 74.3833 | 58.6167
2015-09-06 05:45 | 57 | 53.8667 | 74.1333 | 58.8667
2015-09-06 06:00 | 57.2 | 54.4667 | 73.8833 | 59.35
2015-09-06 06:15 | 57.95 | 55.4667 | 73.6333 | 60.1
2015-09-06 06:30 | 58.7 | 56.4667 | 73.3833 | 60.85
2015-09-06 06:45 | 59.45 | 57.4667 | 73.1333 | 61.6
2015-09-06 07:00 | 60.3333 | 58.4667 | 73.35 | 62.7
2015-09-06 07:15 | 61.5833 | 59.4667 | 74.1 | 64.2
2015-09-06 07:30 | 62.8333 | 60.4667 | 74.85 | 65.7
2015-09-06 07:45 | 64.0833 | 61.4667 | 75.6 | 67.2
2015-09-06 08:00 | 65.1333 | 62.8167 | 76.4667 | 68.5833
2015-09-06 08:15 | 65.6333 | 64.5667 | 77.4667 | 69.8333
2015-09-06 08:30 | 66.1333 | 66.3167 | 78.4667 | 71.0833
2015-09-06 08:45 | 66.6333 | 68.0667 | 79.4667 | 72.3333
2015-09-06 09:00 | 67.1333 | 69.5833 | 80.5833 | 73.5833
2015-09-06 09:15 | 67.6333 | 70.8333 | 81.8333 | 74.8333
2015-09-06 09:30 | 68.1333 | 72.0833 | 83.0833 | 76.0833
2015-09-06 09:45 | 68.6333 | 73.3333 | 84.3333 | 77.3333
2015-09-06 10:00 | 69.1333 | 74.5833 | 85.4667 | 78.2333
2015-09-06 10:15 | 69.6333 | 75.8333 | 86.4667 | 78.7333
2015-09-06 10:30 | 70.1333 | 77.0833 | 87.4667 | 79.2333
2015-09-06 10:45 | 70.6333 | 78.3333 | 88.4667 | 79.7333
2015-09-06 11:00 | 71.2 | 79.35 | 89.35 | 80.5833
2015-09-06 11:15 | 71.95 | 80.1 | 90.1 | 81.8333
2015-09-06 11:30 | 72.7 | 80.85 | 90.85 | 83.0833
2015-09-06 11:45 | 73.45 | 81.6 | 91.6 | 84.3333
2015-09-06 12:00 | 74.5333 | 82.35 | 92.1167 | 85.2333
2015-09-06 12:15 | 76.5333 | 83.1 | 92.3667 | 85.7333
2015-09-06 12:30 | 78.5333 | 83.85 | 92.6167 | 86.2333
2015-09-06 12:45 | 80.5333 | 84.6 | 92.8667 | 86.7333
2015-09-06 13:00 | 82.2 | 85 | 93 | 87.2333
2015-09-06 13:15 | 82.95 | 85 | 93 | 87.7333
2015-09-06 13:30 | 83.7 | 85 | 93 | 88.2333
2015-09-06 13:45 | 84.45 | 85 | 93 | 88.7333
2015-09-06 14:00 | 84.8667 | 85 | 93.35 | 89.1167
2015-09-06 14:15 | 84.3667 | 85 | 94.1 | 89.3667
2015-09-06 14:30 | 83.8667 | 85 | 94.85 | 89.6167
2015-09-06 14:45 | 83.3667 | 85 | 95.6 | 89.8667
2015-09-06 15:00 | 82.8 | 85 | 96 | 90
2015-09-06 15:15 | 82.05 | 85 | 96 | 90
2015-09-06 15:30 | 81.3 | 85 | 96 | 90
2015-09-06 15:45 | 80.55 | 85 | 96 | 90
2015-09-06 16:00 | 79.8 | 84.7667 | 95.8833 | 90
2015-09-06 16:15 | 79.05 | 84.2667 | 95.6333 | 90
2015-09-06 16:30 | 78.3 | 83.7667 | 95.3833 | 90
2015-09-06 16:45 | 77.55 | 83.2667 | 95.1333 | 90
2015-09-06 17:00 | 76.5333 | 82.7667 | 94.65 | 89.65
2015-09-06 17:15 | 74.7833 | 82.2667 | 93.9 | 88.9
2015-09-06 17:30 | 73.0333 | 81.7667 | 93.15 | 88.15
2015-09-06 17:45 | 71.2833 | 81.2667 | 92.4 | 87.4
2015-09-06 18:00 | 69.6667 | 80.3 | 91.7667 | 86.4167
2015-09-06 18:15 | 68.4167 | 78.8 | 91.2667 | 85.1667
2015-09-06 18:30 | 67.1667 | 77.3 | 90.7667 | 83.9167
2015-09-06 18:45 | 65.9167 | 75.8 | 90.2667 | 82.6667
2015-09-06 19:00 | 64.8667 | 74.5333 | 89.65 | 81.65
2015-09-06 19:15 | 64.3667 | 73.5333 | 88.9 | 80.9
2015-09-06 19:30 | 63.8667 | 72.5333 | 88.15 | 80.15
2015-09-06 19:45 | 63.3667 | 71.5333 | 87.4 | 79.4
2015-09-06 20:00 | 63.0667 | 70.7667 | 86.7667 | 78.65
2015-09-06 20:15 | 63.3167 | 70.2667 | 86.2667 | 77.9
2015-09-06 20:30 | 63.5667 | 69.7667 | 85.7667 | 77.15
2015-09-06 20:45 | 63.8167 | 69.2667 | 85.2667 | 76.4
2015-09-06 21:00 | 64 | 68.8833 | 84.8833 | 75.65
2015-09-06 21:15 | 64 | 68.6333 | 84.6333 | 74.9
2015-09-06 21:30 | 64 | 68.3833 | 84.3833 | 74.15
2015-09-06 21:45 | 64 | 68.1333 | 84.1333 | 73.4
2015-09-06 22:00 | 63.8667 | 67.7667 | 83.7667 | 73
2015-09-06 22:15 | 63.3667 | 67.2667 | 83.2667 | 73
2015-09-06 22:30 | 62.8667 | 66.7667 | 82.7667 | 73
2015-09-06 22:45 | 62.3667 | 66.2667 | 82.2667 | 73
2015-09-06 23:00 | 61.8667 | 65.7667 | 81.8833 | 72.4167
2015-09-06 23:15 | 61.3667 | 65.2667 | 81.6333 | 71.1667
2015-09-06 23:30 | 60.8667 | 64.7667 | 81.3833 | 69.9167
2015-09-06 23:45 | 60.3667 | 64.2667 | 81.1333 | 68.6667
2015-09-07 | 60 | 63.7667 | 80.8833 | 67.8833
2015-09-07 00:15 | 60 | 63.2667 | 80.6333 | 67.6333
2015-09-07 00:30 | 60 | 62.7667 | 80.3833 | 67.3833
2015-09-07 00:45 | 60 | 62.2667 | 80.1333 | 67.1333
2015-09-07 01:00 | 59.9333 | 61.65 | 80 | 66.65
2015-09-07 01:15 | 59.6833 | 60.9 | 80 | 65.9
2015-09-07 01:30 | 59.4333 | 60.15 | 80 | 65.15
2015-09-07 01:45 | 59.1833 | 59.4 | 80 | 64.4
2015-09-07 02:00 | 59.0667 | 59.1167 | 79.65 | 63.8833
2015-09-07 02:15 | 59.3167 | 59.3667 | 78.9 | 63.6333
2015-09-07 02:30 | 59.5667 | 59.6167 | 78.15 | 63.3833
2015-09-07 02:45 | 59.8167 | 59.8667 | 77.4 | 63.1333
2015-09-07 03:00 | 59.9333 | 59.65 | 76.8833 | 62.8833
2015-09-07 03:15 | 59.6833 | 58.9 | 76.6333 | 62.6333
2015-09-07 03:30 | 59.4333 | 58.15 | 76.3833 | 62.3833
2015-09-07 03:45 | 59.1833 | 57.4 | 76.1333 | 62.1333
2015-09-07 04:00 | 58.9333 | 57 | 75.8833 | 61.8833
2015-09-07 04:15 | 58.6833 | 57 | 75.6333 | 61.6333
2015-09-07 04:30 | 58.4333 | 57 | 75.3833 | 61.3833
2015-09-07 04:45 | 58.1833 | 57 | 75.1333 | 61.1333
2015-09-07 05:00 | 58 | 57.1167 | 74.7667 | 61
2015-09-07 05:15 | 58 | 57.3667 | 74.2667 | 61
2015-09-07 05:30 | 58 | 57.6167 | 73.7667 | 61
2015-09-07 05:45 | 58 | 57.8667 | 73.2667 | 61
2015-09-07 06:00 | 58.5333 | 58.35 | 72.8833 | 61.5833
2015-09-07 06:15 | 60.5333 | 59.1 | 72.6333 | 62.8333
2015-09-07 06:30 | 62.5333 | 59.85 | 72.3833 | 64.0833
2015-09-07 06:45 | 64.5333 | 60.6 | 72.1333 | 65.3333
2015-09-07 07:00 | 66.1333 | 61.4667 | 72.4667 | 66.8167
2015-09-07 07:15 | 66.6333 | 62.4667 | 73.4667 | 68.5667
2015-09-07 07:30 | 67.1333 | 63.4667 | 74.4667 | 70.3167
2015-09-07 07:45 | 67.6333 | 64.4667 | 75.4667 | 72.0667
2015-09-07 08:00 | 68.1333 | 65.7 | 76.4667 | 73.4667
2015-09-07 08:15 | 68.6333 | 67.2 | 77.4667 | 74.4667
2015-09-07 08:30 | 69.1333 | 68.7 | 78.4667 | 75.4667
2015-09-07 08:45 | 69.6333 | 70.2 | 79.4667 | 76.4667
2015-09-07 09:00 | 70.1333 | 71.7 | 80.5833 | 77.35
2015-09-07 09:15 | 70.6333 | 73.2 | 81.8333 | 78.1
2015-09-07 09:30 | 71.1333 | 74.7 | 83.0833 | 78.85
2015-09-07 09:45 | 71.6333 | 76.2 | 84.3333 | 79.6
2015-09-07 10:00 | 72.2667 | 77.4667 | 85.1167 | 80.35
2015-09-07 10:15 | 73.2667 | 78.4667 | 85.3667 | 81.1
2015-09-07 10:30 | 74.2667 | 79.4667 | 85.6167 | 81.85
2015-09-07 10:45 | 75.2667 | 80.4667 | 85.8667 | 82.6
2015-09-07 11:00 | 76.3333 | 81.7 | 86.4667 | 83.4667
2015-09-07 11:15 | 77.5833 | 83.2 | 87.4667 | 84.4667
2015-09-07 11:30 | 78.8333 | 84.7 | 88.4667 | 85.4667
2015-09-07 11:45 | 80.0833 | 86.2 | 89.4667 | 86.4667
2015-09-07 12:00 | 80.9333 | 87.2333 | 90.35 | 87.35
2015-09-07 12:15 | 80.6833 | 87.7333 | 91.1 | 88.1
2015-09-07 12:30 | 80.4333 | 88.2333 | 91.85 | 88.85
2015-09-07 12:45 | 80.1833 | 88.7333 | 92.6 | 89.6
2015-09-07 13:00 | 80.1333 | 89.2333 | 93 | 90.2333
2015-09-07 13:15 | 80.6333 | 89.7333 | 93 | 90.7333
2015-09-07 13:30 | 81.1333 | 90.2333 | 93 | 91.2333
2015-09-07 13:45 | 81.6333 | 90.7333 | 93 | 91.7333
2015-09-07 14:00 | 82.4 | 91.1167 | 93.2333 | 92.1167
2015-09-07 14:15 | 83.9 | 91.3667 | 93.7333 | 92.3667
2015-09-07 14:30 | 85.4 | 91.6167 | 94.2333 | 92.6167
2015-09-07 14:45 | 86.9 | 91.8667 | 94.7333 | 92.8667
2015-09-07 15:00 | 87.8 | 92 | 95.1167 | 93.2333
2015-09-07 15:15 | 87.05 | 92 | 95.3667 | 93.7333
2015-09-07 15:30 | 86.3 | 92 | 95.6167 | 94.2333
2015-09-07 15:45 | 85.55 | 92 | 95.8667 | 94.7333
2015-09-07 16:00 | 84.7333 | 91.7667 | 95.8833 | 94.8833
2015-09-07 16:15 | 83.7333 | 91.2667 | 95.6333 | 94.6333
2015-09-07 16:30 | 82.7333 | 90.7667 | 95.3833 | 94.3833
2015-09-07 16:45 | 81.7333 | 90.2667 | 95.1333 | 94.1333
2015-09-07 17:00 | 80.9333 | 89.3 | 94.7667 | 93.65
2015-09-07 17:15 | 80.6833 | 87.8 | 94.2667 | 92.9
2015-09-07 17:30 | 80.4333 | 86.3 | 93.7667 | 92.15
2015-09-07 17:45 | 80.1833 | 84.8 | 93.2667 | 91.4
2015-09-07 18:00 | 79.8 | 83.3 | 92.65 | 90.3
2015-09-07 18:15 | 79.05 | 81.8 | 91.9 | 88.8
2015-09-07 18:30 | 78.3 | 80.3 | 91.15 | 87.3
2015-09-07 18:45 | 77.55 | 78.8 | 90.4 | 85.8
2015-09-07 19:00 | 76.9333 | 77.7667 | 89.65 | 84.7667
2015-09-07 19:15 | 76.6833 | 77.2667 | 88.9 | 84.2667
2015-09-07 19:30 | 76.4333 | 76.7667 | 88.15 | 83.7667
2015-09-07 19:45 | 76.1833 | 76.2667 | 87.4 | 83.2667
2015-09-07 20:00 | 75.8667 | 75.8833 | 86.8833 | 82.5333
2015-09-07 20:15 | 75.3667 | 75.6333 | 86.6333 | 81.5333
2015-09-07 20:30 | 74.8667 | 75.3833 | 86.3833 | 80.5333
2015-09-07 20:45 | 74.3667 | 75.1333 | 86.1333 | 79.5333
2015-09-07 21:00 | 73.8 | 74.5333 | 85.7667 | 78.7667
2015-09-07 21:15 | 73.05 | 73.5333 | 85.2667 | 78.2667
2015-09-07 21:30 | 72.3 | 72.5333 | 84.7667 | 77.7667
2015-09-07 21:45 | 71.55 | 71.5333 | 84.2667 | 77.2667
2015-09-07 22:00 | 71 | 70.7667 | 83.7667 | 76.7667
2015-09-07 22:15 | 71 | 70.2667 | 83.2667 | 76.2667
2015-09-07 22:30 | 71 | 69.7667 | 82.7667 | 75.7667
2015-09-07 22:45 | 71 | 69.2667 | 82.2667 | 75.2667
2015-09-07 23:00 | 70.8667 | 69 | 81.8833 | 74.7667
2015-09-07 23:15 | 70.3667 | 69 | 81.6333 | 74.2667
2015-09-07 23:30 | 69.8667 | 69 | 81.3833 | 73.7667
2015-09-07 23:45 | 69.3667 | 69 | 81.1333 | 73.2667
2015-09-08 | 68.8667 | 68.5333 | 80.8833 | 72.5333
2015-09-08 00:15 | 68.3667 | 67.5333 | 80.6333 | 71.5333
2015-09-08 00:30 | 67.8667 | 66.5333 | 80.3833 | 70.5333
2015-09-08 00:45 | 67.3667 | 65.5333 | 80.1333 | 69.5333
2015-09-08 01:00 | 66.8667 | 64.7667 | 79.8833 | 68.8833
2015-09-08 01:15 | 66.3667 | 64.2667 | 79.6333 | 68.6333
2015-09-08 01:30 | 65.8667 | 63.7667 | 79.3833 | 68.3833
2015-09-08 01:45 | 65.3667 | 63.2667 | 79.1333 | 68.1333
2015-09-08 02:00 | 65 | 62.65 | 78.8833 | 67.7667
2015-09-08 02:15 | 65 | 61.9 | 78.6333 | 67.2667
2015-09-08 02:30 | 65 | 61.15 | 78.3833 | 66.7667
2015-09-08 02:45 | 65 | 60.4 | 78.1333 | 66.2667
2015-09-08 03:00 | 64.9333 | 60.1167 | 77.8833 | 65.8833
2015-09-08 03:15 | 64.6833 | 60.3667 | 77.6333 | 65.6333
2015-09-08 03:30 | 64.4333 | 60.6167 | 77.3833 | 65.3833
2015-09-08 03:45 | 64.1833 | 60.8667 | 77.1333 | 65.1333
2015-09-08 04:00 | 63.9333 | 60.8833 | 76.7667 | 64.8833
2015-09-08 04:15 | 63.6833 | 60.6333 | 76.2667 | 64.6333
2015-09-08 04:30 | 63.4333 | 60.3833 | 75.7667 | 64.3833
2015-09-08 04:45 | 63.1833 | 60.1333 | 75.2667 | 64.1333
2015-09-08 05:00 | 63.2 | 60.2333 | 74.8833 | 64
2015-09-08 05:15 | 63.95 | 60.7333 | 74.6333 | 64
2015-09-08 05:30 | 64.7 | 61.2333 | 74.3833 | 64
2015-09-08 05:45 | 65.45 | 61.7333 | 74.1333 | 64
2015-09-08 06:00 | 66.0667 | 62.35 | 73.8833 | 64.2333
2015-09-08 06:15 | 66.3167 | 63.1 | 73.6333 | 64.7333
2015-09-08 06:30 | 66.5667 | 63.85 | 73.3833 | 65.2333
2015-09-08 06:45 | 66.8167 | 64.6 | 73.1333 | 65.7333
2015-09-08 07:00 | 67.2 | 65.7 | 73.4667 | 66.7
2015-09-08 07:15 | 67.95 | 67.2 | 74.4667 | 68.2
2015-09-08 07:30 | 68.7 | 68.7 | 75.4667 | 69.7
2015-09-08 07:45 | 69.45 | 70.2 | 76.4667 | 71.2
2015-09-08 08:00 | 70.2 | 71.8167 | 77.5833 | 72.5833
2015-09-08 08:15 | 70.95 | 73.5667 | 78.8333 | 73.8333
2015-09-08 08:30 | 71.7 | 75.3167 | 80.0833 | 75.0833
2015-09-08 08:45 | 72.45 | 77.0667 | 81.3333 | 76.3333
2015-09-08 09:00 | 72.9333 | 78.7 | 82.4667 | 77.5833
2015-09-08 09:15 | 72.6833 | 80.2 | 83.4667 | 78.8333
2015-09-08 09:30 | 72.4333 | 81.7 | 84.4667 | 80.0833
2015-09-08 09:45 | 72.1833 | 83.2 | 85.4667 | 81.3333
2015-09-08 10:00 | 72.3333 | 84.4667 | 86.4667 | 82.35
2015-09-08 10:15 | 73.5833 | 85.4667 | 87.4667 | 83.1
2015-09-08 10:30 | 74.8333 | 86.4667 | 88.4667 | 83.85
2015-09-08 10:45 | 76.0833 | 87.4667 | 89.4667 | 84.6
2015-09-08 11:00 | 77.1333 | 88.4667 | 90.1167 | 85.35
2015-09-08 11:15 | 77.6333 | 89.4667 | 90.3667 | 86.1
2015-09-08 11:30 | 78.1333 | 90.4667 | 90.6167 | 86.85
2015-09-08 11:45 | 78.6333 | 91.4667 | 90.8667 | 87.6
2015-09-08 12:00 | 79.0667 | 92.2333 | 91.2333 | 88.5833
2015-09-08 12:15 | 79.3167 | 92.7333 | 91.7333 | 89.8333
2015-09-08 12:30 | 79.5667 | 93.2333 | 92.2333 | 91.0833
2015-09-08 12:45 | 79.8167 | 93.7333 | 92.7333 | 92.3333
2015-09-08 13:00 | 80.2 | 94.1167 | 93.35 | 93.35
2015-09-08 13:15 | 80.95 | 94.3667 | 94.1 | 94.1
2015-09-08 13:30 | 81.7 | 94.6167 | 94.85 | 94.85
2015-09-08 13:45 | 82.45 | 94.8667 | 95.6 | 95.6
2015-09-08 14:00 | 83.5333 | 95.1167 | 96.1167 | 96.2333
2015-09-08 14:15 | 85.5333 | 95.3667 | 96.3667 | 96.7333
2015-09-08 14:30 | 87.5333 | 95.6167 | 96.6167 | 97.2333
2015-09-08 14:45 | 89.5333 | 95.8667 | 96.8667 | 97.7333
2015-09-08 15:00 | 90.8 | 96 | 96.7667 | 98.1167
2015-09-08 15:15 | 90.05 | 96 | 96.2667 | 98.3667
2015-09-08 15:30 | 89.3 | 96 | 95.7667 | 98.6167
2015-09-08 15:45 | 88.55 | 96 | 95.2667 | 98.8667
2015-09-08 16:00 | 87.8667 | 95.5333 | 95 | 98.8833
2015-09-08 16:15 | 87.3667 | 94.5333 | 95 | 98.6333
2015-09-08 16:30 | 86.8667 | 93.5333 | 95 | 98.3833
2015-09-08 16:45 | 86.3667 | 92.5333 | 95 | 98.1333
2015-09-08 17:00 | 85.6667 | 91.5333 | 94.7667 | 97.65
2015-09-08 17:15 | 84.4167 | 90.5333 | 94.2667 | 96.9
2015-09-08 17:30 | 83.1667 | 89.5333 | 93.7667 | 96.15
2015-09-08 17:45 | 81.9167 | 88.5333 | 93.2667 | 95.4
2015-09-08 18:00 | 80.7333 | 87.5333 | 92.7667 | 94.5333
2015-09-08 18:15 | 79.7333 | 86.5333 | 92.2667 | 93.5333
2015-09-08 18:30 | 78.7333 | 85.5333 | 91.7667 | 92.5333
2015-09-08 18:45 | 77.7333 | 84.5333 | 91.2667 | 91.5333
2015-09-08 19:00 | 76.9333 | 83.4167 | 90.7407 | 90.5333
2015-09-08 19:15 | 76.6833 | 82.1667 | 90.1852 | 89.5333
2015-09-08 19:30 | 76.4333 | 80.9167 | 87.8571 | 88.5333
2015-09-08 19:45 | 76.1833 | 79.6667 | 84.6429 | 87.5333
2015-09-08 20:00 | 76 | 78.7667 | 84.7667 | 86.7667
2015-09-08 20:15 | 76 | 78.2667 | 84.2667 | 86.2667
2015-09-08 20:30 | 76 | 77.7667 | 83.3 | 85.7667
2015-09-08 20:45 | 76 | 77.2667 | 81.8 | 85.2667
2015-09-08 21:00 | 76 | 76.7667 | 80.7667 | 84.7667
2015-09-08 21:15 | 76 | 76.2667 | 80.2667 | 84.2667
2015-09-08 21:30 | 76 | 75.7667 | 79.7667 | 83.7667
2015-09-08 21:45 | 76 | 75.2667 | 79.2667 | 83.2667
2015-09-08 22:00 | 75.7333 | 74.65 | 79.1167 | 82.65
2015-09-08 22:15 | 74.7333 | 73.9 | 79.3667 | 81.9
2015-09-08 22:30 | 73.7333 | 73.15 | 79.6167 | 81.15
2015-09-08 22:45 | 72.7333 | 72.4 | 79.8667 | 80.4
2015-09-08 23:00 | 72 | 71.8833 | 80.1167 | 79.65
2015-09-08 23:15 | 72 | 71.6333 | 80.3667 | 78.9
2015-09-08 23:30 | 72 | 71.3833 | 80.6167 | 78.15
2015-09-08 23:45 | 72 | 71.1333 | 80.8667 | 77.4
2015-09-09 | 71.8667 | 70.5333 | 80.4167 | 76.65
2015-09-09 00:15 | 71.3667 | 69.5333 | 79.1667 | 75.9
2015-09-09 00:30 | 70.8667 | 68.5333 | 77.9167 | 75.15
2015-09-09 00:45 | 70.3667 | 67.5333 | 76.6667 | 74.4
2015-09-09 01:00 | 69.8667 | 67.2333 | 76.35 | 73.8833
2015-09-09 01:15 | 69.3667 | 67.7333 | 77.1 | 73.6333
2015-09-09 01:30 | 68.8667 | 68.2333 | 77.85 | 73.3833
2015-09-09 01:45 | 68.3667 | 68.7333 | 78.6 | 73.1333
2015-09-09 02:00 | 67.9333 | 68.65 | 78.8833 | 72.65
2015-09-09 02:15 | 67.6833 | 67.9 | 78.6333 | 71.9
2015-09-09 02:30 | 67.4333 | 67.15 | 78.3833 | 71.15
2015-09-09 02:45 | 67.1833 | 66.4 | 78.1333 | 70.4
2015-09-09 03:00 | 66.8667 | 65.8833 | 77.4167 | 70.1167
2015-09-09 03:15 | 66.3667 | 65.6333 | 76.1667 | 70.3667
2015-09-09 03:30 | 65.8667 | 65.3833 | 74.9167 | 70.6167
2015-09-09 03:45 | 65.3667 | 65.1333 | 73.6667 | 70.8667
2015-09-09 04:00 | 65 | 65.1167 | 73.35 | 71
2015-09-09 04:15 | 65 | 65.3667 | 74.1 | 71
2015-09-09 04:30 | 65 | 65.6167 | 74.85 | 71
2015-09-09 04:45 | 65 | 65.8667 | 75.6 | 71
2015-09-09 05:00 | 65 | 66 | 75.8833 | 70.8833
2015-09-09 05:15 | 65 | 66 | 75.6333 | 70.6333
2015-09-09 05:30 | 65 | 66 | 75.3833 | 70.3833
2015-09-09 05:45 | 65 | 66 | 75.1333 | 70.1333
2015-09-09 06:00 | 65.3333 | 66.3182 | 74.8833 | 70.35
2015-09-09 06:15 | 66.5833 | 67 | 74.6333 | 71.1
2015-09-09 06:30 | 67.8333 | 67.6818 | 74.3833 | 71.85
2015-09-09 06:45 | 69.0833 | 68.5 | 74.1333 | 72.6
2015-09-09 07:00 | 70.1333 | 69.4667 | 74.35 | 73.5833
2015-09-09 07:15 | 70.6333 | 70.4667 | 75.1 | 74.8333
2015-09-09 07:30 | 71.1333 | 71.4667 | 75.85 | 76.0833
2015-09-09 07:45 | 71.6333 | 72.4667 | 76.6 | 77.3333
2015-09-09 08:00 | 72.1333 | 73.8167 | 77.5833 | 78.7
2015-09-09 08:15 | 72.6333 | 75.5667 | 78.8333 | 80.2
2015-09-09 08:30 | 73.1333 | 77.3167 | 80.0833 | 81.7
2015-09-09 08:45 | 73.6333 | 79.0667 | 81.3333 | 83.2
2015-09-09 09:00 | 74.0667 | 80.4667 | 82.35 | 84.2333
2015-09-09 09:15 | 74.3167 | 81.4667 | 83.1 | 84.7333
2015-09-09 09:30 | 74.5667 | 82.4667 | 83.85 | 85.2333
2015-09-09 09:45 | 74.8167 | 83.4667 | 84.6 | 85.7333
2015-09-09 10:00 | 75.1333 | 84.4667 | 84.65 | 86.5833
2015-09-09 10:15 | 75.6333 | 85.4667 | 83.9 | 87.8333
2015-09-09 10:30 | 76.1333 | 86.4667 | 83.15 | 89.0833
2015-09-09 10:45 | 76.6333 | 87.4667 | 82.4 | 90.3333
2015-09-09 11:00 | 77.2 | 88.2333 | 81.0667 | 91.35
2015-09-09 11:15 | 77.95 | 88.7333 | 79.0667 | 92.1
2015-09-09 11:30 | 78.7 | 89.2333 | 77.0667 | 92.85
2015-09-09 11:45 | 79.45 | 89.7333 | 75.0667 | 93.6
2015-09-09 12:00 | 80.7111 | 90.5833 | 74.7 | 94.7
2015-09-09 12:15 | 83.3778 | 91.8333 | 76.2 | 96.2
2015-09-09 12:30 | 86.0444 | 93.0833 | 77.7 | 97.7
2015-09-09 12:45 | 88 | 94.3333 | 79.2 | 99.2
2015-09-09 13:00 | 88.1333 | 95 | 80.8167 | 100.1167
2015-09-09 13:15 | 88.6333 | 95 | 82.5667 | 100.3667
2015-09-09 13:30 | 89.1333 | 95 | 84.3167 | 100.6167
2015-09-09 13:45 | 89.6333 | 95 | 86.0667 | 100.8667
2015-09-09 14:00 | 90 | 94.8833 | 87.1167 | 101.2333
2015-09-09 14:15 | 90 | 94.6333 | 87.3667 | 101.7333
2015-09-09 14:30 | 90 | 94.3833 | 87.6167 | 102.2333
2015-09-09 14:45 | 90 | 94.1333 | 87.8667 | 102.7333
2015-09-09 15:00 | 89.8 | 93.8833 | 87.4717 | 102.8833
2015-09-09 15:15 | 89.05 | 93.6333 | 86.3396 | 102.6333
2015-09-09 15:30 | 88.3 | 93.3833 | 85.2075 | 102.3833
2015-09-09 15:45 | 87.55 | 93.1333 | 84.0755 | 102.1333
2015-09-09 16:00 | 86.4667 | 92.7667 | 85.1167 | 102
2015-09-09 16:15 | 84.4667 | 92.2667 | 85.3667 | 102
2015-09-09 16:30 | 82.4667 | 91.7667 | 85.6167 | 102
2015-09-09 16:45 | 80.4667 | 91.2667 | 85.8667 | 102
2015-09-09 17:00 | 78.7333 | 90.5333 | 85.7742 | 101.65
2015-09-09 17:15 | 77.7333 | 89.5333 | 85.2903 | 100.9
2015-09-09 17:30 | 76.7333 | 88.5333 | 82 | 100.15
2015-09-09 17:45 | 75.7333 | 87.5333 | 75.6667 | 99.4
2015-09-09 18:00 | 74.8 | 86.3 | 75.1167 | 98.5333
2015-09-09 18:15 | 74.05 | 84.8 | 75.3667 | 97.5333
2015-09-09 18:30 | 73.3 | 83.3 | 75.6167 | 96.5333
2015-09-09 18:45 | 72.55 | 81.8 | 75.8667 | 95.5333
2015-09-09 19:00 | 71.8 | 80.7667 | 75.7667 | 94.4167
2015-09-09 19:15 | 71.05 | 80.2667 | 75.2667 | 93.1667
2015-09-09 19:30 | 70.3 | 79.7667 | 74.7667 | 91.9167
2015-09-09 19:45 | 69.55 | 79.2667 | 74.2667 | 90.6667
2015-09-09 20:00 | 69 | 78.65 | 74.1167 | 89.5333
2015-09-09 20:15 | 69 | 77.9 | 74.3667 | 88.5333
2015-09-09 20:30 | 69 | 77.15 | 74.6167 | 87.5333
2015-09-09 20:45 | 69 | 76.4 | 74.8667 | 86.5333
2015-09-09 21:00 | 68.8 | 75.65 | 75.1167 | 85.65
2015-09-09 21:15 | 68.05 | 74.9 | 75.3667 | 84.9
2015-09-09 21:30 | 67.3 | 74.15 | 75.6167 | 84.15
2015-09-09 21:45 | 66.55 | 73.4 | 75.8667 | 83.4
2015-09-09 22:00 | 65.9333 | 73.1167 | 75.8833 | 82.7667
2015-09-09 22:15 | 65.6833 | 73.3667 | 75.6333 | 82.2667
2015-09-09 22:30 | 65.4333 | 73.6167 | 75.3833 | 81.7667
2015-09-09 22:45 | 65.1833 | 73.8667 | 75.1333 | 81.2667
2015-09-09 23:00 | 64.6667 | 73.65 | 74.7667 | 80.8833
2015-09-09 23:15 | 63.4167 | 72.9 | 74.2667 | 80.6333
2015-09-09 23:30 | 62.1667 | 72.15 | 73.7667 | 80.3833
2015-09-09 23:45 | 60.9167 | 71.4 | 73.2667 | 80.1333
2015-09-10 | 60.0667 | 71.1167 | 72.8833 | 79.7667
2015-09-10 00:15 | 60.3167 | 71.3667 | 72.6333 | 79.2667
2015-09-10 00:30 | 60.5667 | 71.6167 | 72.3833 | 78.7667
2015-09-10 00:45 | 60.8167 | 71.8667 | 72.1333 | 78.2667
2015-09-10 01:00 | 60.8667 | 71.65 | 72 | 77.8833
2015-09-10 01:15 | 60.3667 | 70.9 | 72 | 77.6333
2015-09-10 01:30 | 59.8667 | 70.15 | 72 | 77.3833
2015-09-10 01:45 | 59.3667 | 69.4 | 72 | 77.1333
2015-09-10 02:00 | 59 | 69 | 71.7667 | 76.7667
2015-09-10 02:15 | 59 | 69 | 71.2667 | 76.2667
2015-09-10 02:30 | 59 | 69 | 70.7667 | 75.7667
2015-09-10 02:45 | 59 | 69 | 70.2667 | 75.2667
2015-09-10 03:00 | 58.9333 | 68.8833 | 69.7667 | 75
2015-09-10 03:15 | 58.6833 | 68.6333 | 69.2667 | 75
2015-09-10 03:30 | 58.4333 | 68.3833 | 68.7667 | 75
2015-09-10 03:45 | 58.1833 | 68.1333 | 68.2667 | 75
2015-09-10 04:00 | 57.9286 | 67.8833 | 67.8833 | 74.8833
2015-09-10 04:15 | 57.6607 | 67.6333 | 67.6333 | 74.6333
2015-09-10 04:30 | 57.3929 | 67.3833 | 67.3833 | 74.3833
2015-09-10 04:45 | 57.125 | 67.1333 | 67.1333 | 74.1333
2015-09-10 05:00 | 57.0667 | 67 | 66.7667 | 73.8833
2015-09-10 05:15 | 57.3167 | 67 | 66.2667 | 73.6333
2015-09-10 05:30 | 57.5667 | 67 | 65.7667 | 73.3833
2015-09-10 05:45 | 57.8167 | 67 | 65.2667 | 73.1333
2015-09-10 06:00 | 58.3333 | 66.75 | 65.1167 | 73.35
2015-09-10 06:15 | 59.5833 | 66.2143 | 65.3667 | 74.1
2015-09-10 06:30 | 60.8333 | 66.8438 | 65.6167 | 74.85
2015-09-10 06:45 | 62.0833 | 68.25 | 65.8667 | 75.6
2015-09-10 07:00 | 63.2667 | 69.4667 | 66.5833 | 76.5833
2015-09-10 07:15 | 64.2667 | 70.4667 | 67.8333 | 77.8333
2015-09-10 07:30 | 65.2667 | 71.4667 | 69.0833 | 79.0833
2015-09-10 07:45 | 66.2667 | 72.4667 | 70.3333 | 80.3333
2015-09-10 08:00 | 67.2 | 73.35 | 71.35 | 81.7
2015-09-10 08:15 | 67.95 | 74.1 | 72.1 | 83.2
2015-09-10 08:30 | 68.7 | 74.85 | 72.85 | 84.7
2015-09-10 08:45 | 69.45 | 75.6 | 73.6 | 86.2
2015-09-10 09:00 | 70.2 | 76.7 | 74.4667 | 87.4667
2015-09-10 09:15 | 70.95 | 78.2 | 75.4667 | 88.4667
2015-09-10 09:30 | 71.7 | 79.7 | 76.4667 | 89.4667
2015-09-10 09:45 | 72.45 | 81.2 | 77.4667 | 90.4667
2015-09-10 10:00 | 73.0667 | 82.7 | 78.4667 | 91.1167
2015-09-10 10:15 | 73.3167 | 84.2 | 79.4667 | 91.3667
2015-09-10 10:30 | 73.5667 | 85.7 | 80.4667 | 91.6167
2015-09-10 10:45 | 73.8167 | 87.2 | 81.4667 | 91.8667
2015-09-10 11:00 | 74.2 | 88.35 | 82.2333 | 92.5833
2015-09-10 11:15 | 74.95 | 89.1 | 82.7333 | 93.8333
2015-09-10 11:30 | 75.7 | 89.85 | 83.2333 | 95.0833
2015-09-10 11:45 | 76.45 | 90.6 | 83.7333 | 96.3333
2015-09-10 12:00 | 77.2 | 91.35 | 84.5833 | 97.1167
2015-09-10 12:15 | 77.95 | 92.1 | 85.8333 | 97.3667
2015-09-10 12:30 | 78.7 | 92.85 | 87.0833 | 97.6167
2015-09-10 12:45 | 79.45 | 93.6 | 88.3333 | 97.8667
2015-09-10 13:00 | 80.0667 | 94 | 89.1167 | 98.35
2015-09-10 13:15 | 80.3167 | 94 | 89.3667 | 99.1
2015-09-10 13:30 | 80.5667 | 94 | 89.6167 | 99.85
2015-09-10 13:45 | 80.8167 | 94 | 89.8667 | 100.6
2015-09-10 14:00 | 80.9333 | 93.3 | 90 | 101.2333
2015-09-10 14:15 | 80.6833 | 91.8 | 90 | 101.7333
2015-09-10 14:30 | 80.4333 | 90.3 | 90 | 102.2333
2015-09-10 14:45 | 80.1833 | 88.8 | 90 | 102.7333
2015-09-10 15:00 | 80 | 88.2333 | 90.35 | 103
2015-09-10 15:15 | 80 | 88.7333 | 91.1 | 103
2015-09-10 15:30 | 80 | 89.2333 | 91.85 | 103
2015-09-10 15:45 | 80 | 89.7333 | 92.6 | 103
2015-09-10 16:00 | 79.6 | 89.8833 | 92.7667 | 102.8833
2015-09-10 16:15 | 78.1 | 89.6333 | 92.2667 | 102.6333
2015-09-10 16:30 | 76.6 | 89.3833 | 91.7667 | 102.3833
2015-09-10 16:45 | 75.1 | 89.1333 | 91.2667 | 102.1333
2015-09-10 17:00 | 73.7333 | 88.4167 | 90.8833 | 101.65
2015-09-10 17:15 | 72.7333 | 87.1667 | 90.6333 | 100.9
2015-09-10 17:30 | 71.7333 | 85.9167 | 90.3833 | 100.15
2015-09-10 17:45 | 70.7333 | 84.6667 | 90.1333 | 99.4
2015-09-10 18:00 | 69.6667 | 83.65 | 89.5333 | 98.65
2015-09-10 18:15 | 68.4167 | 82.9 | 88.5333 | 97.9
2015-09-10 18:30 | 67.1667 | 82.15 | 87.5333 | 97.15
2015-09-10 18:45 | 65.9167 | 81.4 | 86.5333 | 96.4
2015-09-10 19:00 | 64.9333 | 80.5333 | 85.65 | 95.5333
2015-09-10 19:15 | 64.6833 | 79.5333 | 84.9 | 94.5333
2015-09-10 19:30 | 64.4333 | 78.5333 | 84.15 | 93.5333
2015-09-10 19:45 | 64.1833 | 77.5333 | 83.4 | 92.5333
2015-09-10 20:00 | 63.9333 | 76.7667 | 83 | 91.7667
2015-09-10 20:15 | 63.6833 | 76.2667 | 83 | 91.2667
2015-09-10 20:30 | 63.4333 | 75.7667 | 83 | 90.7667
2015-09-10 20:45 | 63.1833 | 75.2667 | 83 | 90.2667
2015-09-10 21:00 | 63 | 74.65 | 82.8833 | 89.5333
2015-09-10 21:15 | 63 | 73.9 | 82.6333 | 88.5333
2015-09-10 21:30 | 63 | 73.15 | 82.3833 | 87.5333
2015-09-10 21:45 | 63 | 72.4 | 82.1333 | 86.5333
2015-09-10 22:00 | 62.8667 | 71.8833 | 81.65 | 85.7667
2015-09-10 22:15 | 62.3667 | 71.6333 | 80.9 | 85.2667
2015-09-10 22:30 | 61.8667 | 71.3833 | 80.15 | 84.7667
2015-09-10 22:45 | 61.3667 | 71.1333 | 79.4 | 84.2667
2015-09-10 23:00 | 60.8667 | 70.7667 | 78.8833 | 83.7667
2015-09-10 23:15 | 60.3667 | 70.2667 | 78.6333 | 83.2667
2015-09-10 23:30 | 59.8667 | 69.7667 | 78.3833 | 82.7667
2015-09-10 23:45 | 59.3667 | 69.2667 | 78.1333 | 82.2667
2015-09-11 | 59 | 68.7667 | 77.7667 | 81.8833
2015-09-11 00:15 | 59 | 68.2667 | 77.2667 | 81.6333
2015-09-11 00:30 | 59 | 67.7667 | 76.7667 | 81.3833
2015-09-11 00:45 | 59 | 67.2667 | 76.2667 | 81.1333
2015-09-11 01:00 | 58.9333 | 67 | 75.7667 | 80.7667
2015-09-11 01:15 | 58.6833 | 67 | 75.2667 | 80.2667
2015-09-11 01:30 | 58.4333 | 67 | 74.7667 | 79.7667
2015-09-11 01:45 | 58.1833 | 67 | 74.2667 | 79.2667
2015-09-11 02:00 | 58 | 66.8833 | 74.1167 | 78.8833
2015-09-11 02:15 | 58 | 66.6333 | 74.3667 | 78.6333
2015-09-11 02:30 | 58 | 66.3833 | 74.6167 | 78.3833
2015-09-11 02:45 | 58 | 66.1333 | 74.8667 | 78.1333
2015-09-11 03:00 | 57.9333 | 66.1167 | 75.1167 | 77.7667
2015-09-11 03:15 | 57.6833 | 66.3667 | 75.3667 | 77.2667
2015-09-11 03:30 | 57.4333 | 66.6167 | 75.6167 | 76.7667
2015-09-11 03:45 | 57.1833 | 66.8667 | 75.8667 | 76.2667
2015-09-11 04:00 | 57 | 66.8654 | 75.65 | 75.8833
2015-09-11 04:15 | 57 | 66.5769 | 74.9 | 75.6333
2015-09-11 04:30 | 57 | 66.2885 | 74.15 | 75.3833
2015-09-11 04:45 | 57 | 66 | 73.4 | 75.1333
2015-09-11 05:00 | 57 | 66.8833 | 73 | 75
2015-09-11 05:15 | 57 | 66.6333 | 73 | 75
2015-09-11 05:30 | 57 | 66.3833 | 73 | 75
2015-09-11 05:45 | 57 | 66.1333 | 73 | 75
2015-09-11 06:00 | 57.0667 | 66.2333 | 72.8833 | 75.1167
2015-09-11 06:15 | 57.3167 | 66.7333 | 72.6333 | 75.3667
2015-09-11 06:30 | 57.5667 | 67.2333 | 72.3833 | 75.6167
2015-09-11 06:45 | 57.8167 | 67.7333 | 72.1333 | 75.8667
2015-09-11 07:00 | 58.1333 | 68.35 | 72.2333 | 76.35
2015-09-11 07:15 | 58.6333 | 69.1 | 72.7333 | 77.1
2015-09-11 07:30 | 59.1333 | 69.85 | 73.2333 | 77.85
2015-09-11 07:45 | 59.6333 | 70.6 | 73.7333 | 78.6
2015-09-11 08:00 | 60.3333 | 71.4667 | 74.5833 | 79.35
2015-09-11 08:15 | 61.5833 | 72.4667 | 75.8333 | 80.1
2015-09-11 08:30 | 62.8333 | 73.4667 | 77.0833 | 80.85
2015-09-11 08:45 | 64.0833 | 74.4667 | 78.3333 | 81.6
2015-09-11 09:00 | 65.2 | 75.2333 | 79.5833 | 82.35
2015-09-11 09:15 | 65.95 | 75.7333 | 80.8333 | 83.1
2015-09-11 09:30 | 66.7 | 76.2333 | 82.0833 | 83.85
2015-09-11 09:45 | 67.45 | 76.7333 | 83.3333 | 84.6
2015-09-11 10:00 | 68.0667 | 77.4667 | 84.5833 | 85.8167
2015-09-11 10:15 | 68.3167 | 78.4667 | 85.8333 | 87.5667
2015-09-11 10:30 | 68.5667 | 79.4667 | 87.0833 | 89.3167
2015-09-11 10:45 | 68.8167 | 80.4667 | 88.3333 | 91.0667
2015-09-11 11:00 | 69.2 | 81.5833 | 89.35 | 92.35
2015-09-11 11:15 | 69.95 | 82.8333 | 90.1 | 93.1
2015-09-11 11:30 | 70.7 | 84.0833 | 90.85 | 93.85
2015-09-11 11:45 | 71.45 | 85.3333 | 91.6 | 94.6
2015-09-11 12:00 | 72.1333 | 86.1167 | 92.1167 | 95.2333
2015-09-11 12:15 | 72.6333 | 86.3667 | 92.3667 | 95.7333
2015-09-11 12:30 | 73.1333 | 86.6167 | 92.6167 | 96.2333
2015-09-11 12:45 | 73.6333 | 86.8667 | 92.8667 | 96.7333
2015-09-11 13:00 | 74 | 87.1167 | 92.8833 | 97.2333
2015-09-11 13:15 | 74 | 87.3667 | 92.6333 | 97.7333
2015-09-11 13:30 | 74 | 87.6167 | 92.3833 | 98.2333
2015-09-11 13:45 | 74 | 87.8667 | 92.1333 | 98.7333
2015-09-11 14:00 | 74 | 88.1167 | 92 | 99.2333
2015-09-11 14:15 | 74 | 88.3667 | 92 | 99.7333
2015-09-11 14:30 | 74 | 88.6167 | 92 | 100.2333
2015-09-11 14:45 | 74 | 88.8667 | 92 | 100.7333
2015-09-11 15:00 | 74.0667 | 88.7667 | 91.3913 | 100.7667
2015-09-11 15:15 | 74.3167 | 88.2667 | 90.087 | 100.2667
2015-09-11 15:30 | 74.5667 | 87.7667 | 82.5882 | 99.7667
2015-09-11 15:45 | 74.8167 | 87.2667 | 81.6667 | 99.2667
2015-09-11 16:00 | 74.6667 | 86.7667 | 85.1667 | 98.65
2015-09-11 16:15 | 73.4167 | 86.2667 | 87.6667 | 97.9
2015-09-11 16:30 | 72.1667 | 85.7667 | 89.4667 | 97.15
2015-09-11 16:45 | 70.9167 | 85.2667 | 90.4667 | 96.4
2015-09-11 17:00 | 69.6667 | 84.5333 | 90.1833 | 95.8833
2015-09-11 17:15 | 68.4167 | 83.5333 | 88.4333 | 95.6333
2015-09-11 17:30 | 67.1667 | 82.5333 | 86.6833 | 95.3833
2015-09-11 17:45 | 65.9167 | 81.5333 | 84.9333 | 95.1333
2015-09-11 18:00 | 64.8667 | 80.3 | 83.7667 | 94.65
2015-09-11 18:15 | 64.3667 | 78.8 | 83.2667 | 93.9
2015-09-11 18:30 | 63.8667 | 77.3 | 82.7667 | 93.15
2015-09-11 18:45 | 63.3667 | 75.8 | 82.2667 | 92.4
2015-09-11 19:00 | 62.8 | 74.7667 | 81.65 | 91.7667
2015-09-11 19:15 | 62.05 | 74.2667 | 80.9 | 91.2667
2015-09-11 19:30 | 61.3 | 73.7667 | 80.15 | 90.7667
2015-09-11 19:45 | 60.55 | 73.2667 | 79.4 | 90.2667
2015-09-11 20:00 | 59.9333 | 72.5333 | 78.65 | 89.8833
2015-09-11 20:15 | 59.6833 | 71.5333 | 77.9 | 89.6333
2015-09-11 20:30 | 59.4333 | 70.5333 | 77.15 | 89.3833
2015-09-11 20:45 | 59.1833 | 69.5333 | 76.4 | 89.1333
2015-09-11 21:00 | 59 | 68.7667 | 76.1167 | 88.65
2015-09-11 21:15 | 59 | 68.2667 | 76.3667 | 87.9
2015-09-11 21:30 | 59 | 67.7667 | 76.6167 | 87.15
2015-09-11 21:45 | 59 | 67.2667 | 76.8667 | 86.4
2015-09-11 22:00 | 59 | 66.7667 | 76.7667 | 85.65
2015-09-11 22:15 | 59 | 66.2667 | 76.2667 | 84.9
2015-09-11 22:30 | 59 | 65.7667 | 75.7667 | 84.15
2015-09-11 22:45 | 59 | 65.2667 | 75.2667 | 83.4
2015-09-11 23:00 | 58.9333 | 64.7667 | 74.65 | 83
2015-09-11 23:15 | 58.6833 | 64.2667 | 73.9 | 83
2015-09-11 23:30 | 58.4333 | 63.7667 | 73.15 | 83
2015-09-11 23:45 | 58.1833 | 63.2667 | 72.4 | 83
2015-09-12 | 58 | 63 | 72.1167 | 82.7667
2015-09-12 00:15 | 58 | 63 | 72.3667 | 82.2667
2015-09-12 00:30 | 58 | 63 | 72.6167 | 81.7667
2015-09-12 00:45 | 58 | 63 | 72.8667 | 81.2667
2015-09-12 01:00 | 57.92 | 62.8833 | 72.65 | 80.5333
2015-09-12 01:15 | 57.62 | 62.6333 | 71.9 | 79.5333
2015-09-12 01:30 | 57.32 | 62.3833 | 71.15 | 78.5333
2015-09-12 01:45 | 57.02 | 62.1333 | 70.4 | 77.5333
2015-09-12 02:00 | 57.9333 | 62 | 69.7667 | 77
2015-09-12 02:15 | 57.6833 | 62 | 69.2667 | 77
2015-09-12 02:30 | 57.4333 | 62 | 68.7667 | 77
2015-09-12 02:45 | 57.1833 | 62 | 68.2667 | 77
2015-09-12 03:00 | 57 | 61.7667 | 67.8833 | 76.8833
2015-09-12 03:15 | 57 | 61.2667 | 67.6333 | 76.6333
2015-09-12 03:30 | 57 | 60.7667 | 67.3833 | 76.3833
2015-09-12 03:45 | 57 | 60.2667 | 67.1333 | 76.1333
2015-09-12 04:00 | 57 | 60 | 66.8833 | 76
2015-09-12 04:15 | 57 | 60 | 66.6333 | 76
2015-09-12 04:30 | 57 | 60 | 66.3833 | 76
2015-09-12 04:45 | 57.0833 | 60 | 66.1333 | 76
2015-09-12 05:00 | 58 | 60.2593 | 65.8833 | 75.7667
2015-09-12 05:15 | 58 | 60.8148 | 65.6333 | 75.2667
2015-09-12 05:30 | 58 | 61 | 65.3833 | 74.7667
2015-09-12 05:45 | 58 | 60.5714 | 65.1333 | 74.2667
2015-09-12 06:00 | 58 | 60.1321 | 65 | 74.35
2015-09-12 06:15 | 58 | 60.4151 | 65 | 75.1
2015-09-12 06:30 | 58 | 60.6981 | 65 | 75.85
2015-09-12 06:45 | 58 | 60.9811 | 65 | 76.6
2015-09-12 07:00 | 58.5 | 61.2333 | 65.5833 | 77.1167
2015-09-12 07:15 | 59.2115 | 61.7333 | 66.8333 | 77.3667
2015-09-12 07:30 | 59.5 | 62.2333 | 68.0833 | 77.6167
2015-09-12 07:45 | 59.7885 | 62.7333 | 69.3333 | 77.8667
2015-09-12 08:00 | 60.0667 | 63.2333 | 70.7 | 78.2333
2015-09-12 08:15 | 60.3167 | 63.7333 | 72.2 | 78.7333
2015-09-12 08:30 | 60.5667 | 64.2333 | 73.7 | 79.2333
2015-09-12 08:45 | 60.8167 | 64.7333 | 75.2 | 79.7333
2015-09-12 09:00 | 61.1333 | 65.35 | 76.35 | 80.8167
2015-09-12 09:15 | 61.6333 | 66.1 | 77.1 | 82.5667
2015-09-12 09:30 | 62.1333 | 66.85 | 77.85 | 84.3167
2015-09-12 09:45 | 62.6333 | 67.6 | 78.6 | 86.0667
2015-09-12 10:00 | 62.75 | 68 | 79.2333 | 87.1167
2015-09-12 10:15 | 61.8125 | 68 | 79.7333 | 87.3667
2015-09-12 10:30 | 61 | 68 | 80.2333 | 87.6167
2015-09-12 10:45 | 61 | 68 | 80.7333 | 87.8667
2015-09-12 11:00 | 60.9333 | 67.7667 | 81.35 | 88.7
2015-09-12 11:15 | 60.6833 | 67.2667 | 82.1 | 90.2
2015-09-12 11:30 | 60.4333 | 66.7667 | 82.85 | 91.7
2015-09-12 11:45 | 60.1833 | 66.2667 | 83.6 | 93.2
2015-09-12 12:00 | 60.125 | 66.1167 | 84.2333 | 94.1167
2015-09-12 12:15 | 60.5938 | 66.3667 | 84.7333 | 94.3667
2015-09-12 12:30 | 61 | 66.6167 | 85.2333 | 94.6167
2015-09-12 12:45 | 61 | 66.8667 | 85.7333 | 94.8667
2015-09-12 13:00 | 61.0667 | 66.8833 | 86.1167 | 95.2333
2015-09-12 13:15 | 61.3167 | 66.6333 | 86.3667 | 95.7333
2015-09-12 13:30 | 61.5667 | 66.3833 | 86.6167 | 96.2333
2015-09-12 13:45 | 61.8167 | 66.1333 | 86.8667 | 96.7333
2015-09-12 14:00 | 62.1333 | 66.4667 | 87 | 96.8833
2015-09-12 14:15 | 62.6333 | 67.4667 | 87 | 96.6333
2015-09-12 14:30 | 63.1333 | 68.4667 | 87 | 96.3833
2015-09-12 14:45 | 63.6333 | 69.4667 | 87 | 96.1333
2015-09-12 15:00 | 64.4667 | 70.35 | 87.1167 | 95.7667
2015-09-12 15:15 | 66.2167 | 71.1 | 87.3667 | 95.2667
2015-09-12 15:30 | 67.9667 | 71.85 | 87.6167 | 94.7667
2015-09-12 15:45 | 69.7167 | 72.6 | 87.8667 | 94.2667
2015-09-12 16:00 | 71 | 73.2333 | 88 | 93.5333
2015-09-12 16:15 | 71 | 73.7333 | 88 | 92.5333
2015-09-12 16:30 | 71 | 74.2333 | 88 | 91.5333
2015-09-12 16:45 | 71 | 74.7333 | 88 | 90.5333
2015-09-12 17:00 | 71.1333 | 75.2333 | 87.8833 | 89.65
2015-09-12 17:15 | 71.6333 | 75.7333 | 87.6333 | 88.9
2015-09-12 17:30 | 72.1333 | 76.2333 | 87.3833 | 88.15
2015-09-12 17:45 | 72.6333 | 76.7333 | 87.1333 | 87.4
2015-09-12 18:00 | 72.6667 | 76.8833 | 86.65 | 86.7667
2015-09-12 18:15 | 71.4167 | 76.6333 | 85.9 | 86.2667
2015-09-12 18:30 | 70.1667 | 76.3833 | 85.15 | 85.7667
2015-09-12 18:45 | 68.9167 | 76.1333 | 84.4 | 85.2667
2015-09-12 19:00 | 67.8 | 75.8833 | 83.7667 | 84.8833
2015-09-12 19:15 | 67.05 | 75.6333 | 83.2667 | 84.6333
2015-09-12 19:30 | 66.3 | 75.3833 | 82.7667 | 84.3833
2015-09-12 19:45 | 65.55 | 75.1333 | 82.2667 | 84.1333
2015-09-12 20:00 | 64.9333 | 74.3 | 81.65 | 83.8833
2015-09-12 20:15 | 64.6833 | 72.8 | 80.9 | 83.6333
2015-09-12 20:30 | 64.4333 | 71.3 | 80.15 | 83.3833
2015-09-12 20:45 | 64.1833 | 69.8 | 79.4 | 83.1333
2015-09-12 21:00 | 63.931 | 68.7667 | 78.65 | 82.8833
2015-09-12 21:15 | 63.6724 | 68.2667 | 77.9 | 82.6333
2015-09-12 21:30 | 63.4138 | 67.7667 | 77.15 | 82.3833
2015-09-12 21:45 | 63.1552 | 67.2667 | 76.4 | 82.1333
2015-09-12 22:00 | 62.9333 | 67 | 76 | 81.8833
2015-09-12 22:15 | 62.6833 | 67 | 76 | 81.6333
2015-09-12 22:30 | 62.4333 | 67 | 76 | 81.3833
2015-09-12 22:45 | 62.1833 | 67 | 76 | 81.1333
2015-09-12 23:00 | 61.9333 | 66.8833 | 75.8833 | 80.8833
2015-09-12 23:15 | 61.6833 | 66.6333 | 75.6333 | 80.6333
2015-09-12 23:30 | 61.4333 | 66.3833 | 75.3833 | 80.3833
2015-09-12 23:45 | 61.1833 | 66.1333 | 75.1333 | 80.1333
2015-09-13 | 61 | 65.7667 | 74.8833 | 79.8833
2015-09-13 00:15 | 61 | 65.2667 | 74.6333 | 79.6333
2015-09-13 00:30 | 61 | 64.7667 | 74.3833 | 79.3833
2015-09-13 00:45 | 61 | 64.2667 | 74.1333 | 79.1333
2015-09-13 01:00 | 60.9333 | 63.8833 | 73.8833 | 79
2015-09-13 01:15 | 60.6833 | 63.6333 | 73.6333 | 79
2015-09-13 01:30 | 60.4333 | 63.3833 | 73.3833 | 79
2015-09-13 01:45 | 60.1833 | 63.1333 | 73.1333 | 79
2015-09-13 02:00 | 60 | 63 | 72.7667 | 78.7667
2015-09-13 02:15 | 60 | 63 | 72.2667 | 78.2667
2015-09-13 02:30 | 60 | 63 | 71.7667 | 77.7667
2015-09-13 02:45 | 60 | 63 | 71.2667 | 77.2667
2015-09-13 03:00 | 60 | 63 | 70.8833 | 76.8833
2015-09-13 03:15 | 60 | 63 | 70.6333 | 76.6333
2015-09-13 03:30 | 60 | 63 | 70.3833 | 76.3833
2015-09-13 03:45 | 60 | 63 | 70.1333 | 76.1333
2015-09-13 04:00 | 60 | 63 | 70 | 75.7667
2015-09-13 04:15 | 60 | 63 | 70 | 75.2667
2015-09-13 04:30 | 60 | 63 | 70 | 74.7667
2015-09-13 04:45 | 60 | 63 | 70 | 74.2667
2015-09-13 05:00 | 59.9333 | 63.1167 | 69.7667 | 74
2015-09-13 05:15 | 59.6833 | 63.3667 | 69.2667 | 74
2015-09-13 05:30 | 59.4333 | 63.6167 | 68.7667 | 74
2015-09-13 05:45 | 59.1833 | 63.8667 | 68.2667 | 74
2015-09-13 06:00 | 59.0667 | 64.1167 | 67.8833 | 74.2333
2015-09-13 06:15 | 59.3167 | 64.3667 | 67.6333 | 74.7333
2015-09-13 06:30 | 59.5667 | 64.6167 | 67.3833 | 75.2333
2015-09-13 06:45 | 59.8167 | 64.8667 | 67.1333 | 75.7333
2015-09-13 07:00 | 60.2 | 65.2333 | 67.9333 | 76.35
2015-09-13 07:15 | 60.95 | 65.7333 | 69.9333 | 77.1
2015-09-13 07:30 | 61.7 | 66.2333 | 71.9333 | 77.85
2015-09-13 07:45 | 62.45 | 66.7333 | 73.9333 | 78.6
2015-09-13 08:00 | 63.1333 | 67.35 | 75.7 | 79.1167
2015-09-13 08:15 | 63.6333 | 68.1 | 77.2 | 79.3667
2015-09-13 08:30 | 64.1333 | 68.85 | 78.7 | 79.6167
2015-09-13 08:45 | 64.6333 | 69.6 | 80.2 | 79.8667
2015-09-13 09:00 | 65.0667 | 70.2333 | 81.5833 | 80.4667
2015-09-13 09:15 | 65.3167 | 70.7333 | 82.8333 | 81.4667
2015-09-13 09:30 | 65.5667 | 71.2333 | 84.0833 | 82.4667
2015-09-13 09:45 | 65.8167 | 71.7333 | 85.3333 | 83.4667
2015-09-13 10:00 | 66.0667 | 72.1167 | 86.4667 | 84.7
2015-09-13 10:15 | 66.3167 | 72.3667 | 87.4667 | 86.2
2015-09-13 10:30 | 66.5667 | 72.6167 | 88.4667 | 87.7
2015-09-13 10:45 | 66.8167 | 72.8667 | 89.4667 | 89.2
2015-09-13 11:00 | 67.2667 | 73.35 | 90.2333 | 90.2333
2015-09-13 11:15 | 68.2667 | 74.1 | 90.7333 | 90.7333
2015-09-13 11:30 | 69.2667 | 74.85 | 91.2333 | 91.2333
2015-09-13 11:45 | 70.2667 | 75.6 | 91.7333 | 91.7333
2015-09-13 12:00 | 70.9333 | 76.1167 | 91.7667 | 92.2333
2015-09-13 12:15 | 70.6833 | 76.3667 | 91.2667 | 92.7333
2015-09-13 12:30 | 70.4333 | 76.6167 | 90.7667 | 93.2333
2015-09-13 12:45 | 70.1833 | 76.8667 | 90.2667 | 93.7333
2015-09-13 13:00 | 69.8667 | 77.35 | 89.0667 | 94.2333
2015-09-13 13:15 | 69.3667 | 78.1 | 87.0667 | 94.7333
2015-09-13 13:30 | 68.8667 | 78.85 | 85.0667 | 95.2333
2015-09-13 13:45 | 68.3667 | 79.6 | 83.0667 | 95.7333
2015-09-13 14:00 | 67.8667 | 79.8833 | 83.2833 | 96.1167
2015-09-13 14:15 | 67.3667 | 79.6333 | 86.0333 | 96.3667
2015-09-13 14:30 | 66.8667 | 79.3833 | 88.7833 | 96.6167
2015-09-13 14:45 | 66.3667 | 79.1333 | 91.5333 | 96.8667
2015-09-13 15:00 | 65.8667 | 79.1167 | 92.8833 | 97
2015-09-13 15:15 | 65.3667 | 79.3667 | 92.6333 | 97
2015-09-13 15:30 | 64.8667 | 79.6167 | 92.3833 | 97
2015-09-13 15:45 | 64.3667 | 79.8667 | 92.1333 | 97
2015-09-13 16:00 | 63.8 | 79.3 | 91.8833 | 96.8833
2015-09-13 16:15 | 63.05 | 77.8 | 91.6333 | 96.6333
2015-09-13 16:30 | 62.3 | 76.3 | 91.3833 | 96.3833
2015-09-13 16:45 | 61.55 | 74.8 | 91.1333 | 96.1333
2015-09-13 17:00 | 60.8667 | 73.5333 | 90.7667 | 95.7667
2015-09-13 17:15 | 60.3667 | 72.5333 | 90.2667 | 95.2667
2015-09-13 17:30 | 59.8667 | 71.5333 | 89.7667 | 94.7667
2015-09-13 17:45 | 59.3667 | 70.5333 | 89.2667 | 94.2667
2015-09-13 18:00 | 59 | 69.65 | 88.5333 | 93.4167
2015-09-13 18:15 | 59 | 68.9 | 87.5333 | 92.1667
2015-09-13 18:30 | 59 | 68.15 | 86.5333 | 90.9167
2015-09-13 18:45 | 59 | 67.4 | 85.5333 | 89.6667
2015-09-13 19:00 | 59.0667 | 66.65 | 84.7667 | 88.7667
2015-09-13 19:15 | 59.3167 | 65.9 | 84.2667 | 88.2667
2015-09-13 19:30 | 59.5667 | 65.15 | 83.7667 | 87.7667
2015-09-13 19:45 | 59.8167 | 64.4 | 83.2667 | 87.2667
2015-09-13 20:00 | 60 | 63.7667 | 82.65 | 86.8833
2015-09-13 20:15 | 60 | 63.2667 | 81.9 | 86.6333
2015-09-13 20:30 | 60 | 62.7667 | 81.15 | 86.3833
2015-09-13 20:45 | 60 | 62.2667 | 80.4 | 86.1333
2015-09-13 21:00 | 60 | 62 | 79.7667 | 85.7667
2015-09-13 21:15 | 60 | 62 | 79.2667 | 85.2667
2015-09-13 21:30 | 60 | 62 | 78.7667 | 84.7667
2015-09-13 21:45 | 60 | 62 | 78.2667 | 84.2667
2015-09-13 22:00 | 60 | 62 | 77.7667 | 83.4167
2015-09-13 22:15 | 60 | 62 | 77.2667 | 82.1667
2015-09-13 22:30 | 60 | 62 | 76.7667 | 80.9167
2015-09-13 22:45 | 60 | 62 | 76.2667 | 79.6667
2015-09-13 23:00 | 60 | 62 | 75.8833 | 78.8833
2015-09-13 23:15 | 60 | 62 | 75.6333 | 78.6333
2015-09-13 23:30 | 60 | 62 | 75.3833 | 78.3833
2015-09-13 23:45 | 60 | 62 | 75.1333 | 78.1333
2015-09-14 | 59.9333 | 61.7667 | 74.8833 | 77.7667
2015-09-14 00:15 | 59.6833 | 61.2667 | 74.6333 | 77.2667
2015-09-14 00:30 | 59.4333 | 60.7667 | 74.3833 | 76.7667
2015-09-14 00:45 | 59.1833 | 60.2667 | 74.1333 | 76.2667
2015-09-14 01:00 | 59 | 60 | 73.7667 | 75.7667
2015-09-14 01:15 | 59 | 60 | 73.2667 | 75.2667
2015-09-14 01:30 | 59 | 60 | 72.7667 | 74.7667
2015-09-14 01:45 | 59 | 60 | 72.2667 | 74.2667
2015-09-14 02:00 | 59 | 60 | 71.8833 | 73.8833
2015-09-14 02:15 | 59 | 60 | 71.6333 | 73.6333
2015-09-14 02:30 | 59 | 60 | 71.3833 | 73.3833
2015-09-14 02:45 | 59 | 60 | 71.1333 | 73.1333
2015-09-14 03:00 | 59 | 60 | 70.8833 | 72.7667
2015-09-14 03:15 | 59 | 60 | 70.6333 | 72.2667
2015-09-14 03:30 | 59 | 60 | 70.3833 | 71.7667
2015-09-14 03:45 | 59 | 60 | 70.1333 | 71.2667
2015-09-14 04:00 | 59.0667 | 60.1429 | 69.8833 | 71.1167
2015-09-14 04:15 | 59.3167 | 60.449 | 69.6333 | 71.3667
2015-09-14 04:30 | 59.5667 | 60.7551 | 69.3833 | 71.6167
2015-09-14 04:45 | 59.8167 | 60.7273 | 69.1333 | 71.8667
2015-09-14 05:00 | 60.2353 | 60 | 68.8833 | 71.7667
2015-09-14 05:15 | 61 | 60 | 68.6333 | 71.2667
2015-09-14 05:30 | 61 | 60 | 68.3833 | 70.7667
2015-09-14 05:45 | 61 | 60 | 68.1333 | 70.2667
2015-09-14 06:00 | 61.1379 | 60.1167 | 67.8833 | 70.35
2015-09-14 06:15 | 61.6552 | 60.3667 | 67.6333 | 71.1
2015-09-14 06:30 | 62.1724 | 60.6167 | 67.3833 | 71.85
2015-09-14 06:45 | 62.6897 | 60.8667 | 67.1333 | 72.6
2015-09-14 07:00 | 62.1379 | 61.1167 | 67.35 | 72.7667
2015-09-14 07:15 | 62.6552 | 61.3667 | 68.1 | 72.2667
2015-09-14 07:30 | 63.1724 | 61.6167 | 68.85 | 71.7667
2015-09-14 07:45 | 63.6897 | 61.8667 | 69.6 | 71.2667
2015-09-14 08:00 | 64 | 62.4667 | 71.05 | 71.2333
2015-09-14 08:15 | 64 | 63.4667 | 73.3 | 71.7333
2015-09-14 08:30 | 64 | 64.4667 | 75.55 | 72.2333
2015-09-14 08:45 | 64 | 65.4667 | 77.8 | 72.7333
2015-09-14 09:00 | 64.0667 | 66.2333 | 79.9333 | 72.7667
2015-09-14 09:15 | 64.3167 | 66.7333 | 81.9333 | 72.2667
2015-09-14 09:30 | 64.5667 | 67.2333 | 83.9333 | 71.7667
2015-09-14 09:45 | 64.8167 | 67.7333 | 85.9333 | 71.2667
2015-09-14 10:00 | 65 | 68.2333 | 87.35 | 71
2015-09-14 10:15 | 65 | 68.7333 | 88.1 | 71
2015-09-14 10:30 | 65 | 69.2333 | 88.85 | 71
2015-09-14 10:45 | 65 | 69.7333 | 89.6 | 71
2015-09-14 11:00 | 65 | 70 | 90.35 | 71.35
2015-09-14 11:15 | 65 | 70 | 91.1 | 72.1
2015-09-14 11:30 | 65 | 70 | 91.85 | 72.85
2015-09-14 11:45 | 65 | 70 | 92.6 | 73.6
2015-09-14 12:00 | 65.2 | 70 | 92.8833 | 74.2333
2015-09-14 12:15 | 65.95 | 70 | 92.6333 | 74.7333
2015-09-14 12:30 | 66.7 | 70 | 92.3833 | 75.2333
2015-09-14 12:45 | 67.45 | 70 | 92.1333 | 75.7333
2015-09-14 13:00 | 67.9333 | 70.2333 | 92.1167 | 76.4667
2015-09-14 13:15 | 67.6833 | 70.7333 | 92.3667 | 77.4667
2015-09-14 13:30 | 67.4333 | 71.2333 | 92.6167 | 78.4667
2015-09-14 13:45 | 67.1833 | 71.7333 | 92.8667 | 79.4667
2015-09-14 14:00 | 67 | 71.5333 | 93.2692 | 80
2015-09-14 14:15 | 67 | 70.5333 | 93.8462 | 80
2015-09-14 14:30 | 67 | 69.5333 | 94 | 80
2015-09-14 14:45 | 67 | 68.5333 | 94 | 80
2015-09-14 15:00 | 66.9333 | 68.2333 | 93.8833 | 80.1167
2015-09-14 15:15 | 66.6833 | 68.7333 | 93.6333 | 80.3667
2015-09-14 15:30 | 66.4333 | 69.2333 | 93.3833 | 80.6167
2015-09-14 15:45 | 66.1833 | 69.7333 | 93.1333 | 80.8667
2015-09-14 16:00 | 65.8667 | 70 | 92.7667 | 80.8833
2015-09-14 16:15 | 65.3667 | 70 | 92.2667 | 80.6333
2015-09-14 16:30 | 64.8667 | 70 | 91.7667 | 80.3833
2015-09-14 16:45 | 64.3667 | 70 | 91.2667 | 80.1333
2015-09-14 17:00 | 63.9333 | 69.8833 | 90.65 | 79.65
2015-09-14 17:15 | 63.6833 | 69.6333 | 89.9 | 78.9
2015-09-14 17:30 | 63.4333 | 69.3833 | 89.15 | 78.15
2015-09-14 17:45 | 63.1833 | 69.1333 | 88.4 | 77.4
2015-09-14 18:00 | 62.9333 | 68.8372 | 87.5333 | 76.8833
2015-09-14 18:15 | 62.6833 | 68.4884 | 86.5333 | 76.6333
2015-09-14 18:30 | 62.4333 | 68.1395 | 85.5333 | 76.3833
2015-09-14 18:45 | 62.1833 | 68 | 84.5333 | 76.1333
2015-09-14 19:00 | 62 | 67.8833 | 83.65 | 75.8833
2015-09-14 19:15 | 62 | 67.6333 | 82.9 | 75.6333
2015-09-14 19:30 | 62 | 67.3833 | 82.15 | 75.3833
2015-09-14 19:45 | 62 | 67.1333 | 81.4 | 75.1333
2015-09-14 20:00 | 61.8667 | 66.8679 | 80.7667 | 74.8833
2015-09-14 20:15 | 61.3667 | 66.5849 | 80.2667 | 74.6333
2015-09-14 20:30 | 60.8667 | 66.3019 | 79.7667 | 74.3833
2015-09-14 20:45 | 60.3667 | 66.0189 | 79.2667 | 74.1333
2015-09-14 21:00 | 60.0667 | 65.8833 | 78.8833 | 73.8833
2015-09-14 21:15 | 60.3167 | 65.6333 | 78.6333 | 73.6333
2015-09-14 21:30 | 60.5667 | 65.3833 | 78.3833 | 73.3833
2015-09-14 21:45 | 60.8167 | 65.1333 | 78.1333 | 73.1333
2015-09-14 22:00 | 61 | 64.7586 | 77.7667 | 72.8833
2015-09-14 22:15 | 61 | 64.2414 | 77.2667 | 72.6333
2015-09-14 22:30 | 61 | 64.2581 | 76.7667 | 72.3833
2015-09-14 22:45 | 61 | 64.7419 | 76.2667 | 72.1333
2015-09-14 23:00 | 60.8667 | 64.75 | 75.8833 | 72
2015-09-14 23:15 | 60.3667 | 64.2143 | 75.6333 | 72
2015-09-14 23:30 | 59.8667 | 64 | 75.3833 | 72
2015-09-14 23:45 | 59.3667 | 64 | 75.1333 | 72
2015-09-15 | 59 | 64 | 74.8833 | 71.7667
2015-09-15 00:15 | 59 | 64 | 74.6333 | 71.2667
2015-09-15 00:30 | 59 | 64 | 74.3833 | 70.7667
2015-09-15 00:45 | 59 | 64 | 74.1333 | 70.2667
2015-09-15 01:00 | 58.9333 | 63.8833 | 73.8833 | 70.1167
2015-09-15 01:15 | 58.6833 | 63.6333 | 73.6333 | 70.3667
2015-09-15 01:30 | 58.4333 | 63.3833 | 73.3833 | 70.6167
2015-09-15 01:45 | 58.1833 | 63.1333 | 73.1333 | 70.8667
2015-09-15 02:00 | 57.8824 | 63 | 72.8833 | 70.8833
2015-09-15 02:15 | 57.4412 | 63 | 72.6333 | 70.6333
2015-09-15 02:30 | 57 | 63 | 72.3833 | 70.3833
2015-09-15 02:45 | 57 | 63 | 72.1333 | 70.1333
2015-09-15 03:00 | 57 | 63 | 71.8833 | 69.8833
2015-09-15 03:15 | 57 | 63 | 71.6333 | 69.6333
2015-09-15 03:30 | 57 | 63 | 71.3833 | 69.3833
2015-09-15 03:45 | 57 | 63 | 71.1333 | 69.1333
2015-09-15 04:00 | 57 | 61.7742 | 70.7667 | 68.7667
2015-09-15 04:15 | 57 | 61.2903 | 70.2667 | 68.2667
2015-09-15 04:30 | 57 | 61 | 69.7667 | 67.7667
2015-09-15 04:45 | 57 | 61 | 69.2667 | 67.2667
2015-09-15 05:00 | 57 | 59.8833 | 68.8833 | 66.8833
2015-09-15 05:15 | 57 | 59.6333 | 68.6333 | 66.6333
2015-09-15 05:30 | 57 | 59.3833 | 68.3833 | 66.3833
2015-09-15 05:45 | 57 | 59.1333 | 68.1333 | 66.1333
2015-09-15 06:00 | 58.0667 | 59.1167 | 67.7667 | 66.2333
2015-09-15 06:15 | 58.3167 | 59.3667 | 67.2667 | 66.7333
2015-09-15 06:30 | 58.5667 | 59.6167 | 66.7667 | 67.2333
2015-09-15 06:45 | 58.8167 | 59.8667 | 66.2667 | 67.7333
2015-09-15 07:00 | 59 | 60.1167 | 66.4667 | 68.2333
2015-09-15 07:15 | 59 | 60.3667 | 67.4667 | 68.7333
2015-09-15 07:30 | 59 | 60.6167 | 68.4667 | 69.2333
2015-09-15 07:45 | 59 | 60.8667 | 69.4667 | 69.7333
2015-09-15 08:00 | 59.2 | 62.2727 | 70.8167 | 70.35
2015-09-15 08:15 | 59.95 | 63 | 72.5667 | 71.1
2015-09-15 08:30 | 60.7 | 63 | 74.3167 | 71.85
2015-09-15 08:45 | 61.45 | 63 | 76.0667 | 72.6
2015-09-15 09:00 | 62.2 | 63.4667 | 77.5833 | 73.4667
2015-09-15 09:15 | 62.95 | 64.4667 | 78.8333 | 74.4667
2015-09-15 09:30 | 63.7 | 65.4667 | 80.0833 | 75.4667
2015-09-15 09:45 | 64.45 | 66.4667 | 81.3333 | 76.4667
2015-09-15 10:00 | 64.9333 | 67.35 | 82.7 | 77.2333
2015-09-15 10:15 | 64.6833 | 68.1 | 84.2 | 77.7333
2015-09-15 10:30 | 64.4333 | 68.85 | 85.7 | 78.2333
2015-09-15 10:45 | 64.1833 | 69.6 | 87.2 | 78.7333
2015-09-15 11:00 | 64.0667 | 70 | 88.7 | 79.1167
2015-09-15 11:15 | 64.3167 | 70 | 90.2 | 79.3667
2015-09-15 11:30 | 64.5667 | 70 | 91.7 | 79.6167
2015-09-15 11:45 | 64.8167 | 70 | 93.2 | 79.8667
2015-09-15 12:00 | 65.1333 | 70.2333 | 94.1167 | 80.4667
2015-09-15 12:15 | 65.6333 | 70.7333 | 94.3667 | 81.4667
2015-09-15 12:30 | 66.1333 | 71.2333 | 94.6167 | 82.4667
2015-09-15 12:45 | 66.6333 | 71.7333 | 94.8667 | 83.4667
2015-09-15 13:00 | 67 | 71.8833 | 95.1167 | 84
2015-09-15 13:15 | 67 | 71.6333 | 95.3667 | 84
2015-09-15 13:30 | 67 | 71.3833 | 95.6167 | 84
2015-09-15 13:45 | 67 | 71.1333 | 95.8667 | 84
2015-09-15 14:00 | 66.8 | 70.8833 | 96 | 83.8833
2015-09-15 14:15 | 66.05 | 70.6333 | 96 | 83.6333
2015-09-15 14:30 | 65.3 | 70.3833 | 96 | 83.3833
2015-09-15 14:45 | 64.55 | 70.1333 | 96 | 83.1333
2015-09-15 15:00 | 63.9333 | 69.7667 | 95.7667 | 83
2015-09-15 15:15 | 63.6833 | 69.2667 | 95.2667 | 83
2015-09-15 15:30 | 63.4333 | 68.7667 | 94.7667 | 83
2015-09-15 15:45 | 63.1833 | 68.2667 | 94.2667 | 83
2015-09-15 16:00 | 62.8667 | 67.7667 | 93.8833 | 82.8833
2015-09-15 16:15 | 62.3667 | 67.2667 | 93.6333 | 82.6333
2015-09-15 16:30 | 61.8667 | 66.7667 | 93.3833 | 82.3833
2015-09-15 16:45 | 61.3667 | 66.2667 | 93.1333 | 82.1333
2015-09-15 17:00 | 61 | 65.65 | 92.65 | 81.65
2015-09-15 17:15 | 61 | 64.9 | 91.9 | 80.9
2015-09-15 17:30 | 61 | 64.15 | 91.15 | 80.15
2015-09-15 17:45 | 61 | 63.4 | 90.4 | 79.4
2015-09-15 18:00 | 60.9333 | 62.7667 | 89.5333 | 78.65
2015-09-15 18:15 | 60.6833 | 62.2667 | 88.5333 | 77.9
2015-09-15 18:30 | 60.4333 | 61.7667 | 87.5333 | 77.15
2015-09-15 18:45 | 60.1833 | 61.2667 | 86.5333 | 76.4
2015-09-15 19:00 | 59.9333 | 60.8833 | 85.65 | 75.65
2015-09-15 19:15 | 59.6833 | 60.6333 | 84.9 | 74.9
2015-09-15 19:30 | 59.4333 | 60.3833 | 84.15 | 74.15
2015-09-15 19:45 | 59.1833 | 60.1333 | 83.4 | 73.4
2015-09-15 20:00 | 59 | 59.8833 | 82.7667 | 72.7667
2015-09-15 20:15 | 59 | 59.6333 | 82.2667 | 72.2667
2015-09-15 20:30 | 59 | 59.3833 | 81.7667 | 71.7667
2015-09-15 20:45 | 59 | 59.1333 | 81.2667 | 71.2667
2015-09-15 21:00 | 59 | 59 | 80.7667 | 70.65
2015-09-15 21:15 | 59 | 59 | 80.2667 | 69.9
2015-09-15 21:30 | 59 | 59 | 79.7667 | 69.15
2015-09-15 21:45 | 59 | 59 | 79.2667 | 68.4
2015-09-15 22:00 | 59 | 58.8833 | 78.7667 | 67.8833
2015-09-15 22:15 | 59 | 58.6333 | 78.2667 | 67.6333
2015-09-15 22:30 | 59 | 58.3833 | 77.7667 | 67.3833
2015-09-15 22:45 | 59 | 58.1333 | 77.2667 | 67.1333
2015-09-15 23:00 | 59 | 58.1842 | 76.8833 | 66.7667
2015-09-15 23:15 | 59 | 58.5789 | 76.6333 | 66.2667
2015-09-15 23:30 | 59 | 58.9737 | 76.3833 | 65.7667
2015-09-15 23:45 | 59 | 58.3636 | 76.1333 | 65.2667
2015-09-16 | 59.0667 | 57.5625 | 75.8833 | 64.7667
2015-09-16 00:15 | 59.3167 | 56.8636 | 75.6333 | 64.2667
2015-09-16 00:30 | 59.5667 | 56.5227 | 75.3833 | 63.7667
2015-09-16 00:45 | 59.8167 | 56.1818 | 75.1333 | 63.2667
2015-09-16 01:00 | 59.7647 | 55.8833 | 75 | 62.8833
2015-09-16 01:15 | 59 | 55.6333 | 75 | 62.6333
2015-09-16 01:30 | 59 | 55.3833 | 75 | 62.3833
2015-09-16 01:45 | 59 | 55.1333 | 75 | 62.1333
2015-09-16 02:00 | 58.9333 | 54.7667 | 74.8833 | 61.7667
2015-09-16 02:15 | 58.6833 | 54.2667 | 74.6333 | 61.2667
2015-09-16 02:30 | 58.4333 | 53.7667 | 74.3833 | 60.7667
2015-09-16 02:45 | 58.1833 | 53.2667 | 74.1333 | 60.2667
2015-09-16 03:00 | 58.0667 | 53.1167 | 74 | 59.8833
2015-09-16 03:15 | 58.3167 | 53.3667 | 74 | 59.6333
2015-09-16 03:30 | 58.5667 | 53.6167 | 74 | 59.3833
2015-09-16 03:45 | 58.8167 | 53.8667 | 74 | 59.1333
2015-09-16 04:00 | 59 | 54 | 73.7667 | 58.7667
2015-09-16 04:15 | 59 | 54 | 73.2667 | 58.2667
2015-09-16 04:30 | 59 | 54 | 72.7667 | 57.7667
2015-09-16 04:45 | 59 | 54 | 72.2667 | 57.2667
2015-09-16 05:00 | 59 | 54 | 71.8833 | 56.8833
2015-09-16 05:15 | 59 | 54 | 71.6333 | 56.6333
2015-09-16 05:30 | 59 | 54 | 71.3833 | 56.3833
2015-09-16 05:45 | 59 | 54 | 71.1333 | 56.1333
2015-09-16 06:00 | 59 | 54.35 | 70.7667 | 56.2333
2015-09-16 06:15 | 59 | 55.1 | 70.2667 | 56.7333
2015-09-16 06:30 | 59 | 55.85 | 69.7667 | 57.2333
2015-09-16 06:45 | 59 | 56.6 | 69.2667 | 57.7333
2015-09-16 07:00 | 59.2667 | 57.35 | 69.5833 | 58.35
2015-09-16 07:15 | 60.2667 | 58.1 | 70.8333 | 59.1
2015-09-16 07:30 | 61.2667 | 58.85 | 72.0833 | 59.85
2015-09-16 07:45 | 62.2667 | 59.6 | 73.3333 | 60.6
2015-09-16 08:00 | 63.0667 | 60.4667 | 74.5833 | 61.7
2015-09-16 08:15 | 63.3167 | 61.4667 | 75.8333 | 63.2
2015-09-16 08:30 | 63.5667 | 62.4667 | 77.0833 | 64.7
2015-09-16 08:45 | 63.8167 | 63.4667 | 78.3333 | 66.2
2015-09-16 09:00 | 64.2 | 64.35 | 79.7 | 67.2333
2015-09-16 09:15 | 64.95 | 65.1 | 81.2 | 67.7333
2015-09-16 09:30 | 65.7 | 65.85 | 82.7 | 68.2333
2015-09-16 09:45 | 66.45 | 66.6 | 84.2 | 68.7333
2015-09-16 10:00 | 67.0667 | 67.35 | 85.4667 | 69.2333
2015-09-16 10:15 | 67.3167 | 68.1 | 86.4667 | 69.7333
2015-09-16 10:30 | 67.5667 | 68.85 | 87.4667 | 70.2333
2015-09-16 10:45 | 67.8167 | 69.6 | 88.4667 | 70.7333
2015-09-16 11:00 | 68.1333 | 70.1167 | 89.4667 | 71.35
2015-09-16 11:15 | 68.6333 | 70.3667 | 90.4667 | 72.1
2015-09-16 11:30 | 69.1333 | 70.6167 | 91.4667 | 72.85
2015-09-16 11:45 | 69.6333 | 70.8667 | 92.4667 | 73.6
2015-09-16 12:00 | 69.9333 | 71 | 93.1167 | 74.1167
2015-09-16 12:15 | 69.6833 | 71 | 93.3667 | 74.3667
2015-09-16 12:30 | 69.4333 | 71 | 93.6167 | 74.6167
2015-09-16 12:45 | 69.1833 | 71 | 93.8667 | 74.8667
2015-09-16 13:00 | 69 | 71.2333 | 94 | 75.2333
2015-09-16 13:15 | 69 | 71.7333 | 94 | 75.7333
2015-09-16 13:30 | 69 | 72.2333 | 94 | 76.2333
2015-09-16 13:45 | 69 | 72.7333 | 94 | 76.7333
2015-09-16 14:00 | 69 | 73 | 94.1167 | 77.1167
2015-09-16 14:15 | 69 | 73 | 94.3667 | 77.3667
2015-09-16 14:30 | 69 | 73 | 94.6167 | 77.6167
2015-09-16 14:45 | 69 | 73 | 94.8667 | 77.8667
2015-09-16 15:00 | 68.8667 | 73 | 95 | 78.1167
2015-09-16 15:15 | 68.3667 | 73 | 95 | 78.3667
2015-09-16 15:30 | 67.8667 | 73 | 95 | 78.6167
2015-09-16 15:45 | 67.3667 | 73 | 95 | 78.8667
2015-09-16 16:00 | 66.9333 | 72.65 | 94.65 | 79
2015-09-16 16:15 | 66.6833 | 71.9 | 93.9 | 79
2015-09-16 16:30 | 66.4333 | 71.15 | 93.15 | 79
2015-09-16 16:45 | 66.1833 | 70.4 | 92.4 | 79
2015-09-16 17:00 | 65.7333 | 69.7667 | 91.65 | 78.65
2015-09-16 17:15 | 64.7333 | 69.2667 | 90.9 | 77.9
2015-09-16 17:30 | 63.7333 | 68.7667 | 90.15 | 77.15
2015-09-16 17:45 | 62.7333 | 68.2667 | 89.4 | 76.4
2015-09-16 18:00 | 62.1333 | 67.8833 | 88.5333 | 75.7667
2015-09-16 18:15 | 62.6333 | 67.6333 | 87.5333 | 75.2667
2015-09-16 18:30 | 63.1333 | 67.3833 | 86.5333 | 74.7667
2015-09-16 18:45 | 63.6333 | 67.1333 | 85.5333 | 74.2667
2015-09-16 19:00 | 63.7778 | 66.8833 | 84.65 | 73.65
2015-09-16 19:15 | 63 | 66.6333 | 83.9 | 72.9
2015-09-16 19:30 | 63 | 66.3833 | 83.15 | 72.15
2015-09-16 19:45 | 63 | 66.1333 | 82.4 | 71.4
2015-09-16 20:00 | 63 | 66 | 81.7667 | 70.65
2015-09-16 20:15 | 63 | 66 | 81.2667 | 69.9
2015-09-16 20:30 | 63 | 66 | 80.7667 | 69.15
2015-09-16 20:45 | 63 | 66 | 80.2667 | 68.4
2015-09-16 21:00 | 63.069 | 65.7667 | 79.7667 | 67.7667
2015-09-16 21:15 | 63.3276 | 65.2667 | 79.2667 | 67.2667
2015-09-16 21:30 | 63.5862 | 64.7667 | 78.7667 | 66.7667
2015-09-16 21:45 | 63.8448 | 64.2667 | 78.2667 | 66.2667
2015-09-16 22:00 | 63.9333 | 63.8833 | 77.8833 | 65.7667
2015-09-16 22:15 | 63.6833 | 63.6333 | 77.6333 | 65.2667
2015-09-16 22:30 | 63.4333 | 63.3833 | 77.3833 | 64.7667
2015-09-16 22:45 | 63.1833 | 63.1333 | 77.1333 | 64.2667
2015-09-16 23:00 | 63 | 63 | 76.8833 | 63.8833
2015-09-16 23:15 | 63 | 63 | 76.6333 | 63.6333
2015-09-16 23:30 | 63 | 63 | 76.3833 | 63.3833
2015-09-16 23:45 | 62.55 | 63 | 76.1333 | 63.1333
2015-09-17 | 62 | 62.8833 | 76 | 62.8833
2015-09-17 00:15 | 62 | 62.6333 | 76 | 62.6333
2015-09-17 00:30 | 62 | 62.3833 | 76 | 62.3833
2015-09-17 00:45 | 62 | 62.1333 | 76 | 62.1333
2015-09-17 01:00 | 61.9111 | 61.8833 | 75.8833 | 61.8833
2015-09-17 01:15 | 61.5778 | 61.6333 | 75.6333 | 61.6333
2015-09-17 01:30 | 61.2444 | 61.3833 | 75.3833 | 61.3833
2015-09-17 01:45 | 60.7333 | 61.1333 | 75.1333 | 61.1333
2015-09-17 02:00 | 60.2222 | 60.8833 | 74.8833 | 61
2015-09-17 02:15 | 60.9762 | 60.6333 | 74.6333 | 61
2015-09-17 02:30 | 60.619 | 60.3833 | 74.3833 | 61
2015-09-17 02:45 | 60.2619 | 60.1333 | 74.1333 | 61
2015-09-17 03:00 | 60.1212 | 60 | 73.8833 | 60.8833
2015-09-17 03:15 | 60.5758 | 60 | 73.6333 | 60.6333
2015-09-17 03:30 | 61 | 60 | 73.3833 | 60.3833
2015-09-17 03:45 | 61 | 60 | 73.1333 | 60.1333
2015-09-17 04:00 | 60 | 59.8627 | 72.8833 | 59.8833
2015-09-17 04:15 | 60 | 59.5686 | 72.6333 | 59.6333
2015-09-17 04:30 | 60 | 59.2745 | 72.3833 | 59.3833
2015-09-17 04:45 | 60 | 59 | 72.1333 | 59.1333
2015-09-17 05:00 | 59.931 | 59 | 71.8833 | 58.8833
2015-09-17 05:15 | 59.6724 | 59 | 71.6333 | 58.6333
2015-09-17 05:30 | 59.4138 | 59 | 71.3833 | 58.3833
2015-09-17 05:45 | 59.1552 | 59 | 71.1333 | 58.1333
2015-09-17 06:00 | 59 | 59.1167 | 70.8833 | 58.2333
2015-09-17 06:15 | 59 | 59.3667 | 70.6333 | 58.7333
2015-09-17 06:30 | 59 | 59.6167 | 70.3833 | 59.2333
2015-09-17 06:45 | 59 | 59.8667 | 70.1333 | 59.7333
2015-09-17 07:00 | 59.1379 | 60.35 | 70.35 | 60.5833
2015-09-17 07:15 | 59.6552 | 61.1 | 71.1 | 61.8333
2015-09-17 07:30 | 60.1724 | 61.85 | 71.85 | 63.0833
2015-09-17 07:45 | 60.6897 | 62.6 | 72.6 | 64.3333
2015-09-17 08:00 | 61.8 | 63.2333 | 73.7 | 65.4667
2015-09-17 08:15 | 62.82 | 63.7333 | 75.2 | 66.4667
2015-09-17 08:30 | 62.52 | 64.2333 | 76.7 | 67.4667
2015-09-17 08:45 | 62.22 | 64.7333 | 78.2 | 68.4667
2015-09-17 09:00 | 62.0667 | 65.1556 | 79.5833 | 69.35
2015-09-17 09:15 | 62.3167 | 65.4889 | 80.8333 | 70.1
2015-09-17 09:30 | 62.5667 | 65.8222 | 82.0833 | 70.85
2015-09-17 09:45 | 62.8167 | 66.4667 | 83.3333 | 71.6
2015-09-17 10:00 | 63.069 | 67.2333 | 84.8167 | 72.35
2015-09-17 10:15 | 63.3276 | 67.7333 | 86.5667 | 73.1
2015-09-17 10:30 | 63.5862 | 68.2333 | 88.3167 | 73.85
2015-09-17 10:45 | 63.8448 | 68.7333 | 90.0667 | 74.6
2015-09-17 11:00 | 66 | 69.1167 | 91.35 | 75.1167
2015-09-17 11:15 | 66 | 69.3667 | 92.1 | 75.3667
2015-09-17 11:30 | 66 | 69.6167 | 92.85 | 75.6167
2015-09-17 11:45 | 66 | 69.8667 | 93.6 | 75.8667
2015-09-17 12:00 | 66.2 | 70.35 | 94.2333 | 76.2333
2015-09-17 12:15 | 66.95 | 71.1 | 94.7333 | 76.7333
2015-09-17 12:30 | 67.7 | 71.85 | 95.2333 | 77.2333
2015-09-17 12:45 | 68.45 | 72.6 | 95.7333 | 77.7333
2015-09-17 13:00 | 68.9333 | 73.2333 | 96.35 | 78.2333
2015-09-17 13:15 | 68.6833 | 73.7333 | 97.1 | 78.7333
2015-09-17 13:30 | 68.4333 | 74.2333 | 97.85 | 79.2333
2015-09-17 13:45 | 68.1833 | 74.7333 | 98.6 | 79.7333
2015-09-17 14:00 | 68 | 74.8833 | 99 | 80
2015-09-17 14:15 | 68 | 74.6333 | 99 | 80
2015-09-17 14:30 | 68 | 74.3833 | 99 | 80
2015-09-17 14:45 | 68 | 74.1333 | 99 | 80
2015-09-17 15:00 | 67.7333 | 73.8833 | 98.7667 | 80
2015-09-17 15:15 | 66.7333 | 73.6333 | 98.2667 | 80
2015-09-17 15:30 | 65.7333 | 73.3833 | 97.7667 | 80
2015-09-17 15:45 | 64.7333 | 73.1333 | 97.2667 | 80
2015-09-17 16:00 | 63.9333 | 72.65 | 96.7667 | 80
2015-09-17 16:15 | 63.6833 | 71.9 | 96.2667 | 80
2015-09-17 16:30 | 63.4333 | 71.15 | 95.7667 | 80
2015-09-17 16:45 | 63.1833 | 70.4 | 95.2667 | 80
2015-09-17 17:00 | 62.8 | 69.65 | 94.5333 | 79.65
2015-09-17 17:15 | 62.05 | 68.9 | 93.5333 | 78.9
2015-09-17 17:30 | 61.3 | 68.15 | 92.5333 | 78.15
2015-09-17 17:45 | 60.55 | 67.4 | 91.5333 | 77.4
2015-09-17 18:00 | 60 | 66.65 | 90.65 | 76.7667
2015-09-17 18:15 | 60 | 65.9 | 89.9 | 76.2667
2015-09-17 18:30 | 60 | 65.15 | 89.15 | 75.7667
2015-09-17 18:45 | 60 | 64.4 | 88.4 | 75.2667
2015-09-17 19:00 | 60 | 63.7667 | 87.65 | 74.7667
2015-09-17 19:15 | 60 | 63.2667 | 86.9 | 74.2667
2015-09-17 19:30 | 60 | 62.7667 | 86.15 | 73.7667
2015-09-17 19:45 | 60 | 62.2667 | 85.4 | 73.2667
2015-09-17 20:00 | 60 | 61.8833 | 84.7667 | 72.8833
2015-09-17 20:15 | 60 | 61.6333 | 84.2667 | 72.6333
2015-09-17 20:30 | 60 | 61.3833 | 83.7667 | 72.3833
2015-09-17 20:45 | 60 | 61.1333 | 83.2667 | 72.1333
2015-09-17 21:00 | 60 | 61.1167 | 82.7667 | 71.7667
2015-09-17 21:15 | 60 | 61.3667 | 82.2667 | 71.2667
2015-09-17 21:30 | 60 | 61.6167 | 81.7667 | 70.7667
2015-09-17 21:45 | 60 | 61.8667 | 81.2667 | 70.2667
2015-09-17 22:00 | 59.9333 | 61.8833 | 80.7667 | 69.7667
2015-09-17 22:15 | 59.6833 | 61.6333 | 80.2667 | 69.2667
2015-09-17 22:30 | 59.4333 | 61.3833 | 79.7667 | 68.7667
2015-09-17 22:45 | 59.1833 | 61.1333 | 79.2667 | 68.2667
2015-09-17 23:00 | 58.9333 | 60.8833 | 78.8833 | 67.65
2015-09-17 23:15 | 58.6833 | 60.6333 | 78.6333 | 66.9
2015-09-17 23:30 | 58.4333 | 60.3833 | 78.3833 | 66.15
2015-09-17 23:45 | 58.1833 | 60.1333 | 78.1333 | 65.4
2015-09-18 | 58.0667 | 59.8833 | 77.7667 | 64.8833
2015-09-18 00:15 | 58.3167 | 59.6333 | 77.2667 | 64.6333
2015-09-18 00:30 | 58.5667 | 59.3833 | 76.7667 | 64.3833
2015-09-18 00:45 | 58.8167 | 59.1333 | 76.2667 | 64.1333
2015-09-18 01:00 | 58.9333 | 58.8833 | 75.8833 | 63.8833
2015-09-18 01:15 | 58.6833 | 58.6333 | 75.6333 | 63.6333
2015-09-18 01:30 | 58.4333 | 58.3833 | 75.3833 | 63.3833
2015-09-18 01:45 | 58.1833 | 58.1333 | 75.1333 | 63.1333
2015-09-18 02:00 | 58 | 57.8833 | 74.8833 | 62.7667
2015-09-18 02:15 | 58 | 57.6333 | 74.6333 | 62.2667
2015-09-18 02:30 | 58 | 57.3833 | 74.3833 | 61.7667
2015-09-18 02:45 | 58 | 57.1333 | 74.1333 | 61.2667
2015-09-18 03:00 | 57.9333 | 56.8833 | 73.8833 | 61
2015-09-18 03:15 | 57.6833 | 56.6333 | 73.6333 | 61
2015-09-18 03:30 | 57.4333 | 56.3833 | 73.3833 | 61
2015-09-18 03:45 | 57.1833 | 56.1333 | 73.1333 | 61
2015-09-18 04:00 | 57 | 56 | 73 | 60.8833
2015-09-18 04:15 | 57 | 56 | 73 | 60.6333
2015-09-18 04:30 | 57 | 56 | 73 | 60.3833
2015-09-18 04:45 | 57 | 56 | 73 | 60.1333
2015-09-18 05:00 | 57.0667 | 56 | 72.8833 | 59.8833
2015-09-18 05:15 | 57.3167 | 56 | 72.6333 | 59.6333
2015-09-18 05:30 | 57.5667 | 56 | 72.3833 | 59.3833
2015-09-18 05:45 | 57.8167 | 56 | 72.1333 | 59.1333
2015-09-18 06:00 | 58.2 | 56.2333 | 71.8833 | 59.35
2015-09-18 06:15 | 58.95 | 56.7333 | 71.6333 | 60.1
2015-09-18 06:30 | 59.7 | 57.2333 | 71.3833 | 60.85
2015-09-18 06:45 | 60.45 | 57.7333 | 71.1333 | 61.6
2015-09-18 07:00 | 61.1333 | 58.4667 | 71.525 | 62.4667
2015-09-18 07:15 | 61.6333 | 59.4667 | 72.65 | 63.4667
2015-09-18 07:30 | 62.1333 | 60.4667 | 73.775 | 64.4667
2015-09-18 07:45 | 62.6333 | 61.4667 | 74.9 | 65.4667
2015-09-18 08:00 | 63.1333 | 62.4667 | 76.025 | 66.4667
2015-09-18 08:15 | 63.6333 | 63.4667 | 77.15 | 67.4667
2015-09-18 08:30 | 64.1333 | 64.4667 | 78.275 | 68.4667
2015-09-18 08:45 | 64.6333 | 65.4667 | 79.4 | 69.4667
2015-09-18 09:00 | 65.2 | 66.4667 | 80.5833 | 70.35
2015-09-18 09:15 | 65.95 | 67.4667 | 81.8333 | 71.1
2015-09-18 09:30 | 66.7 | 68.4667 | 83.0833 | 71.85
2015-09-18 09:45 | 67.45 | 69.4667 | 84.3333 | 72.6
2015-09-18 10:00 | 68.1333 | 70.35 | 85.5833 | 73.4667
2015-09-18 10:15 | 68.6333 | 71.1 | 86.8333 | 74.4667
2015-09-18 10:30 | 69.1333 | 71.85 | 88.0833 | 75.4667
2015-09-18 10:45 | 69.6333 | 72.6 | 89.3333 | 76.4667
2015-09-18 11:00 | 70.2 | 73.4667 | 90.4667 | 77.35
2015-09-18 11:15 | 70.95 | 74.4667 | 91.4667 | 78.1
2015-09-18 11:30 | 71.7 | 75.4667 | 92.4667 | 78.85
2015-09-18 11:45 | 72.45 | 76.4667 | 93.4667 | 79.6
2015-09-18 12:00 | 73.3333 | 77.35 | 94.2333 | 80.4667
2015-09-18 12:15 | 74.5833 | 78.1 | 94.7333 | 81.4667
2015-09-18 12:30 | 75.8333 | 78.85 | 95.2333 | 82.4667
2015-09-18 12:45 | 77.0833 | 79.6 | 95.7333 | 83.4667
2015-09-18 13:00 | 77.6667 | 80 | 96.4667 | 84
2015-09-18 13:15 | 76.4167 | 80 | 97.4667 | 84
2015-09-18 13:30 | 75.1667 | 80 | 98.4667 | 84
2015-09-18 13:45 | 73.9167 | 80 | 99.4667 | 84
2015-09-18 14:00 | 73 | 80 | 99.65 | 84.35
2015-09-18 14:15 | 73 | 80 | 98.9 | 85.1
2015-09-18 14:30 | 73 | 80 | 98.15 | 85.85
2015-09-18 14:45 | 73 | 80 | 97.4 | 86.6
2015-09-18 15:00 | 72.8667 | 79.8833 | 97.3684 | 86.8833
2015-09-18 15:15 | 72.3667 | 79.6333 | 97.1 | 86.6333
2015-09-18 15:30 | 71.8667 | 79.3833 | 92.6 | 86.3833
2015-09-18 15:45 | 71.3667 | 79.1333 | 81.4375 | 86.1333
2015-09-18 16:00 | 70.8667 | 78.7667 | 80.1176 | 86
2015-09-18 16:15 | 70.3667 | 78.2667 | 74.75 | 86
2015-09-18 16:30 | 69.8667 | 77.7667 | 75.2 | 86
2015-09-18 16:45 | 69.3667 | 77.2667 | 76.7692 | 86
2015-09-18 17:00 | 68.6 | 76.4167 | 79.6471 | 85.65
2015-09-18 17:15 | 67.1 | 75.1667 | 82 | 84.9
2015-09-18 17:30 | 65.6 | 73.9167 | 82 | 84.15
2015-09-18 17:45 | 64.1 | 72.6667 | 81.4 | 83.4
2015-09-18 18:00 | 62.9333 | 71.5333 | 81.2333 | 82.65
2015-09-18 18:15 | 62.6833 | 70.5333 | 81.7333 | 81.9
2015-09-18 18:30 | 62.4333 | 69.5333 | 82.2333 | 81.15
2015-09-18 18:45 | 62.1833 | 68.5333 | 82.7333 | 80.4
2015-09-18 19:00 | 61.9333 | 67.65 | 83 | 79.5333
2015-09-18 19:15 | 61.6833 | 66.9 | 83 | 78.5333
2015-09-18 19:30 | 61.4333 | 66.15 | 83 | 77.5333
2015-09-18 19:45 | 61.1833 | 65.4 | 83 | 76.5333
2015-09-18 20:00 | 60.9333 | 64.8833 | 82.65 | 75.8833
2015-09-18 20:15 | 60.6833 | 64.6333 | 81.9 | 75.6333
2015-09-18 20:30 | 60.4333 | 64.3833 | 81.15 | 75.3833
2015-09-18 20:45 | 60.1833 | 64.1333 | 80.4 | 75.1333
2015-09-18 21:00 | 60 | 64 | 79.8833 | 74.7667
2015-09-18 21:15 | 60 | 64 | 79.6333 | 74.2667
2015-09-18 21:30 | 60 | 64 | 79.3833 | 73.7667
2015-09-18 21:45 | 60 | 64 | 79.1333 | 73.2667
2015-09-18 22:00 | 59.9333 | 63.7667 | 79 | 72.7667
2015-09-18 22:15 | 59.6833 | 63.2667 | 79 | 72.2667
2015-09-18 22:30 | 59.4333 | 62.7667 | 79 | 71.7667
2015-09-18 22:45 | 59.1833 | 62.2667 | 79 | 71.2667
2015-09-18 23:00 | 58.9333 | 61.8833 | 78.7667 | 70.65
2015-09-18 23:15 | 58.6833 | 61.6333 | 78.2667 | 69.9
2015-09-18 23:30 | 58.4333 | 61.3833 | 77.7667 | 69.15
2015-09-18 23:45 | 58.1833 | 61.1333 | 77.2667 | 68.4
2015-09-19 | 58 | 61 | 76.8833 | 67.8833
2015-09-19 00:15 | 58 | 61 | 76.6333 | 67.6333
2015-09-19 00:30 | 58 | 61 | 76.3833 | 67.3833
2015-09-19 00:45 | 58 | 61 | 76.1333 | 67.1333
2015-09-19 01:00 | 57.9333 | 60.65 | 75.7667 | 66.7667
2015-09-19 01:15 | 57.6833 | 59.9 | 75.2667 | 66.2667
2015-09-19 01:30 | 57.4333 | 59.15 | 74.7667 | 65.7667
2015-09-19 01:45 | 57.1833 | 58.4 | 74.2667 | 65.2667
2015-09-19 02:00 | 56.9333 | 57.8833 | 74.1167 | 64.7667
2015-09-19 02:15 | 56.6833 | 57.6333 | 74.3667 | 64.2667
2015-09-19 02:30 | 56.4333 | 57.3833 | 74.6167 | 63.7667
2015-09-19 02:45 | 56.1833 | 57.1333 | 74.8667 | 63.2667
2015-09-19 03:00 | 56 | 57 | 74.8833 | 62.8833
2015-09-19 03:15 | 56 | 57 | 74.6333 | 62.6333
2015-09-19 03:30 | 56 | 57 | 74.3833 | 62.3833
2015-09-19 03:45 | 56 | 57 | 74.1333 | 62.1333
2015-09-19 04:00 | 56 | 56.8833 | 73.8833 | 62
2015-09-19 04:15 | 56 | 56.6333 | 73.6333 | 62
2015-09-19 04:30 | 56 | 56.3833 | 73.3833 | 62
2015-09-19 04:45 | 56 | 56.1333 | 73.1333 | 62
2015-09-19 05:00 | 56 | 56 | 72.8833 | 61.7667
2015-09-19 05:15 | 56 | 56 | 72.6333 | 61.2667
2015-09-19 05:30 | 56 | 56 | 72.3833 | 60.7667
2015-09-19 05:45 | 56 | 56 | 72.1333 | 60.2667
2015-09-19 06:00 | 56.3333 | 56.2333 | 72 | 60.5833
2015-09-19 06:15 | 57.5833 | 56.7333 | 72 | 61.8333
2015-09-19 06:30 | 58.8333 | 57.2333 | 72 | 63.0833
2015-09-19 06:45 | 60.0833 | 57.7333 | 72 | 64.3333
2015-09-19 07:00 | 61.2667 | 58.5833 | 72 | 65.4667
2015-09-19 07:15 | 62.2667 | 59.8333 | 72 | 66.4667
2015-09-19 07:30 | 63.2667 | 61.0833 | 72 | 67.4667
2015-09-19 07:45 | 64.2667 | 62.3333 | 72 | 68.4667
2015-09-19 08:00 | 65.1333 | 63.5833 | 72.2333 | 69.4667
2015-09-19 08:15 | 65.6333 | 64.8333 | 72.7333 | 70.4667
2015-09-19 08:30 | 66.1333 | 66.0833 | 73.2333 | 71.4667
2015-09-19 08:45 | 66.6333 | 67.3333 | 73.7333 | 72.4667
2015-09-19 09:00 | 67.1333 | 68.4667 | 74.4667 | 73.7
2015-09-19 09:15 | 67.6333 | 69.4667 | 75.4667 | 75.2
2015-09-19 09:30 | 68.1333 | 70.4667 | 76.4667 | 76.7
2015-09-19 09:45 | 68.6333 | 71.4667 | 77.4667 | 78.2
2015-09-19 10:00 | 69.1333 | 72.5833 | 78.2333 | 79.35
2015-09-19 10:15 | 69.6333 | 73.8333 | 78.7333 | 80.1
2015-09-19 10:30 | 70.1333 | 75.0833 | 79.2333 | 80.85
2015-09-19 10:45 | 70.6333 | 76.3333 | 79.7333 | 81.6
2015-09-19 11:00 | 71.2 | 77.4667 | 80.35 | 82.35
2015-09-19 11:15 | 71.95 | 78.4667 | 81.1 | 83.1
2015-09-19 11:30 | 72.7 | 79.4667 | 81.85 | 83.85
2015-09-19 11:45 | 73.45 | 80.4667 | 82.6 | 84.6
2015-09-19 12:00 | 74.1333 | 81.4667 | 83.4667 | 85.35
2015-09-19 12:15 | 74.6333 | 82.4667 | 84.4667 | 86.1
2015-09-19 12:30 | 75.1333 | 83.4667 | 85.4667 | 86.85
2015-09-19 12:45 | 75.6333 | 84.4667 | 86.4667 | 87.6
2015-09-19 13:00 | 76.5333 | 85 | 87 | 88.35
2015-09-19 13:15 | 78.5333 | 85 | 87 | 89.1
2015-09-19 13:30 | 80.5333 | 85 | 87 | 89.85
2015-09-19 13:45 | 82.5333 | 85 | 87 | 90.6
2015-09-19 14:00 | 83.9333 | 85.1167 | 86.8833 | 91.2333
2015-09-19 14:15 | 83.6833 | 85.3667 | 86.6333 | 91.7333
2015-09-19 14:30 | 83.4333 | 85.6167 | 86.3833 | 92.2333
2015-09-19 14:45 | 83.1833 | 85.8667 | 86.1333 | 92.7333
2015-09-19 15:00 | 82.9333 | 86 | 85.8833 | 93.1167
2015-09-19 15:15 | 82.6833 | 86 | 85.6333 | 93.3667
2015-09-19 15:30 | 82.4333 | 86 | 85.3833 | 93.6167
2015-09-19 15:45 | 82.1833 | 86 | 85.1333 | 93.8667
2015-09-19 16:00 | 81.9333 | 85.8833 | 84 | 93.7667
2015-09-19 16:15 | 81.6833 | 85.6333 | 81.8571 | 93.2667
2015-09-19 16:30 | 81.4333 | 85.3833 | 79.7143 | 92.7667
2015-09-19 16:45 | 81.1833 | 85.1333 | 78 | 92.2667
2015-09-19 17:00 | 80.8 | 84.5333 | 78 | 91.5333
2015-09-19 17:15 | 80.05 | 83.5333 | 78 | 90.5333
2015-09-19 17:30 | 79.3 | 82.5333 | 76.8158 | 89.5333
2015-09-19 17:45 | 78.55 | 81.5333 | 75.6316 | 88.5333
2015-09-19 18:00 | 77.6667 | 80.4167 | 74.65 | 87.4167
2015-09-19 18:15 | 76.4167 | 79.1667 | 73.9 | 86.1667
2015-09-19 18:30 | 75.1667 | 77.9167 | 73.15 | 84.9167
2015-09-19 18:45 | 73.9167 | 76.6667 | 72.4 | 83.6667
2015-09-19 19:00 | 72.8667 | 75.7667 | 72 | 82.65
2015-09-19 19:15 | 72.3667 | 75.2667 | 72 | 81.9
2015-09-19 19:30 | 71.8667 | 74.7667 | 72 | 81.15
2015-09-19 19:45 | 71.3667 | 74.2667 | 72 | 80.4
2015-09-19 20:00 | 71 | 73.8833 | 71.8833 | 79.8833
2015-09-19 20:15 | 71 | 73.6333 | 71.6333 | 79.6333
2015-09-19 20:30 | 71 | 73.3833 | 71.3833 | 79.3833
2015-09-19 20:45 | 71 | 73.1333 | 71.1333 | 79.1333
2015-09-19 21:00 | 70.9333 | 72.7667 | 70.8833 | 78.65
2015-09-19 21:15 | 70.6833 | 72.2667 | 70.6333 | 77.9
2015-09-19 21:30 | 70.4333 | 71.7667 | 70.3833 | 77.15
2015-09-19 21:45 | 70.1833 | 71.2667 | 70.1333 | 76.4
2015-09-19 22:00 | 70 | 70.7667 | 70 | 75.7667
2015-09-19 22:15 | 70 | 70.2667 | 70 | 75.2667
2015-09-19 22:30 | 70 | 69.7667 | 70 | 74.7667
2015-09-19 22:45 | 70 | 69.2667 | 70 | 74.2667
2015-09-19 23:00 | 69.8 | 68.7667 | 70 | 73.8833
2015-09-19 23:15 | 69.05 | 68.2667 | 70 | 73.6333
2015-09-19 23:30 | 68.3 | 67.7667 | 70 | 73.3833
2015-09-19 23:45 | 67.55 | 67.2667 | 70 | 73.1333
2015-09-20 | 66.8667 | 66.8833 | 70 | 72.65
2015-09-20 00:15 | 66.3667 | 66.6333 | 69.7812 | 71.9
2015-09-20 00:30 | 65.8667 | 66.3833 | 69.3125 | 71.15
2015-09-20 00:45 | 65.3667 | 66.1333 | 69 | 70.4
2015-09-20 01:00 | 64.9333 | 65.5333 | 68.6667 | 69.65
2015-09-20 01:15 | 64.6833 | 64.5333 | 68 | 68.9
2015-09-20 01:30 | 64.4333 | 63.5333 | 68 | 68.15
2015-09-20 01:45 | 64.1833 | 62.5333 | 68 | 67.4
2015-09-20 02:00 | 64 | 62.1167 | 67.8833 | 66.8833
2015-09-20 02:15 | 64 | 62.3667 | 67.6333 | 66.6333
2015-09-20 02:30 | 64 | 62.6167 | 67.3833 | 66.3833
2015-09-20 02:45 | 64 | 62.8667 | 67.1333 | 66.1333
2015-09-20 03:00 | 63.8667 | 62.8833 | 67 | 65.8833
2015-09-20 03:15 | 63.3667 | 62.6333 | 67 | 65.6333
2015-09-20 03:30 | 62.8667 | 62.3833 | 67 | 65.3833
2015-09-20 03:45 | 62.3667 | 62.1333 | 67 | 65.1333
2015-09-20 04:00 | 61.9333 | 61.65 | 67 | 65
2015-09-20 04:15 | 61.6833 | 60.9 | 67 | 65
2015-09-20 04:30 | 61.4333 | 60.15 | 67 | 65
2015-09-20 04:45 | 61.1833 | 59.4 | 67 | 65
2015-09-20 05:00 | 61.1333 | 59.2333 | 66.8833 | 64.8833
2015-09-20 05:15 | 61.6333 | 59.7333 | 66.6333 | 64.6333
2015-09-20 05:30 | 62.1333 | 60.2333 | 66.3833 | 64.3833
2015-09-20 05:45 | 62.6333 | 60.7333 | 66.1333 | 64.1333
2015-09-20 06:00 | 63.1333 | 61 | 66 | 64.4667
2015-09-20 06:15 | 63.6333 | 61 | 66 | 65.4667
2015-09-20 06:30 | 64.1333 | 61 | 66 | 66.4667
2015-09-20 06:45 | 64.6333 | 61.9333 | 65.381 | 67.4667
2015-09-20 07:00 | 65.2667 | 63.7 | 65 | 68.4667
2015-09-20 07:15 | 66.2667 | 65.2 | 65 | 69.4667
2015-09-20 07:30 | 67.2667 | 66.7 | 65 | 70.4667
2015-09-20 07:45 | 68.2667 | 68.2 | 65 | 71.4667
2015-09-20 08:00 | 69.1333 | 69.5833 | 65.2333 | 72.8167
2015-09-20 08:15 | 69.6333 | 70.8333 | 65.7333 | 74.5667
2015-09-20 08:30 | 70.1333 | 72.0833 | 66.2333 | 76.3167
2015-09-20 08:45 | 70.6333 | 73.3333 | 66.7333 | 78.0667
2015-09-20 09:00 | 71.1333 | 74.7 | 67.4667 | 79.5833
2015-09-20 09:15 | 71.6333 | 76.2 | 68.4667 | 80.8333
2015-09-20 09:30 | 72.1333 | 77.7 | 69.4667 | 82.0833
2015-09-20 09:45 | 72.6333 | 79.2 | 70.4667 | 83.3333
2015-09-20 10:00 | 73.2 | 80.5833 | 71.7 | 84.35
2015-09-20 10:15 | 73.95 | 81.8333 | 73.2 | 85.1
2015-09-20 10:30 | 74.7 | 83.0833 | 74.7 | 85.85
2015-09-20 10:45 | 75.45 | 84.3333 | 76.2 | 86.6
2015-09-20 11:00 | 76.0667 | 85.35 | 77.35 | 87.7
2015-09-20 11:15 | 76.3167 | 86.1 | 78.1 | 89.2
2015-09-20 11:30 | 76.5667 | 86.85 | 78.85 | 90.7
2015-09-20 11:45 | 76.8167 | 87.6 | 79.6 | 92.2
2015-09-20 12:00 | 77.1333 | 88.5833 | 80.1167 | 93.35
2015-09-20 12:15 | 77.6333 | 89.8333 | 80.3667 | 94.1
2015-09-20 12:30 | 78.1333 | 91.0833 | 80.6167 | 94.85
2015-09-20 12:45 | 78.6333 | 92.3333 | 80.8667 | 95.6
2015-09-20 13:00 | 79.3333 | 93 | 80.7667 | 96.35
2015-09-20 13:15 | 80.5833 | 93 | 80.2667 | 97.1
2015-09-20 13:30 | 81.8333 | 93 | 79.7667 | 97.85
2015-09-20 13:45 | 83.0833 | 93 | 79.2667 | 98.6
2015-09-20 14:00 | 84.3333 | 93 | 79 | 99.1167
2015-09-20 14:15 | 85.5833 | 93 | 79 | 99.3667
2015-09-20 14:30 | 86.8333 | 93 | 79 | 99.6167
2015-09-20 14:45 | 88.0833 | 93 | 79 | 99.8667
2015-09-20 15:00 | 89 | 93 | 78.6 | 100
2015-09-20 15:15 | 89 | 93 | 77.7429 | 100
2015-09-20 15:30 | 89 | 93 | 77 | 100
2015-09-20 15:45 | 89 | 93 | 77 | 100
2015-09-20 16:00 | 88.6667 | 92.7667 | 75.8333 | 99.8833
2015-09-20 16:15 | 87.4167 | 92.2667 | 70.8333 | 99.6333
2015-09-20 16:30 | 86.1667 | 91.7667 | 68.2143 | 99.3833
2015-09-20 16:45 | 84.9167 | 91.2667 | 68 | 99.1333
2015-09-20 17:00 | 83.8 | 90.3 | 67 | 98.5333
2015-09-20 17:15 | 83.05 | 88.8 | 67.0256 | 97.5333
2015-09-20 17:30 | 82.3 | 87.3 | 67.4103 | 96.5333
2015-09-20 17:45 | 81.55 | 85.8 | 67.7949 | 95.5333
2015-09-20 18:00 | 80.7333 | 84.4167 | 68.1167 | 94.5333
2015-09-20 18:15 | 79.7333 | 83.1667 | 68.3667 | 93.5333
2015-09-20 18:30 | 78.7333 | 81.9167 | 68.6167 | 92.5333
2015-09-20 18:45 | 77.7333 | 80.6667 | 68.8667 | 91.5333
2015-09-20 19:00 | 77 | 79.8833 | 69.1167 | 90.7667
2015-09-20 19:15 | 77 | 79.6333 | 69.3667 | 90.2667
2015-09-20 19:30 | 77 | 79.3833 | 69.6167 | 89.7667
2015-09-20 19:45 | 77 | 79.1333 | 69.8667 | 89.2667
2015-09-20 20:00 | 77 | 78.65 | 70 | 88.65
2015-09-20 20:15 | 77 | 77.9 | 70 | 87.9
2015-09-20 20:30 | 77 | 77.15 | 70 | 87.15
2015-09-20 20:45 | 77 | 76.4 | 70 | 86.4
2015-09-20 21:00 | 76.9333 | 75.8833 | 70 | 85.65
2015-09-20 21:15 | 76.6833 | 75.6333 | 70 | 84.9
2015-09-20 21:30 | 76.4333 | 75.3833 | 70 | 84.15
2015-09-20 21:45 | 76.1833 | 75.1333 | 70 | 83.4
2015-09-20 22:00 | 75.9333 | 74.8833 | 70 | 82.65
2015-09-20 22:15 | 75.6833 | 74.6333 | 70 | 81.9
2015-09-20 22:30 | 75.4333 | 74.3833 | 70 | 81.15
2015-09-20 22:45 | 75.1833 | 74.1333 | 70 | 80.4
2015-09-20 23:00 | 74.8 | 73.7667 | 70.1167 | 79.5333
2015-09-20 23:15 | 74.05 | 73.2667 | 70.3667 | 78.5333
2015-09-20 23:30 | 73.3 | 72.7667 | 70.6167 | 77.5333
2015-09-20 23:45 | 72.55 | 72.2667 | 70.8667 | 76.5333
2015-09-21 | 71.9333 | 71.7667 | 71 | 75.7667
2015-09-21 00:15 | 71.6833 | 71.2667 | 71 | 75.2667
2015-09-21 00:30 | 71.4333 | 70.7667 | 71 | 74.7667
2015-09-21 00:45 | 71.1833 | 70.2667 | 71 | 74.2667
2015-09-21 01:00 | 70.8667 | 69.8833 | 71 | 73.8833
2015-09-21 01:15 | 70.3667 | 69.6333 | 71 | 73.6333
2015-09-21 01:30 | 69.8667 | 69.3833 | 71 | 73.3833
2015-09-21 01:45 | 69.3667 | 69.1333 | 71 | 73.1333
2015-09-21 02:00 | 69 | 68.8833 | 70.7667 | 73
2015-09-21 02:15 | 69 | 68.6333 | 70.2667 | 73
2015-09-21 02:30 | 69 | 68.3833 | 69.7667 | 73
2015-09-21 02:45 | 69 | 68.1333 | 69.2667 | 73
2015-09-21 03:00 | 68.8667 | 68 | 68.7667 | 72.65
2015-09-21 03:15 | 68.3667 | 68 | 68.2667 | 71.9
2015-09-21 03:30 | 67.8667 | 68 | 67.7667 | 71.15
2015-09-21 03:45 | 67.3667 | 68 | 67.2667 | 70.4
2015-09-21 04:00 | 67.0667 | 67.7667 | 67 | 70
2015-09-21 04:15 | 67.3167 | 67.2667 | 67 | 70
2015-09-21 04:30 | 67.5667 | 66.7667 | 67 | 70
2015-09-21 04:45 | 67.8167 | 66.2667 | 67 | 70
2015-09-21 05:00 | 67.9333 | 66.1167 | 67 | 70
2015-09-21 05:15 | 67.6833 | 66.3667 | 67 | 70
2015-09-21 05:30 | 67.4333 | 66.6167 | 67 | 70
2015-09-21 05:45 | 67.1833 | 66.8667 | 67 | 70
2015-09-21 06:00 | 67.2 | 67.6364 | 66.65 | 70.35
2015-09-21 06:15 | 67.95 | 69 | 65.9 | 71.1
2015-09-21 06:30 | 68.7 | 70 | 65.15 | 71.85
2015-09-21 06:45 | 69.45 | 70 | 64.4 | 72.6
2015-09-21 07:00 | 70.1333 | 70.5833 | 64.4667 | 73.7
2015-09-21 07:15 | 70.6333 | 71.8333 | 65.4667 | 75.2
2015-09-21 07:30 | 71.1333 | 73.0833 | 66.4667 | 76.7
2015-09-21 07:45 | 71.6333 | 74.3333 | 67.4667 | 78.2
2015-09-21 08:00 | 72.1333 | 75.7 | 68.7 | 79.7
2015-09-21 08:15 | 72.6333 | 77.2 | 70.2 | 81.2
2015-09-21 08:30 | 73.1333 | 78.7 | 71.7 | 82.7
2015-09-21 08:45 | 73.6333 | 80.2 | 73.2 | 84.2
2015-09-21 09:00 | 74.0667 | 81.2333 | 74.5833 | 85.5833
2015-09-21 09:15 | 74.3167 | 81.7333 | 75.8333 | 86.8333
2015-09-21 09:30 | 74.5667 | 82.2333 | 77.0833 | 88.0833
2015-09-21 09:45 | 74.8167 | 82.7333 | 78.3333 | 89.3333
2015-09-21 10:00 | 75.1333 | 83.35 | 79.4667 | 90.2333
2015-09-21 10:15 | 75.6333 | 84.1 | 80.4667 | 90.7333
2015-09-21 10:30 | 76.1333 | 84.85 | 81.4667 | 91.2333
2015-09-21 10:45 | 76.6333 | 85.6 | 82.4667 | 91.7333
2015-09-21 11:00 | 77.2 | 86.5833 | 83.2333 | 92.35
2015-09-21 11:15 | 77.95 | 87.8333 | 83.7333 | 93.1
2015-09-21 11:30 | 78.7 | 89.0833 | 84.2333 | 93.85
2015-09-21 11:45 | 79.45 | 90.3333 | 84.7333 | 94.6
2015-09-21 12:00 | 80.5333 | 91.35 | 85.2333 | 95.2333
2015-09-21 12:15 | 82.5333 | 92.1 | 85.7333 | 95.7333
2015-09-21 12:30 | 84.5333 | 92.85 | 86.2333 | 96.2333
2015-09-21 12:45 | 86.5333 | 93.6 | 86.7333 | 96.7333
2015-09-21 13:00 | 87.9333 | 94.2333 | 86.5333 | 97.2333
2015-09-21 13:15 | 87.6833 | 94.7333 | 85.5333 | 97.7333
2015-09-21 13:30 | 87.4333 | 95.2333 | 84.5333 | 98.2333
2015-09-21 13:45 | 87.1833 | 95.7333 | 83.5333 | 98.7333
2015-09-21 14:00 | 86.6 | 96 | 83.35 | 99.1167
2015-09-21 14:15 | 85.1 | 96 | 84.1 | 99.3667
2015-09-21 14:30 | 83.6 | 96 | 84.85 | 99.6167
2015-09-21 14:45 | 82.1 | 96 | 85.6 | 99.8667
2015-09-21 15:00 | 80.8 | 95.5333 | 85.8833 | 100.1167
2015-09-21 15:15 | 80.05 | 94.5333 | 85.6333 | 100.3667
2015-09-21 15:30 | 79.3 | 93.5333 | 85.3833 | 100.6167
2015-09-21 15:45 | 78.55 | 92.5333 | 85.1333 | 100.8667
2015-09-21 16:00 | 77.5333 | 91.8833 | 84.8833 | 100.8833
2015-09-21 16:15 | 75.7833 | 91.6333 | 84.6333 | 100.6333
2015-09-21 16:30 | 74.0333 | 91.3833 | 84.3833 | 100.3833
2015-09-21 16:45 | 72.2833 | 91.1333 | 84.1333 | 100.1333
2015-09-21 17:00 | 70.6667 | 90.0667 | 83.8571 | 99.65
2015-09-21 17:15 | 69.4167 | 88.0667 | 83.551 | 98.9
2015-09-21 17:30 | 68.1667 | 86.0667 | 83.2449 | 98.15
2015-09-21 17:45 | 66.9167 | 84.0667 | 81.6667 | 97.4
2015-09-21 18:00 | 65.8 | 82.3 | 78.3 | 96.3
2015-09-21 18:15 | 65.05 | 80.8 | 76.8 | 94.8
2015-09-21 18:30 | 64.3 | 79.3 | 75.3 | 93.3
2015-09-21 18:45 | 63.55 | 77.8 | 73.8 | 91.8
2015-09-21 19:00 | 63 | 76.65 | 73 | 90.65
2015-09-21 19:15 | 63 | 75.9 | 73 | 89.9
2015-09-21 19:30 | 63 | 75.15 | 73 | 89.15
2015-09-21 19:45 | 63 | 74.4 | 73 | 88.4
2015-09-21 20:00 | 62.9333 | 73.65 | 72.7667 | 87.65
2015-09-21 20:15 | 62.6833 | 72.9 | 72.2667 | 86.9
2015-09-21 20:30 | 62.4333 | 72.15 | 71.7667 | 86.15
2015-09-21 20:45 | 62.1833 | 71.4 | 71.2667 | 85.4
2015-09-21 21:00 | 61.9333 | 70.5333 | 71.1167 | 84.7667
2015-09-21 21:15 | 61.6833 | 69.5333 | 71.3667 | 84.2667
2015-09-21 21:30 | 61.4333 | 68.5333 | 71.6167 | 83.7667
2015-09-21 21:45 | 61.1833 | 67.5333 | 71.8667 | 83.2667
2015-09-21 22:00 | 61 | 66.8833 | 72.1167 | 82.7667
2015-09-21 22:15 | 61 | 66.6333 | 72.3667 | 82.2667
2015-09-21 22:30 | 61 | 66.3833 | 72.6167 | 81.7667
2015-09-21 22:45 | 61 | 66.1333 | 72.8667 | 81.2667
2015-09-21 23:00 | 60.9333 | 65.7667 | 73 | 80.7667
2015-09-21 23:15 | 60.6833 | 65.2667 | 73 | 80.2667
2015-09-21 23:30 | 60.4333 | 64.7667 | 73 | 79.7667
2015-09-21 23:45 | 60.1833 | 64.2667 | 73 | 79.2667
2015-09-22 | 60 | 64 | 73 | 78.7667
2015-09-22 00:15 | 60 | 64 | 73 | 78.2667
2015-09-22 00:30 | 60 | 64 | 73 | 77.7667
2015-09-22 00:45 | 60 | 64 | 73 | 77.2667
2015-09-22 01:00 | 59.9333 | 64 | 73.35 | 76.7667
2015-09-22 01:15 | 59.6833 | 64 | 74.1 | 76.2667
2015-09-22 01:30 | 59.4333 | 64 | 74.85 | 75.7667
2015-09-22 01:45 | 59.1833 | 64 | 75.6 | 75.2667
2015-09-22 02:00 | 59 | 63.8833 | 75.8833 | 74.8833
2015-09-22 02:15 | 59 | 63.6333 | 75.6333 | 74.6333
2015-09-22 02:30 | 59 | 63.3833 | 75.3833 | 74.3833
2015-09-22 02:45 | 59 | 63.1333 | 75.1333 | 74.1333
2015-09-22 03:00 | 59.0667 | 63 | 74.8833 | 73.8833
2015-09-22 03:15 | 59.3167 | 63 | 74.6333 | 73.6333
2015-09-22 03:30 | 59.5667 | 63 | 74.3833 | 73.3833
2015-09-22 03:45 | 59.8167 | 63 | 74.1333 | 73.1333
2015-09-22 04:00 | 59.9333 | 62.8833 | 73.8833 | 72.8833
2015-09-22 04:15 | 59.6833 | 62.6333 | 73.6333 | 72.6333
2015-09-22 04:30 | 59.4333 | 62.3833 | 73.3833 | 72.3833
2015-09-22 04:45 | 59.1833 | 62.1333 | 73.1333 | 72.1333
2015-09-22 05:00 | 58.8621 | 62 | 73 | 72.1167
2015-09-22 05:15 | 58.3448 | 62 | 73 | 72.3667
2015-09-22 05:30 | 57.8276 | 62 | 73 | 72.6167
2015-09-22 05:45 | 57.3103 | 62 | 73 | 72.8667
2015-09-22 06:00 | 58.1333 | 62.1167 | 72.8833 | 73.35
2015-09-22 06:15 | 58.6333 | 62.3667 | 72.6333 | 74.1
2015-09-22 06:30 | 59.1333 | 62.6167 | 72.3833 | 74.85
2015-09-22 06:45 | 59.6333 | 62.8667 | 72.1333 | 75.6
2015-09-22 07:00 | 60.0667 | 63.2333 | 72.1167 | 76.2333
2015-09-22 07:15 | 60.3167 | 63.7333 | 72.3667 | 76.7333
2015-09-22 07:30 | 60.5667 | 64.2333 | 72.6167 | 77.2333
2015-09-22 07:45 | 60.8167 | 64.7333 | 72.8667 | 77.7333
2015-09-22 08:00 | 61.1379 | 65.35 | 73.4667 | 78.4667
2015-09-22 08:15 | 61.6552 | 66.1 | 74.4667 | 79.4667
2015-09-22 08:30 | 62.1724 | 66.85 | 75.4667 | 80.4667
2015-09-22 08:45 | 62.6897 | 67.6 | 76.4667 | 81.4667
2015-09-22 09:00 | 63.0667 | 68.3684 | 77.4667 | 82.4667
2015-09-22 09:15 | 63.3167 | 69.1579 | 78.4667 | 83.4667
2015-09-22 09:30 | 63.5667 | 69.9474 | 79.4667 | 84.4667
2015-09-22 09:45 | 63.8167 | 70.6364 | 80.4667 | 85.4667
2015-09-22 10:00 | 64 | 71.4667 | 81.2333 | 86.4667
2015-09-22 10:15 | 64 | 72.4667 | 81.7333 | 87.4667
2015-09-22 10:30 | 64 | 73.4667 | 82.2333 | 88.4667
2015-09-22 10:45 | 64 | 74.4667 | 82.7333 | 89.4667
2015-09-22 11:00 | 64 | 74.8833 | 83.2333 | 90.4667
2015-09-22 11:15 | 64 | 74.6333 | 83.7333 | 91.4667
2015-09-22 11:30 | 64 | 74.3833 | 84.2333 | 92.4667
2015-09-22 11:45 | 64 | 74.1333 | 84.7333 | 93.4667
2015-09-22 12:00 | 64 | 73.7667 | 85.2333 | 94.2333
2015-09-22 12:15 | 64 | 73.2667 | 85.7333 | 94.7333
2015-09-22 12:30 | 64 | 72.7667 | 86.2333 | 95.2333
2015-09-22 12:45 | 64 | 72.2667 | 86.7333 | 95.7333
2015-09-22 13:00 | 64 | 72 | 87.1167 | 96.1167
2015-09-22 13:15 | 64 | 72 | 87.3667 | 96.3667
2015-09-22 13:30 | 64 | 72 | 87.6167 | 96.6167
2015-09-22 13:45 | 64 | 72 | 87.8667 | 96.8667
2015-09-22 14:00 | 64 | 71.7667 | 88 | 97
2015-09-22 14:15 | 64 | 71.2667 | 88 | 97
2015-09-22 14:30 | 64 | 70.7667 | 88 | 97
2015-09-22 14:45 | 64 | 70.2667 | 88 | 97
2015-09-22 15:00 | 63.8 | 69.8833 | 88 | 97
2015-09-22 15:15 | 63.05 | 69.6333 | 88 | 97
2015-09-22 15:30 | 62.3 | 69.3833 | 88 | 97
2015-09-22 15:45 | 61.55 | 69.1333 | 88 | 97
2015-09-22 16:00 | 61.0667 | 68.65 | 87.8833 | 96.65
2015-09-22 16:15 | 61.3167 | 67.9 | 87.6333 | 95.9
2015-09-22 16:30 | 61.5667 | 67.15 | 87.3833 | 95.15
2015-09-22 16:45 | 61.8167 | 66.4 | 87.1333 | 94.4
2015-09-22 17:00 | 61.8667 | 65.5333 | 86.65 | 93.65
2015-09-22 17:15 | 61.3667 | 64.5333 | 85.9 | 92.9
2015-09-22 17:30 | 60.8667 | 63.5333 | 85.15 | 92.15
2015-09-22 17:45 | 60.3667 | 62.5333 | 84.4 | 91.4
2015-09-22 18:00 | 59.9333 | 61.7667 | 83.8833 | 90.5333
2015-09-22 18:15 | 59.6833 | 61.2667 | 83.6333 | 89.5333
2015-09-22 18:30 | 59.4333 | 60.7667 | 83.3833 | 88.5333
2015-09-22 18:45 | 59.1833 | 60.2667 | 83.1333 | 87.5333
2015-09-22 19:00 | 59 | 59.8833 | 82.7667 | 86.5333
2015-09-22 19:15 | 59 | 59.6333 | 82.2667 | 85.5333
2015-09-22 19:30 | 59 | 59.3833 | 81.7667 | 84.5333
2015-09-22 19:45 | 59 | 59.1333 | 81.2667 | 83.5333
2015-09-22 20:00 | 59 | 59 | 80.7667 | 82.5333
2015-09-22 20:15 | 59 | 59 | 80.2667 | 81.5333
2015-09-22 20:30 | 59 | 59 | 79.7667 | 80.5333
2015-09-22 20:45 | 59 | 59 | 79.2667 | 79.5333
2015-09-22 21:00 | 59 | 59 | 78.8833 | 78.65
2015-09-22 21:15 | 59 | 59 | 78.6333 | 77.9
2015-09-22 21:30 | 59 | 59 | 78.3833 | 77.15
2015-09-22 21:45 | 59 | 59 | 78.1333 | 76.4
2015-09-22 22:00 | 58.9333 | 59 | 77.8833 | 75.7667
2015-09-22 22:15 | 58.6833 | 59 | 77.6333 | 75.2667
2015-09-22 22:30 | 58.4333 | 59 | 77.3833 | 74.7667
2015-09-22 22:45 | 58.1833 | 59 | 77.1333 | 74.2667
2015-09-22 23:00 | 58 | 58.8833 | 76.8833 | 73.65
2015-09-22 23:15 | 58 | 58.6333 | 76.6333 | 72.9
2015-09-22 23:30 | 58 | 58.3833 | 76.3833 | 72.15
2015-09-22 23:45 | 58 | 58.1333 | 76.1333 | 71.4
2015-09-23 | 58 | 58 | 75.8833 | 70.7667
2015-09-23 00:15 | 58 | 58 | 75.6333 | 70.2667
2015-09-23 00:30 | 58 | 58 | 75.3833 | 69.7667
2015-09-23 00:45 | 58 | 58 | 75.1333 | 69.2667
2015-09-23 01:00 | 57.8667 | 57.7667 | 75 | 68.7667
2015-09-23 01:15 | 57.3667 | 57.2667 | 75 | 68.2667
2015-09-23 01:30 | 56.8667 | 56.7667 | 75 | 67.7667
2015-09-23 01:45 | 56.3667 | 56.2667 | 75 | 67.2667
2015-09-23 02:00 | 56 | 55.8833 | 74.8833 | 66.8833
2015-09-23 02:15 | 56 | 55.6333 | 74.6333 | 66.6333
2015-09-23 02:30 | 56 | 55.3833 | 74.3833 | 66.3833
2015-09-23 02:45 | 56 | 55.1333 | 74.1333 | 66.1333
2015-09-23 03:00 | 56 | 54.8833 | 73.8833 | 65.7667
2015-09-23 03:15 | 56 | 54.6333 | 73.6333 | 65.2667
2015-09-23 03:30 | 56 | 54.3833 | 73.3833 | 64.7667
2015-09-23 03:45 | 56 | 54.1333 | 73.1333 | 64.2667
2015-09-23 04:00 | 56 | 54 | 72.8833 | 63.8833
2015-09-23 04:15 | 56 | 54 | 72.6333 | 63.6333
2015-09-23 04:30 | 56 | 54 | 72.3833 | 63.3833
2015-09-23 04:45 | 56 | 54 | 72.1333 | 63.1333
2015-09-23 05:00 | 55.931 | 54 | 71.8833 | 62.8833
2015-09-23 05:15 | 55.6724 | 54 | 71.6333 | 62.6333
2015-09-23 05:30 | 55.4138 | 54 | 71.3833 | 62.3833
2015-09-23 05:45 | 55.1552 | 54 | 71.1333 | 62.1333
2015-09-23 06:00 | 57 | 54.1167 | 70.8833 | 62.2333
2015-09-23 06:15 | 57 | 54.3667 | 70.6333 | 62.7333
2015-09-23 06:30 | 57 | 54.6167 | 70.3833 | 63.2333
2015-09-23 06:45 | 57 | 54.8667 | 70.1333 | 63.7333
2015-09-23 07:00 | 57.3333 | 55.4667 | 70.35 | 64.4667
2015-09-23 07:15 | 58.5833 | 56.4667 | 71.1 | 65.4667
2015-09-23 07:30 | 59.8333 | 57.4667 | 71.85 | 66.4667
2015-09-23 07:45 | 61.0833 | 58.4667 | 72.6 | 67.4667
2015-09-23 08:00 | 62 | 59.4667 | 73.35 | 68.4667
2015-09-23 08:15 | 62 | 60.4667 | 74.1 | 69.4667
2015-09-23 08:30 | 62 | 61.4667 | 74.85 | 70.4667
2015-09-23 08:45 | 62 | 62.4667 | 75.6 | 71.4667
2015-09-23 09:00 | 62.1333 | 63.5833 | 76.4667 | 72.7
2015-09-23 09:15 | 62.6333 | 64.8333 | 77.4667 | 74.2
2015-09-23 09:30 | 63.1333 | 66.0833 | 78.4667 | 75.7
2015-09-23 09:45 | 63.6333 | 67.3333 | 79.4667 | 77.2
2015-09-23 10:00 | 64.1333 | 68.4667 | 80.35 | 78.35
2015-09-23 10:15 | 64.6333 | 69.4667 | 81.1 | 79.1
2015-09-23 10:30 | 65.1333 | 70.4667 | 81.85 | 79.85
2015-09-23 10:45 | 65.6333 | 71.4667 | 82.6 | 80.6
2015-09-23 11:00 | 66.4 | 72.35 | 83.35 | 81.5833
2015-09-23 11:15 | 67.9 | 73.1 | 84.1 | 82.8333
2015-09-23 11:30 | 69.4 | 73.85 | 84.85 | 84.0833
2015-09-23 11:45 | 70.9 | 74.6 | 85.6 | 85.3333
2015-09-23 12:00 | 72.0667 | 75.35 | 86.2333 | 86.2333
2015-09-23 12:15 | 72.3167 | 76.1 | 86.7333 | 86.7333
2015-09-23 12:30 | 72.5667 | 76.85 | 87.2333 | 87.2333
2015-09-23 12:45 | 72.8167 | 77.6 | 87.7333 | 87.7333
2015-09-23 13:00 | 73 | 78.2333 | 88.1167 | 88.1167
2015-09-23 13:15 | 73 | 78.7333 | 88.3667 | 88.3667
2015-09-23 13:30 | 73 | 79.2333 | 88.6167 | 88.6167
2015-09-23 13:45 | 73 | 79.7333 | 88.8667 | 88.8667
2015-09-23 14:00 | 72.9333 | 80.1167 | 89 | 89.1167
2015-09-23 14:15 | 72.6833 | 80.3667 | 89 | 89.3667
2015-09-23 14:30 | 72.4333 | 80.6167 | 89 | 89.6167
2015-09-23 14:45 | 72.1833 | 80.8667 | 89 | 89.8667
2015-09-23 15:00 | 71.9333 | 81 | 88.7667 | 90
2015-09-23 15:15 | 71.6833 | 81 | 88.2667 | 90
2015-09-23 15:30 | 71.4333 | 81 | 87.7667 | 90
2015-09-23 15:45 | 71.1833 | 81 | 87.2667 | 90
2015-09-23 16:00 | 70.7333 | 80.5333 | 87 | 89.8833
2015-09-23 16:15 | 69.7333 | 79.5333 | 87 | 89.6333
2015-09-23 16:30 | 68.7333 | 78.5333 | 87 | 89.3833
2015-09-23 16:45 | 67.7333 | 77.5333 | 87 | 89.1333
2015-09-23 17:00 | 66.9333 | 76.4167 | 86.7667 | 88.5333
2015-09-23 17:15 | 66.6833 | 75.1667 | 86.2667 | 87.5333
2015-09-23 17:30 | 66.4333 | 73.9167 | 85.7667 | 86.5333
2015-09-23 17:45 | 66.1833 | 72.6667 | 85.2667 | 85.5333
2015-09-23 18:00 | 65.9333 | 71.65 | 84.65 | 84.7667
2015-09-23 18:15 | 65.6833 | 70.9 | 83.9 | 84.2667
2015-09-23 18:30 | 65.4333 | 70.15 | 83.15 | 83.7667
2015-09-23 18:45 | 65.1833 | 69.4 | 82.4 | 83.2667
2015-09-23 19:00 | 64.9333 | 68.7667 | 82 | 82.5333
2015-09-23 19:15 | 64.6833 | 68.2667 | 78.6154 | 81.5333
2015-09-23 19:30 | 64.4333 | 67.7667 | 72.2692 | 80.5333
2015-09-23 19:45 | 64.1833 | 67.2667 | 68.2308 | 79.5333
2015-09-23 20:00 | 63.9333 | 67.1167 | 66.3333 | 78.65
2015-09-23 20:15 | 63.6833 | 67.3667 | 67.7333 | 77.9
2015-09-23 20:30 | 63.4333 | 67.6167 | 69.1481 | 77.15
2015-09-23 20:45 | 63.1833 | 67.8667 | 69.7037 | 76.4
2015-09-23 21:00 | 62.9333 | 67.7667 | 70.35 | 75.8833
2015-09-23 21:15 | 62.6833 | 67.2667 | 71.1 | 75.6333
2015-09-23 21:30 | 62.4333 | 66.7667 | 71.85 | 75.3833
2015-09-23 21:45 | 62.1833 | 66.2667 | 72.6 | 75.1333
2015-09-23 22:00 | 61.9333 | 65.7667 | 72.5962 | 74.7667
2015-09-23 22:15 | 61.6833 | 65.2667 | 71.7308 | 74.2667
2015-09-23 22:30 | 61.4333 | 64.7667 | 70.8654 | 73.7667
2015-09-23 22:45 | 61.1833 | 64.2667 | 70 | 73.2667
2015-09-23 23:00 | 61.0667 | 63.8833 | 69.8898 | 72.65
2015-09-23 23:15 | 61.3167 | 63.6333 | 69.6535 | 71.9
2015-09-23 23:30 | 61.5667 | 63.3833 | 69.4173 | 71.15
2015-09-23 23:45 | 61.8167 | 63.1333 | 69.1811 | 70.4
2015-09-24 | 62 | 62.8833 | 68.9449 | 69.7667
2015-09-24 00:15 | 62 | 62.6333 | 68.7087 | 69.2667
2015-09-24 00:30 | 62 | 62.3833 | 68.4724 | 68.7667
2015-09-24 00:45 | 62 | 62.1333 | 68.2362 | 68.2667
2015-09-24 01:00 | 61.9333 | 62 | 68 | 67.7667
2015-09-24 01:15 | 61.6833 | 62 | 67.7638 | 67.2667
2015-09-24 01:30 | 61.4333 | 62 | 67.5276 | 66.7667
2015-09-24 01:45 | 61.1833 | 62 | 67.2913 | 66.2667
2015-09-24 02:00 | 61 | 61.8833 | 67.0551 | 65.8833
2015-09-24 02:15 | 61 | 61.6333 | 66.8189 | 65.6333
2015-09-24 02:30 | 61 | 61.3833 | 66.5827 | 65.3833
2015-09-24 02:45 | 61 | 61.1333 | 66.3465 | 65.1333
2015-09-24 03:00 | 61 | 60.8833 | 66.1102 | 65
2015-09-24 03:15 | 61 | 60.6333 | 65.874 | 65
2015-09-24 03:30 | 61 | 60.3833 | 65.6378 | 65
2015-09-24 03:45 | 61 | 60.1333 | 65.4016 | 65
2015-09-24 04:00 | 61 | 60 | 65.1654 | 64.8833
2015-09-24 04:15 | 61 | 60 | 64.9291 | 64.6333
2015-09-24 04:30 | 61 | 60 | 64.6929 | 64.3833
2015-09-24 04:45 | 61 | 60 | 64.4567 | 64.1333
2015-09-24 05:00 | 61.0667 | 60 | 64.2205 | 64.1167
2015-09-24 05:15 | 61.3167 | 60 | 64.0556 | 64.3667
2015-09-24 05:30 | 61.5667 | 60 | 64.8889 | 64.6167
2015-09-24 05:45 | 61.8167 | 60 | 65 | 64.8667
2015-09-24 06:00 | 62.0667 | 60.1167 | 65.1167 | 65
2015-09-24 06:15 | 62.3167 | 60.3667 | 65.3667 | 65
2015-09-24 06:30 | 62.5667 | 60.6167 | 65.6167 | 65
2015-09-24 06:45 | 62.8167 | 60.8667 | 65.8667 | 65
2015-09-24 07:00 | 63.2667 | 61.5833 | 66 | 65.5833
2015-09-24 07:15 | 64.2667 | 62.8333 | 65.6 | 66.8333
2015-09-24 07:30 | 65.2667 | 64.0833 | 64.1154 | 68.0833
2015-09-24 07:45 | 66.2667 | 65.3333 | 64.6923 | 69.3333
2015-09-24 08:00 | 67.0667 | 66.5833 | 65.1167 | 70.5833
2015-09-24 08:15 | 67.3167 | 67.8333 | 65.3667 | 71.8333
2015-09-24 08:30 | 67.5667 | 69.0833 | 65.6167 | 73.0833
2015-09-24 08:45 | 67.8167 | 70.3333 | 65.8667 | 74.3333
2015-09-24 09:00 | 68.1333 | 71.35 | 66.5833 | 75.7
2015-09-24 09:15 | 68.6333 | 72.1 | 67.8333 | 77.2
2015-09-24 09:30 | 69.1333 | 72.85 | 69.0833 | 78.7
2015-09-24 09:45 | 69.6333 | 73.6 | 70.3333 | 80.2
2015-09-24 10:00 | 70.2 | 74.4667 | 71.5833 | 81.5833
2015-09-24 10:15 | 70.95 | 75.4667 | 72.8333 | 82.8333
2015-09-24 10:30 | 71.7 | 76.4667 | 74.0833 | 84.0833
2015-09-24 10:45 | 72.45 | 77.4667 | 75.3333 | 85.3333
2015-09-24 11:00 | 73.1333 | 78.7 | 76.35 | 86.35
2015-09-24 11:15 | 73.6333 | 80.2 | 77.1 | 87.1
2015-09-24 11:30 | 74.1333 | 81.7 | 77.85 | 87.85
2015-09-24 11:45 | 74.6333 | 83.2 | 78.6 | 88.6
2015-09-24 12:00 | 75.1333 | 84 | 79.2333 | 89.35
2015-09-24 12:15 | 75.6333 | 84 | 79.7333 | 90.1
2015-09-24 12:30 | 76.1333 | 84 | 80.2333 | 90.85
2015-09-24 12:45 | 76.6333 | 84 | 80.7333 | 91.6
2015-09-24 13:00 | 77.0667 | 84.2333 | 81.2333 | 92.1167
2015-09-24 13:15 | 77.3167 | 84.7333 | 81.7333 | 92.3667
2015-09-24 13:30 | 77.5667 | 85.2333 | 82.2333 | 92.6167
2015-09-24 13:45 | 77.8167 | 85.7333 | 82.7333 | 92.8667
2015-09-24 14:00 | 78 | 86.35 | 83.2333 | 93
2015-09-24 14:15 | 78 | 87.1 | 83.7333 | 93
2015-09-24 14:30 | 78 | 87.85 | 84.2333 | 93
2015-09-24 14:45 | 78 | 88.6 | 84.7333 | 93
2015-09-24 15:00 | 78 | 88.7667 | 84.7667 | 93.1167
2015-09-24 15:15 | 78 | 88.2667 | 84.2667 | 93.3667
2015-09-24 15:30 | 78 | 87.7667 | 83.7667 | 93.6167
2015-09-24 15:45 | 78 | 87.2667 | 83.2667 | 93.8667
2015-09-24 16:00 | 77.6 | 86.7667 | 82.8333 | 93.7667
2015-09-24 16:15 | 76.1 | 86.2667 | 82.4762 | 93.2667
2015-09-24 16:30 | 74.6 | 85.7667 | 82.119 | 92.7667
2015-09-24 16:45 | 73.1 | 85.2667 | 82 | 92.2667
2015-09-24 17:00 | 72 | 84.1833 | 81.5333 | 91.5333
2015-09-24 17:15 | 72 | 82.4333 | 80.5333 | 90.5333
2015-09-24 17:30 | 72 | 80.6833 | 79.5333 | 89.5333
2015-09-24 17:45 | 72 | 78.9333 | 78.5333 | 88.5333
2015-09-24 18:00 | 71.7333 | 77.65 | 77.7667 | 87.7667
2015-09-24 18:15 | 70.7333 | 76.9 | 77.2667 | 87.2667
2015-09-24 18:30 | 69.7333 | 76.15 | 76.7667 | 86.7667
2015-09-24 18:45 | 68.7333 | 75.4 | 76.2667 | 86.2667
2015-09-24 19:00 | 67.9333 | 74.7667 | 75.7667 | 85.7667
2015-09-24 19:15 | 67.6833 | 74.2667 | 75.2667 | 85.2667
2015-09-24 19:30 | 67.4333 | 73.7667 | 74.7667 | 84.7667
2015-09-24 19:45 | 67.1833 | 73.2667 | 74.2667 | 84.2667
2015-09-24 20:00 | 66.8667 | 72.8833 | 73.7667 | 83.65
2015-09-24 20:15 | 66.3667 | 72.6333 | 73.2667 | 82.9
2015-09-24 20:30 | 65.8667 | 72.3833 | 72.7667 | 82.15
2015-09-24 20:45 | 65.3667 | 72.1333 | 72.2667 | 81.4
2015-09-24 21:00 | 64.9333 | 71.65 | 71.8833 | 80.7667
2015-09-24 21:15 | 64.6833 | 70.9 | 71.6333 | 80.2667
2015-09-24 21:30 | 64.4333 | 70.15 | 71.3833 | 79.7667
2015-09-24 21:45 | 64.1833 | 69.4 | 71.1333 | 79.2667
2015-09-24 22:00 | 63.8667 | 68.8833 | 70.8833 | 78.65
2015-09-24 22:15 | 63.3667 | 68.6333 | 70.6333 | 77.9
2015-09-24 22:30 | 62.8667 | 68.3833 | 70.3833 | 77.15
2015-09-24 22:45 | 62.3667 | 68.1333 | 70.1333 | 76.4
2015-09-24 23:00 | 62 | 67.7667 | 69.8833 | 75.7667
2015-09-24 23:15 | 62 | 67.2667 | 69.6333 | 75.2667
2015-09-24 23:30 | 62 | 66.7667 | 69.3833 | 74.7667
2015-09-24 23:45 | 62 | 66.2667 | 69.1333 | 74.2667
2015-09-25 | 61.9333 | 66 | 68.8833 | 73.8833
2015-09-25 00:15 | 61.6833 | 66 | 68.6333 | 73.6333
2015-09-25 00:30 | 61.4333 | 66 | 68.3833 | 73.3833
2015-09-25 00:45 | 61.1833 | 66 | 68.1333 | 73.1333
2015-09-25 01:00 | 60.9333 | 65.65 | 67.7667 | 72.7667
2015-09-25 01:15 | 60.6833 | 64.9 | 67.2667 | 72.2667
2015-09-25 01:30 | 60.4333 | 64.15 | 66.7667 | 71.7667
2015-09-25 01:45 | 60.1833 | 63.4 | 66.2667 | 71.2667
2015-09-25 02:00 | 59.9333 | 63 | 66 | 70.8833
2015-09-25 02:15 | 59.6833 | 63 | 66 | 70.6333
2015-09-25 02:30 | 59.4333 | 63 | 66 | 70.3833
2015-09-25 02:45 | 59.1833 | 63 | 66 | 70.1333
2015-09-25 03:00 | 59 | 63 | 65.8833 | 69.8833
2015-09-25 03:15 | 59 | 63 | 65.6333 | 69.6333
2015-09-25 03:30 | 59 | 63 | 65.3833 | 69.3833
2015-09-25 03:45 | 59 | 63 | 65.1333 | 69.1333
2015-09-25 04:00 | 59.0667 | 63 | 64.65 | 69
2015-09-25 04:15 | 59.3167 | 63 | 63.9 | 69
2015-09-25 04:30 | 59.5667 | 63 | 63.15 | 69
2015-09-25 04:45 | 59.8167 | 62.7778 | 62.4 | 69
2015-09-25 05:00 | 60 | 61 | 62 | 68.65
2015-09-25 05:15 | 60 | 61 | 62 | 67.9
2015-09-25 05:30 | 60 | 61 | 62 | 67.15
2015-09-25 05:45 | 60 | 61 | 62 | 66.4
2015-09-25 06:00 | 59.9333 | 61.2333 | 62 | 66.4667
2015-09-25 06:15 | 59.6833 | 61.7333 | 62 | 67.4667
2015-09-25 06:30 | 59.4333 | 62.2333 | 62 | 68.4667
2015-09-25 06:45 | 59.1833 | 62.7333 | 62 | 69.4667
2015-09-25 07:00 | 59.2667 | 63.35 | 62.35 | 70.7
2015-09-25 07:15 | 60.2667 | 64.1 | 63.1 | 72.2
2015-09-25 07:30 | 61.2667 | 64.85 | 63.85 | 73.7
2015-09-25 07:45 | 62.2667 | 65.6 | 64.6 | 75.2
2015-09-25 08:00 | 63.3333 | 66.35 | 65.2333 | 76.8167
2015-09-25 08:15 | 64.5833 | 67.1 | 65.7333 | 78.5667
2015-09-25 08:30 | 65.8333 | 67.85 | 66.2333 | 80.3167
2015-09-25 08:45 | 67.0833 | 68.6 | 66.7333 | 82.0667
2015-09-25 09:00 | 68.0667 | 69.5833 | 67.5833 | 83.4667
2015-09-25 09:15 | 68.3167 | 70.8333 | 68.8333 | 84.4667
2015-09-25 09:30 | 68.5667 | 72.0833 | 70.0833 | 85.4667
2015-09-25 09:45 | 68.8167 | 73.3333 | 71.3333 | 86.4667
2015-09-25 10:00 | 69.2 | 74.5833 | 72.35 | 87.4667
2015-09-25 10:15 | 69.95 | 75.8333 | 73.1 | 88.4667
2015-09-25 10:30 | 70.7 | 77.0833 | 73.85 | 89.4667
2015-09-25 10:45 | 71.45 | 78.3333 | 74.6 | 90.4667
2015-09-25 11:00 | 72.0667 | 79.4667 | 75.4667 | 91.35
2015-09-25 11:15 | 72.3167 | 80.4667 | 76.4667 | 92.1
2015-09-25 11:30 | 72.5667 | 81.4667 | 77.4667 | 92.85
2015-09-25 11:45 | 72.8167 | 82.4667 | 78.4667 | 93.6
2015-09-25 12:00 | 72.9333 | 83.35 | 79.35 | 94.1167
2015-09-25 12:15 | 72.6833 | 84.1 | 80.1 | 94.3667
2015-09-25 12:30 | 72.4333 | 84.85 | 80.85 | 94.6167
2015-09-25 12:45 | 72.1833 | 85.6 | 81.6 | 94.8667
2015-09-25 13:00 | 72.0667 | 85.4167 | 81.8833 | 95.1167
2015-09-25 13:15 | 72.3167 | 84.1667 | 81.6333 | 95.3667
2015-09-25 13:30 | 72.5667 | 82.9167 | 81.3833 | 95.6167
2015-09-25 13:45 | 72.8167 | 81.6667 | 81.1333 | 95.8667
2015-09-25 14:00 | 72.8 | 80.7667 | 81.1167 | 96.2333
2015-09-25 14:15 | 72.05 | 80.2667 | 81.3667 | 96.7333
2015-09-25 14:30 | 71.3 | 79.7667 | 81.6167 | 97.2333
2015-09-25 14:45 | 70.55 | 79.2667 | 81.8667 | 97.7333
2015-09-25 15:00 | 70.1333 | 78.65 | 82.2333 | 98
2015-09-25 15:15 | 70.6333 | 77.9 | 82.7333 | 98
2015-09-25 15:30 | 71.1333 | 77.15 | 83.2333 | 98
2015-09-25 15:45 | 71.6333 | 76.4 | 83.7333 | 98
2015-09-25 16:00 | 71.8 | 75.8833 | 83.8833 | 97.7667
2015-09-25 16:15 | 71.05 | 75.6333 | 83.6333 | 97.2667
2015-09-25 16:30 | 70.3 | 75.3833 | 83.3833 | 96.7667
2015-09-25 16:45 | 69.55 | 75.1333 | 83.1333 | 96.2667
2015-09-25 17:00 | 68.7333 | 74.4167 | 83 | 95.65
2015-09-25 17:15 | 67.7333 | 73.1667 | 83 | 94.9
2015-09-25 17:30 | 66.7333 | 71.9167 | 83 | 94.15
2015-09-25 17:45 | 65.7333 | 70.6667 | 83 | 93.4
2015-09-25 18:00 | 64.8667 | 69.7667 | 82.3 | 92.65
2015-09-25 18:15 | 64.3667 | 69.2667 | 80.8 | 91.9
2015-09-25 18:30 | 63.8667 | 68.7667 | 79.3 | 91.15
2015-09-25 18:45 | 63.3667 | 68.2667 | 77.8 | 90.4
2015-09-25 19:00 | 62.9333 | 67.8833 | 76.5333 | 89.5333
2015-09-25 19:15 | 62.6833 | 67.6333 | 75.5333 | 88.5333
2015-09-25 19:30 | 62.4333 | 67.3833 | 74.5333 | 87.5333
2015-09-25 19:45 | 62.1833 | 67.1333 | 73.5333 | 86.5333
2015-09-25 20:00 | 62 | 67 | 72.8833 | 85.7667
2015-09-25 20:15 | 62 | 67 | 72.6333 | 85.2667
2015-09-25 20:30 | 62 | 67 | 72.3833 | 84.7667
2015-09-25 20:45 | 62 | 67 | 72.1333 | 84.2667
2015-09-25 21:00 | 62 | 66.8833 | 71.7667 | 83.7667
2015-09-25 21:15 | 62 | 66.6333 | 71.2667 | 83.2667
2015-09-25 21:30 | 62 | 66.3833 | 70.7667 | 82.7667
2015-09-25 21:45 | 62 | 66.1333 | 70.2667 | 82.2667
2015-09-25 22:00 | 61.9333 | 65.8833 | 70.35 | 81.7667
2015-09-25 22:15 | 61.6833 | 65.6333 | 71.1 | 81.2667
2015-09-25 22:30 | 61.4333 | 65.3833 | 71.85 | 80.7667
2015-09-25 22:45 | 61.1833 | 65.1333 | 72.6 | 80.2667
2015-09-25 23:00 | 61 | 64.7667 | 72.65 | 79.5333
2015-09-25 23:15 | 61 | 64.2667 | 71.9 | 78.5333
2015-09-25 23:30 | 61 | 63.7667 | 71.15 | 77.5333
2015-09-25 23:45 | 61 | 63.2667 | 70.4 | 76.5333
2015-09-26 | 60.9333 | 63 | 69.8833 | 75.8833
2015-09-26 00:15 | 60.6833 | 63 | 69.6333 | 75.6333
2015-09-26 00:30 | 60.4333 | 63 | 69.3833 | 75.3833
2015-09-26 00:45 | 60.1833 | 63 | 69.1333 | 75.1333
2015-09-26 01:00 | 59.9333 | 62.7667 | 68.65 | 74.8833
2015-09-26 01:15 | 59.6833 | 62.2667 | 67.9 | 74.6333
2015-09-26 01:30 | 59.4333 | 61.7667 | 67.15 | 74.3833
2015-09-26 01:45 | 59.1833 | 61.2667 | 66.4 | 74.1333
2015-09-26 02:00 | 58.9333 | 60.8833 | 65.8833 | 74
2015-09-26 02:15 | 58.6833 | 60.6333 | 65.6333 | 74
2015-09-26 02:30 | 58.4333 | 60.3833 | 65.3833 | 74
2015-09-26 02:45 | 58.1833 | 60.1333 | 65.1333 | 74
2015-09-26 03:00 | 57.9333 | 60 | 65 | 73.5333
2015-09-26 03:15 | 57.6833 | 60 | 65 | 72.5333
2015-09-26 03:30 | 57.4333 | 60 | 65 | 71.5333
2015-09-26 03:45 | 57.1833 | 60 | 65 | 70.5333
2015-09-26 04:00 | 57 | 60 | 64.8833 | 69.8833
2015-09-26 04:15 | 57 | 60 | 64.6333 | 69.6333
2015-09-26 04:30 | 57 | 60 | 64.3833 | 69.3833
2015-09-26 04:45 | 57 | 60 | 64.1333 | 69.1333
2015-09-26 05:00 | 57 | 59.8833 | 63.8833 | 68.7667
2015-09-26 05:15 | 57 | 59.6333 | 63.6333 | 68.2667
2015-09-26 05:30 | 57 | 59.3833 | 63.3833 | 67.7667
2015-09-26 05:45 | 57 | 59.1333 | 63.1333 | 67.2667
2015-09-26 06:00 | 57.0667 | 59.2333 | 63 | 67.2333
2015-09-26 06:15 | 57.3167 | 59.7333 | 63 | 67.7333
2015-09-26 06:30 | 57.5667 | 60.2333 | 63 | 68.2333
2015-09-26 06:45 | 57.8167 | 60.7333 | 63 | 68.7333
2015-09-26 07:00 | 58.2 | 61.4667 | 63.2333 | 69.4667
2015-09-26 07:15 | 58.95 | 62.4667 | 63.7333 | 70.4667
2015-09-26 07:30 | 59.7 | 63.4667 | 64.2333 | 71.4667
2015-09-26 07:45 | 60.45 | 64.4667 | 64.7333 | 72.4667
2015-09-26 08:00 | 61.1333 | 65.2333 | 65.8167 | 73.4667
2015-09-26 08:15 | 61.6333 | 65.7333 | 67.5667 | 74.4667
2015-09-26 08:30 | 62.1333 | 66.2333 | 69.3167 | 75.4667
2015-09-26 08:45 | 62.6333 | 66.7333 | 71.0667 | 76.4667
2015-09-26 09:00 | 63.0667 | 67.35 | 72.4667 | 77.5833
2015-09-26 09:15 | 63.3167 | 68.1 | 73.4667 | 78.8333
2015-09-26 09:30 | 63.5667 | 68.85 | 74.4667 | 80.0833
2015-09-26 09:45 | 63.8167 | 69.6 | 75.4667 | 81.3333
2015-09-26 10:00 | 64.3333 | 70.5833 | 76.4667 | 82.35
2015-09-26 10:15 | 65.5833 | 71.8333 | 77.4667 | 83.1
2015-09-26 10:30 | 66.8333 | 73.0833 | 78.4667 | 83.85
2015-09-26 10:45 | 68.0833 | 74.3333 | 79.4667 | 84.6
2015-09-26 11:00 | 69 | 75.4667 | 80.35 | 85.4667
2015-09-26 11:15 | 69 | 76.4667 | 81.1 | 86.4667
2015-09-26 11:30 | 69 | 77.4667 | 81.85 | 87.4667
2015-09-26 11:45 | 69 | 78.4667 | 82.6 | 88.4667
2015-09-26 12:00 | 69.0667 | 79.2333 | 83.1167 | 89.2333
2015-09-26 12:15 | 69.3167 | 79.7333 | 83.3667 | 89.7333
2015-09-26 12:30 | 69.5667 | 80.2333 | 83.6167 | 90.2333
2015-09-26 12:45 | 69.8167 | 80.7333 | 83.8667 | 90.7333
2015-09-26 13:00 | 70 | 81 | 84.1167 | 91.1167
2015-09-26 13:15 | 70 | 81 | 84.3667 | 91.3667
2015-09-26 13:30 | 70 | 81 | 84.6167 | 91.6167
2015-09-26 13:45 | 70 | 81 | 84.8667 | 91.8667
2015-09-26 14:00 | 70 | 81 | 85.2333 | 92.2333
2015-09-26 14:15 | 70 | 81 | 85.7333 | 92.7333
2015-09-26 14:30 | 70 | 81 | 86.2333 | 93.2333
2015-09-26 14:45 | 70 | 81 | 86.7333 | 93.7333
2015-09-26 15:00 | 70 | 80.7667 | 87 | 94
2015-09-26 15:15 | 70 | 80.2667 | 87 | 94
2015-09-26 15:30 | 70 | 79.7667 | 87 | 94
2015-09-26 15:45 | 70 | 79.2667 | 87 | 94
2015-09-26 16:00 | 69.8 | 78.5333 | 87 | 93.7667
2015-09-26 16:15 | 69.05 | 77.5333 | 87 | 93.2667
2015-09-26 16:30 | 68.3 | 76.5333 | 87 | 92.7667
2015-09-26 16:45 | 67.55 | 75.5333 | 87 | 92.2667
2015-09-26 17:00 | 66.7333 | 74.5333 | 86.7667 | 91.8833
2015-09-26 17:15 | 65.7333 | 73.5333 | 86.2667 | 91.6333
2015-09-26 17:30 | 64.7333 | 72.5333 | 85.7667 | 91.3833
2015-09-26 17:45 | 63.7333 | 71.5333 | 85.2667 | 91.1333
2015-09-26 18:00 | 62.9333 | 70.7667 | 84.1833 | 90.65
2015-09-26 18:15 | 62.6833 | 70.2667 | 82.4333 | 89.9
2015-09-26 18:30 | 62.4333 | 69.7667 | 80.6833 | 89.15
2015-09-26 18:45 | 62.1833 | 69.2667 | 78.9333 | 88.4
2015-09-26 19:00 | 61.9333 | 68.7667 | 77.5333 | 87.7667
2015-09-26 19:15 | 61.6833 | 68.2667 | 76.5333 | 87.2667
2015-09-26 19:30 | 61.4333 | 67.7667 | 75.5333 | 86.7667
2015-09-26 19:45 | 61.1833 | 67.2667 | 74.5333 | 86.2667
2015-09-26 20:00 | 60.9333 | 66.8833 | 73.8833 | 85.7667
2015-09-26 20:15 | 60.6833 | 66.6333 | 73.6333 | 85.2667
2015-09-26 20:30 | 60.4333 | 66.3833 | 73.3833 | 84.7667
2015-09-26 20:45 | 60.1833 | 66.1333 | 73.1333 | 84.2667
2015-09-26 21:00 | 60 | 65.8833 | 72.8833 | 83.5333
2015-09-26 21:15 | 60 | 65.6333 | 72.6333 | 82.5333
2015-09-26 21:30 | 60 | 65.3833 | 72.3833 | 81.5333
2015-09-26 21:45 | 60 | 65.1333 | 72.1333 | 80.5333
2015-09-26 22:00 | 59.9333 | 64.8833 | 71.7667 | 79.65
2015-09-26 22:15 | 59.6833 | 64.6333 | 71.2667 | 78.9
2015-09-26 22:30 | 59.4333 | 64.3833 | 70.7667 | 78.15
2015-09-26 22:45 | 59.1833 | 64.1333 | 70.2667 | 77.4
2015-09-26 23:00 | 59 | 64 | 69.8833 | 76.8833
2015-09-26 23:15 | 59 | 64 | 69.6333 | 76.6333
2015-09-26 23:30 | 59 | 64 | 69.3833 | 76.3833
2015-09-26 23:45 | 59 | 64 | 69.1333 | 76.1333
2015-09-27 | 59 | 63.8833 | 68.8833 | 75.7667
2015-09-27 00:15 | 59 | 63.6333 | 68.6333 | 75.2667
2015-09-27 00:30 | 59 | 63.3833 | 68.3833 | 74.7667
2015-09-27 00:45 | 59 | 63.1333 | 68.1333 | 74.2667
2015-09-27 01:00 | 58.9333 | 62.8833 | 67.8833 | 73.7667
2015-09-27 01:15 | 58.6833 | 62.6333 | 67.6333 | 73.2667
2015-09-27 01:30 | 58.4333 | 62.3833 | 67.3833 | 72.7667
2015-09-27 01:45 | 58.1833 | 62.1333 | 67.1333 | 72.2667
2015-09-27 02:00 | 58 | 61.7667 | 66.65 | 72
2015-09-27 02:15 | 58 | 61.2667 | 65.9 | 72
2015-09-27 02:30 | 58 | 60.7667 | 65.15 | 72
2015-09-27 02:45 | 58 | 60.2667 | 64.4 | 72
2015-09-27 03:00 | 58 | 60 | 64.1167 | 71.7667
2015-09-27 03:15 | 58 | 60 | 64.3667 | 71.2667
2015-09-27 03:30 | 58 | 60 | 64.6167 | 70.7667
2015-09-27 03:45 | 58 | 60 | 64.8667 | 70.2667
2015-09-27 04:00 | 57.9333 | 60 | 64.8833 | 69.8833
2015-09-27 04:15 | 57.6833 | 60 | 64.6333 | 69.6333
2015-09-27 04:30 | 57.4333 | 60 | 64.3833 | 69.3833
2015-09-27 04:45 | 57.1833 | 60 | 64.1333 | 69.1333
2015-09-27 05:00 | 57 | 59.8833 | 64 | 69.1167
2015-09-27 05:15 | 57 | 59.6333 | 64 | 69.3667
2015-09-27 05:30 | 57 | 59.3833 | 64 | 69.6167
2015-09-27 05:45 | 57 | 59.1333 | 64 | 69.8667
2015-09-27 06:00 | 57.0667 | 59.1167 | 64 | 70.1167
2015-09-27 06:15 | 57.3167 | 59.3667 | 64 | 70.3667
2015-09-27 06:30 | 57.5667 | 59.6167 | 64 | 70.6167
2015-09-27 06:45 | 57.8167 | 59.8667 | 64 | 70.8667
2015-09-27 07:00 | 58.2667 | 60.35 | 64.4667 | 71.5833
2015-09-27 07:15 | 59.2667 | 61.1 | 65.4667 | 72.8333
2015-09-27 07:30 | 60.2667 | 61.85 | 66.4667 | 74.0833
2015-09-27 07:45 | 61.2667 | 62.6 | 67.4667 | 75.3333
2015-09-27 08:00 | 62.2 | 63.35 | 68.8167 | 76.5833
2015-09-27 08:15 | 62.95 | 64.1 | 70.5667 | 77.8333
2015-09-27 08:30 | 63.7 | 64.85 | 72.3167 | 79.0833
2015-09-27 08:45 | 64.45 | 65.6 | 74.0667 | 80.3333
2015-09-27 09:00 | 65.1333 | 66.5833 | 75.7 | 81.1167
2015-09-27 09:15 | 65.6333 | 67.8333 | 77.2 | 81.3667
2015-09-27 09:30 | 66.1333 | 69.0833 | 78.7 | 81.6167
2015-09-27 09:45 | 66.6333 | 70.3333 | 80.2 | 81.8667
2015-09-27 10:00 | 67 | 71.5833 | 81.35 | 82.35
2015-09-27 10:15 | 67 | 72.8333 | 82.1 | 83.1
2015-09-27 10:30 | 67 | 74.0833 | 82.85 | 83.85
2015-09-27 10:45 | 67 | 75.3333 | 83.6 | 84.6
2015-09-27 11:00 | 67.1333 | 76.1167 | 84.2333 | 85.35
2015-09-27 11:15 | 67.6333 | 76.3667 | 84.7333 | 86.1
2015-09-27 11:30 | 68.1333 | 76.6167 | 85.2333 | 86.85
2015-09-27 11:45 | 68.6333 | 76.8667 | 85.7333 | 87.6
2015-09-27 12:00 | 69 | 77.2333 | 86.2333 | 88.2333
2015-09-27 12:15 | 69 | 77.7333 | 86.7333 | 88.7333
2015-09-27 12:30 | 69 | 78.2333 | 87.2333 | 89.2333
2015-09-27 12:45 | 69 | 78.7333 | 87.7333 | 89.7333
2015-09-27 13:00 | 69 | 79 | 88.2333 | 90.2333
2015-09-27 13:15 | 69 | 79 | 88.7333 | 90.7333
2015-09-27 13:30 | 69 | 79 | 89.2333 | 91.2333
2015-09-27 13:45 | 69 | 79 | 89.7333 | 91.7333
2015-09-27 14:00 | 68.8667 | 78.7358 | 90 | 91.8833
2015-09-27 14:15 | 68.3667 | 78.1698 | 90 | 91.6333
2015-09-27 14:30 | 67.8667 | 77.6038 | 90 | 91.3833
2015-09-27 14:45 | 67.3667 | 77.0377 | 90 | 91.1333
2015-09-27 15:00 | 67.1333 | 76.8833 | 89.8833 | 91.1167
2015-09-27 15:15 | 67.6333 | 76.6333 | 89.6333 | 91.3667
2015-09-27 15:30 | 68.1333 | 76.3833 | 89.3833 | 91.6167
2015-09-27 15:45 | 68.6333 | 76.1333 | 89.1333 | 91.8667
2015-09-27 16:00 | 68.8667 | 75.7667 | 89 | 91.8833
2015-09-27 16:15 | 68.3667 | 75.2667 | 89 | 91.6333
2015-09-27 16:30 | 67.8667 | 74.7667 | 89 | 91.3833
2015-09-27 16:45 | 67.3667 | 74.2667 | 89 | 91.1333
2015-09-27 17:00 | 66.6667 | 73.7667 | 88.65 | 90.4167
2015-09-27 17:15 | 65.4167 | 73.2667 | 87.9 | 89.1667
2015-09-27 17:30 | 64.1667 | 72.7667 | 87.15 | 87.9167
2015-09-27 17:45 | 62.9167 | 72.2667 | 86.4 | 86.6667
2015-09-27 18:00 | 61.9333 | 71.7667 | 85.5333 | 85.8833
2015-09-27 18:15 | 61.6833 | 71.2667 | 84.5333 | 85.6333
2015-09-27 18:30 | 61.4333 | 70.7667 | 83.5333 | 85.3833
2015-09-27 18:45 | 61.1833 | 70.2667 | 82.5333 | 85.1333
2015-09-27 19:00 | 61 | 69.5333 | 81.65 | 84.65
2015-09-27 19:15 | 61 | 68.5333 | 80.9 | 83.9
2015-09-27 19:30 | 61 | 67.5333 | 80.15 | 83.15
2015-09-27 19:45 | 61 | 66.5333 | 79.4 | 82.4
2015-09-27 20:00 | 60.9333 | 65.7667 | 78.7667 | 81.8833
2015-09-27 20:15 | 60.6833 | 65.2667 | 78.2667 | 81.6333
2015-09-27 20:30 | 60.4333 | 64.7667 | 77.7667 | 81.3833
2015-09-27 20:45 | 60.1833 | 64.2667 | 77.2667 | 81.1333
2015-09-27 21:00 | 59.9333 | 63.8833 | 76.65 | 80.7667
2015-09-27 21:15 | 59.6833 | 63.6333 | 75.9 | 80.2667
2015-09-27 21:30 | 59.4333 | 63.3833 | 75.15 | 79.7667
2015-09-27 21:45 | 59.1833 | 63.1333 | 74.4 | 79.2667
2015-09-27 22:00 | 58.8667 | 63.1167 | 73.7667 | 78.7667
2015-09-27 22:15 | 58.3667 | 63.3667 | 73.2667 | 78.2667
2015-09-27 22:30 | 57.8667 | 63.6167 | 72.7667 | 77.7667
2015-09-27 22:45 | 57.3667 | 63.8667 | 72.2667 | 77.2667
2015-09-27 23:00 | 57 | 63.8833 | 72 | 76.8833
2015-09-27 23:15 | 57 | 63.6333 | 72 | 76.6333
2015-09-27 23:30 | 57 | 63.3833 | 72 | 76.3833
2015-09-27 23:45 | 57 | 63.1333 | 72 | 76.1333
2015-09-28 | 56.9333 | 62.8833 | 71.8833 | 76
2015-09-28 00:15 | 56.6833 | 62.6333 | 71.6333 | 76
2015-09-28 00:30 | 56.4333 | 62.3833 | 71.3833 | 76
2015-09-28 00:45 | 56.1833 | 62.1333 | 71.1333 | 76
2015-09-28 01:00 | 56 | 62 | 70.7667 | 75.5333
2015-09-28 01:15 | 56 | 62 | 70.2667 | 74.5333
2015-09-28 01:30 | 56 | 62 | 69.7667 | 73.5333
2015-09-28 01:45 | 56 | 62 | 69.2667 | 72.5333
2015-09-28 02:00 | 56 | 61.8833 | 68.7667 | 71.8833
2015-09-28 02:15 | 56 | 61.6333 | 68.2667 | 71.6333
2015-09-28 02:30 | 56 | 61.3833 | 67.7667 | 71.3833
2015-09-28 02:45 | 56 | 61.1333 | 67.2667 | 71.1333
2015-09-28 03:00 | 56 | 61 | 67 | 71
2015-09-28 03:15 | 56 | 61 | 67 | 71
2015-09-28 03:30 | 56 | 61 | 67 | 71
2015-09-28 03:45 | 56 | 61 | 67 | 71
2015-09-28 04:00 | 56 | 61 | 66.7667 | 71
2015-09-28 04:15 | 56 | 61 | 66.2667 | 71
2015-09-28 04:30 | 56 | 61 | 65.7667 | 71
2015-09-28 04:45 | 56 | 61 | 65.2667 | 71
2015-09-28 05:00 | 56 | 60.1167 | 65 | 70.8833
2015-09-28 05:15 | 56 | 60.3667 | 65 | 70.6333
2015-09-28 05:30 | 56 | 60.6167 | 65 | 70.3833
2015-09-28 05:45 | 56 | 60.8667 | 65 | 70.1333
2015-09-28 06:00 | 56.0667 | 61 | 64.8833 | 70.35
2015-09-28 06:15 | 56.3167 | 61 | 64.6333 | 71.1
2015-09-28 06:30 | 56.5667 | 61 | 64.3833 | 71.85
2015-09-28 06:45 | 56.8167 | 61 | 64.1333 | 72.6
2015-09-28 07:00 | 57.1333 | 61.1167 | 64.5833 | 73.2333
2015-09-28 07:15 | 57.6333 | 61.3667 | 65.8333 | 73.7333
2015-09-28 07:30 | 58.1333 | 61.6167 | 67.0833 | 74.2333
2015-09-28 07:45 | 58.6333 | 61.8667 | 68.3333 | 74.7333
2015-09-28 08:00 | 59.1333 | 62.1167 | 69.7 | 75.1167
2015-09-28 08:15 | 59.6333 | 62.3667 | 71.2 | 75.3667
2015-09-28 08:30 | 60.1333 | 62.6167 | 72.7 | 75.6167
2015-09-28 08:45 | 60.6333 | 62.8667 | 74.2 | 75.8667
2015-09-28 09:00 | 61.0667 | 63.35 | 75.5833 | 76.2333
2015-09-28 09:15 | 61.3167 | 64.1 | 76.8333 | 76.7333
2015-09-28 09:30 | 61.5667 | 64.85 | 78.0833 | 77.2333
2015-09-28 09:45 | 61.8167 | 65.6 | 79.3333 | 77.7333
2015-09-28 10:00 | 62.2 | 66.1167 | 80.4667 | 78.35
2015-09-28 10:15 | 62.95 | 66.3667 | 81.4667 | 79.1
2015-09-28 10:30 | 63.7 | 66.6167 | 82.4667 | 79.85
2015-09-28 10:45 | 64.45 | 66.8667 | 83.4667 | 80.6
2015-09-28 11:00 | 65.0667 | 67.4667 | 84.35 | 81.1167
2015-09-28 11:15 | 65.3167 | 68.4667 | 85.1 | 81.3667
2015-09-28 11:30 | 65.5667 | 69.4667 | 85.85 | 81.6167
2015-09-28 11:45 | 65.8167 | 70.4667 | 86.6 | 81.8667
2015-09-28 12:00 | 66.1333 | 71.35 | 87.1167 | 82.7
2015-09-28 12:15 | 66.6333 | 72.1 | 87.3667 | 84.2
2015-09-28 12:30 | 67.1333 | 72.85 | 87.6167 | 85.7
2015-09-28 12:45 | 67.6333 | 73.6 | 87.8667 | 87.2
2015-09-28 13:00 | 68.0667 | 74 | 88 | 87.8833
2015-09-28 13:15 | 68.3167 | 74 | 88 | 87.6333
2015-09-28 13:30 | 68.5667 | 74 | 88 | 87.3833
2015-09-28 13:45 | 68.8167 | 74 | 88 | 87.1333
2015-09-28 14:00 | 69 | 73.8833 | 88.2333 | 86.8833
2015-09-28 14:15 | 69 | 73.6333 | 88.7333 | 86.6333
2015-09-28 14:30 | 69 | 73.3833 | 89.2333 | 86.3833
2015-09-28 14:45 | 69 | 73.1333 | 89.7333 | 86.1333
2015-09-28 15:00 | 68.8667 | 73 | 89.8833 | 85.7667
2015-09-28 15:15 | 68.3667 | 73 | 89.6333 | 85.2667
2015-09-28 15:30 | 67.8667 | 73 | 89.3833 | 84.7667
2015-09-28 15:45 | 67.3667 | 73 | 89.1333 | 84.2667
2015-09-28 16:00 | 66.8 | 72.65 | 88.8833 | 84.1167
2015-09-28 16:15 | 66.05 | 71.9 | 88.6333 | 84.3667
2015-09-28 16:30 | 65.3 | 71.15 | 88.3833 | 84.6167
2015-09-28 16:45 | 64.55 | 70.4 | 88.1333 | 84.8667
2015-09-28 17:00 | 63.8667 | 69.4167 | 87.7667 | 84.5333
2015-09-28 17:15 | 63.3667 | 68.1667 | 87.2667 | 83.5333
2015-09-28 17:30 | 62.8667 | 66.9167 | 86.7667 | 82.5333
2015-09-28 17:45 | 62.3667 | 65.6667 | 86.2667 | 81.5333
2015-09-28 18:00 | 61.9333 | 64.7667 | 85.1833 | 80.7667
2015-09-28 18:15 | 61.6833 | 64.2667 | 83.4333 | 80.2667
2015-09-28 18:30 | 61.4333 | 63.7667 | 81.6833 | 79.7667
2015-09-28 18:45 | 61.1833 | 63.2667 | 79.9333 | 79.2667
2015-09-28 19:00 | 60.9333 | 62.8833 | 78.5333 | 79
2015-09-28 19:15 | 60.6833 | 62.6333 | 77.5333 | 79
2015-09-28 19:30 | 60.4333 | 62.3833 | 76.5333 | 79
2015-09-28 19:45 | 60.1833 | 62.1333 | 75.5333 | 79
2015-09-28 20:00 | 60 | 62 | 74.8833 | 78.8833
2015-09-28 20:15 | 60 | 62 | 74.6333 | 78.6333
2015-09-28 20:30 | 60 | 62 | 74.3833 | 78.3833
2015-09-28 20:45 | 60 | 62 | 74.1333 | 78.1333
2015-09-28 21:00 | 59.9333 | 61.8833 | 73.8833 | 77.8833
2015-09-28 21:15 | 59.6833 | 61.6333 | 73.6333 | 77.6333
2015-09-28 21:30 | 59.4333 | 61.3833 | 73.3833 | 77.3833
2015-09-28 21:45 | 59.1833 | 61.1333 | 73.1333 | 77.1333
2015-09-28 22:00 | 59.0667 | 60.8833 | 72.65 | 76.8833
2015-09-28 22:15 | 59.3167 | 60.6333 | 71.9 | 76.6333
2015-09-28 22:30 | 59.5667 | 60.3833 | 71.15 | 76.3833
2015-09-28 22:45 | 59.8167 | 60.1333 | 70.4 | 76.1333
2015-09-28 23:00 | 59.9333 | 59.7667 | 70 | 75.7667
2015-09-28 23:15 | 59.6833 | 59.2667 | 70 | 75.2667
2015-09-28 23:30 | 59.4333 | 58.7667 | 70 | 74.7667
2015-09-28 23:45 | 59.1833 | 58.2667 | 70 | 74.2667
2015-09-29 | 59 | 58.1167 | 69.8833 | 73.8833
2015-09-29 00:15 | 59 | 58.3667 | 69.6333 | 73.6333
2015-09-29 00:30 | 59 | 58.6167 | 69.3833 | 73.3833
2015-09-29 00:45 | 59 | 58.8667 | 69.1333 | 73.1333
2015-09-29 01:00 | 58.9333 | 58.7667 | 68.7667 | 72.65
2015-09-29 01:15 | 58.6833 | 58.2667 | 68.2667 | 71.9
2015-09-29 01:30 | 58.4333 | 57.7667 | 67.7667 | 71.15
2015-09-29 01:45 | 58.1833 | 57.2667 | 67.2667 | 70.4
2015-09-29 02:00 | 58 | 57.2414 | 67 | 69.7667
2015-09-29 02:15 | 58 | 57.7586 | 67 | 69.2667
2015-09-29 02:30 | 58 | 58.2759 | 67 | 68.7667
2015-09-29 02:45 | 58 | 58.7931 | 67 | 68.2667
2015-09-29 03:00 | 58 | 59.1167 | 67.1167 | 67.8833
2015-09-29 03:15 | 58 | 59.3667 | 67.3667 | 67.6333
2015-09-29 03:30 | 58 | 59.6167 | 67.6167 | 67.3833
2015-09-29 03:45 | 58 | 59.8667 | 67.8667 | 67.1333
2015-09-29 04:00 | 58 | 60 | 67.8833 | 67
2015-09-29 04:15 | 58 | 60 | 67.6333 | 67
2015-09-29 04:30 | 58 | 60 | 67.3833 | 67
2015-09-29 04:45 | 58 | 60 | 67.1333 | 67
2015-09-29 05:00 | 58.0667 | 60.1321 | 66.8833 | 66.8833
2015-09-29 05:15 | 58.3167 | 60.4151 | 66.6333 | 66.6333
2015-09-29 05:30 | 58.5667 | 60.6981 | 66.3833 | 66.3833
2015-09-29 05:45 | 58.8167 | 60.9811 | 66.1333 | 66.1333
2015-09-29 06:00 | 59 | 60 | 65.8833 | 66.1167
2015-09-29 06:15 | 59 | 60 | 65.6333 | 66.3667
2015-09-29 06:30 | 59 | 60 | 65.3833 | 66.6167
2015-09-29 06:45 | 59 | 60 | 65.1333 | 66.8667
2015-09-29 07:00 | 59.1379 | 60.1167 | 65.4667 | 67.2333
2015-09-29 07:15 | 59.6552 | 60.3667 | 66.4667 | 67.7333
2015-09-29 07:30 | 60.1724 | 60.6167 | 67.4667 | 68.2333
2015-09-29 07:45 | 60.6897 | 60.8667 | 68.4667 | 68.7333
2015-09-29 08:00 | 61.1379 | 61.2333 | 69.5833 | 69.35
2015-09-29 08:15 | 61.6552 | 61.7333 | 70.8333 | 70.1
2015-09-29 08:30 | 62.1724 | 62.2333 | 72.0833 | 70.85
2015-09-29 08:45 | 62.6897 | 62.7333 | 73.3333 | 71.6
2015-09-29 09:00 | 62 | 63.2333 | 74.7 | 72.2333
2015-09-29 09:15 | 62 | 63.7333 | 76.2 | 72.7333
2015-09-29 09:30 | 62 | 64.2333 | 77.7 | 73.2333
2015-09-29 09:45 | 62 | 64.7333 | 79.2 | 73.7333
2015-09-29 10:00 | 62.2667 | 65.35 | 80.4667 | 74.35
2015-09-29 10:15 | 63.2667 | 66.1 | 81.4667 | 75.1
2015-09-29 10:30 | 64.2667 | 66.85 | 82.4667 | 75.85
2015-09-29 10:45 | 65.2667 | 67.6 | 83.4667 | 76.6
2015-09-29 11:00 | 66.0667 | 68 | 84.2333 | 77.35
2015-09-29 11:15 | 66.3167 | 68 | 84.7333 | 78.1
2015-09-29 11:30 | 66.5667 | 68 | 85.2333 | 78.85
2015-09-29 11:45 | 66.8167 | 68 | 85.7333 | 79.6
2015-09-29 12:00 | 67 | 68.1167 | 86.2333 | 80.2333
2015-09-29 12:15 | 67 | 68.3667 | 86.7333 | 80.7333
2015-09-29 12:30 | 67 | 68.6167 | 87.2333 | 81.2333
2015-09-29 12:45 | 67 | 68.8667 | 87.7333 | 81.7333
2015-09-29 13:00 | 66.9333 | 69 | 88 | 81.7667
2015-09-29 13:15 | 66.6833 | 69 | 88 | 81.2667
2015-09-29 13:30 | 66.4333 | 69 | 88 | 80.7667
2015-09-29 13:45 | 66.1833 | 69 | 88 | 80.2667
2015-09-29 14:00 | 66 | 69.2333 | 88 | 80.1167
2015-09-29 14:15 | 66 | 69.7333 | 88 | 80.3667
2015-09-29 14:30 | 66 | 70.2333 | 88 | 80.6167
2015-09-29 14:45 | 66 | 70.7333 | 88 | 80.8667
2015-09-29 15:00 | 65.8667 | 70.5333 | 87.8833 | 80.7667
2015-09-29 15:15 | 65.3667 | 69.5333 | 87.6333 | 80.2667
2015-09-29 15:30 | 64.8667 | 68.5333 | 87.3833 | 79.7667
2015-09-29 15:45 | 64.3667 | 67.5333 | 87.1333 | 79.2667
2015-09-29 16:00 | 63.8667 | 67 | 87 | 78.7667
2015-09-29 16:15 | 63.3667 | 67 | 87 | 78.2667
2015-09-29 16:30 | 62.8667 | 67 | 87 | 77.7667
2015-09-29 16:45 | 62.3667 | 67 | 87 | 77.2667
2015-09-29 17:00 | 61.8667 | 66.65 | 86.65 | 76.7667
2015-09-29 17:15 | 61.3667 | 65.9 | 85.9 | 76.2667
2015-09-29 17:30 | 60.8667 | 65.15 | 85.15 | 75.7667
2015-09-29 17:45 | 60.3667 | 64.4 | 84.4 | 75.2667
2015-09-29 18:00 | 60 | 63.8833 | 83.3 | 74.7667
2015-09-29 18:15 | 60 | 63.6333 | 81.8 | 74.2667
2015-09-29 18:30 | 60 | 63.3833 | 80.3 | 73.7667
2015-09-29 18:45 | 60 | 63.1333 | 78.8 | 73.2667
2015-09-29 19:00 | 60 | 62.8833 | 77.5333 | 72.7667
2015-09-29 19:15 | 60 | 62.6333 | 76.5333 | 72.2667
2015-09-29 19:30 | 60 | 62.3833 | 75.5333 | 71.7667
2015-09-29 19:45 | 60 | 62.1333 | 74.5333 | 71.2667
2015-09-29 20:00 | 59.9333 | 61.8833 | 73.65 | 71
2015-09-29 20:15 | 59.6833 | 61.6333 | 72.9 | 71
2015-09-29 20:30 | 59.4333 | 61.3833 | 72.15 | 71
2015-09-29 20:45 | 59.1833 | 61.1333 | 71.4 | 71
2015-09-29 21:00 | 59 | 61 | 71.2333 | 70.7667
2015-09-29 21:15 | 59 | 61 | 71.7333 | 70.2667
2015-09-29 21:30 | 59 | 61 | 72.2333 | 69.7667
2015-09-29 21:45 | 59 | 61 | 72.7333 | 69.2667
2015-09-29 22:00 | 59 | 60.8833 | 72.5333 | 68.65
2015-09-29 22:15 | 59 | 60.6333 | 71.5333 | 67.9
2015-09-29 22:30 | 59 | 60.3833 | 70.5333 | 67.15
2015-09-29 22:45 | 59 | 60.1333 | 69.5333 | 66.4
2015-09-29 23:00 | 59 | 60 | 68.8833 | 66
2015-09-29 23:15 | 59 | 60 | 68.6333 | 66
2015-09-29 23:30 | 59 | 60 | 68.3833 | 66
2015-09-29 23:45 | 59 | 60 | 68.1333 | 66
2015-09-30 | 59 | 60 | 67.7667 | 66
2015-09-30 00:15 | 59 | 60 | 67.2667 | 66
2015-09-30 00:30 | 59 | 60 | 66.7667 | 66
2015-09-30 00:45 | 59 | 60 | 66.2667 | 66
2015-09-30 01:00 | 59 | 59.8833 | 65.8833 | 65.8833
2015-09-30 01:15 | 59 | 59.6333 | 65.6333 | 65.6333
2015-09-30 01:30 | 59 | 59.3833 | 65.3833 | 65.3833
2015-09-30 01:45 | 59 | 59.1333 | 65.1333 | 65.1333
2015-09-30 02:00 | 59 | 59 | 65 | 65
2015-09-30 02:15 | 59 | 59 | 65 | 65
2015-09-30 02:30 | 59 | 59 | 65 | 65
2015-09-30 02:45 | 59 | 59 | 65 | 65
2015-09-30 03:00 | 58.9333 | 59 | 64.8833 | 65
2015-09-30 03:15 | 58.6833 | 59 | 64.6333 | 65
2015-09-30 03:30 | 58.4333 | 59 | 64.3833 | 65
2015-09-30 03:45 | 58.1833 | 59 | 64.1333 | 65
2015-09-30 04:00 | 58.0667 | 59 | 64 | 64.8833
2015-09-30 04:15 | 58.3167 | 59 | 64 | 64.6333
2015-09-30 04:30 | 58.5667 | 59 | 64 | 64.3833
2015-09-30 04:45 | 58.8167 | 59 | 64 | 64.1333
2015-09-30 05:00 | 59 | 59.1167 | 63.8833 | 63.8833
2015-09-30 05:15 | 59 | 59.3667 | 63.6333 | 63.6333
2015-09-30 05:30 | 59 | 59.6167 | 63.3833 | 63.3833
2015-09-30 05:45 | 59 | 59.8667 | 63.1333 | 63.1333
2015-09-30 06:00 | 59 | 60 | 63 | 63.1167
2015-09-30 06:15 | 59 | 60 | 63 | 63.3667
2015-09-30 06:30 | 59 | 60 | 63 | 63.6167
2015-09-30 06:45 | 59 | 60 | 63 | 63.8667
2015-09-30 07:00 | 59 | 60.1167 | 63.5833 | 64.1167
2015-09-30 07:15 | 59 | 60.3667 | 64.8333 | 64.3667
2015-09-30 07:30 | 59 | 60.6167 | 66.0833 | 64.6167
2015-09-30 07:45 | 59 | 60.8667 | 67.3333 | 64.8667
2015-09-30 08:00 | 59.0667 | 61.1167 | 68.4667 | 65.2333
2015-09-30 08:15 | 59.3167 | 61.3667 | 69.4667 | 65.7333
2015-09-30 08:30 | 59.5667 | 61.6167 | 70.4667 | 66.2333
2015-09-30 08:45 | 59.8167 | 61.8667 | 71.4667 | 66.7333
2015-09-30 09:00 | 60.0667 | 62 | 72.7 | 67.4667
2015-09-30 09:15 | 60.3167 | 62 | 74.2 | 68.4667
2015-09-30 09:30 | 60.5667 | 62 | 75.7 | 69.4667
2015-09-30 09:45 | 60.8167 | 62 | 77.2 | 70.4667
2015-09-30 10:00 | 61 | 62.1167 | 78.4667 | 71.4667
2015-09-30 10:15 | 61 | 62.3667 | 79.4667 | 72.4667
2015-09-30 10:30 | 61 | 62.6167 | 80.4667 | 73.4667
2015-09-30 10:45 | 61 | 62.8667 | 81.4667 | 74.4667
2015-09-30 11:00 | 61 | 63.1167 | 82.4667 | 75
2015-09-30 11:15 | 61 | 63.3667 | 83.4667 | 75
2015-09-30 11:30 | 61 | 63.6167 | 84.4667 | 75
2015-09-30 11:45 | 61 | 63.8667 | 85.4667 | 75
2015-09-30 12:00 | 61.0667 | 64 | 86 | 75.2333
2015-09-30 12:15 | 61.3167 | 64 | 86 | 75.7333
2015-09-30 12:30 | 61.5667 | 64 | 86 | 76.2333
2015-09-30 12:45 | 61.8167 | 64 | 86 | 76.7333
2015-09-30 13:00 | 62.0667 | 63.8833 | 86.2333 | 77.1167
2015-09-30 13:15 | 62.3167 | 63.6333 | 86.7333 | 77.3667
2015-09-30 13:30 | 62.5667 | 63.3833 | 87.2333 | 77.6167
2015-09-30 13:45 | 62.8167 | 63.1333 | 87.7333 | 77.8667
2015-09-30 14:00 | 63.0667 | 63 | 88.1167 | 78
2015-09-30 14:15 | 63.3167 | 63 | 88.3667 | 78
2015-09-30 14:30 | 63.5667 | 63 | 88.6167 | 78
2015-09-30 14:45 | 63.8167 | 63 | 88.8667 | 78
2015-09-30 15:00 | 64 | 63 | 89 | 77.8833
2015-09-30 15:15 | 64 | 63 | 89 | 77.6333
2015-09-30 15:30 | 64 | 63 | 89 | 77.3833
2015-09-30 15:45 | 64 | 63 | 89 | 77.1333
2015-09-30 16:00 | 64.0667 | 63.1167 | 89 | 76.7667
2015-09-30 16:15 | 64.3167 | 63.3667 | 89 | 76.2667
2015-09-30 16:30 | 64.5667 | 63.6167 | 89 | 75.7667
2015-09-30 16:45 | 64.8167 | 63.8667 | 89 | 75.2667
2015-09-30 17:00 | 65 | 64 | 88.7667 | 74.7667
2015-09-30 17:15 | 65 | 64 | 88.2667 | 74.2667
2015-09-30 17:30 | 65 | 64 | 87.7667 | 73.7667
2015-09-30 17:45 | 65 | 64 | 87.2667 | 73.2667
2015-09-30 18:00 | 65 | 64 | 86.4167 | 72.8833
2015-09-30 18:15 | 65 | 64 | 85.1667 | 72.6333
2015-09-30 18:30 | 65 | 64 | 83.9167 | 72.3833
2015-09-30 18:45 | 65 | 64 | 82.6667 | 72.1333
2015-09-30 19:00 | 64.9333 | 64 | 82 | 71.8833
2015-09-30 19:15 | 64.6833 | 64 | 82 | 71.6333
2015-09-30 19:30 | 64.4333 | 64 | 82 | 71.3833
2015-09-30 19:45 | 64.1833 | 64 | 82 | 71.1333
2015-09-30 20:00 | 63.8667 | 64 | 81.4167 | 70.7667
2015-09-30 20:15 | 63.3667 | 64 | 80.1667 | 70.2667
2015-09-30 20:30 | 62.8667 | 64 | 78.9167 | 69.7667
2015-09-30 20:45 | 62.3667 | 64 | 77.6667 | 69.2667
2015-09-30 21:00 | 61.9333 | 64 | 76.5333 | 68.7667
2015-09-30 21:15 | 61.6833 | 64 | 75.5333 | 68.2667
2015-09-30 21:30 | 61.4333 | 64 | 74.5333 | 67.7667
2015-09-30 21:45 | 61.1833 | 64 | 73.5333 | 67.2667
2015-09-30 22:00 | 61 | 63.8833 | 73 | 66.8833
2015-09-30 22:15 | 61 | 63.6333 | 73 | 66.6333
2015-09-30 22:30 | 61 | 63.3833 | 73 | 66.3833
2015-09-30 22:45 | 61 | 63.1333 | 73 | 66.1333
2015-09-30 23:00 | 61 | 63 | 72.7667 | 66
2015-09-30 23:15 | 61 | 63 | 72.2667 | 66
2015-09-30 23:30 | 61 | 63 | 71.7667 | 66
2015-09-30 23:45 | 61 | 63 | 71.2667 | 66
2015-10-01 | 61 | 63 | 71 | 65.8833
2015-10-01 00:15 | 61 | 63 | 71 | 65.6333
2015-10-01 00:30 | 61 | 63 | 71 | 65.3833
2015-10-01 00:45 | 61 | 63 | 71 | 65.1333
2015-10-01 01:00 | 60.9333 | 63 | 71 | 64.8833
2015-10-01 01:15 | 60.6833 | 63 | 71 | 64.6333
2015-10-01 01:30 | 60.4333 | 63 | 71 | 64.3833
2015-10-01 01:45 | 60.1833 | 63 | 71 | 64.1333
2015-10-01 02:00 | 60 | 62.8833 | 70.8833 | 64
2015-10-01 02:15 | 60 | 62.6333 | 70.6333 | 64
2015-10-01 02:30 | 60 | 62.3833 | 70.3833 | 64
2015-10-01 02:45 | 60 | 62.1333 | 70.1333 | 64
2015-10-01 03:00 | 60.0667 | 62 | 69.65 | 64
2015-10-01 03:15 | 60.3167 | 62 | 68.9 | 64
2015-10-01 03:30 | 60.5667 | 62 | 68.15 | 64
2015-10-01 03:45 | 60.8167 | 62 | 67.4 | 64
2015-10-01 04:00 | 60.9333 | 62.1667 | 66.7667 | 63.8833
2015-10-01 04:15 | 60.6833 | 62.5238 | 66.2667 | 63.6333
2015-10-01 04:30 | 60.4333 | 62.881 | 65.7667 | 63.3833
2015-10-01 04:45 | 60.1833 | 62.4444 | 65.2667 | 63.1333
2015-10-01 05:00 | 60.0667 | 62 | 64.7667 | 62.8833
2015-10-01 05:15 | 60.3167 | 62 | 64.2667 | 62.6333
2015-10-01 05:30 | 60.5667 | 62 | 63.7667 | 62.3833
2015-10-01 05:45 | 60.8167 | 62 | 63.2667 | 62.1333
2015-10-01 06:00 | 61.0667 | 62 | 63.2333 | 62.1167
2015-10-01 06:15 | 61.3167 | 62 | 63.7333 | 62.3667
2015-10-01 06:30 | 61.5667 | 62 | 64.2333 | 62.6167
2015-10-01 06:45 | 61.8167 | 62 | 64.7333 | 62.8667
2015-10-01 07:00 | 62.2 | 62.1167 | 65.5833 | 63.2333
2015-10-01 07:15 | 62.95 | 62.3667 | 66.8333 | 63.7333
2015-10-01 07:30 | 63.7 | 62.6167 | 68.0833 | 64.2333
2015-10-01 07:45 | 64.45 | 62.8667 | 69.3333 | 64.7333
2015-10-01 08:00 | 65 | 63 | 70.8167 | 64.8833
2015-10-01 08:15 | 65 | 63 | 72.5667 | 64.6333
2015-10-01 08:30 | 65 | 63 | 74.3167 | 64.3833
2015-10-01 08:45 | 65 | 63 | 76.0667 | 64.1333
2015-10-01 09:00 | 65.2 | 63.2333 | 77.5833 | 64.2333
2015-10-01 09:15 | 65.95 | 63.7333 | 78.8333 | 64.7333
2015-10-01 09:30 | 66.7 | 64.2333 | 80.0833 | 65.2333
2015-10-01 09:45 | 67.45 | 64.7333 | 81.3333 | 65.7333
2015-10-01 10:00 | 68 | 65.4667 | 82.4667 | 66.2333
2015-10-01 10:15 | 68 | 66.4667 | 83.4667 | 66.7333
2015-10-01 10:30 | 68 | 67.4667 | 84.4667 | 67.2333
2015-10-01 10:45 | 68 | 68.4667 | 85.4667 | 67.7333
2015-10-01 11:00 | 68.0667 | 69.4667 | 86.35 | 67.65
2015-10-01 11:15 | 68.3167 | 70.4667 | 87.1 | 66.9
2015-10-01 11:30 | 68.5667 | 71.4667 | 87.85 | 66.15
2015-10-01 11:45 | 68.8167 | 72.4667 | 88.6 | 65.4
2015-10-01 12:00 | 69.2667 | 73 | 89.1167 | 65.35
2015-10-01 12:15 | 70.2667 | 73 | 89.3667 | 66.1
2015-10-01 12:30 | 71.2667 | 73 | 89.6167 | 66.85
2015-10-01 12:45 | 72.2667 | 73 | 89.8667 | 67.6
2015-10-01 13:00 | 72.9333 | 73.2333 | 90.35 | 68.7
2015-10-01 13:15 | 72.6833 | 73.7333 | 91.1 | 70.2
2015-10-01 13:30 | 72.4333 | 74.2333 | 91.85 | 71.7
2015-10-01 13:45 | 72.1833 | 74.7333 | 92.6 | 73.2
2015-10-01 14:00 | 71.8 | 75.1167 | 93.1167 | 74.35
2015-10-01 14:15 | 71.05 | 75.3667 | 93.3667 | 75.1
2015-10-01 14:30 | 70.3 | 75.6167 | 93.6167 | 75.85
2015-10-01 14:45 | 69.55 | 75.8667 | 93.8667 | 76.6
2015-10-01 15:00 | 69 | 75.7667 | 94.1167 | 77
2015-10-01 15:15 | 69 | 75.2667 | 94.3667 | 77
2015-10-01 15:30 | 69 | 74.7667 | 94.6167 | 77
2015-10-01 15:45 | 69 | 74.2667 | 94.8667 | 77
2015-10-01 16:00 | 68.9333 | 73.65 | 94.8833 | 76.8833
2015-10-01 16:15 | 68.6833 | 72.9 | 94.6333 | 76.6333
2015-10-01 16:30 | 68.4333 | 72.15 | 94.3833 | 76.3833
2015-10-01 16:45 | 68.1833 | 71.4 | 94.1333 | 76.1333
2015-10-01 17:00 | 67.7333 | 70.65 | 93.5333 | 75.65
2015-10-01 17:15 | 66.7333 | 69.9 | 92.5333 | 74.9
2015-10-01 17:30 | 65.7333 | 69.15 | 91.5333 | 74.15
2015-10-01 17:45 | 64.7333 | 68.4 | 90.5333 | 73.4
2015-10-01 18:00 | 63.9333 | 67.7667 | 89.65 | 72.7667
2015-10-01 18:15 | 63.6833 | 67.2667 | 88.9 | 72.2667
2015-10-01 18:30 | 63.4333 | 66.7667 | 88.15 | 71.7667
2015-10-01 18:45 | 63.1833 | 66.2667 | 87.4 | 71.2667
2015-10-01 19:00 | 63 | 65.7667 | 86.65 | 71
2015-10-01 19:15 | 63 | 65.2667 | 85.9 | 71
2015-10-01 19:30 | 63 | 64.7667 | 85.15 | 71
2015-10-01 19:45 | 63 | 64.2667 | 84.4 | 71
2015-10-01 20:00 | 62.8667 | 63.8833 | 83.65 | 70.65
2015-10-01 20:15 | 62.3667 | 63.6333 | 82.9 | 69.9
2015-10-01 20:30 | 61.8667 | 63.3833 | 82.15 | 69.15
2015-10-01 20:45 | 61.3667 | 63.1333 | 81.4 | 68.4
2015-10-01 21:00 | 60.9333 | 62.8833 | 80.8833 | 67.8833
2015-10-01 21:15 | 60.6833 | 62.6333 | 80.6333 | 67.6333
2015-10-01 21:30 | 60.4333 | 62.3833 | 80.3833 | 67.3833
2015-10-01 21:45 | 60.1833 | 62.1333 | 80.1333 | 67.1333
2015-10-01 22:00 | 60 | 61.8833 | 79.7667 | 66.7667
2015-10-01 22:15 | 60 | 61.6333 | 79.2667 | 66.2667
2015-10-01 22:30 | 60 | 61.3833 | 78.7667 | 65.7667
2015-10-01 22:45 | 60 | 61.1333 | 78.2667 | 65.2667
2015-10-01 23:00 | 59.9333 | 61 | 77.8833 | 64.7667
2015-10-01 23:15 | 59.6833 | 61 | 77.6333 | 64.2667
2015-10-01 23:30 | 59.4333 | 61 | 77.3833 | 63.7667
2015-10-01 23:45 | 59.1833 | 61 | 77.1333 | 63.2667
2015-10-02 | 59 | 60.8833 | 76.8833 | 63.1167
2015-10-02 00:15 | 59 | 60.6333 | 76.6333 | 63.3667
2015-10-02 00:30 | 59 | 60.3833 | 76.3833 | 63.6167
2015-10-02 00:45 | 59 | 60.1333 | 76.1333 | 63.8667
2015-10-02 01:00 | 59 | 59.8833 | 75.8833 | 63.7667
2015-10-02 01:15 | 59 | 59.6333 | 75.6333 | 63.2667
2015-10-02 01:30 | 59 | 59.3833 | 75.3833 | 62.7667
2015-10-02 01:45 | 59 | 59.1333 | 75.1333 | 62.2667
2015-10-02 02:00 | 58.9333 | 58.7667 | 74.7667 | 61.8833
2015-10-02 02:15 | 58.6833 | 58.2667 | 74.2667 | 61.6333
2015-10-02 02:30 | 58.4333 | 57.7667 | 73.7667 | 61.3833
2015-10-02 02:45 | 58.1833 | 57.2667 | 73.2667 | 61.1333
2015-10-02 03:00 | 57.9333 | 56.8833 | 73 | 60.8833
2015-10-02 03:15 | 57.6833 | 56.6333 | 73 | 60.6333
2015-10-02 03:30 | 57.4333 | 56.3833 | 73 | 60.3833
2015-10-02 03:45 | 57.1833 | 56.1333 | 73 | 60.1333
2015-10-02 04:00 | 57 | 55.8654 | 73 | 59.8833
2015-10-02 04:15 | 57 | 55.5769 | 73 | 59.6333
2015-10-02 04:30 | 57 | 55.2885 | 73 | 59.3833
2015-10-02 04:45 | 57 | 55 | 73 | 59.1333
2015-10-02 05:00 | 57 | 56 | 72.7667 | 58.8833
2015-10-02 05:15 | 57 | 56 | 72.2667 | 58.6333
2015-10-02 05:30 | 57 | 56 | 71.7667 | 58.3833
2015-10-02 05:45 | 57 | 56 | 71.2667 | 58.1333
2015-10-02 06:00 | 58.0667 | 56.1167 | 70.8833 | 58.1167
2015-10-02 06:15 | 58.3167 | 56.3667 | 70.6333 | 58.3667
2015-10-02 06:30 | 58.5667 | 56.6167 | 70.3833 | 58.6167
2015-10-02 06:45 | 58.8167 | 56.8667 | 70.1333 | 58.8667
2015-10-02 07:00 | 59.2 | 57.4667 | 70.1167 | 59.35
2015-10-02 07:15 | 59.95 | 58.4667 | 70.3667 | 60.1
2015-10-02 07:30 | 60.7 | 59.4667 | 70.6167 | 60.85
2015-10-02 07:45 | 61.45 | 60.4667 | 70.8667 | 61.6
2015-10-02 08:00 | 62.2667 | 61.2333 | 71.5833 | 62.35
2015-10-02 08:15 | 63.2667 | 61.7333 | 72.8333 | 63.1
2015-10-02 08:30 | 64.2667 | 62.2333 | 74.0833 | 63.85
2015-10-02 08:45 | 65.2667 | 62.7333 | 75.3333 | 64.6
2015-10-02 09:00 | 66 | 63.5833 | 76.5833 | 65.4667
2015-10-02 09:15 | 66 | 64.8333 | 77.8333 | 66.4667
2015-10-02 09:30 | 66 | 66.0833 | 79.0833 | 67.4667
2015-10-02 09:45 | 66 | 67.3333 | 80.3333 | 68.4667
2015-10-02 10:00 | 66.1333 | 68.4667 | 81.5833 | 69.2333
2015-10-02 10:15 | 66.6333 | 69.4667 | 82.8333 | 69.7333
2015-10-02 10:30 | 67.1333 | 70.4667 | 84.0833 | 70.2333
2015-10-02 10:45 | 67.6333 | 71.4667 | 85.3333 | 70.7333
2015-10-02 11:00 | 68.1333 | 72.4667 | 86.35 | 71.4667
2015-10-02 11:15 | 68.6333 | 73.4667 | 87.1 | 72.4667
2015-10-02 11:30 | 69.1333 | 74.4667 | 87.85 | 73.4667
2015-10-02 11:45 | 69.6333 | 75.4667 | 88.6 | 74.4667
2015-10-02 12:00 | 70.2 | 76.35 | 89.35 | 75.35
2015-10-02 12:15 | 70.95 | 77.1 | 90.1 | 76.1
2015-10-02 12:30 | 71.7 | 77.85 | 90.85 | 76.85
2015-10-02 12:45 | 72.45 | 78.6 | 91.6 | 77.6
2015-10-02 13:00 | 72.7333 | 79 | 92.1167 | 78.2333
2015-10-02 13:15 | 71.7333 | 79 | 92.3667 | 78.7333
2015-10-02 13:30 | 70.7333 | 79 | 92.6167 | 79.2333
2015-10-02 13:45 | 69.7333 | 79 | 92.8667 | 79.7333
2015-10-02 14:00 | 68.9333 | 79 | 92.8833 | 80
2015-10-02 14:15 | 68.6833 | 79 | 92.6333 | 80
2015-10-02 14:30 | 68.4333 | 79 | 92.3833 | 80
2015-10-02 14:45 | 68.1833 | 79 | 92.1333 | 80
2015-10-02 15:00 | 68.0667 | 78.7667 | 92 | 80
2015-10-02 15:15 | 68.3167 | 78.2667 | 92 | 80
2015-10-02 15:30 | 68.5667 | 77.7667 | 92 | 80
2015-10-02 15:45 | 68.8167 | 77.2667 | 92 | 80
2015-10-02 16:00 | 68.8667 | 76.7667 | 91.5333 | 80
2015-10-02 16:15 | 68.3667 | 76.2667 | 90.5333 | 80
2015-10-02 16:30 | 67.8667 | 75.7667 | 89.5333 | 80
2015-10-02 16:45 | 67.3667 | 75.2667 | 88.5333 | 80
2015-10-02 17:00 | 66.7333 | 74.3 | 87.8833 | 79.7667
2015-10-02 17:15 | 65.7333 | 72.8 | 87.6333 | 79.2667
2015-10-02 17:30 | 64.7333 | 71.3 | 87.3833 | 78.7667
2015-10-02 17:45 | 63.7333 | 69.8 | 87.1333 | 78.2667
2015-10-02 18:00 | 62.8667 | 68.65 | 86.65 | 77.65
2015-10-02 18:15 | 62.3667 | 67.9 | 85.9 | 76.9
2015-10-02 18:30 | 61.8667 | 67.15 | 85.15 | 76.15
2015-10-02 18:45 | 61.3667 | 66.4 | 84.4 | 75.4
2015-10-02 19:00 | 61 | 65.7667 | 83.7667 | 74.8833
2015-10-02 19:15 | 61 | 65.2667 | 83.2667 | 74.6333
2015-10-02 19:30 | 61 | 64.7667 | 82.7667 | 74.3833
2015-10-02 19:45 | 61 | 64.2667 | 82.2667 | 74.1333
2015-10-02 20:00 | 60.9333 | 63.8833 | 81.7667 | 73.7667
2015-10-02 20:15 | 60.6833 | 63.6333 | 81.2667 | 73.2667
2015-10-02 20:30 | 60.4333 | 63.3833 | 80.7667 | 72.7667
2015-10-02 20:45 | 60.1833 | 63.1333 | 80.2667 | 72.2667
2015-10-02 21:00 | 60 | 62.8833 | 79.8833 | 71.65
2015-10-02 21:15 | 60 | 62.6333 | 79.6333 | 70.9
2015-10-02 21:30 | 60 | 62.3833 | 79.3833 | 70.15
2015-10-02 21:45 | 60 | 62.1333 | 79.1333 | 69.4
2015-10-02 22:00 | 59.9333 | 62 | 78.7667 | 69
2015-10-02 22:15 | 59.6833 | 62 | 78.2667 | 69
2015-10-02 22:30 | 59.4333 | 62 | 77.7667 | 69
2015-10-02 22:45 | 59.1833 | 62 | 77.2667 | 69
2015-10-02 23:00 | 59 | 61.7667 | 76.8833 | 68.65
2015-10-02 23:15 | 59 | 61.2667 | 76.6333 | 67.9
2015-10-02 23:30 | 59 | 60.7667 | 76.3833 | 67.15
2015-10-02 23:45 | 59 | 60.2667 | 76.1333 | 66.4
2015-10-03 | 58.9333 | 59.8833 | 75.8833 | 65.8833
2015-10-03 00:15 | 58.6833 | 59.6333 | 75.6333 | 65.6333
2015-10-03 00:30 | 58.4333 | 59.3833 | 75.3833 | 65.3833
2015-10-03 00:45 | 58.1833 | 59.1333 | 75.1333 | 65.1333
2015-10-03 01:00 | 58 | 58.8833 | 74.8833 | 64.8833
2015-10-03 01:15 | 58 | 58.6333 | 74.6333 | 64.6333
2015-10-03 01:30 | 58 | 58.3833 | 74.3833 | 64.3833
2015-10-03 01:45 | 58 | 58.1333 | 74.1333 | 64.1333
2015-10-03 02:00 | 57.9333 | 58 | 73.7667 | 63.8833
2015-10-03 02:15 | 57.6833 | 58 | 73.2667 | 63.6333
2015-10-03 02:30 | 57.4333 | 58 | 72.7667 | 63.3833
2015-10-03 02:45 | 57.1833 | 58 | 72.2667 | 63.1333
2015-10-03 03:00 | 56.9333 | 57.8833 | 72 | 62.8833
2015-10-03 03:15 | 56.6833 | 57.6333 | 72 | 62.6333
2015-10-03 03:30 | 56.4333 | 57.3833 | 72 | 62.3833
2015-10-03 03:45 | 56.1833 | 57.1333 | 72 | 62.1333
2015-10-03 04:00 | 56 | 56.65 | 71.8833 | 61.8833
2015-10-03 04:15 | 56 | 55.9 | 71.6333 | 61.6333
2015-10-03 04:30 | 56 | 55.15 | 71.3833 | 61.3833
2015-10-03 04:45 | 56 | 54.4 | 71.1333 | 61.1333
2015-10-03 05:00 | 56.0667 | 54.1167 | 70.7667 | 61.1167
2015-10-03 05:15 | 56.3167 | 54.3667 | 70.2667 | 61.3667
2015-10-03 05:30 | 56.5667 | 54.6167 | 69.7667 | 61.6167
2015-10-03 05:45 | 56.8167 | 54.8667 | 69.2667 | 61.8667
2015-10-03 06:00 | 57 | 55 | 68.8833 | 62.1167
2015-10-03 06:15 | 57 | 55 | 68.6333 | 62.3667
2015-10-03 06:30 | 57 | 55 | 68.3833 | 62.6167
2015-10-03 06:45 | 57 | 55 | 68.1333 | 62.8667
2015-10-03 07:00 | 57.2 | 55.35 | 68.1167 | 63.7
2015-10-03 07:15 | 57.95 | 56.1 | 68.3667 | 65.2
2015-10-03 07:30 | 58.7 | 56.85 | 68.6167 | 66.7
2015-10-03 07:45 | 59.45 | 57.6 | 68.8667 | 68.2
2015-10-03 08:00 | 60.2 | 58.5833 | 69.35 | 69.5833
2015-10-03 08:15 | 60.95 | 59.8333 | 70.1 | 70.8333
2015-10-03 08:30 | 61.7 | 61.0833 | 70.85 | 72.0833
2015-10-03 08:45 | 62.45 | 62.3333 | 71.6 | 73.3333
2015-10-03 09:00 | 63.1333 | 63.5833 | 72.5833 | 74.35
2015-10-03 09:15 | 63.6333 | 64.8333 | 73.8333 | 75.1
2015-10-03 09:30 | 64.1333 | 66.0833 | 75.0833 | 75.85
2015-10-03 09:45 | 64.6333 | 67.3333 | 76.3333 | 76.6
2015-10-03 10:00 | 65.2667 | 68.4667 | 77.5833 | 77.2333
2015-10-03 10:15 | 66.2667 | 69.4667 | 78.8333 | 77.7333
2015-10-03 10:30 | 67.2667 | 70.4667 | 80.0833 | 78.2333
2015-10-03 10:45 | 68.2667 | 71.4667 | 81.3333 | 78.7333
2015-10-03 11:00 | 69.0667 | 72.4667 | 81.8833 | 79.35
2015-10-03 11:15 | 69.3167 | 73.4667 | 81.6333 | 80.1
2015-10-03 11:30 | 69.5667 | 74.4667 | 81.3833 | 80.85
2015-10-03 11:45 | 69.8167 | 75.4667 | 81.1333 | 81.6
2015-10-03 12:00 | 69.8 | 76.1167 | 81.4667 | 82.1167
2015-10-03 12:15 | 69.05 | 76.3667 | 82.4667 | 82.3667
2015-10-03 12:30 | 68.3 | 76.6167 | 83.4667 | 82.6167
2015-10-03 12:45 | 67.55 | 76.8667 | 84.4667 | 82.8667
2015-10-03 13:00 | 66.8667 | 76.65 | 85.35 | 83.1167
2015-10-03 13:15 | 66.3667 | 75.9 | 86.1 | 83.3667
2015-10-03 13:30 | 65.8667 | 75.15 | 86.85 | 83.6167
2015-10-03 13:45 | 65.3667 | 74.4 | 87.6 | 83.8667
2015-10-03 14:00 | 64.8667 | 73.8833 | 88 | 84.1167
2015-10-03 14:15 | 64.3667 | 73.6333 | 88 | 84.3667
2015-10-03 14:30 | 63.8667 | 73.3833 | 88 | 84.6167
2015-10-03 14:45 | 63.3667 | 73.1333 | 88 | 84.8667
2015-10-03 15:00 | 62.8 | 72.3 | 88 | 85
2015-10-03 15:15 | 62.05 | 70.8 | 88 | 85
2015-10-03 15:30 | 61.3 | 69.3 | 88 | 85
2015-10-03 15:45 | 60.55 | 67.8 | 88 | 85
2015-10-03 16:00 | 59.9333 | 66.5333 | 87.7667 | 84.8833
2015-10-03 16:15 | 59.6833 | 65.5333 | 87.2667 | 84.6333
2015-10-03 16:30 | 59.4333 | 64.5333 | 86.7667 | 84.3833
2015-10-03 16:45 | 59.1833 | 63.5333 | 86.2667 | 84.1333
2015-10-03 17:00 | 58.9333 | 62.4167 | 85.4167 | 83.4167
2015-10-03 17:15 | 58.6833 | 61.1667 | 84.1667 | 82.1667
2015-10-03 17:30 | 58.4333 | 59.9167 | 82.9167 | 80.9167
2015-10-03 17:45 | 58.1833 | 58.6667 | 81.6667 | 79.6667
2015-10-03 18:00 | 58 | 58 | 80.65 | 78.8833
2015-10-03 18:15 | 58 | 58 | 79.9 | 78.6333
2015-10-03 18:30 | 58 | 58 | 79.15 | 78.3833
2015-10-03 18:45 | 58 | 58 | 78.4 | 78.1333
2015-10-03 19:00 | 58 | 58 | 77.7667 | 77.7667
2015-10-03 19:15 | 58 | 58 | 77.2667 | 77.2667
2015-10-03 19:30 | 58 | 58 | 76.7667 | 76.7667
2015-10-03 19:45 | 58 | 58 | 76.2667 | 76.2667
2015-10-03 20:00 | 58 | 58 | 75.8833 | 74.7167
2015-10-03 20:15 | 58 | 58 | 75.6333 | 71.9667
2015-10-03 20:30 | 58 | 58 | 75.3833 | 69.2167
2015-10-03 20:45 | 58 | 58 | 75.1333 | 66.4667
2015-10-03 21:00 | 57.931 | 58 | 74.8833 | 64.5333
2015-10-03 21:15 | 57.6724 | 58 | 74.6333 | 63.5333
2015-10-03 21:30 | 57.4138 | 58 | 74.3833 | 62.5333
2015-10-03 21:45 | 57.1552 | 58 | 74.1333 | 61.5333
2015-10-03 22:00 | 58 | 57.7667 | 73.8833 | 60.65
2015-10-03 22:15 | 58 | 57.2667 | 73.6333 | 59.9
2015-10-03 22:30 | 58 | 56.7667 | 73.3833 | 59.15
2015-10-03 22:45 | 58 | 56.2667 | 73.1333 | 58.4
2015-10-03 23:00 | 57.8 | 55.8833 | 72.8833 | 58
2015-10-03 23:15 | 57.05 | 55.6333 | 72.6333 | 58
2015-10-03 23:30 | 56.3 | 55.3833 | 72.3833 | 58
2015-10-03 23:45 | 55.55 | 55.1333 | 72.1333 | 58
2015-10-04 | 55.0667 | 54.8833 | 72 | 57.8833
2015-10-04 00:15 | 55.3167 | 54.6333 | 72 | 57.6333
2015-10-04 00:30 | 55.5667 | 54.3833 | 72 | 57.3833
2015-10-04 00:45 | 55.8167 | 54.1333 | 72 | 57.1333
2015-10-04 01:00 | 56.0667 | 54 | 71.4167 | 56.8833
2015-10-04 01:15 | 56.3167 | 54 | 70.1667 | 56.6333
2015-10-04 01:30 | 56.5667 | 54 | 68.9167 | 56.3833
2015-10-04 01:45 | 56.8167 | 54 | 67.6667 | 56.1333
2015-10-04 02:00 | 56.8667 | 54 | 66.4167 | 55.8833
2015-10-04 02:15 | 56.3667 | 54 | 65.1667 | 55.6333
2015-10-04 02:30 | 55.8667 | 54 | 63.9167 | 55.3833
2015-10-04 02:45 | 55.3667 | 54 | 62.6667 | 55.1333
2015-10-04 03:00 | 54.9333 | 54.1167 | 61.7667 | 54.7667
2015-10-04 03:15 | 54.6833 | 54.3667 | 61.2667 | 54.2667
2015-10-04 03:30 | 54.4333 | 54.6167 | 60.7667 | 53.7667
2015-10-04 03:45 | 54.1833 | 54.8667 | 60.2667 | 53.2667
2015-10-04 04:00 | 54.0667 | 54.8833 | 59.8833 | 53.1296
2015-10-04 04:15 | 54.3167 | 54.6333 | 59.6333 | 53.4074
2015-10-04 04:30 | 54.5667 | 54.3833 | 59.3833 | 53.6852
2015-10-04 04:45 | 54.8167 | 54.1333 | 59.1333 | 53.963
2015-10-04 05:00 | 55 | 54 | 59 | 54
2015-10-04 05:15 | 55 | 54 | 59 | 54
2015-10-04 05:30 | 55 | 54 | 59 | 54.2333
2015-10-04 05:45 | 55 | 54 | 59 | 54.7333
2015-10-04 06:00 | 55 | 54 | 58.8833 | 55.1167
2015-10-04 06:15 | 55 | 54 | 58.6333 | 55.3667
2015-10-04 06:30 | 55 | 54 | 58.3833 | 55.6167
2015-10-04 06:45 | 55 | 54 | 58.1333 | 55.8667
2015-10-04 07:00 | 55.2 | 54.4667 | 58.1167 | 56.2333
2015-10-04 07:15 | 55.95 | 55.4667 | 58.3667 | 56.7333
2015-10-04 07:30 | 56.7 | 56.4667 | 58.6167 | 57.2333
2015-10-04 07:45 | 57.45 | 57.4667 | 58.8667 | 57.7333
2015-10-04 08:00 | 58.2667 | 58.5833 | 59 | 58.35
2015-10-04 08:15 | 59.2667 | 59.8333 | 59 | 59.1
2015-10-04 08:30 | 60.2667 | 61.0833 | 59 | 59.85
2015-10-04 08:45 | 61.2667 | 62.3333 | 59 | 60.6
2015-10-04 09:00 | 62.2667 | 63.5833 | 59.1167 | 61.4667
2015-10-04 09:15 | 63.2667 | 64.8333 | 59.3667 | 62.4667
2015-10-04 09:30 | 64.2667 | 66.0833 | 59.6167 | 63.4667
2015-10-04 09:45 | 65.2667 | 67.3333 | 59.8667 | 64.4667
2015-10-04 10:00 | 66.2 | 68.35 | 60.2333 | 65.35
2015-10-04 10:15 | 66.95 | 69.1 | 60.7333 | 66.1
2015-10-04 10:30 | 67.7 | 69.85 | 61.2333 | 66.85
2015-10-04 10:45 | 68.45 | 70.6 | 61.7333 | 67.6
2015-10-04 11:00 | 69.2 | 71.35 | 62 | 68.35
2015-10-04 11:15 | 69.95 | 72.1 | 62 | 69.1
2015-10-04 11:30 | 70.7 | 72.85 | 62 | 69.85
2015-10-04 11:45 | 71.45 | 73.6 | 62 | 70.6
2015-10-04 12:00 | 72 | 74.35 | 61.7667 | 71
2015-10-04 12:15 | 72 | 75.1 | 61.2667 | 71
2015-10-04 12:30 | 72 | 75.85 | 60.7667 | 71
2015-10-04 12:45 | 71.6875 | 76.6 | 60.2667 | 71
2015-10-04 13:00 | 71.0667 | 77.4667 | 59.7667 | 71.2333
2015-10-04 13:15 | 71.3167 | 78.4667 | 59.2667 | 71.7333
2015-10-04 13:30 | 71.5667 | 79.4667 | 59 | 72.2333
2015-10-04 13:45 | 71.8167 | 80.4667 | 59 | 72.7333
2015-10-04 14:00 | 72 | 80.5333 | 59 | 72.7667
2015-10-04 14:15 | 72 | 79.5333 | 59 | 72.2667
2015-10-04 14:30 | 72 | 78.5333 | 59 | 71.7667
2015-10-04 14:45 | 72 | 77.5333 | 59 | 71.2667
2015-10-04 15:00 | 71.9333 | 76.5333 | 59 | 71
2015-10-04 15:15 | 71.6833 | 75.5333 | 59 | 71
2015-10-04 15:30 | 71.4333 | 74.5333 | 59 | 71
2015-10-04 15:45 | 71.1833 | 73.5333 | 59.2727 | 71
2015-10-04 16:00 | 70.8667 | 72.65 | 60 | 71
2015-10-04 16:15 | 70.3667 | 71.9 | 60 | 71
2015-10-04 16:30 | 69.8667 | 71.15 | 60 | 71
2015-10-04 16:45 | 69.3667 | 70.4 | 60 | 71
2015-10-04 17:00 | 68.7333 | 69.7667 | 60 | 70.7667
2015-10-04 17:15 | 67.7333 | 69.2667 | 60 | 70.2667
2015-10-04 17:30 | 66.7333 | 68.7667 | 60 | 69.7667
2015-10-04 17:45 | 65.7333 | 68.2667 | 60 | 69.2667
2015-10-04 18:00 | 64.8667 | 67.7667 | 60 | 68.7667
2015-10-04 18:15 | 64.3667 | 67.2667 | 60 | 68.2667
2015-10-04 18:30 | 63.8667 | 66.7667 | 60 | 67.7667
2015-10-04 18:45 | 63.3667 | 66.2667 | 60 | 67.2667
2015-10-04 19:00 | 63 | 65.7667 | 60 | 66.8833
2015-10-04 19:15 | 63 | 65.2667 | 60 | 66.6333
2015-10-04 19:30 | 63 | 64.7667 | 60 | 66.3833
2015-10-04 19:45 | 63 | 64.2667 | 60 | 66.1333
2015-10-04 20:00 | 63 | 63.8833 | 60 | 65.7667
2015-10-04 20:15 | 63 | 63.6333 | 60 | 65.2667
2015-10-04 20:30 | 63 | 63.3833 | 60 | 64.7667
2015-10-04 20:45 | 63 | 63.1333 | 60 | 64.2667
2015-10-04 21:00 | 62.9333 | 63 | 60 | 63.7667
2015-10-04 21:15 | 62.6833 | 63 | 60 | 63.2667
2015-10-04 21:30 | 62.4333 | 63 | 60 | 62.7667
2015-10-04 21:45 | 62.1833 | 63 | 60 | 62.2667
2015-10-04 22:00 | 62 | 62.7667 | 60 | 62.1167
2015-10-04 22:15 | 62 | 62.2667 | 60 | 62.3667
2015-10-04 22:30 | 62 | 61.7667 | 60 | 62.6167
2015-10-04 22:45 | 62 | 61.2667 | 60 | 62.8667
2015-10-04 23:00 | 61.8667 | 60.8833 | 60 | 62.65
2015-10-04 23:15 | 61.3667 | 60.6333 | 60 | 61.9
2015-10-04 23:30 | 60.8667 | 60.3833 | 60 | 61.15
2015-10-04 23:45 | 60.3667 | 60.1333 | 60.7895 | 60.4
2015-10-05 | 60.0667 | 60 | 59.2222 | 60
2015-10-05 00:15 | 60.3167 | 60 | 59.8125 | 60
2015-10-05 00:30 | 60.5667 | 60 | 60 | 60
2015-10-05 00:45 | 60.8167 | 60 | 60.7333 | 60
2015-10-05 01:00 | 61.0667 | 59.8833 | 60 | 60
2015-10-05 01:15 | 61.3167 | 59.6333 | 60 | 60
2015-10-05 01:30 | 61.5667 | 59.3833 | 60 | 60
2015-10-05 01:45 | 61.8167 | 59.1333 | 60 | 60
2015-10-05 02:00 | 61.7333 | 59 | 60 | 60
2015-10-05 02:15 | 60.7333 | 59 | 60 | 60
2015-10-05 02:30 | 59.7333 | 59 | 60 | 60
2015-10-05 02:45 | 58.7333 | 59 | 60 | 60
2015-10-05 03:00 | 58 | 58.8833 | 60 | 60
2015-10-05 03:15 | 58 | 58.6333 | 60 | 60
2015-10-05 03:30 | 58 | 58.3833 | 60 | 60
2015-10-05 03:45 | 58 | 58.1333 | 60 | 60
2015-10-05 04:00 | 58.1333 | 58 | 59.8833 | 59.8833
2015-10-05 04:15 | 58.6333 | 58 | 59.6333 | 59.6333
2015-10-05 04:30 | 59.1333 | 58 | 59.3833 | 59.3833
2015-10-05 04:45 | 59.6333 | 58 | 59.1333 | 59.1333
2015-10-05 05:00 | 60.0667 | 57.8833 | 59 | 58.8833
2015-10-05 05:15 | 60.3167 | 57.6333 | 59 | 58.6333
2015-10-05 05:30 | 60.5667 | 57.3833 | 59.0417 | 58.3833
2015-10-05 05:45 | 60.8167 | 57.1333 | 59.6667 | 58.1333
2015-10-05 06:00 | 61.1333 | 57 | 59.3636 | 58.2333
2015-10-05 06:15 | 61.6333 | 57 | 59 | 58.7333
2015-10-05 06:30 | 62.1333 | 57 | 59 | 59.2333
2015-10-05 06:45 | 62.6333 | 57 | 59 | 59.7333
2015-10-05 07:00 | 63.0667 | 57.5833 | 59 | 60.7
2015-10-05 07:15 | 63.3167 | 58.8333 | 59 | 62.2
2015-10-05 07:30 | 63.5667 | 60.0833 | 59 | 63.7
2015-10-05 07:45 | 63.8167 | 61.3333 | 59 | 65.2
2015-10-05 08:00 | 64.0667 | 62.35 | 59.1167 | 66.4667
2015-10-05 08:15 | 64.3167 | 63.1 | 59.3667 | 67.4667
2015-10-05 08:30 | 64.5667 | 63.85 | 59.6167 | 68.4667
2015-10-05 08:45 | 64.8167 | 64.6 | 59.8667 | 69.4667
2015-10-05 09:00 | 65.0667 | 65.4667 | 60.2692 | 70.2333
2015-10-05 09:15 | 65.3167 | 66.4667 | 60.8462 | 70.7333
2015-10-05 09:30 | 65.5667 | 67.4667 | 61.4231 | 71.2333
2015-10-05 09:45 | 65.8167 | 68.4667 | 62 | 71.7333
2015-10-05 10:00 | 66.0667 | 69.35 | 62.4667 | 72.35
2015-10-05 10:15 | 66.3167 | 70.1 | 63.4667 | 73.1
2015-10-05 10:30 | 66.5667 | 70.85 | 64.4667 | 73.85
2015-10-05 10:45 | 66.8167 | 71.6 | 65.4667 | 74.6
2015-10-05 11:00 | 67.0667 | 72.35 | 66.35 | 75.1167
2015-10-05 11:15 | 67.3167 | 73.1 | 67.1 | 75.3667
2015-10-05 11:30 | 67.5667 | 73.85 | 67.85 | 75.6167
2015-10-05 11:45 | 67.8167 | 74.6 | 68.6 | 75.8667
2015-10-05 12:00 | 68.1333 | 75.1167 | 69.35 | 76.1167
2015-10-05 12:15 | 68.6333 | 75.3667 | 70.1 | 76.3667
2015-10-05 12:30 | 69.1333 | 75.6167 | 70.85 | 76.6167
2015-10-05 12:45 | 69.6333 | 75.8667 | 71.6 | 76.8667
2015-10-05 13:00 | 70.0667 | 76.35 | 72.1167 | 77.35
2015-10-05 13:15 | 70.3167 | 77.1 | 72.3667 | 78.1
2015-10-05 13:30 | 70.5667 | 77.85 | 72.6167 | 78.85
2015-10-05 13:45 | 70.8167 | 78.6 | 72.8667 | 79.6
2015-10-05 14:00 | 71.1333 | 78.65 | 73.35 | 80
2015-10-05 14:15 | 71.6333 | 77.9 | 74.1 | 80
2015-10-05 14:30 | 72.1333 | 77.15 | 74.85 | 80
2015-10-05 14:45 | 72.6333 | 76.4 | 75.6 | 80
2015-10-05 15:00 | 72.9333 | 75.8833 | 76.1167 | 79.8833
2015-10-05 15:15 | 72.6833 | 75.6333 | 76.3667 | 79.6333
2015-10-05 15:30 | 72.4333 | 75.3833 | 76.6167 | 79.3833
2015-10-05 15:45 | 72.1833 | 75.1333 | 76.8667 | 79.1333
2015-10-05 16:00 | 71.8 | 74.8833 | 76.8833 | 79
2015-10-05 16:15 | 71.05 | 74.6333 | 76.6333 | 79
2015-10-05 16:30 | 70.3 | 74.3833 | 76.3833 | 79
2015-10-05 16:45 | 69.55 | 74.1333 | 76.1333 | 79
2015-10-05 17:00 | 68.9333 | 73.65 | 75.8833 | 78.7667
2015-10-05 17:15 | 68.6833 | 72.9 | 75.6333 | 78.2667
2015-10-05 17:30 | 68.4333 | 72.15 | 75.3833 | 77.7667
2015-10-05 17:45 | 68.1833 | 71.4 | 75.1333 | 77.2667
2015-10-05 18:00 | 67.9333 | 70.7667 | 74.5333 | 76.8833
2015-10-05 18:15 | 67.6833 | 70.2667 | 73.5333 | 76.6333
2015-10-05 18:30 | 67.4333 | 69.7667 | 72.5333 | 76.3833
2015-10-05 18:45 | 67.1833 | 69.2667 | 71.5333 | 76.1333
2015-10-05 19:00 | 66.9333 | 68.7667 | 70.65 | 75.8833
2015-10-05 19:15 | 66.6833 | 68.2667 | 69.9 | 75.6333
2015-10-05 19:30 | 66.4333 | 67.7667 | 69.15 | 75.3833
2015-10-05 19:45 | 66.1833 | 67.2667 | 68.4 | 75.1333
2015-10-05 20:00 | 65.9333 | 66.7667 | 67.7667 | 74.7667
2015-10-05 20:15 | 65.6833 | 66.2667 | 67.2667 | 74.2667
2015-10-05 20:30 | 65.4333 | 65.7667 | 66.7667 | 73.7667
2015-10-05 20:45 | 65.1833 | 65.2667 | 66.2667 | 73.2667
2015-10-05 21:00 | 65 | 65 | 66 | 72.7667
2015-10-05 21:15 | 65 | 65 | 66 | 72.2667
2015-10-05 21:30 | 65 | 65 | 66 | 71.7667
2015-10-05 21:45 | 65 | 65 | 66 | 71.2667
2015-10-05 22:00 | 64.9333 | 64.7667 | 65.8833 | 70.8833
2015-10-05 22:15 | 64.6833 | 64.2667 | 65.6333 | 70.6333
2015-10-05 22:30 | 64.4333 | 63.7667 | 65.3833 | 70.3833
2015-10-05 22:45 | 64.1833 | 63.2667 | 65.1333 | 70.1333
2015-10-05 23:00 | 63.8667 | 62.8833 | 64.8833 | 69.4167
2015-10-05 23:15 | 63.3667 | 62.6333 | 64.6333 | 68.1667
2015-10-05 23:30 | 62.8667 | 62.3833 | 64.3833 | 66.9167
2015-10-05 23:45 | 62.3667 | 62.1333 | 64.1333 | 65.6667
2015-10-06 | 62.0667 | 61.8833 | 63.7667 | 65
2015-10-06 00:15 | 62.3167 | 61.6333 | 63.2667 | 65
2015-10-06 00:30 | 62.5667 | 61.3833 | 62.7667 | 65
2015-10-06 00:45 | 62.8167 | 61.1333 | 62.2667 | 65
2015-10-06 01:00 | 63 | 61 | 61.7667 | 64.8833
2015-10-06 01:15 | 63 | 61 | 61.2667 | 64.6333
2015-10-06 01:30 | 63 | 61 | 60.7667 | 64.3833
2015-10-06 01:45 | 63 | 61 | 60.2667 | 64.1333
2015-10-06 02:00 | 62.9333 | 60.8833 | 60 | 63.7667
2015-10-06 02:15 | 62.6833 | 60.6333 | 60 | 63.2667
2015-10-06 02:30 | 62.4333 | 60.3833 | 60 | 62.7667
2015-10-06 02:45 | 62.1833 | 60.1333 | 60 | 62.2667
2015-10-06 03:00 | 61.8667 | 60.1167 | 59.7667 | 61.8833
2015-10-06 03:15 | 61.3667 | 60.3667 | 59.2667 | 61.6333
2015-10-06 03:30 | 60.8667 | 60.6167 | 58.7667 | 61.3833
2015-10-06 03:45 | 60.3667 | 60.8667 | 58.2667 | 61.1333
2015-10-06 04:00 | 60.0667 | 60.7667 | 58 | 60.8833
2015-10-06 04:15 | 60.3167 | 60.2667 | 58 | 60.6333
2015-10-06 04:30 | 60.5667 | 59.7667 | 58 | 60.3833
2015-10-06 04:45 | 60.8167 | 59.2667 | 58 | 60.1333
2015-10-06 05:00 | 60.9333 | 58.8833 | 58 | 60
2015-10-06 05:15 | 60.6833 | 58.6333 | 58 | 60
2015-10-06 05:30 | 60.4333 | 58.3833 | 58 | 60
2015-10-06 05:45 | 60.1833 | 58.1333 | 58 | 60
2015-10-06 06:00 | 60.2069 | 58.1167 | 57.7667 | 60.1167
2015-10-06 06:15 | 60.9828 | 58.3667 | 57.2667 | 60.3667
2015-10-06 06:30 | 61.7586 | 58.6167 | 56.7667 | 60.6167
2015-10-06 06:45 | 62.5345 | 58.8667 | 56.2667 | 60.8667
2015-10-06 07:00 | 63.069 | 59.35 | 56.35 | 61.4667
2015-10-06 07:15 | 63.3276 | 60.1 | 57.1 | 62.4667
2015-10-06 07:30 | 63.5862 | 60.85 | 57.85 | 63.4667
2015-10-06 07:45 | 63.8448 | 61.6 | 58.6 | 64.4667
2015-10-06 08:00 | 65.1333 | 62.35 | 59.8167 | 65.5833
2015-10-06 08:15 | 65.6333 | 63.1 | 61.5667 | 66.8333
2015-10-06 08:30 | 66.1333 | 63.85 | 63.3167 | 68.0833
2015-10-06 08:45 | 66.6333 | 64.6 | 65.0667 | 69.3333
2015-10-06 09:00 | 67.0667 | 65.35 | 66.7 | 70.4667
2015-10-06 09:15 | 67.3167 | 66.1 | 68.2 | 71.4667
2015-10-06 09:30 | 67.5667 | 66.85 | 69.7 | 72.4667
2015-10-06 09:45 | 67.8167 | 67.6 | 71.2 | 73.4667
2015-10-06 10:00 | 68.0667 | 68.5833 | 72.4667 | 74.35
2015-10-06 10:15 | 68.3167 | 69.8333 | 73.4667 | 75.1
2015-10-06 10:30 | 68.5667 | 71.0833 | 74.4667 | 75.85
2015-10-06 10:45 | 68.8167 | 72.3333 | 75.4667 | 76.6
2015-10-06 11:00 | 69 | 73 | 76.2333 | 77.2333
2015-10-06 11:15 | 69 | 73 | 76.7333 | 77.7333
2015-10-06 11:30 | 69 | 73 | 77.2333 | 78.2333
2015-10-06 11:45 | 69 | 73 | 77.7333 | 78.7333
2015-10-06 12:00 | 69.1333 | 73.35 | 78.35 | 79.2333
2015-10-06 12:15 | 69.6333 | 74.1 | 79.1 | 79.7333
2015-10-06 12:30 | 70.1333 | 74.85 | 79.85 | 80.2333
2015-10-06 12:45 | 70.6333 | 75.6 | 80.6 | 80.7333
2015-10-06 13:00 | 71.1333 | 76.1167 | 81.1167 | 81.1167
2015-10-06 13:15 | 71.6333 | 76.3667 | 81.3667 | 81.3667
2015-10-06 13:30 | 72.1333 | 76.6167 | 81.6167 | 81.6167
2015-10-06 13:45 | 72.6333 | 76.8667 | 81.8667 | 81.8667
2015-10-06 14:00 | 73 | 76.8833 | 82 | 82
2015-10-06 14:15 | 73 | 76.6333 | 82 | 82
2015-10-06 14:30 | 72.4857 | 76.3833 | 82 | 82
2015-10-06 14:45 | 71.6286 | 76.1333 | 82 | 82
2015-10-06 15:00 | 70.9333 | 75.7667 | 81.8833 | 82
2015-10-06 15:15 | 70.6833 | 75.2667 | 81.6333 | 82
2015-10-06 15:30 | 70.4333 | 74.7667 | 81.3833 | 82
2015-10-06 15:45 | 70.1833 | 74.2667 | 81.1333 | 82
2015-10-06 16:00 | 69.8 | 73.5333 | 81.2333 | 81.8833
2015-10-06 16:15 | 69.05 | 72.5333 | 81.7333 | 81.6333
2015-10-06 16:30 | 68.3 | 71.5333 | 82.2333 | 81.3833
2015-10-06 16:45 | 67.55 | 70.5333 | 82.7333 | 81.1333
2015-10-06 17:00 | 66.8 | 69.65 | 82.4167 | 80.7667
2015-10-06 17:15 | 66.05 | 68.9 | 81.1667 | 80.2667
2015-10-06 17:30 | 65.3 | 68.15 | 79.9167 | 79.7667
2015-10-06 17:45 | 64.55 | 67.4 | 78.6667 | 79.2667
2015-10-06 18:00 | 63.9333 | 66.8833 | 77.7667 | 78.7667
2015-10-06 18:15 | 63.6833 | 66.6333 | 77.2667 | 78.2667
2015-10-06 18:30 | 63.4333 | 66.3833 | 76.7667 | 77.7667
2015-10-06 18:45 | 63.1833 | 66.1333 | 76.2667 | 77.2667
2015-10-06 19:00 | 62.9333 | 65.65 | 76 | 76.65
2015-10-06 19:15 | 62.6833 | 64.9 | 76 | 75.9
2015-10-06 19:30 | 62.4333 | 64.15 | 76 | 75.15
2015-10-06 19:45 | 62.1833 | 63.4 | 76 | 74.4
2015-10-06 20:00 | 62 | 63.1167 | 75.65 | 73.8833
2015-10-06 20:15 | 62 | 63.3667 | 74.9 | 73.6333
2015-10-06 20:30 | 62 | 63.6167 | 74.15 | 73.3833
2015-10-06 20:45 | 62 | 63.8667 | 73.4 | 73.1333
2015-10-06 21:00 | 61.9333 | 63.7667 | 72.65 | 72.8833
2015-10-06 21:15 | 61.6833 | 63.2667 | 71.9 | 72.6333
2015-10-06 21:30 | 61.4333 | 62.7667 | 71.15 | 72.3833
2015-10-06 21:45 | 61.1833 | 62.2667 | 70.4 | 72.1333
2015-10-06 22:00 | 61 | 62 | 69.65 | 71.7667
2015-10-06 22:15 | 61 | 62 | 68.9 | 71.2667
2015-10-06 22:30 | 61 | 62 | 68.15 | 70.7667
2015-10-06 22:45 | 61 | 62 | 67.4 | 70.2667
2015-10-06 23:00 | 61 | 61.7667 | 67 | 69.7667
2015-10-06 23:15 | 61 | 61.2667 | 67 | 69.2667
2015-10-06 23:30 | 61 | 60.7667 | 67 | 68.7667
2015-10-06 23:45 | 61 | 60.2667 | 67 | 68.2667
2015-10-07 | 60.9333 | 60.1167 | 67 | 67.8833
2015-10-07 00:15 | 60.6833 | 60.3667 | 67 | 67.6333
2015-10-07 00:30 | 60.4333 | 60.6167 | 67 | 67.3833
2015-10-07 00:45 | 60.1833 | 60.8667 | 67 | 67.1333
2015-10-07 01:00 | 60.1053 | 61 | 66.8833 | 66.7667
2015-10-07 01:15 | 60.5 | 61 | 66.6333 | 66.2667
2015-10-07 01:30 | 60.8947 | 61 | 66.3833 | 65.7667
2015-10-07 01:45 | 60.5 | 61 | 66.1333 | 65.2667
2015-10-07 02:00 | 60 | 61.1167 | 65.7667 | 65
2015-10-07 02:15 | 60 | 61.3667 | 65.2667 | 65
2015-10-07 02:30 | 60 | 61.6167 | 64.7667 | 65
2015-10-07 02:45 | 60 | 61.8667 | 64.2667 | 65
2015-10-07 03:00 | 60.08 | 61.8833 | 64 | 64.7667
2015-10-07 03:15 | 60.38 | 61.6333 | 64 | 64.2667
2015-10-07 03:30 | 60.68 | 61.3833 | 64 | 63.7667
2015-10-07 03:45 | 60.98 | 61.1333 | 64 | 63.2667
2015-10-07 04:00 | 61 | 61 | 64.1167 | 62.8833
2015-10-07 04:15 | 61 | 61 | 64.3667 | 62.6333
2015-10-07 04:30 | 61 | 61 | 64.6167 | 62.3833
2015-10-07 04:45 | 61 | 61 | 64.8667 | 62.1333
2015-10-07 05:00 | 61 | 61 | 64.7667 | 61.8833
2015-10-07 05:15 | 61 | 61 | 64.2667 | 61.6333
2015-10-07 05:30 | 61 | 61 | 63.7667 | 61.3833
2015-10-07 05:45 | 61 | 61 | 63.2667 | 61.1333
2015-10-07 06:00 | 61.0667 | 61 | 63.1167 | 61.1167
2015-10-07 06:15 | 61.3167 | 61 | 63.3667 | 61.3667
2015-10-07 06:30 | 61.5667 | 61 | 63.6167 | 61.6167
2015-10-07 06:45 | 61.8167 | 61 | 63.8667 | 61.8667
2015-10-07 07:00 | 62.0667 | 61.1167 | 64 | 62.5833
2015-10-07 07:15 | 62.3167 | 61.3667 | 64 | 63.8333
2015-10-07 07:30 | 62.5667 | 61.6167 | 64 | 65.0833
2015-10-07 07:45 | 62.8167 | 61.8667 | 64 | 66.3333
2015-10-07 08:00 | 63.069 | 62.1892 | 64 | 67.5833
2015-10-07 08:15 | 63.3276 | 62.5946 | 64 | 68.8333
2015-10-07 08:30 | 63.5862 | 63 | 64 | 70.0833
2015-10-07 08:45 | 63.8448 | 63.6522 | 64 | 71.3333
2015-10-07 09:00 | 64.1333 | 64.4667 | 64.4667 | 72.4667
2015-10-07 09:15 | 64.6333 | 65.4667 | 65.4667 | 73.4667
2015-10-07 09:30 | 65.1333 | 66.4667 | 66.4667 | 74.4667
2015-10-07 09:45 | 65.6333 | 67.4667 | 67.4667 | 75.4667
2015-10-07 10:00 | 66.0667 | 68.35 | 68.8167 | 76.35
2015-10-07 10:15 | 66.3167 | 69.1 | 70.5667 | 77.1
2015-10-07 10:30 | 66.5667 | 69.85 | 72.3167 | 77.85
2015-10-07 10:45 | 66.8167 | 70.6 | 74.0667 | 78.6
2015-10-07 11:00 | 67.3333 | 71.5833 | 75.4667 | 79.4667
2015-10-07 11:15 | 68.5833 | 72.8333 | 76.4667 | 80.4667
2015-10-07 11:30 | 69.8333 | 74.0833 | 77.4667 | 81.4667
2015-10-07 11:45 | 71.0833 | 75.3333 | 78.4667 | 82.4667
2015-10-07 12:00 | 72.0667 | 76.35 | 79.1167 | 83.1167
2015-10-07 12:15 | 72.3167 | 77.1 | 79.3667 | 83.3667
2015-10-07 12:30 | 72.5667 | 77.85 | 79.6167 | 83.6167
2015-10-07 12:45 | 72.8167 | 78.6 | 79.8667 | 83.8667
2015-10-07 13:00 | 72.7333 | 78.8833 | 80.1167 | 84.1167
2015-10-07 13:15 | 71.7333 | 78.6333 | 80.3667 | 84.3667
2015-10-07 13:30 | 70.7333 | 78.3833 | 80.6167 | 84.6167
2015-10-07 13:45 | 69.7333 | 78.1333 | 80.8667 | 84.8667
2015-10-07 14:00 | 68.8667 | 77.65 | 81 | 85.1167
2015-10-07 14:15 | 68.3667 | 76.9 | 81 | 85.3667
2015-10-07 14:30 | 67.8667 | 76.15 | 81 | 85.6167
2015-10-07 14:45 | 67.3667 | 75.4 | 81 | 85.8667
2015-10-07 15:00 | 66.9333 | 74.7667 | 81.2333 | 85.8833
2015-10-07 15:15 | 66.6833 | 74.2667 | 81.7333 | 85.6333
2015-10-07 15:30 | 66.4333 | 73.7667 | 82.2333 | 85.3833
2015-10-07 15:45 | 66.1833 | 73.2667 | 82.7333 | 85.1333
2015-10-07 16:00 | 65.8667 | 72.65 | 82.65 | 84.8833
2015-10-07 16:15 | 65.3667 | 71.9 | 81.9 | 84.6333
2015-10-07 16:30 | 64.8667 | 71.15 | 81.15 | 84.3833
2015-10-07 16:45 | 64.3667 | 70.4 | 80.4 | 84.1333
2015-10-07 17:00 | 63.8667 | 69.65 | 79.8833 | 83.5333
2015-10-07 17:15 | 63.3667 | 68.9 | 79.6333 | 82.5333
2015-10-07 17:30 | 62.8667 | 68.15 | 79.3833 | 81.5333
2015-10-07 17:45 | 62.3667 | 67.4 | 79.1333 | 80.5333
2015-10-07 18:00 | 61.9333 | 66.8833 | 78.7308 | 79.7667
2015-10-07 18:15 | 61.6833 | 66.6333 | 78.1538 | 79.2667
2015-10-07 18:30 | 61.4333 | 66.3833 | 77.5769 | 78.7667
2015-10-07 18:45 | 61.1833 | 66.1333 | 77 | 78.2667
2015-10-07 19:00 | 60.9333 | 65.8833 | 76 | 77.7667
2015-10-07 19:15 | 60.6833 | 65.6333 | 76 | 77.2667
2015-10-07 19:30 | 60.4333 | 65.3833 | 75.2143 | 76.7667
2015-10-07 19:45 | 60.1833 | 65.1333 | 75 | 76.2667
2015-10-07 20:00 | 59.9333 | 64.8833 | 74.6316 | 75.7667
2015-10-07 20:15 | 59.6833 | 64.6333 | 73.8421 | 75.2667
2015-10-07 20:30 | 59.4333 | 64.3833 | 73.0526 | 74.7667
2015-10-07 20:45 | 59.1833 | 64.1333 | 72.2632 | 74.2667
2015-10-07 21:00 | 59 | 63.8833 | 70.2632 | 74
2015-10-07 21:15 | 59 | 63.6333 | 69.2727 | 74
2015-10-07 21:30 | 59 | 63.3833 | 69.125 | 74
2015-10-07 21:45 | 59 | 63.1333 | 67.2857 | 74
2015-10-07 22:00 | 59.1333 | 62.8833 | 67 | 73.8833
2015-10-07 22:15 | 59.6333 | 62.6333 | 67 | 73.6333
2015-10-07 22:30 | 60.1333 | 62.3833 | 67.3611 | 73.3833
2015-10-07 22:45 | 60.6333 | 62.1333 | 67.7778 | 73.1333
2015-10-07 23:00 | 61.0667 | 62 | 67.5333 | 72.8833
2015-10-07 23:15 | 61.3167 | 62 | 66.5333 | 72.6333
2015-10-07 23:30 | 61.5667 | 62 | 65.5333 | 72.3833
2015-10-07 23:45 | 61.8167 | 62 | 64.5333 | 72.1333
2015-10-08 | 61.8667 | 62 | 63.7255 | 71.8833
2015-10-08 00:15 | 61.3667 | 62 | 63.1373 | 71.6333
2015-10-08 00:30 | 60.8667 | 62 | 62.549 | 71.3833
2015-10-08 00:45 | 60.3667 | 62 | 62.1429 | 71.1333
2015-10-08 01:00 | 60 | 62 | 62.1207 | 70.7667
2015-10-08 01:15 | 60 | 62 | 62.3793 | 70.2667
2015-10-08 01:30 | 60 | 62 | 62.6379 | 69.7667
2015-10-08 01:45 | 60 | 62 | 62.8966 | 69.2667
2015-10-08 02:00 | 60 | 61.8833 | 61.7586 | 68.8833
2015-10-08 02:15 | 60 | 61.6333 | 61.2414 | 68.6333
2015-10-08 02:30 | 60 | 61.3833 | 61 | 68.3833
2015-10-08 02:45 | 60 | 61.1333 | 61 | 68.1333
2015-10-08 03:00 | 59.9333 | 61 | 61 | 68
2015-10-08 03:15 | 59.6833 | 61 | 60.381 | 68
2015-10-08 03:30 | 59.4333 | 61 | 60 | 68
2015-10-08 03:45 | 59.1833 | 61 | 59 | 68
2015-10-08 04:00 | 59 | 61 | 59 | 67.8833
2015-10-08 04:15 | 59 | 61 | 59 | 67.6333
2015-10-08 04:30 | 59 | 61 | 59 | 67.3833
2015-10-08 04:45 | 59 | 61 | 59 | 67.1333
2015-10-08 05:00 | 59.1333 | 61 | 59 | 66.8833
2015-10-08 05:15 | 59.6333 | 61 | 59 | 66.6333
2015-10-08 05:30 | 60.1333 | 61 | 58.375 | 66.3833
2015-10-08 05:45 | 60.6333 | 61 | 58 | 66.1333
2015-10-08 06:00 | 61 | 61 | 58 | 66.4667
2015-10-08 06:15 | 61 | 61 | 58 | 67.4667
2015-10-08 06:30 | 61 | 61 | 57.7391 | 68.4667
2015-10-08 06:45 | 61 | 61 | 57.087 | 69.4667
2015-10-08 07:00 | 61.2 | 61.2333 | 58 | 70.35
2015-10-08 07:15 | 61.95 | 61.7333 | 58 | 71.1
2015-10-08 07:30 | 62.7 | 62.2333 | 58 | 71.85
2015-10-08 07:45 | 63.45 | 62.7333 | 58 | 72.6
2015-10-08 08:00 | 64.0667 | 63.7 | 58.35 | 73.5833
2015-10-08 08:15 | 64.3167 | 65.2 | 59 | 74.8333
2015-10-08 08:30 | 64.5667 | 66.7 | 59 | 76.0833
2015-10-08 08:45 | 64.8167 | 68.2 | 59 | 77.3333
2015-10-08 09:00 | 65.2 | 69.5833 | 59 | 78.2333
2015-10-08 09:15 | 65.95 | 70.8333 | 58 | 78.7333
2015-10-08 09:30 | 66.7 | 72.0833 | 59 | 79.2333
2015-10-08 09:45 | 67.45 | 73.3333 | 59 | 79.7333
2015-10-08 10:00 | 68.0667 | 74.5833 | 59 | 80.1167
2015-10-08 10:15 | 68.3167 | 75.8333 | 60 | 80.3667
2015-10-08 10:30 | 68.5667 | 77.0833 | 60 | 80.6167
2015-10-08 10:45 | 68.8167 | 78.3333 | 60 | 80.8667
2015-10-08 11:00 | 69.1333 | 79.4667 | 60.1707 | 81.35
2015-10-08 11:15 | 69.6333 | 80.4667 | 60.5366 | 82.1
2015-10-08 11:30 | 70.1333 | 81.4667 | 60.9024 | 82.85
2015-10-08 11:45 | 70.6333 | 82.4667 | 62.2941 | 83.6
2015-10-08 12:00 | 71.5333 | 83.1167 | 62.1522 | 84.35
2015-10-08 12:15 | 73.5333 | 83.3667 | 62.4783 | 85.1
2015-10-08 12:30 | 75.5333 | 83.6167 | 62.8043 | 85.85
2015-10-08 12:45 | 77.5333 | 83.8667 | 62.1429 | 86.6
2015-10-08 13:00 | 79 | 84.1167 | 62 | 87
2015-10-08 13:15 | 79 | 84.3667 | 62 | 87
2015-10-08 13:30 | 79 | 84.6167 | 63.1351 | 87
2015-10-08 13:45 | 79 | 84.8667 | 64.3514 | 87
2015-10-08 14:00 | 78.7333 | 85 | 65.2333 | 87.2333
2015-10-08 14:15 | 77.7333 | 85 | 65.7333 | 87.7333
2015-10-08 14:30 | 76.7333 | 85 | 66.2333 | 88.2333
2015-10-08 14:45 | 75.7333 | 85 | 66.7333 | 88.7333
2015-10-08 15:00 | 74.8 | 84.3 | 66.6111 | 88.8833
2015-10-08 15:15 | 74.05 | 82.8 | 65.7778 | 88.6333
2015-10-08 15:30 | 73.3 | 81.3 | 64.9444 | 88.3833
2015-10-08 15:45 | 72.55 | 79.8 | 64.1111 | 88.1333
2015-10-08 16:00 | 72 | 78.65 | 63.6818 | 87.7667
2015-10-08 16:15 | 72 | 77.9 | 63 | 87.2667
2015-10-08 16:30 | 72 | 77.15 | 63 | 86.7667
2015-10-08 16:45 | 72 | 76.4 | 63 | 86.2667
2015-10-08 17:00 | 71.6667 | 75.8833 | 61.5333 | 85.65
2015-10-08 17:15 | 70.4167 | 75.6333 | 61 | 84.9
2015-10-08 17:30 | 69.1667 | 75.3833 | 61 | 84.15
2015-10-08 17:45 | 67.9167 | 75.1333 | 61 | 83.4
2015-10-08 18:00 | 66.8 | 74.7667 | 61 | 82.7667
2015-10-08 18:15 | 66.05 | 74.2667 | 61 | 82.2667
2015-10-08 18:30 | 65.3 | 73.7667 | 61 | 81.7667
2015-10-08 18:45 | 64.55 | 73.2667 | 61 | 81.2667
2015-10-08 19:00 | 63.9333 | 72.8833 | 61.4375 | 80.65
2015-10-08 19:15 | 63.6833 | 72.6333 | 62 | 79.9
2015-10-08 19:30 | 63.4333 | 72.3833 | 62 | 79.15
2015-10-08 19:45 | 63.1833 | 72.1333 | 62 | 78.4
2015-10-08 20:00 | 63 | 71.65 | 62 | 77.8833
2015-10-08 20:15 | 63 | 70.9 | 62 | 77.6333
2015-10-08 20:30 | 63 | 70.15 | 62 | 77.3833
2015-10-08 20:45 | 63 | 69.4 | 62 | 77.1333
2015-10-08 21:00 | 63 | 68.8833 | 62 | 76.8833
2015-10-08 21:15 | 63 | 68.6333 | 62 | 76.6333
2015-10-08 21:30 | 63 | 68.3833 | 62 | 76.3833
2015-10-08 21:45 | 63 | 68.1333 | 61.6667 | 76.1333
2015-10-08 22:00 | 62.9333 | 67.8833 | 61.1167 | 75.7667
2015-10-08 22:15 | 62.6833 | 67.6333 | 61.3667 | 75.2667
2015-10-08 22:30 | 62.4333 | 67.3833 | 61.6167 | 74.7667
2015-10-08 22:45 | 62.1833 | 67.1333 | 61.8667 | 74.2667
2015-10-08 23:00 | 61.9333 | 66.8833 | 61.8793 | 73.8833
2015-10-08 23:15 | 61.6833 | 66.6333 | 61.6207 | 73.6333
2015-10-08 23:30 | 61.4333 | 66.3833 | 61.3621 | 73.3833
2015-10-08 23:45 | 61.1833 | 66.1333 | 61.1034 | 73.1333
2015-10-09 | 60.9333 | 65.8833 | 61.1167 | 72.65
2015-10-09 00:15 | 60.6833 | 65.6333 | 61.3667 | 71.9
2015-10-09 00:30 | 60.4333 | 65.3833 | 61.6167 | 71.15
2015-10-09 00:45 | 60.1833 | 65.1333 | 61.8667 | 70.4
2015-10-09 01:00 | 59.9333 | 64.7667 | 62 | 69.7667
2015-10-09 01:15 | 59.6833 | 64.2667 | 62 | 69.2667
2015-10-09 01:30 | 59.4333 | 63.7667 | 62 | 68.7667
2015-10-09 01:45 | 59.1833 | 63.2667 | 62 | 68.2667
2015-10-09 02:00 | 58.8667 | 62.8833 | 62 | 67.7667
2015-10-09 02:15 | 58.3667 | 62.6333 | 62 | 67.2667
2015-10-09 02:30 | 57.8667 | 62.3833 | 62 | 66.7667
2015-10-09 02:45 | 57.3667 | 62.1333 | 62 | 66.2667
2015-10-09 03:00 | 57.0667 | 61.7667 | 62 | 66
2015-10-09 03:15 | 57.3167 | 61.2667 | 62 | 66
2015-10-09 03:30 | 57.5667 | 60.7667 | 62 | 66
2015-10-09 03:45 | 57.8167 | 60.2667 | 62.7 | 66
2015-10-09 04:00 | 57.9333 | 59.8833 | 62.3684 | 66
2015-10-09 04:15 | 57.6833 | 59.6333 | 62.9268 | 66
2015-10-09 04:30 | 57.4333 | 59.3833 | 62.561 | 66
2015-10-09 04:45 | 57.1833 | 59.1333 | 62.1951 | 66
2015-10-09 05:00 | 57 | 59 | 62 | 65.8833
2015-10-09 05:15 | 57 | 59 | 62 | 65.6333
2015-10-09 05:30 | 57 | 59 | 62 | 65.3833
2015-10-09 05:45 | 57 | 59 | 62 | 65.1333
2015-10-09 06:00 | 57.2667 | 59 | 62 | 65.1167
2015-10-09 06:15 | 58.2667 | 59 | 62 | 65.3667
2015-10-09 06:30 | 59.2667 | 59 | 62.125 | 65.6167
2015-10-09 06:45 | 60.2667 | 59 | 62.75 | 65.8667
2015-10-09 07:00 | 61.0667 | 59.7 | 62.1167 | 66.4667
2015-10-09 07:15 | 61.3167 | 61.2 | 62.3667 | 67.4667
2015-10-09 07:30 | 61.5667 | 62.7 | 62.6167 | 68.4667
2015-10-09 07:45 | 61.8167 | 64.2 | 62.8667 | 69.4667
2015-10-09 08:00 | 62.2667 | 65.5833 | 63 | 70.4667
2015-10-09 08:15 | 63.2667 | 66.8333 | 63 | 71.4667
2015-10-09 08:30 | 64.2667 | 68.0833 | 63 | 72.4667
2015-10-09 08:45 | 65.2667 | 69.3333 | 63 | 73.4667
2015-10-09 09:00 | 66.0667 | 70.4667 | 63.7778 | 74.5833
2015-10-09 09:15 | 66.3167 | 71.4667 | 66 | 75.8333
2015-10-09 09:30 | 66.5667 | 72.4667 | 67 | 77.0833
2015-10-09 09:45 | 66.8167 | 73.4667 | 67 | 78.3333
2015-10-09 10:00 | 66.5 | 74.8167 | 67.4667 | 79.4667
2015-10-09 10:15 | 66 | 76.5667 | 68.4667 | 80.4667
2015-10-09 10:30 | 66 | 78.3167 | 69.4667 | 81.4667
2015-10-09 10:45 | 66 | 80.0667 | 70.4667 | 82.4667
2015-10-09 11:00 | 66.7333 | 80.8833 | 71 | 83.35
2015-10-09 11:15 | 69.4833 | 80.6333 | 71 | 84.1
2015-10-09 11:30 | 72.2333 | 80.3833 | 71 | 84.85
2015-10-09 11:45 | 74.9833 | 80.1333 | 71 | 85.6
2015-10-09 12:00 | 77 | 79.8833 | 71.1167 | 86.35
2015-10-09 12:15 | 77 | 79.6333 | 71.3667 | 87.1
2015-10-09 12:30 | 77 | 79.3833 | 71.6167 | 87.85
2015-10-09 12:45 | 77 | 79.1333 | 71.8667 | 88.6
2015-10-09 13:00 | 77 | 79 | 72.1167 | 89.1167
2015-10-09 13:15 | 77 | 79 | 72.3667 | 89.3667
2015-10-09 13:30 | 77 | 79 | 72.6167 | 89.6167
2015-10-09 13:45 | 77 | 79 | 72.8667 | 89.8667
2015-10-09 14:00 | 76.9333 | 79.1167 | 73.35 | 90.2333
2015-10-09 14:15 | 76.6833 | 79.3667 | 74.1 | 90.7333
2015-10-09 14:30 | 76.4333 | 79.6167 | 74.85 | 91.2333
2015-10-09 14:45 | 76.1833 | 79.8667 | 75.6 | 91.7333
2015-10-09 15:00 | 75.9333 | 80.1167 | 75.7667 | 91.8833
2015-10-09 15:15 | 75.6833 | 80.3667 | 75.2667 | 91.6333
2015-10-09 15:30 | 75.4333 | 80.6167 | 74.7667 | 91.3833
2015-10-09 15:45 | 75.1833 | 80.8667 | 74.2667 | 91.1333
2015-10-09 16:00 | 74.6 | 80.4167 | 74.1167 | 90.7667
2015-10-09 16:15 | 73.1 | 79.1667 | 74.3667 | 90.2667
2015-10-09 16:30 | 71.6 | 77.9167 | 74.6167 | 89.7667
2015-10-09 16:45 | 70.1 | 76.6667 | 74.8667 | 89.2667
2015-10-09 17:00 | 68.5122 | 75.65 | 74.7667 | 88.65
2015-10-09 17:15 | 66.6829 | 74.9 | 74.2667 | 87.9
2015-10-09 17:30 | 64.8537 | 74.15 | 73.7667 | 87.15
2015-10-09 17:45 | 64.4211 | 73.4 | 73.2667 | 86.4
2015-10-09 18:00 | 64.9333 | 72.5333 | 72.65 | 85.65
2015-10-09 18:15 | 64.6833 | 71.5333 | 71.9 | 84.9
2015-10-09 18:30 | 64.4333 | 70.5333 | 71.15 | 84.15
2015-10-09 18:45 | 64.1833 | 69.5333 | 70.4 | 83.4
2015-10-09 19:00 | 63.9333 | 68.65 | 69.7667 | 82.8833
2015-10-09 19:15 | 63.6833 | 67.9 | 69.2667 | 82.6333
2015-10-09 19:30 | 63.4333 | 67.15 | 68.7667 | 82.3833
2015-10-09 19:45 | 63.1833 | 66.4 | 68.2667 | 82.1333
2015-10-09 20:00 | 63 | 66 | 68 | 81.5333
2015-10-09 20:15 | 63 | 66 | 68 | 80.5333
2015-10-09 20:30 | 63 | 66 | 68 | 79.5333
2015-10-09 20:45 | 63 | 66 | 68 | 78.5333
2015-10-09 21:00 | 62.9333 | 65.8833 | 67.7667 | 77.7667
2015-10-09 21:15 | 62.6833 | 65.6333 | 67.2667 | 77.2667
2015-10-09 21:30 | 62.4333 | 65.3833 | 66.7667 | 76.7667
2015-10-09 21:45 | 62.1833 | 65.1333 | 66.2667 | 76.2667
2015-10-09 22:00 | 62.0816 | 65 | 65.7667 | 75.7667
2015-10-09 22:15 | 62.3878 | 65 | 65.2667 | 75.2667
2015-10-09 22:30 | 62.6939 | 65 | 64.7667 | 74.7667
2015-10-09 22:45 | 63 | 65 | 64.2667 | 74.2667
2015-10-09 23:00 | 61.9 | 64.7667 | 64 | 73.7667
2015-10-09 23:15 | 61.525 | 64.2667 | 64 | 73.2667
2015-10-09 23:30 | 61.15 | 63.7667 | 64 | 72.7667
2015-10-09 23:45 | 61 | 63.2667 | 64 | 72.2667
2015-10-10 | 61 | 62.8833 | 64 | 71.5333
2015-10-10 00:15 | 61 | 62.6333 | 64 | 70.5333
2015-10-10 00:30 | 61 | 62.3833 | 64 | 69.5333
2015-10-10 00:45 | 61 | 62.1333 | 64 | 68.5333
2015-10-10 01:00 | 61 | 61.8833 | 63.8833 | 67.8833
2015-10-10 01:15 | 61 | 61.6333 | 63.6333 | 67.6333
2015-10-10 01:30 | 61 | 61.3833 | 63.3833 | 67.3833
2015-10-10 01:45 | 61 | 61.1333 | 63.1333 | 67.1333
2015-10-10 02:00 | 61 | 60.8833 | 62.8833 | 66.8833
2015-10-10 02:15 | 61 | 60.6333 | 62.6333 | 66.6333
2015-10-10 02:30 | 61 | 60.3833 | 62.3833 | 66.3833
2015-10-10 02:45 | 61 | 60.1333 | 62.1333 | 66.1333
2015-10-10 03:00 | 61 | 59.8833 | 61.7667 | 66
2015-10-10 03:15 | 61 | 59.6333 | 61.2667 | 66
2015-10-10 03:30 | 61 | 59.3833 | 60.7667 | 66
2015-10-10 03:45 | 61 | 59.1333 | 60.2667 | 66
2015-10-10 04:00 | 60.1143 | 59 | 60 | 66
2015-10-10 04:15 | 60.5429 | 58.9048 | 60 | 66
2015-10-10 04:30 | 60.9714 | 58.5476 | 60 | 66
2015-10-10 04:45 | 61 | 58.1905 | 59 | 66
2015-10-10 05:00 | 61 | 57 | 59 | 66
2015-10-10 05:15 | 61 | 58 | 59 | 66
2015-10-10 05:30 | 61 | 57 | 59 | 66
2015-10-10 05:45 | 61 | 57 | 59 | 66
2015-10-10 06:00 | 60.1379 | 57 | 59 | 66.1167
2015-10-10 06:15 | 60.6552 | 57 | 58.4615 | 66.3667
2015-10-10 06:30 | 61 | 57 | 58 | 66.6167
2015-10-10 06:45 | 60.6875 | 57.619 | 58 | 66.8667
2015-10-10 07:00 | 60.2 | 58.3889 | 58.1167 | 67.7
2015-10-10 07:15 | 60.95 | 59.2857 | 58.3667 | 69.2
2015-10-10 07:30 | 61.7 | 60.3571 | 58.6167 | 70.7
2015-10-10 07:45 | 62.45 | 61 | 58.8667 | 72.2
2015-10-10 08:00 | 63 | 61 | 59.2333 | 73.5833
2015-10-10 08:15 | 63 | 61.16 | 59.7333 | 74.8333
2015-10-10 08:30 | 63 | 62.36 | 60.2333 | 76.0833
2015-10-10 08:45 | 63 | 62.5333 | 60.7333 | 77.3333
2015-10-10 09:00 | 63.375 | 62.2414 | 61.2 | 78.7
2015-10-10 09:15 | 64.7812 | 62.7586 | 61.6286 | 80.2
2015-10-10 09:30 | 66.2667 | 63 | 62 | 81.7
2015-10-10 09:45 | 68 | 63 | 62.3333 | 83.2
2015-10-10 10:00 | 67.9333 | 63.2333 | 62 | 84.35
2015-10-10 10:15 | 67.6833 | 63.7333 | 63.7308 | 85.1
2015-10-10 10:30 | 67.4333 | 64.2333 | 65.5714 | 85.85
2015-10-10 10:45 | 67.1833 | 64.7333 | 67.7692 | 86.6
2015-10-10 11:00 | 67.1429 | 65.4118 | 69 | 87.35
2015-10-10 11:15 | 67.6786 | 66.1163 | 69.4091 | 88.1
2015-10-10 11:30 | 68.375 | 66.4651 | 70.4318 | 88.85
2015-10-10 11:45 | 69.3125 | 66.814 | 71.4545 | 89.6
2015-10-10 12:00 | 69.9333 | 66.5333 | 72.2333 | 90.35
2015-10-10 12:15 | 69.6833 | 66.7778 | 72.7333 | 91.1
2015-10-10 12:30 | 69.4333 | 68.4444 | 73.2333 | 91.85
2015-10-10 12:45 | 69.1833 | 70.1111 | 73.7333 | 92.6
2015-10-10 13:00 | 69.0667 | 71.5833 | 74.35 | 93.35
2015-10-10 13:15 | 69.3167 | 72.8333 | 75.1 | 94.1
2015-10-10 13:30 | 69.5667 | 74.0833 | 75.85 | 94.85
2015-10-10 13:45 | 69.8167 | 75.3333 | 76.6 | 95.6
2015-10-10 14:00 | 70.0667 | 75.65 | 77.2333 | 96
2015-10-10 14:15 | 70.3167 | 74.9 | 77.7333 | 96
2015-10-10 14:30 | 70.5667 | 74.15 | 78.2333 | 96
2015-10-10 14:45 | 70.8167 | 73.4 | 78.7333 | 96
2015-10-10 15:00 | 70.8667 | 73.2333 | 79.1167 | 95.8833
2015-10-10 15:15 | 70.3667 | 73.7333 | 79.3667 | 95.6333
2015-10-10 15:30 | 69.8667 | 74.2333 | 79.6167 | 95.3833
2015-10-10 15:45 | 69.3667 | 74.7333 | 79.8667 | 95.1333
2015-10-10 16:00 | 68.8667 | 74.4167 | 80 | 94.7667
2015-10-10 16:15 | 68.3667 | 73.1667 | 80 | 94.2667
2015-10-10 16:30 | 67.8667 | 71.9167 | 80 | 93.7667
2015-10-10 16:45 | 67.3667 | 70.6667 | 80 | 93.2667
2015-10-10 17:00 | 66.8667 | 69.7667 | 79.65 | 92.4167
2015-10-10 17:15 | 66.3667 | 69.2667 | 78.9 | 91.1667
2015-10-10 17:30 | 65.8667 | 68.7667 | 78.15 | 89.9167
2015-10-10 17:45 | 65.3667 | 68.2667 | 77.4 | 88.6667
2015-10-10 18:00 | 65 | 67.7667 | 76.5333 | 87.65
2015-10-10 18:15 | 65 | 67.2667 | 75.5333 | 86.9
2015-10-10 18:30 | 65 | 66.7667 | 74.5333 | 86.15
2015-10-10 18:45 | 65 | 66.2667 | 73.5333 | 85.4
2015-10-10 19:00 | 64.9333 | 65.8833 | 73 | 84.65
2015-10-10 19:15 | 64.6833 | 65.6333 | 73 | 83.9
2015-10-10 19:30 | 64.4333 | 65.3833 | 73 | 83.15
2015-10-10 19:45 | 64.1833 | 65.1333 | 73 | 82.4
2015-10-10 20:00 | 64 | 65 | 72.5333 | 81.65
2015-10-10 20:15 | 64 | 65 | 71.5333 | 80.9
2015-10-10 20:30 | 64 | 65 | 70.5333 | 80.15
2015-10-10 20:45 | 64 | 65 | 69.5333 | 79.4
2015-10-10 21:00 | 64 | 64.8833 | 68.7667 | 78.7667
2015-10-10 21:15 | 64 | 64.6333 | 68.2667 | 78.2667
2015-10-10 21:30 | 64 | 64.3833 | 67.7667 | 77.7667
2015-10-10 21:45 | 64 | 64.1333 | 67.2667 | 77.2667
2015-10-10 22:00 | 63.9333 | 63.8833 | 67 | 76.65
2015-10-10 22:15 | 63.6833 | 63.6333 | 67 | 75.9
2015-10-10 22:30 | 63.4333 | 63.3833 | 67 | 75.15
2015-10-10 22:45 | 63.1833 | 63.1333 | 67 | 74.4
2015-10-10 23:00 | 63 | 62.7667 | 66.8833 | 73.7667
2015-10-10 23:15 | 63 | 62.2667 | 66.6333 | 73.2667
2015-10-10 23:30 | 63 | 61.7667 | 66.3833 | 72.7667
2015-10-10 23:45 | 63 | 61.2667 | 66.1333 | 72.2667
2015-10-11 | 62.9333 | 60.8833 | 66 | 71.7667
2015-10-11 00:15 | 62.6833 | 60.6333 | 66 | 71.2667
2015-10-11 00:30 | 62.4333 | 60.3833 | 66 | 70.7667
2015-10-11 00:45 | 62.1833 | 60.1333 | 66 | 70.2667
2015-10-11 01:00 | 61.9333 | 59.65 | 66 | 69.8833
2015-10-11 01:15 | 61.6833 | 58.9 | 66 | 69.6333
2015-10-11 01:30 | 61.4333 | 58.15 | 66 | 69.3833
2015-10-11 01:45 | 61.1833 | 57.4 | 66 | 69.1333
2015-10-11 02:00 | 61 | 57.1167 | 65.8833 | 68.8833
2015-10-11 02:15 | 61 | 57.3667 | 65.6333 | 68.6333
2015-10-11 02:30 | 61 | 57.6167 | 65.3833 | 68.3833
2015-10-11 02:45 | 61 | 57.8667 | 65.1333 | 68.1333
2015-10-11 03:00 | 60.9333 | 57.8833 | 64.7667 | 67.8833
2015-10-11 03:15 | 60.6833 | 57.6333 | 64.2667 | 67.6333
2015-10-11 03:30 | 60.4333 | 57.3833 | 63.7667 | 67.3833
2015-10-11 03:45 | 60.1833 | 57.1333 | 63.2667 | 67.1333
2015-10-11 04:00 | 59.9333 | 57 | 63.1167 | 66.7667
2015-10-11 04:15 | 59.6833 | 57 | 63.3667 | 66.2667
2015-10-11 04:30 | 59.4333 | 57 | 63.6167 | 65.7667
2015-10-11 04:45 | 59.1833 | 57 | 63.8667 | 65.2667
2015-10-11 05:00 | 59.0667 | 56.8833 | 64 | 65
2015-10-11 05:15 | 59.3167 | 56.6333 | 64 | 65
2015-10-11 05:30 | 59.5667 | 56.3833 | 64 | 65
2015-10-11 05:45 | 59.8167 | 56.1333 | 64 | 65
2015-10-11 06:00 | 60.0667 | 56.2333 | 64.1167 | 65
2015-10-11 06:15 | 60.3167 | 56.7333 | 64.3667 | 65
2015-10-11 06:30 | 60.5667 | 57.2333 | 64.6167 | 65
2015-10-11 06:45 | 60.8167 | 57.7333 | 64.8667 | 65
2015-10-11 07:00 | 61.1333 | 58.35 | 65.2333 | 65.5833
2015-10-11 07:15 | 61.6333 | 59.1 | 65.7333 | 66.8333
2015-10-11 07:30 | 62.1333 | 59.85 | 66.2333 | 68.0833
2015-10-11 07:45 | 62.6333 | 60.6 | 66.7333 | 69.3333
2015-10-11 08:00 | 63.2 | 61.7 | 67.7 | 70.4667
2015-10-11 08:15 | 63.95 | 63.2 | 69.2 | 71.4667
2015-10-11 08:30 | 64.7 | 64.7 | 70.7 | 72.4667
2015-10-11 08:45 | 65.45 | 66.2 | 72.2 | 73.4667
2015-10-11 09:00 | 66.0667 | 67.4667 | 73.7 | 74.4667
2015-10-11 09:15 | 66.3167 | 68.4667 | 75.2 | 75.4667
2015-10-11 09:30 | 66.5667 | 69.4667 | 76.7 | 76.4667
2015-10-11 09:45 | 66.8167 | 70.4667 | 78.2 | 77.4667
2015-10-11 10:00 | 67.0667 | 71.35 | 79.35 | 78.35
2015-10-11 10:15 | 67.3167 | 72.1 | 80.1 | 79.1
2015-10-11 10:30 | 67.5667 | 72.85 | 80.85 | 79.85
2015-10-11 10:45 | 67.8167 | 73.6 | 81.6 | 80.6
2015-10-11 11:00 | 68.3333 | 74.35 | 82.35 | 81.4667
2015-10-11 11:15 | 69.5833 | 75.1 | 83.1 | 82.4667
2015-10-11 11:30 | 70.8333 | 75.85 | 83.85 | 83.4667
2015-10-11 11:45 | 72.0833 | 76.6 | 84.6 | 84.4667
2015-10-11 12:00 | 72.9474 | 77.2333 | 85.2333 | 85.2333
2015-10-11 12:15 | 72.1579 | 77.7333 | 85.7333 | 85.7333
2015-10-11 12:30 | 71.3684 | 78.2333 | 86.2333 | 86.2333
2015-10-11 12:45 | 70.5789 | 78.7333 | 86.7333 | 86.7333
2015-10-11 13:00 | 69.9333 | 79.2333 | 87.1167 | 87.2333
2015-10-11 13:15 | 69.6833 | 79.7333 | 87.3667 | 87.7333
2015-10-11 13:30 | 69.4333 | 80.2333 | 87.6167 | 88.2333
2015-10-11 13:45 | 69.1833 | 80.7333 | 87.8667 | 88.7333
2015-10-11 14:00 | 68.8 | 81.1167 | 88 | 89.1167
2015-10-11 14:15 | 68.05 | 81.3667 | 88 | 89.3667
2015-10-11 14:30 | 67.3 | 81.6167 | 88 | 89.6167
2015-10-11 14:45 | 66.55 | 81.8667 | 88 | 89.8667
2015-10-11 15:00 | 65.8 | 81.5333 | 88.1167 | 90
2015-10-11 15:15 | 65.05 | 80.5333 | 88.3667 | 90
2015-10-11 15:30 | 64.3 | 79.5333 | 88.6167 | 90
2015-10-11 15:45 | 63.55 | 78.5333 | 88.8667 | 90
2015-10-11 16:00 | 62.8667 | 77.4167 | 89 | 89.7667
2015-10-11 16:15 | 62.3667 | 76.1667 | 89 | 89.2667
2015-10-11 16:30 | 61.8667 | 74.9167 | 89 | 88.7667
2015-10-11 16:45 | 61.3667 | 73.6667 | 89 | 88.2667
2015-10-11 17:00 | 61 | 72.4167 | 88.5333 | 87.5333
2015-10-11 17:15 | 61 | 71.1667 | 87.5333 | 86.5333
2015-10-11 17:30 | 61 | 69.9167 | 86.5333 | 85.5333
2015-10-11 17:45 | 61 | 68.6667 | 85.5333 | 84.5333
2015-10-11 18:00 | 61 | 67.65 | 84.0667 | 83.65
2015-10-11 18:15 | 61 | 66.9 | 82.0667 | 82.9
2015-10-11 18:30 | 61 | 66.15 | 80.0667 | 82.15
2015-10-11 18:45 | 61 | 65.4 | 78.0667 | 81.4
2015-10-11 19:00 | 61 | 64.7667 | 76.65 | 80.65
2015-10-11 19:15 | 61 | 64.2667 | 75.9 | 79.9
2015-10-11 19:30 | 61 | 63.7667 | 75.15 | 79.15
2015-10-11 19:45 | 61 | 63.2667 | 74.4 | 78.4
2015-10-11 20:00 | 60.9333 | 63 | 73.7667 | 77.8833
2015-10-11 20:15 | 60.6833 | 63 | 73.2667 | 77.6333
2015-10-11 20:30 | 60.4333 | 63 | 72.7667 | 77.3833
2015-10-11 20:45 | 60.1833 | 63 | 72.2667 | 77.1333
2015-10-11 21:00 | 60 | 62.8833 | 72 | 76.7667
2015-10-11 21:15 | 60 | 62.6333 | 72 | 76.2667
2015-10-11 21:30 | 60 | 62.3833 | 72 | 75.7667
2015-10-11 21:45 | 60 | 62.1333 | 72 | 75.2667
2015-10-11 22:00 | 60 | 62 | 71.8833 | 74.7667
2015-10-11 22:15 | 60 | 62 | 71.6333 | 74.2667
2015-10-11 22:30 | 60 | 62 | 71.3833 | 73.7667
2015-10-11 22:45 | 60 | 62 | 71.1333 | 73.2667
2015-10-11 23:00 | 59.9333 | 61.7667 | 71 | 73
2015-10-11 23:15 | 59.6833 | 61.2667 | 71 | 73
2015-10-11 23:30 | 59.4333 | 60.7667 | 71 | 73
2015-10-11 23:45 | 59.1833 | 60.2667 | 71 | 73
2015-10-12 | 58.9333 | 60 | 71 | 72.7667
2015-10-12 00:15 | 58.6833 | 60 | 71 | 72.2667
2015-10-12 00:30 | 58.4333 | 60 | 71 | 71.7667
2015-10-12 00:45 | 58.1833 | 60 | 71 | 71.2667
2015-10-12 01:00 | 57.9333 | 59.8833 | 71 | 70.7667
2015-10-12 01:15 | 57.6833 | 59.6333 | 71 | 70.2667
2015-10-12 01:30 | 57.4333 | 59.3833 | 71 | 69.7667
2015-10-12 01:45 | 57.1833 | 59.1333 | 71 | 69.2667
2015-10-12 02:00 | 57 | 58.8833 | 71 | 68.7667
2015-10-12 02:15 | 57 | 58.6333 | 71 | 68.2667
2015-10-12 02:30 | 57 | 58.3833 | 71 | 67.7667
2015-10-12 02:45 | 57 | 58.1333 | 71 | 67.2667
2015-10-12 03:00 | 57 | 57.8833 | 71 | 67
2015-10-12 03:15 | 57 | 57.6333 | 71 | 67
2015-10-12 03:30 | 57 | 57.3833 | 71 | 67
2015-10-12 03:45 | 57 | 57.1333 | 71 | 67
2015-10-12 04:00 | 57 | 57 | 70.7667 | 66.8833
2015-10-12 04:15 | 57 | 57 | 70.2667 | 66.6333
2015-10-12 04:30 | 57 | 57 | 69.7667 | 66.3833
2015-10-12 04:45 | 57 | 57 | 69.2667 | 66.1333
2015-10-12 05:00 | 57 | 57 | 69 | 65.7667
2015-10-12 05:15 | 57 | 57 | 69 | 65.2667
2015-10-12 05:30 | 57 | 57 | 69 | 64.7667
2015-10-12 05:45 | 57 | 57 | 69 | 64.2667
2015-10-12 06:00 | 57.1333 | 57.1167 | 69 | 64.2333
2015-10-12 06:15 | 57.6333 | 57.3667 | 69 | 64.7333
2015-10-12 06:30 | 58.1333 | 57.6167 | 69 | 65.2333
2015-10-12 06:45 | 58.6333 | 57.8667 | 69 | 65.7333
2015-10-12 07:00 | 59.2667 | 58.4667 | 69.2333 | 66.4667
2015-10-12 07:15 | 60.2667 | 59.4667 | 69.7333 | 67.4667
2015-10-12 07:30 | 61.2667 | 60.4667 | 70.2333 | 68.4667
2015-10-12 07:45 | 62.2667 | 61.4667 | 70.7333 | 69.4667
2015-10-12 08:00 | 63.2 | 62.7 | 71.7 | 70.5833
2015-10-12 08:15 | 63.95 | 64.2 | 73.2 | 71.8333
2015-10-12 08:30 | 64.7 | 65.7 | 74.7 | 73.0833
2015-10-12 08:45 | 65.45 | 67.2 | 76.2 | 74.3333
2015-10-12 09:00 | 66.0667 | 68.5833 | 77.8167 | 75.5833
2015-10-12 09:15 | 66.3167 | 69.8333 | 79.5667 | 76.8333
2015-10-12 09:30 | 66.5667 | 71.0833 | 81.3167 | 78.0833
2015-10-12 09:45 | 66.8167 | 72.3333 | 83.0667 | 79.3333
2015-10-12 10:00 | 67.1333 | 73.7 | 84.35 | 80.5833
2015-10-12 10:15 | 67.6333 | 75.2 | 85.1 | 81.8333
2015-10-12 10:30 | 68.1333 | 76.7 | 85.85 | 83.0833
2015-10-12 10:45 | 68.6333 | 78.2 | 86.6 | 84.3333
2015-10-12 11:00 | 69.1333 | 79.35 | 86.8833 | 85.4667
2015-10-12 11:15 | 69.6333 | 80.1 | 86.6333 | 86.4667
2015-10-12 11:30 | 70.1333 | 80.85 | 86.3833 | 87.4667
2015-10-12 11:45 | 70.6333 | 81.6 | 86.1333 | 88.4667
2015-10-12 12:00 | 71.1333 | 82.35 | 85.8833 | 89.1167
2015-10-12 12:15 | 71.6333 | 83.1 | 85.6333 | 89.3667
2015-10-12 12:30 | 72.1333 | 83.85 | 85.3833 | 89.6167
2015-10-12 12:45 | 72.6333 | 84.6 | 85.1333 | 89.8667
2015-10-12 13:00 | 73.0667 | 85.2333 | 85 | 90.2333
2015-10-12 13:15 | 73.3167 | 85.7333 | 85 | 90.7333
2015-10-12 13:30 | 73.5667 | 86.2333 | 85 | 91.2333
2015-10-12 13:45 | 73.8167 | 86.7333 | 85 | 91.7333
2015-10-12 14:00 | 74.4667 | 87 | 84.8833 | 92
2015-10-12 14:15 | 76.2167 | 87 | 84.6333 | 92
2015-10-12 14:30 | 77.9667 | 87 | 84.3833 | 92
2015-10-12 14:45 | 79.7167 | 87 | 84.1333 | 92
2015-10-12 15:00 | 80.8667 | 87 | 83.8833 | 92.1167
2015-10-12 15:15 | 80.3667 | 87 | 83.6333 | 92.3667
2015-10-12 15:30 | 79.8667 | 87 | 83.3833 | 92.6167
2015-10-12 15:45 | 79.3667 | 87 | 83.1333 | 92.8667
2015-10-12 16:00 | 78.7333 | 86.7667 | 82.7667 | 92.8833
2015-10-12 16:15 | 77.7333 | 86.2667 | 82.2667 | 92.6333
2015-10-12 16:30 | 76.7333 | 85.7667 | 81.7667 | 92.3833
2015-10-12 16:45 | 75.7333 | 85.2667 | 81.2667 | 92.1333
2015-10-12 17:00 | 74.8 | 84.3 | 80.8833 | 91.4167
2015-10-12 17:15 | 74.05 | 82.8 | 80.6333 | 90.1667
2015-10-12 17:30 | 73.3 | 81.3 | 80.3833 | 88.9167
2015-10-12 17:45 | 72.55 | 79.8 | 80.1333 | 87.6667
2015-10-12 18:00 | 72.0667 | 78.4167 | 79.4167 | 86.65
2015-10-12 18:15 | 72.3167 | 77.1667 | 78.1667 | 85.9
2015-10-12 18:30 | 72.5667 | 75.9167 | 76.9167 | 85.15
2015-10-12 18:45 | 72.8167 | 74.6667 | 75.6667 | 84.4
2015-10-12 19:00 | 73 | 73.7667 | 74.7667 | 83.65
2015-10-12 19:15 | 73 | 73.2667 | 74.2667 | 82.9
2015-10-12 19:30 | 73 | 72.7667 | 73.7667 | 82.15
2015-10-12 19:45 | 73 | 72.2667 | 73.2667 | 81.4
2015-10-12 20:00 | 72.8667 | 72.1167 | 73.1167 | 80.8833
2015-10-12 20:15 | 72.3667 | 72.3667 | 73.3667 | 80.6333
2015-10-12 20:30 | 71.8667 | 72.6167 | 73.6167 | 80.3833
2015-10-12 20:45 | 71.3667 | 72.8667 | 73.8667 | 80.1333
2015-10-12 21:00 | 70.9333 | 72.7667 | 73.5333 | 79.7667
2015-10-12 21:15 | 70.6833 | 72.2667 | 72.5333 | 79.2667
2015-10-12 21:30 | 70.4333 | 71.7667 | 71.5333 | 78.7667
2015-10-12 21:45 | 70.1833 | 71.2667 | 70.5333 | 78.2667
2015-10-12 22:00 | 69.8667 | 70.7667 | 69.65 | 77.7667
2015-10-12 22:15 | 69.3667 | 70.2667 | 68.9 | 77.2667
2015-10-12 22:30 | 68.8667 | 69.7667 | 68.15 | 76.7667
2015-10-12 22:45 | 68.3667 | 69.2667 | 67.4 | 76.2667
2015-10-12 23:00 | 67.8 | 68.8833 | 67 | 75.65
2015-10-12 23:15 | 67.05 | 68.6333 | 67 | 74.9
2015-10-12 23:30 | 66.3 | 68.3833 | 67 | 74.15
2015-10-12 23:45 | 65.55 | 68.1333 | 67 | 73.4
2015-10-13 | 64.9333 | 67.8833 | 66.65 | 72.7667
2015-10-13 00:15 | 64.6833 | 67.6333 | 65.9 | 72.2667
2015-10-13 00:30 | 64.4333 | 67.3833 | 65.15 | 71.7667
2015-10-13 00:45 | 64.1833 | 67.1333 | 64.4 | 71.2667
2015-10-13 01:00 | 63.9333 | 66.8833 | 63.65 | 71
2015-10-13 01:15 | 63.6833 | 66.6333 | 62.9 | 71
2015-10-13 01:30 | 63.4333 | 66.3833 | 62.15 | 71
2015-10-13 01:45 | 63.1833 | 66.1333 | 61.4 | 71
2015-10-13 02:00 | 63 | 65.8833 | 61 | 70.7667
2015-10-13 02:15 | 63 | 65.6333 | 61 | 70.2667
2015-10-13 02:30 | 63 | 65.3833 | 61 | 69.7667
2015-10-13 02:45 | 63 | 65.1333 | 61 | 69.2667
2015-10-13 03:00 | 62.9333 | 64.8833 | 61.1167 | 69
2015-10-13 03:15 | 62.6833 | 64.6333 | 61.3667 | 69
2015-10-13 03:30 | 62.4333 | 64.3833 | 61.6167 | 69
2015-10-13 03:45 | 62.1833 | 64.1333 | 61.8667 | 69
2015-10-13 04:00 | 62.0667 | 63.8833 | 61.8833 | 68.65
2015-10-13 04:15 | 62.3167 | 63.6333 | 61.6333 | 67.9
2015-10-13 04:30 | 62.5667 | 63.3833 | 61.3833 | 67.15
2015-10-13 04:45 | 62.8167 | 63.1333 | 61.1333 | 66.4
2015-10-13 05:00 | 63.0667 | 63.1167 | 60.65 | 66
2015-10-13 05:15 | 63.3167 | 63.3667 | 59.9 | 66
2015-10-13 05:30 | 63.5667 | 63.6167 | 59.15 | 66
2015-10-13 05:45 | 63.8167 | 63.8667 | 58.4 | 66
2015-10-13 06:00 | 64 | 63.8833 | 58 | 66.1167
2015-10-13 06:15 | 64 | 63.6333 | 58 | 66.3667
2015-10-13 06:30 | 64 | 63.3833 | 58 | 66.6167
2015-10-13 06:45 | 64 | 63.1333 | 58 | 66.8667
2015-10-13 07:00 | 64.3333 | 63.5833 | 58.5833 | 67.5833
2015-10-13 07:15 | 65.5833 | 64.8333 | 59.8333 | 68.8333
2015-10-13 07:30 | 66.8333 | 66.0833 | 61.0833 | 70.0833
2015-10-13 07:45 | 68.0833 | 67.3333 | 62.3333 | 71.3333
2015-10-13 08:00 | 69.0667 | 68.5833 | 63.7 | 72.7
2015-10-13 08:15 | 69.3167 | 69.8333 | 65.2 | 74.2
2015-10-13 08:30 | 69.5667 | 71.0833 | 66.7 | 75.7
2015-10-13 08:45 | 69.8167 | 72.3333 | 68.2 | 77.2
2015-10-13 09:00 | 70.1333 | 73.8167 | 69.5833 | 78.4667
2015-10-13 09:15 | 70.6333 | 75.5667 | 70.8333 | 79.4667
2015-10-13 09:30 | 71.1333 | 77.3167 | 72.0833 | 80.4667
2015-10-13 09:45 | 71.6333 | 79.0667 | 73.3333 | 81.4667
2015-10-13 10:00 | 72.0667 | 80.4667 | 74.2333 | 82.5833
2015-10-13 10:15 | 72.3167 | 81.4667 | 74.7333 | 83.8333
2015-10-13 10:30 | 72.5667 | 82.4667 | 75.2333 | 85.0833
2015-10-13 10:45 | 72.8167 | 83.4667 | 75.7333 | 86.3333
2015-10-13 11:00 | 73.1333 | 84.7 | 76.35 | 87.35
2015-10-13 11:15 | 73.6333 | 86.2 | 77.1 | 88.1
2015-10-13 11:30 | 74.1333 | 87.7 | 77.85 | 88.85
2015-10-13 11:45 | 74.6333 | 89.2 | 78.6 | 89.6
2015-10-13 12:00 | 75 | 90.1167 | 79.2333 | 89.8833
2015-10-13 12:15 | 75 | 90.3667 | 79.7333 | 89.6333
2015-10-13 12:30 | 75 | 90.6167 | 80.2333 | 89.3833
2015-10-13 12:45 | 75 | 90.8667 | 80.7333 | 89.1333
2015-10-13 13:00 | 75.8 | 91.1167 | 81.2333 | 89.35
2015-10-13 13:15 | 78.8 | 91.3667 | 81.7333 | 90.1
2015-10-13 13:30 | 81.8 | 91.6167 | 82.2333 | 90.85
2015-10-13 13:45 | 84.8 | 91.8667 | 82.7333 | 91.6
2015-10-13 14:00 | 86.8667 | 92 | 83.2333 | 92.2333
2015-10-13 14:15 | 86.3667 | 92 | 83.7333 | 92.7333
2015-10-13 14:30 | 85.8667 | 92 | 84.2333 | 93.2333
2015-10-13 14:45 | 85.3667 | 92 | 84.7333 | 93.7333
2015-10-13 15:00 | 84.6667 | 91.4167 | 85 | 93.7667
2015-10-13 15:15 | 83.4167 | 90.1667 | 85 | 93.2667
2015-10-13 15:30 | 82.1667 | 88.9167 | 85 | 92.7667
2015-10-13 15:45 | 80.9167 | 87.6667 | 85 | 92.2667
2015-10-13 16:00 | 79.6 | 86.8833 | 85 | 91.5333
2015-10-13 16:15 | 78.1 | 86.6333 | 85 | 90.5333
2015-10-13 16:30 | 76.6 | 86.3833 | 85 | 89.5333
2015-10-13 16:45 | 75.1 | 86.1333 | 85 | 88.5333
2015-10-13 17:00 | 73.8 | 85.4167 | 84.5333 | 87.7667
2015-10-13 17:15 | 73.05 | 84.1667 | 83.5333 | 87.2667
2015-10-13 17:30 | 72.3 | 82.9167 | 82.5333 | 86.7667
2015-10-13 17:45 | 71.55 | 81.6667 | 81.5333 | 86.2667
2015-10-13 18:00 | 70.9333 | 80.65 | 80.0667 | 85.8833
2015-10-13 18:15 | 70.6833 | 79.9 | 78.0667 | 85.6333
2015-10-13 18:30 | 70.4333 | 79.15 | 76.0667 | 85.3833
2015-10-13 18:45 | 70.1833 | 78.4 | 74.0667 | 85.1333
2015-10-13 19:00 | 69.8667 | 77.65 | 73 | 84.65
2015-10-13 19:15 | 69.3667 | 76.9 | 73 | 83.9
2015-10-13 19:30 | 68.8667 | 76.15 | 73 | 83.15
2015-10-13 19:45 | 68.3667 | 75.4 | 73 | 82.4
2015-10-13 20:00 | 68 | 74.7667 | 72.5333 | 81.8833
2015-10-13 20:15 | 68 | 74.2667 | 71.5333 | 81.6333
2015-10-13 20:30 | 68 | 73.7667 | 70.5333 | 81.3833
2015-10-13 20:45 | 68 | 73.2667 | 69.5333 | 81.1333
2015-10-13 21:00 | 68 | 72.8833 | 68.8833 | 80.7667
2015-10-13 21:15 | 68 | 72.6333 | 68.6333 | 80.2667
2015-10-13 21:30 | 68 | 72.3833 | 68.3833 | 79.7667
2015-10-13 21:45 | 68 | 72.1333 | 68.1333 | 79.2667
2015-10-13 22:00 | 67.8667 | 71.8833 | 68.1167 | 78.7667
2015-10-13 22:15 | 67.3667 | 71.6333 | 68.3667 | 78.2667
2015-10-13 22:30 | 66.8667 | 71.3833 | 68.6167 | 77.7667
2015-10-13 22:45 | 66.3667 | 71.1333 | 68.8667 | 77.2667
2015-10-13 23:00 | 65.9333 | 70.65 | 69 | 76.8833
2015-10-13 23:15 | 65.6833 | 69.9 | 69 | 76.6333
2015-10-13 23:30 | 65.4333 | 69.15 | 69 | 76.3833
2015-10-13 23:45 | 65.1833 | 68.4 | 69 | 76.1333
2015-10-14 | 65 | 68 | 68.65 | 75.7667
2015-10-14 00:15 | 65 | 68 | 67.9 | 75.2667
2015-10-14 00:30 | 65 | 68 | 67.15 | 74.7667
2015-10-14 00:45 | 65 | 68 | 66.4 | 74.2667
2015-10-14 01:00 | 65 | 67.8833 | 65.8833 | 73.5333
2015-10-14 01:15 | 65 | 67.6333 | 65.6333 | 72.5333
2015-10-14 01:30 | 65 | 67.3833 | 65.3833 | 71.5333
2015-10-14 01:45 | 65 | 67.1333 | 65.1333 | 70.5333
2015-10-14 02:00 | 64.8667 | 66.8833 | 65 | 69.8833
2015-10-14 02:15 | 64.3667 | 66.6333 | 65 | 69.6333
2015-10-14 02:30 | 63.8667 | 66.3833 | 65 | 69.3833
2015-10-14 02:45 | 63.3667 | 66.1333 | 65 | 69.1333
2015-10-14 03:00 | 63.0667 | 66 | 64.8833 | 68.8833
2015-10-14 03:15 | 63.3167 | 66 | 64.6333 | 68.6333
2015-10-14 03:30 | 63.5667 | 66 | 64.3833 | 68.3833
2015-10-14 03:45 | 63.8167 | 66 | 64.1333 | 68.1333
2015-10-14 04:00 | 63.9333 | 65.8833 | 63.7667 | 68.1167
2015-10-14 04:15 | 63.6833 | 65.6333 | 63.2667 | 68.3667
2015-10-14 04:30 | 63.4333 | 65.3833 | 62.7667 | 68.6167
2015-10-14 04:45 | 63.1833 | 65.1333 | 62.2667 | 68.8667
2015-10-14 05:00 | 63 | 64.8833 | 62 | 68.8833
2015-10-14 05:15 | 63 | 64.6333 | 62 | 68.6333
2015-10-14 05:30 | 63 | 64.3833 | 62 | 68.3833
2015-10-14 05:45 | 63 | 64.1333 | 62 | 68.1333
2015-10-14 06:00 | 63.0667 | 64 | 61.8833 | 68.1167
2015-10-14 06:15 | 63.3167 | 64 | 61.6333 | 68.3667
2015-10-14 06:30 | 63.5667 | 64 | 61.3833 | 68.6167
2015-10-14 06:45 | 63.8167 | 64 | 61.1333 | 68.8667
2015-10-14 07:00 | 64.1333 | 64.2333 | 61.7 | 69.35
2015-10-14 07:15 | 64.6333 | 64.7333 | 63.2 | 70.1
2015-10-14 07:30 | 65.1333 | 65.2333 | 64.7 | 70.85
2015-10-14 07:45 | 65.6333 | 65.7333 | 66.2 | 71.6
2015-10-14 08:00 | 66.2667 | 66.5833 | 67.4667 | 72.5833
2015-10-14 08:15 | 67.2667 | 67.8333 | 68.4667 | 73.8333
2015-10-14 08:30 | 68.2667 | 69.0833 | 69.4667 | 75.0833
2015-10-14 08:45 | 69.2667 | 70.3333 | 70.4667 | 76.3333
2015-10-14 09:00 | 70.0667 | 71.4667 | 71.8235 | 77.4667
2015-10-14 09:15 | 70.3167 | 72.4667 | 73.5882 | 78.4667
2015-10-14 09:30 | 70.5667 | 73.4667 | 75.3462 | 79.4667
2015-10-14 09:45 | 70.8167 | 74.4667 | 77.0769 | 80.4667
2015-10-14 10:00 | 71.1333 | 75.4667 | 78.5833 | 81.2333
2015-10-14 10:15 | 71.6333 | 76.4667 | 79.8333 | 81.7333
2015-10-14 10:30 | 72.1333 | 77.4667 | 81.0833 | 82.2333
2015-10-14 10:45 | 72.6333 | 78.4667 | 82.3333 | 82.7333
2015-10-14 11:00 | 73 | 79 | 83.35 | 83.2333
2015-10-14 11:15 | 73 | 79 | 84.1 | 83.7333
2015-10-14 11:30 | 73 | 79 | 84.85 | 84.2333
2015-10-14 11:45 | 73 | 79 | 85.6 | 84.7333
2015-10-14 12:00 | 73.1333 | 79.2333 | 86.2333 | 85.1167
2015-10-14 12:15 | 73.6333 | 79.7333 | 86.7333 | 85.3667
2015-10-14 12:30 | 74.1333 | 80.2333 | 87.2333 | 85.6167
2015-10-14 12:45 | 74.6333 | 80.7333 | 87.7333 | 85.8667
2015-10-14 13:00 | 74.814 | 81.2333 | 88.2333 | 86.1167
2015-10-14 13:15 | 74.1163 | 81.7333 | 88.7333 | 86.3667
2015-10-14 13:30 | 73.4186 | 82.2333 | 89.2333 | 86.6167
2015-10-14 13:45 | 73.7059 | 82.7333 | 89.7333 | 86.8667
2015-10-14 14:00 | 75.1333 | 82.8833 | 90.1167 | 87.2333
2015-10-14 14:15 | 75.6333 | 82.6333 | 90.3667 | 87.7333
2015-10-14 14:30 | 76.1333 | 82.3833 | 90.6167 | 88.2333
2015-10-14 14:45 | 76.6333 | 82.1333 | 90.8667 | 88.7333
2015-10-14 15:00 | 77 | 81.7667 | 91 | 88.8833
2015-10-14 15:15 | 77 | 81.2667 | 91 | 88.6333
2015-10-14 15:30 | 77 | 80.7667 | 91 | 88.3833
2015-10-14 15:45 | 77 | 80.2667 | 91 | 88.1333
2015-10-14 16:00 | 76.9333 | 79.8833 | 91 | 87.8833
2015-10-14 16:15 | 76.6833 | 79.6333 | 91 | 87.6333
2015-10-14 16:30 | 76.4333 | 79.3833 | 91 | 87.3833
2015-10-14 16:45 | 76.1833 | 79.1333 | 91 | 87.1333
2015-10-14 17:00 | 76.3636 | 78.65 | 90.5333 | 86.65
2015-10-14 17:15 | 77.7273 | 77.9 | 89.5333 | 85.9
2015-10-14 17:30 | 78.7037 | 77.15 | 88.5333 | 85.15
2015-10-14 17:45 | 74.2593 | 76.4 | 87.5333 | 84.4
2015-10-14 18:00 | 70.4667 | 75.8833 | 86.1833 | 83.65
2015-10-14 18:15 | 68.4667 | 75.6333 | 84.4333 | 82.9
2015-10-14 18:30 | 66.4667 | 75.3833 | 82.6833 | 82.15
2015-10-14 18:45 | 64.4667 | 75.1333 | 80.9333 | 81.4
2015-10-14 19:00 | 62.9333 | 74.8833 | 79.65 | 80.7667
2015-10-14 19:15 | 62.6833 | 74.6333 | 78.9 | 80.2667
2015-10-14 19:30 | 62.4333 | 74.3833 | 78.15 | 79.7667
2015-10-14 19:45 | 62.1833 | 74.1333 | 77.4 | 79.2667
2015-10-14 20:00 | 61.9333 | 73.65 | 76.7667 | 78.65
2015-10-14 20:15 | 61.6833 | 72.9 | 76.2667 | 77.9
2015-10-14 20:30 | 61.4333 | 72.15 | 75.7667 | 77.15
2015-10-14 20:45 | 61.1833 | 71.4 | 75.2667 | 76.4
2015-10-14 21:00 | 61.0667 | 70.5333 | 75 | 75.8833
2015-10-14 21:15 | 61.3167 | 69.5333 | 75 | 75.6333
2015-10-14 21:30 | 61.5667 | 68.5333 | 75 | 75.3833
2015-10-14 21:45 | 61.8167 | 67.5333 | 75 | 75.1333
2015-10-14 22:00 | 62 | 67 | 74.7667 | 75
2015-10-14 22:15 | 62 | 67 | 74.2667 | 75
2015-10-14 22:30 | 62 | 67 | 73.7667 | 75
2015-10-14 22:45 | 62 | 67 | 73.2667 | 75
2015-10-14 23:00 | 62 | 66.8833 | 72.8833 | 74.8833
2015-10-14 23:15 | 62 | 66.6333 | 72.6333 | 74.6333
2015-10-14 23:30 | 62 | 66.3833 | 72.3833 | 74.3833
2015-10-14 23:45 | 62 | 66.1333 | 72.1333 | 74.1333
2015-10-15 | 62 | 66 | 71.8833 | 74.1167
2015-10-15 00:15 | 62 | 66 | 71.6333 | 74.3667
2015-10-15 00:30 | 62 | 66 | 71.3833 | 74.6167
2015-10-15 00:45 | 62 | 66 | 71.1333 | 74.8667
2015-10-15 01:00 | 62 | 66.1167 | 70.7667 | 74.7667
2015-10-15 01:15 | 62 | 66.3667 | 70.2667 | 74.2667
2015-10-15 01:30 | 62 | 66.6167 | 69.7667 | 73.7667
2015-10-15 01:45 | 62 | 66.8667 | 69.2667 | 73.2667
2015-10-15 02:00 | 62 | 67 | 68.8833 | 72.7667
2015-10-15 02:15 | 62 | 67 | 68.6333 | 72.2667
2015-10-15 02:30 | 62 | 67 | 68.3833 | 71.7667
2015-10-15 02:45 | 62 | 67 | 68.1333 | 71.2667
2015-10-15 03:00 | 62 | 66.8833 | 67.8833 | 71.2333
2015-10-15 03:15 | 62 | 66.6333 | 67.6333 | 71.7333
2015-10-15 03:30 | 62 | 66.3833 | 67.3833 | 72.2333
2015-10-15 03:45 | 62 | 66.1333 | 67.1333 | 72.7333
2015-10-15 04:00 | 62 | 66 | 66.8833 | 73.1167
2015-10-15 04:15 | 62 | 66 | 66.6333 | 73.3667
2015-10-15 04:30 | 62 | 66 | 66.3833 | 73.6167
2015-10-15 04:45 | 62 | 66 | 66.1333 | 73.8667
2015-10-15 05:00 | 62 | 65.7667 | 65.8833 | 73.65
2015-10-15 05:15 | 62 | 65.2667 | 65.6333 | 72.9
2015-10-15 05:30 | 62 | 64.7667 | 65.3833 | 72.15
2015-10-15 05:45 | 62 | 64.2667 | 65.1333 | 71.4
2015-10-15 06:00 | 62.069 | 64.1167 | 64.7667 | 70.65
2015-10-15 06:15 | 62.3276 | 64.3667 | 64.2667 | 69.9
2015-10-15 06:30 | 62.5862 | 64.6167 | 63.7667 | 69.15
2015-10-15 06:45 | 62.8448 | 64.8667 | 63.2667 | 68.4
2015-10-15 07:00 | 62 | 65.1167 | 63.35 | 68.2333
2015-10-15 07:15 | 62 | 65.3667 | 64.1 | 68.7333
2015-10-15 07:30 | 62 | 65.6167 | 64.85 | 69.2333
2015-10-15 07:45 | 62 | 65.8667 | 65.6 | 69.7333
2015-10-15 08:00 | 62.1333 | 66.1167 | 66.8167 | 70.2333
2015-10-15 08:15 | 62.6333 | 66.3667 | 68.5667 | 70.7333
2015-10-15 08:30 | 63.1333 | 66.6167 | 70.3167 | 71.2333
2015-10-15 08:45 | 63.6333 | 66.8667 | 72.0667 | 71.7333
2015-10-15 09:00 | 64.0667 | 67.1167 | 73.5833 | 72.35
2015-10-15 09:15 | 64.3167 | 67.3667 | 74.8333 | 73.1
2015-10-15 09:30 | 64.5667 | 67.6167 | 76.0833 | 73.85
2015-10-15 09:45 | 64.8167 | 67.8667 | 77.3333 | 74.6
2015-10-15 10:00 | 65.1333 | 68.1167 | 78.4667 | 75.2333
2015-10-15 10:15 | 65.6333 | 68.3667 | 79.4667 | 75.7333
2015-10-15 10:30 | 66.1333 | 68.6167 | 80.4667 | 76.2333
2015-10-15 10:45 | 66.6333 | 68.8667 | 81.4667 | 76.7333
2015-10-15 11:00 | 67.1333 | 69.4667 | 82.5833 | 77.35
2015-10-15 11:15 | 67.6333 | 70.4667 | 83.8333 | 78.1
2015-10-15 11:30 | 68.1333 | 71.4667 | 85.0833 | 78.85
2015-10-15 11:45 | 68.6333 | 72.4667 | 86.3333 | 79.6
2015-10-15 12:00 | 69 | 73.2333 | 87.35 | 80.4667
2015-10-15 12:15 | 69 | 73.7333 | 88.1 | 81.4667
2015-10-15 12:30 | 69 | 74.2333 | 88.85 | 82.4667
2015-10-15 12:45 | 69 | 74.7333 | 89.6 | 83.4667
2015-10-15 13:00 | 69.48 | 75.2333 | 90 | 84.2333
2015-10-15 13:15 | 71.28 | 75.7333 | 90 | 84.7333
2015-10-15 13:30 | 70.7143 | 76.2333 | 90 | 85.2333
2015-10-15 13:45 | 68.5714 | 76.7333 | 90 | 85.7333
2015-10-15 14:00 | 66.9333 | 77 | 90 | 86.1167
2015-10-15 14:15 | 66.6833 | 77 | 90 | 86.3667
2015-10-15 14:30 | 66.4333 | 77 | 90 | 86.6167
2015-10-15 14:45 | 66.1833 | 77 | 90 | 86.8667
2015-10-15 15:00 | 65.9333 | 76.3 | 90 | 86.8833
2015-10-15 15:15 | 65.6833 | 74.8 | 90 | 86.6333
2015-10-15 15:30 | 65.4333 | 73.3 | 90 | 86.3833
2015-10-15 15:45 | 65.1833 | 71.8 | 90 | 86.1333
2015-10-15 16:00 | 64.8667 | 70.65 | 89.65 | 86
2015-10-15 16:15 | 64.3667 | 69.9 | 88.9 | 86
2015-10-15 16:30 | 63.8667 | 69.15 | 88.15 | 86
2015-10-15 16:45 | 63.3667 | 68.4 | 87.4 | 86
2015-10-15 17:00 | 63 | 67.7667 | 86.65 | 85.5333
2015-10-15 17:15 | 63 | 67.2667 | 85.9 | 84.5333
2015-10-15 17:30 | 63 | 66.7667 | 85.15 | 83.5333
2015-10-15 17:45 | 63 | 66.2667 | 84.4 | 82.5333
2015-10-15 18:00 | 63 | 65.8833 | 83.5333 | 81.4146
2015-10-15 18:15 | 63 | 65.6333 | 82.5333 | 78.4878
2015-10-15 18:30 | 63 | 65.3833 | 81.5333 | 75.561
2015-10-15 18:45 | 63 | 65.1333 | 80.5333 | 73.5333
2015-10-15 19:00 | 62.9333 | 65 | 79.5333 | 72.7667
2015-10-15 19:15 | 62.6833 | 65 | 78.5333 | 72.2667
2015-10-15 19:30 | 62.4333 | 65 | 77.5333 | 71.7667
2015-10-15 19:45 | 62.1833 | 65 | 76.5333 | 71.2667
2015-10-15 20:00 | 62 | 65 | 75.7667 | 70.8833
2015-10-15 20:15 | 62 | 65 | 75.2667 | 70.6333
2015-10-15 20:30 | 62 | 65 | 74.7667 | 70.3833
2015-10-15 20:45 | 62 | 65 | 74.2667 | 70.1333
2015-10-15 21:00 | 61.9333 | 65 | 73.7667 | 69.8654
2015-10-15 21:15 | 61.6833 | 65 | 73.2667 | 69.5769
2015-10-15 21:30 | 61.4333 | 65 | 72.7667 | 69.2885
2015-10-15 21:45 | 61.1833 | 65 | 72.2667 | 69
2015-10-15 22:00 | 61 | 64.8833 | 71.8833 | 70
2015-10-15 22:15 | 61 | 64.6333 | 71.6333 | 70
2015-10-15 22:30 | 61 | 64.3833 | 71.3833 | 70
2015-10-15 22:45 | 61 | 64.1333 | 71.1333 | 70
2015-10-15 23:00 | 61 | 64 | 70.8833 | 70
2015-10-15 23:15 | 61 | 64 | 70.6333 | 70
2015-10-15 23:30 | 61 | 64 | 70.3833 | 70
2015-10-15 23:45 | 61 | 64 | 70.1333 | 70
2015-10-16 | 61 | 63.8833 | 69.8833 | 69.8833
2015-10-16 00:15 | 61 | 63.6333 | 69.6333 | 69.6333
2015-10-16 00:30 | 61 | 63.3833 | 69.3833 | 69.3833
2015-10-16 00:45 | 61 | 63.1333 | 69.1333 | 69.1333
2015-10-16 01:00 | 61 | 63 | 68.8833 | 68.8833
2015-10-16 01:15 | 61 | 63 | 68.6333 | 68.6333
2015-10-16 01:30 | 61 | 63 | 68.3833 | 68.3833
2015-10-16 01:45 | 61 | 63 | 68.1333 | 68.1333
2015-10-16 02:00 | 61 | 62.8833 | 67.8833 | 67.8833
2015-10-16 02:15 | 61 | 62.6333 | 67.6333 | 67.6333
2015-10-16 02:30 | 61 | 62.3833 | 67.3833 | 67.3833
2015-10-16 02:45 | 61 | 62.1333 | 67.1333 | 67.1333
2015-10-16 03:00 | 61 | 62.6364 | 66.7667 | 67
2015-10-16 03:15 | 61 | 62.9744 | 66.2667 | 67
2015-10-16 03:30 | 61 | 62.5897 | 65.7667 | 67
2015-10-16 03:45 | 61 | 62.2051 | 65.2667 | 67
2015-10-16 04:00 | 61 | 62.1628 | 64.7667 | 66.7667
2015-10-16 04:15 | 61 | 62.5116 | 64.2667 | 66.2667
2015-10-16 04:30 | 61 | 62.8605 | 63.7667 | 65.7667
2015-10-16 04:45 | 61 | 62.4706 | 63.2667 | 65.2667
2015-10-16 05:00 | 60.9333 | 62 | 62.65 | 64.8833
2015-10-16 05:15 | 60.6833 | 62 | 61.9 | 64.6333
2015-10-16 05:30 | 60.4333 | 62 | 61.15 | 64.3833
2015-10-16 05:45 | 60.1833 | 62 | 60.4 | 64.1333
2015-10-16 06:00 | 60 | 62 | 60 | 64
2015-10-16 06:15 | 60 | 62 | 60 | 64
2015-10-16 06:30 | 60 | 62 | 60 | 64.3611
2015-10-16 06:45 | 60 | 62 | 60 | 64.7778
2015-10-16 07:00 | 60.0667 | 62.2333 | 60.35 | 65.3111
2015-10-16 07:15 | 60.3167 | 62.7333 | 61.1 | 65.9778
2015-10-16 07:30 | 60.5667 | 63.2333 | 61.85 | 66.6444
2015-10-16 07:45 | 60.8167 | 63.7333 | 62.6 | 66.4615
2015-10-16 08:00 | 61.0667 | 64.1167 | 63.5833 | 67.35
2015-10-16 08:15 | 61.3167 | 64.3667 | 64.8333 | 68.1
2015-10-16 08:30 | 61.5667 | 64.6167 | 66.0833 | 68.85
2015-10-16 08:45 | 61.8167 | 64.8667 | 67.3333 | 69.6
2015-10-16 09:00 | 62.1905 | 65.4667 | 68.4242 | 70.35
2015-10-16 09:15 | 62.9048 | 66.3111 | 69.3333 | 71.1
2015-10-16 09:30 | 63.619 | 66.9778 | 69.8519 | 71.85
2015-10-16 09:45 | 64.7778 | 67.6444 | 69.2963 | 72.6
2015-10-16 10:00 | 66 | 68.2333 | 69.14 | 73.35
2015-10-16 10:15 | 66 | 68.7333 | 69.44 | 74.1
2015-10-16 10:30 | 66 | 69.2333 | 69.74 | 74.85
2015-10-16 10:45 | 66 | 69.7333 | 69.8 | 75.6
2015-10-16 11:00 | 66.1333 | 70.2333 | 69.6667 | 76.4667
2015-10-16 11:15 | 66.6333 | 70.7333 | 71.0556 | 77.4667
2015-10-16 11:30 | 67.1333 | 71.2333 | 71.8889 | 78.4667
2015-10-16 11:45 | 67.6333 | 71.7333 | 72 | 79.4667
2015-10-16 12:00 | 68.2759 | 72.2333 | 72.2333 | 80.2333
2015-10-16 12:15 | 69.3103 | 72.7333 | 72.7333 | 80.7333
2015-10-16 12:30 | 69.8387 | 73.2333 | 73.2333 | 81.2333
2015-10-16 12:45 | 69.3548 | 73.7333 | 73.7333 | 81.7333
2015-10-16 13:00 | 69.1333 | 74.35 | 74.2414 | 82.1167
2015-10-16 13:15 | 69.6333 | 75.1 | 74.7586 | 82.3667
2015-10-16 13:30 | 70.1333 | 75.85 | 76 | 82.6167
2015-10-16 13:45 | 70.6333 | 76.6 | 76 | 82.8667
2015-10-16 14:00 | 70.8947 | 77.1167 | 76.5833 | 83.1167
2015-10-16 14:15 | 70.5 | 77.3667 | 75 | 83.3667
2015-10-16 14:30 | 70.1053 | 77.6167 | 75 | 83.6167
2015-10-16 14:45 | 68.5 | 77.8667 | 75 | 83.8667
2015-10-16 15:00 | 66.9333 | 77.8833 | 75.35 | 84
2015-10-16 15:15 | 66.6833 | 77.6333 | 76.1 | 84
2015-10-16 15:30 | 66.4333 | 77.3833 | 76.85 | 84
2015-10-16 15:45 | 66.1833 | 77.1333 | 77.6 | 84
2015-10-16 16:00 | 65.8 | 76.4167 | 78 | 83.8833
2015-10-16 16:15 | 65.05 | 75.1667 | 78 | 83.6333
2015-10-16 16:30 | 64.3 | 73.9167 | 78 | 83.3833
2015-10-16 16:45 | 63.55 | 72.6667 | 78 | 83.1333
2015-10-16 17:00 | 62.9333 | 71.5333 | 77.5333 | 82.7667
2015-10-16 17:15 | 62.6833 | 70.5333 | 76.5333 | 82.2667
2015-10-16 17:30 | 62.4333 | 69.5333 | 75.5333 | 81.7667
2015-10-16 17:45 | 62.1833 | 68.5333 | 74.5333 | 81.2667
2015-10-16 18:00 | 62 | 67.5333 | 73.65 | 80.8833
2015-10-16 18:15 | 62 | 66.5333 | 72.9 | 80.6333
2015-10-16 18:30 | 62 | 65.5333 | 72.15 | 80.3833
2015-10-16 18:45 | 62 | 64.5333 | 71.4 | 80.1333
2015-10-16 19:00 | 62 | 63.7667 | 70.5333 | 79.5333
2015-10-16 19:15 | 62 | 63.2667 | 69.5333 | 78.5333
2015-10-16 19:30 | 62 | 62.7667 | 68.5333 | 77.5333
2015-10-16 19:45 | 62 | 62.2667 | 67.5333 | 76.5333
2015-10-16 20:00 | 61.9333 | 62 | 66.65 | 75.8833
2015-10-16 20:15 | 61.6833 | 62 | 65.9 | 75.6333
2015-10-16 20:30 | 61.4333 | 62 | 65.15 | 75.3833
2015-10-16 20:45 | 61.1833 | 62 | 64.4 | 75.1333
2015-10-16 21:00 | 61 | 62 | 64.1167 | 74.7667
2015-10-16 21:15 | 61 | 62 | 64.3667 | 74.2667
2015-10-16 21:30 | 61 | 62 | 64.6167 | 73.7667
2015-10-16 21:45 | 61 | 62 | 64.8667 | 73.2667
2015-10-16 22:00 | 61 | 61.7667 | 64.7667 | 73
2015-10-16 22:15 | 61 | 61.2667 | 64.2667 | 73
2015-10-16 22:30 | 61 | 60.7667 | 63.7667 | 73
2015-10-16 22:45 | 61 | 60.2667 | 63.2667 | 73
2015-10-16 23:00 | 61 | 60.4565 | 62.7667 | 72.8833
2015-10-16 23:15 | 61 | 61.4348 | 62.2667 | 72.6333
2015-10-16 23:30 | 61 | 62.413 | 61.7667 | 72.3833
2015-10-16 23:45 | 61 | 62.5714 | 61.2667 | 72.1333
2015-10-17 | 61 | 62 | 60.65 | 72
2015-10-17 00:15 | 61 | 62 | 59.9 | 72
2015-10-17 00:30 | 61 | 62 | 59.15 | 72
2015-10-17 00:45 | 61 | 62 | 58.4 | 72
2015-10-17 01:00 | 61 | 62 | 57.7667 | 71.8833
2015-10-17 01:15 | 61 | 62 | 57.2667 | 71.6333
2015-10-17 01:30 | 61 | 62 | 56.7667 | 71.3833
2015-10-17 01:45 | 61 | 62 | 56.2667 | 71.1333
2015-10-17 02:00 | 61 | 62.1167 | 56 | 70.8833
2015-10-17 02:15 | 61 | 62.3667 | 56 | 70.6333
2015-10-17 02:30 | 61 | 62.6167 | 56 | 70.3833
2015-10-17 02:45 | 61 | 62.8667 | 56 | 70.1333
2015-10-17 03:00 | 61 | 63 | 55.8833 | 70
2015-10-17 03:15 | 61 | 63 | 55.6333 | 70
2015-10-17 03:30 | 61 | 63 | 55.3833 | 70
2015-10-17 03:45 | 61 | 63 | 55.1333 | 70
2015-10-17 04:00 | 61.0667 | 62.8833 | 54.7667 | 70
2015-10-17 04:15 | 61.3167 | 62.6333 | 54.2667 | 70
2015-10-17 04:30 | 61.5667 | 62.3833 | 53.7667 | 70
2015-10-17 04:45 | 61.8167 | 62.1333 | 53.2667 | 70
2015-10-17 05:00 | 62 | 61.8833 | 53.1167 | 69.8833
2015-10-17 05:15 | 62 | 61.6333 | 53.3667 | 69.6333
2015-10-17 05:30 | 62 | 61.3833 | 53.6167 | 69.3833
2015-10-17 05:45 | 62 | 61.1333 | 53.8667 | 69.1333
2015-10-17 06:00 | 62 | 61.1167 | 53.8833 | 68.65
2015-10-17 06:15 | 62 | 61.3667 | 53.6333 | 67.9
2015-10-17 06:30 | 62 | 61.6167 | 53.3833 | 67.15
2015-10-17 06:45 | 62 | 61.8667 | 53.1333 | 66.4
2015-10-17 07:00 | 62.0667 | 62.1167 | 53.35 | 66
2015-10-17 07:15 | 62.3167 | 62.3667 | 54.1 | 66
2015-10-17 07:30 | 62.5667 | 62.6167 | 54.85 | 66
2015-10-17 07:45 | 62.8167 | 62.8667 | 55.6 | 66
2015-10-17 08:00 | 63.1333 | 63 | 56.5833 | 66.2333
2015-10-17 08:15 | 63.6333 | 63.0732 | 57.8333 | 66.7333
2015-10-17 08:30 | 64.1333 | 63.439 | 59.0833 | 67.2333
2015-10-17 08:45 | 64.6333 | 63.8049 | 60.3333 | 67.7333
2015-10-17 09:00 | 65.0667 | 64 | 61.7 | 68.35
2015-10-17 09:15 | 65.3167 | 64 | 63.2 | 69.1
2015-10-17 09:30 | 65.5667 | 64 | 64.7 | 69.85
2015-10-17 09:45 | 65.8167 | 64.6522 | 66.2 | 70.6
2015-10-17 10:00 | 66 | 65.3889 | 67.8167 | 71.5833
2015-10-17 10:15 | 66 | 66.0952 | 69.5667 | 72.8333
2015-10-17 10:30 | 66 | 66.4524 | 71.3167 | 74.0833
2015-10-17 10:45 | 66 | 66.8095 | 73.0667 | 75.3333
2015-10-17 11:00 | 66.0667 | 67.2333 | 74.2333 | 76.2333
2015-10-17 11:15 | 66.3167 | 67.7333 | 74.7333 | 76.7333
2015-10-17 11:30 | 66.5667 | 68.2333 | 75.2333 | 77.2333
2015-10-17 11:45 | 66.8167 | 68.7333 | 75.7333 | 77.7333
2015-10-17 12:00 | 67 | 69.2333 | 76.2333 | 78.35
2015-10-17 12:15 | 67 | 69.7333 | 76.7333 | 79.1
2015-10-17 12:30 | 67 | 70.2333 | 77.2333 | 79.85
2015-10-17 12:45 | 67 | 70.7333 | 77.7333 | 80.6
2015-10-17 13:00 | 67.1333 | 71.1167 | 78 | 81
2015-10-17 13:15 | 67.6333 | 71.3667 | 78 | 81
2015-10-17 13:30 | 68.1333 | 71.6167 | 78 | 81
2015-10-17 13:45 | 68.6333 | 71.8667 | 78 | 81
2015-10-17 14:00 | 68.8667 | 71.7667 | 77.8833 | 81
2015-10-17 14:15 | 68.3667 | 71.2667 | 77.6333 | 81
2015-10-17 14:30 | 67.8667 | 70.7667 | 77.3833 | 81
2015-10-17 14:45 | 67.3667 | 70.2667 | 77.1333 | 81
2015-10-17 15:00 | 66.8974 | 69.8833 | 77 | 80.7667
2015-10-17 15:15 | 66.5128 | 69.6333 | 77 | 80.2667
2015-10-17 15:30 | 66.1282 | 69.3833 | 77 | 79.7667
2015-10-17 15:45 | 66 | 69.1333 | 77 | 79.2667
2015-10-17 16:00 | 65.8667 | 68.7667 | 76.7667 | 78.7667
2015-10-17 16:15 | 65.3667 | 68.2667 | 76.2667 | 78.2667
2015-10-17 16:30 | 64.8667 | 67.7667 | 75.7667 | 77.7667
2015-10-17 16:45 | 64.3667 | 67.2667 | 75.2667 | 77.2667
2015-10-17 17:00 | 63.9333 | 66.8833 | 74.7667 | 76.7667
2015-10-17 17:15 | 63.6833 | 66.6333 | 74.2667 | 76.2667
2015-10-17 17:30 | 63.4333 | 66.3833 | 73.7667 | 75.7667
2015-10-17 17:45 | 63.1833 | 66.1333 | 73.2667 | 75.2667
2015-10-17 18:00 | 63 | 65.7667 | 72.7667 | 74.65
2015-10-17 18:15 | 63 | 65.2667 | 72.2667 | 73.9
2015-10-17 18:30 | 63 | 64.7667 | 71.7667 | 73.15
2015-10-17 18:45 | 63 | 64.2667 | 71.2667 | 72.4
2015-10-17 19:00 | 63 | 63.8833 | 70.7667 | 71.7667
2015-10-17 19:15 | 63 | 63.6333 | 70.2667 | 71.2667
2015-10-17 19:30 | 63 | 63.3833 | 69.7667 | 70.7667
2015-10-17 19:45 | 63 | 63.1333 | 69.2667 | 70.2667
2015-10-17 20:00 | 63 | 63 | 68.8833 | 69.8833
2015-10-17 20:15 | 63 | 63 | 68.6333 | 69.6333
2015-10-17 20:30 | 63 | 63 | 68.3833 | 69.3833
2015-10-17 20:45 | 63 | 63 | 68.1333 | 69.1333
2015-10-17 21:00 | 63 | 63 | 67.7667 | 68.8833
2015-10-17 21:15 | 63 | 63 | 67.2667 | 68.6333
2015-10-17 21:30 | 63 | 63 | 66.7667 | 68.3833
2015-10-17 21:45 | 63 | 63 | 66.2667 | 68.1333
2015-10-17 22:00 | 62.08 | 63 | 66 | 67.8833
2015-10-17 22:15 | 62.38 | 63 | 66 | 67.6333
2015-10-17 22:30 | 62.68 | 63 | 66 | 67.3833
2015-10-17 22:45 | 62.98 | 63 | 66 | 67.1333
2015-10-17 23:00 | 62.1176 | 63 | 66 | 66.7667
2015-10-17 23:15 | 62.5588 | 63 | 66 | 66.2667
2015-10-17 23:30 | 63 | 63 | 66 | 65.7667
2015-10-17 23:45 | 61.8462 | 63 | 66 | 65.2667
2015-10-18 | 61 | 62.8833 | 66 | 65
2015-10-18 00:15 | 61 | 62.6333 | 66 | 65
2015-10-18 00:30 | 61 | 62.3833 | 66 | 65
2015-10-18 00:45 | 61 | 62.1333 | 66 | 65
2015-10-18 01:00 | 61 | 62 | 65.8833 | 64.8833
2015-10-18 01:15 | 61 | 62 | 65.6333 | 64.6333
2015-10-18 01:30 | 61 | 62 | 65.3833 | 64.3833
2015-10-18 01:45 | 61 | 62 | 65.1333 | 64.1333
2015-10-18 02:00 | 61 | 62 | 64.8833 | 64
2015-10-18 02:15 | 61 | 62 | 64.6333 | 64
2015-10-18 02:30 | 61 | 62 | 64.3833 | 64
2015-10-18 02:45 | 61 | 62 | 64.1333 | 64
2015-10-18 03:00 | 61 | 61.5333 | 63.8833 | 63.8833
2015-10-18 03:15 | 61 | 60.5333 | 63.6333 | 63.6333
2015-10-18 03:30 | 61 | 59.5333 | 63.3833 | 63.3833
2015-10-18 03:45 | 61 | 58.5333 | 63.1333 | 63.1333
2015-10-18 04:00 | 61 | 57.8205 | 62.8833 | 63
2015-10-18 04:15 | 61 | 57.4359 | 62.6333 | 63
2015-10-18 04:30 | 61 | 57.0513 | 62.3833 | 63
2015-10-18 04:45 | 61 | 57.619 | 62.1333 | 63
2015-10-18 05:00 | 61.1951 | 58 | 61.8833 | 63
2015-10-18 05:15 | 61.9268 | 58 | 61.6333 | 63
2015-10-18 05:30 | 62.6585 | 58 | 61.3833 | 63
2015-10-18 05:45 | 62.5789 | 58 | 61.1333 | 63
2015-10-18 06:00 | 62 | 58.1522 | 61 | 63
2015-10-18 06:15 | 62 | 58.4783 | 61 | 63
2015-10-18 06:30 | 62 | 58.8043 | 61 | 63
2015-10-18 06:45 | 62 | 59.4286 | 61 | 63
2015-10-18 07:00 | 62.4 | 60.2333 | 61.2333 | 63
2015-10-18 07:15 | 63.18 | 60.7333 | 61.7333 | 63
2015-10-18 07:30 | 63.48 | 61.2333 | 62.2333 | 63
2015-10-18 07:45 | 63.78 | 61.7333 | 62.7333 | 63
2015-10-18 08:00 | 64 | 62.1167 | 63.35 | 63.2333
2015-10-18 08:15 | 64 | 62.3667 | 64.1 | 63.7333
2015-10-18 08:30 | 64 | 62.6167 | 64.85 | 64.2333
2015-10-18 08:45 | 64 | 62.8667 | 65.6 | 64.7333
2015-10-18 09:00 | 64.0667 | 63.35 | 66.2333 | 65.2333
2015-10-18 09:15 | 64.3167 | 64.1 | 66.7333 | 65.7333
2015-10-18 09:30 | 64.5667 | 64.85 | 67.2333 | 66.2333
2015-10-18 09:45 | 64.8167 | 65.6 | 67.7333 | 66.7333
2015-10-18 10:00 | 65.0667 | 66.2333 | 68.1167 | 67.4667
2015-10-18 10:15 | 65.3167 | 66.7333 | 68.3667 | 68.4667
2015-10-18 10:30 | 65.5667 | 67.2333 | 68.6167 | 69.4667
2015-10-18 10:45 | 65.8167 | 67.7333 | 68.8667 | 70.4667
2015-10-18 11:00 | 66.1333 | 68.1167 | 68.8833 | 71.1167
2015-10-18 11:15 | 66.6333 | 68.3667 | 68.6333 | 71.3667
2015-10-18 11:30 | 67.1333 | 68.6167 | 68.3833 | 71.6167
2015-10-18 11:45 | 67.6333 | 68.8667 | 68.1333 | 71.8667
2015-10-18 12:00 | 68 | 69.1167 | 68.35 | 72
2015-10-18 12:15 | 68 | 69.3667 | 69.1 | 72
2015-10-18 12:30 | 68 | 69.6167 | 69.85 | 72
2015-10-18 12:45 | 68 | 69.8667 | 70.6 | 72
2015-10-18 13:00 | 68 | 70 | 71.1167 | 72.2333
2015-10-18 13:15 | 68 | 70 | 71.3667 | 72.7333
2015-10-18 13:30 | 68 | 70 | 71.6167 | 73.2333
2015-10-18 13:45 | 68 | 70 | 71.8667 | 73.7333
2015-10-18 14:00 | 67.9333 | 70.1167 | 72.2333 | 74
2015-10-18 14:15 | 67.6833 | 70.3667 | 72.7333 | 74
2015-10-18 14:30 | 67.4333 | 70.6167 | 73.2333 | 74
2015-10-18 14:45 | 67.1833 | 70.8667 | 73.7333 | 74
2015-10-18 15:00 | 66.9333 | 70.7667 | 74.1167 | 74
2015-10-18 15:15 | 66.6833 | 70.2667 | 74.3667 | 74
2015-10-18 15:30 | 66.4333 | 69.7667 | 74.6167 | 74
2015-10-18 15:45 | 66.1833 | 69.2667 | 74.8667 | 74
2015-10-18 16:00 | 65.8667 | 68.7667 | 74.8833 | 73.8833
2015-10-18 16:15 | 65.3667 | 68.2667 | 74.6333 | 73.6333
2015-10-18 16:30 | 64.8667 | 67.7667 | 74.3833 | 73.3833
2015-10-18 16:45 | 64.3667 | 67.2667 | 74.1333 | 73.1333
2015-10-18 17:00 | 63.9048 | 66.65 | 73.7667 | 72.7667
2015-10-18 17:15 | 63.5476 | 65.9 | 73.2667 | 72.2667
2015-10-18 17:30 | 63.1905 | 65.15 | 72.7667 | 71.7667
2015-10-18 17:45 | 63 | 64.4 | 72.2667 | 71.2667
2015-10-18 18:00 | 63 | 63.8833 | 71.7667 | 70.7667
2015-10-18 18:15 | 63 | 63.6333 | 71.2667 | 70.2667
2015-10-18 18:30 | 63 | 63.3833 | 70.7667 | 69.7667
2015-10-18 18:45 | 62.6111 | 63.1333 | 70.2667 | 69.2667
2015-10-18 19:00 | 62.0889 | 63 | 69.7667 | 69
2015-10-18 19:15 | 62.4222 | 63 | 69.2667 | 69
2015-10-18 19:30 | 62.7556 | 63 | 68.7667 | 69
2015-10-18 19:45 | 62.7333 | 63 | 68.2667 | 69
2015-10-18 20:00 | 62 | 62.8833 | 67.8833 | 68.65
2015-10-18 20:15 | 62 | 62.6333 | 67.6333 | 67.9
2015-10-18 20:30 | 62 | 62.3833 | 67.3833 | 67.15
2015-10-18 20:45 | 62 | 62.1333 | 67.1333 | 66.4
2015-10-18 21:00 | 62.0851 | 62 | 66.8833 | 65.7667
2015-10-18 21:15 | 62.4043 | 62 | 66.6333 | 65.2667
2015-10-18 21:30 | 62.7234 | 62 | 66.3833 | 64.7667
2015-10-18 21:45 | 62.8462 | 62 | 66.1333 | 64.2667
2015-10-18 22:00 | 62 | 61.8833 | 65.8833 | 64
2015-10-18 22:15 | 62 | 61.6333 | 65.6333 | 64
2015-10-18 22:30 | 62 | 61.3833 | 65.3833 | 64
2015-10-18 22:45 | 62 | 61.1333 | 65.1333 | 64
2015-10-18 23:00 | 62 | 61 | 65 | 63.7667
2015-10-18 23:15 | 62 | 61 | 65 | 63.2667
2015-10-18 23:30 | 62 | 61 | 65 | 62.7667
2015-10-18 23:45 | 62 | 61 | 65 | 62.2667
2015-10-19 | 62.1667 | 61 | 64.8833 | 61.8833
2015-10-19 00:15 | 62.7917 | 61 | 64.6333 | 61.6333
2015-10-19 00:30 | 62.4444 | 61 | 64.3833 | 61.3833
2015-10-19 00:45 | 61.6111 | 61 | 64.1333 | 61.1333
2015-10-19 01:00 | 61 | 61 | 64 | 60.8833
2015-10-19 01:15 | 61 | 61 | 64 | 60.6333
2015-10-19 01:30 | 61 | 61 | 64 | 60.3833
2015-10-19 01:45 | 61 | 61 | 64 | 60.1333
2015-10-19 02:00 | 61 | 61 | 63.8833 | 59.8833
2015-10-19 02:15 | 61 | 61 | 63.6333 | 59.6333
2015-10-19 02:30 | 61 | 61 | 63.3833 | 59.3833
2015-10-19 02:45 | 61 | 61 | 63.1333 | 59.1333
2015-10-19 03:00 | 61 | 61 | 62.8833 | 58.8833
2015-10-19 03:15 | 61 | 61 | 62.6333 | 58.6333
2015-10-19 03:30 | 61 | 61 | 62.3833 | 58.3833
2015-10-19 03:45 | 60.7333 | 61 | 62.1333 | 58.1333
2015-10-19 04:00 | 60.1053 | 61 | 61.8833 | 57.8833
2015-10-19 04:15 | 60.5 | 61 | 61.6333 | 57.6333
2015-10-19 04:30 | 60.8947 | 61 | 61.3833 | 57.3833
2015-10-19 04:45 | 61 | 61 | 61.1333 | 57.1333
2015-10-19 05:00 | 61 | 60.8833 | 60.8833 | 56.8833
2015-10-19 05:15 | 61 | 60.6333 | 60.6333 | 56.6333
2015-10-19 05:30 | 61 | 60.3833 | 60.3833 | 56.3833
2015-10-19 05:45 | 61 | 60.1333 | 60.1333 | 56.1333
2015-10-19 06:00 | 60 | 60.1489 | 60 | 56
2015-10-19 06:15 | 60 | 60.4681 | 60 | 56
2015-10-19 06:30 | 60 | 60.7872 | 60 | 56
2015-10-19 06:45 | 60 | 60.6154 | 60 | 56
2015-10-19 07:00 | 60.1333 | 60.2333 | 60.2333 | 56.4667
2015-10-19 07:15 | 60.6333 | 60.7333 | 60.7333 | 57.4667
2015-10-19 07:30 | 61.1333 | 61.2333 | 61.2333 | 58.4667
2015-10-19 07:45 | 61.6333 | 61.7333 | 61.7333 | 59.4667
2015-10-19 08:00 | 62.0667 | 62.1167 | 62.4667 | 60.5833
2015-10-19 08:15 | 62.3167 | 62.3667 | 63.4667 | 61.8333
2015-10-19 08:30 | 62.5667 | 62.6167 | 64.4667 | 63.0833
2015-10-19 08:45 | 62.8167 | 62.8667 | 65.4667 | 64.3333
2015-10-19 09:00 | 63.0667 | 63.2333 | 66.9333 | 65.35
2015-10-19 09:15 | 63.3167 | 63.7333 | 68.9333 | 66.1
2015-10-19 09:30 | 63.5667 | 64.2333 | 70.9333 | 66.85
2015-10-19 09:45 | 63.8167 | 64.7333 | 72.9333 | 67.6
2015-10-19 10:00 | 64 | 65.1167 | 74.5833 | 68.2333
2015-10-19 10:15 | 64 | 65.3667 | 75.8333 | 68.7333
2015-10-19 10:30 | 64 | 65.6167 | 77.0833 | 69.2333
2015-10-19 10:45 | 64 | 65.8667 | 78.3333 | 69.7333
2015-10-19 11:00 | 65.0667 | 66.2333 | 79.2333 | 70.2333
2015-10-19 11:15 | 65.3167 | 66.7333 | 79.7333 | 70.7333
2015-10-19 11:30 | 65.5667 | 67.2333 | 80.2333 | 71.2333
2015-10-19 11:45 | 65.8167 | 67.7333 | 80.7333 | 71.7333
2015-10-19 12:00 | 66.0667 | 68 | 81.35 | 71.8833
2015-10-19 12:15 | 66.3167 | 68.24 | 82.1 | 71.6333
2015-10-19 12:30 | 66.5667 | 68.54 | 82.85 | 71.3833
2015-10-19 12:45 | 66.8167 | 68.84 | 83.6 | 71.1333
2015-10-19 13:00 | 67 | 69.2333 | 84 | 71.4667
2015-10-19 13:15 | 67 | 69.7333 | 84 | 72.4667
2015-10-19 13:30 | 67 | 70.2333 | 84 | 73.4667
2015-10-19 13:45 | 67 | 70.7333 | 84 | 74.4667
2015-10-19 14:00 | 67 | 71 | 83.7667 | 75
2015-10-19 14:15 | 67 | 71 | 83.2667 | 75
2015-10-19 14:30 | 67 | 71 | 82.7667 | 75
2015-10-19 14:45 | 67 | 71 | 82.2667 | 75
2015-10-19 15:00 | 66.9333 | 70.7667 | 81.8833 | 74.8833
2015-10-19 15:15 | 66.6833 | 70.2667 | 81.6333 | 74.6333
2015-10-19 15:30 | 66.4333 | 69.7667 | 81.3833 | 74.3833
2015-10-19 15:45 | 66.1833 | 69.2667 | 81.1333 | 74.1333
2015-10-19 16:00 | 65.9333 | 68.7667 | 80.7667 | 73.8833
2015-10-19 16:15 | 65.6833 | 68.2667 | 80.2667 | 73.6333
2015-10-19 16:30 | 65.4333 | 67.7667 | 79.7667 | 73.3833
2015-10-19 16:45 | 65.1833 | 67.2667 | 79.2667 | 73.1333
2015-10-19 17:00 | 64.8667 | 66.7667 | 78.5333 | 72.7667
2015-10-19 17:15 | 64.3667 | 66.2667 | 77.5333 | 72.2667
2015-10-19 17:30 | 63.8667 | 65.7667 | 76.5333 | 71.7667
2015-10-19 17:45 | 63.3667 | 65.2667 | 75.5333 | 71.2667
2015-10-19 18:00 | 63 | 64.8833 | 74.5333 | 70.7667
2015-10-19 18:15 | 63 | 64.6333 | 73.5333 | 70.2667
2015-10-19 18:30 | 63 | 64.3833 | 72.5333 | 69.7667
2015-10-19 18:45 | 63 | 64.1333 | 71.5333 | 69.2667
2015-10-19 19:00 | 62.9333 | 63.8833 | 70.65 | 69
2015-10-19 19:15 | 62.6833 | 63.6333 | 69.9 | 69
2015-10-19 19:30 | 62.4333 | 63.3833 | 69.15 | 69
2015-10-19 19:45 | 62.1833 | 63.1333 | 68.4 | 69
2015-10-19 20:00 | 62 | 62.8833 | 67.8833 | 68.7667
2015-10-19 20:15 | 62 | 62.6333 | 67.6333 | 68.2667
2015-10-19 20:30 | 62 | 62.3833 | 67.3833 | 67.7667
2015-10-19 20:45 | 62 | 62.1333 | 67.1333 | 67.2667
2015-10-19 21:00 | 61.9333 | 62 | 66.8833 | 66.7667
2015-10-19 21:15 | 61.6833 | 62 | 66.6333 | 66.2667
2015-10-19 21:30 | 61.4333 | 62 | 66.3833 | 65.7667
2015-10-19 21:45 | 61.1833 | 62 | 66.1333 | 65.2667
2015-10-19 22:00 | 61 | 61.8833 | 66 | 64.7667
2015-10-19 22:15 | 61 | 61.6333 | 66 | 64.2667
2015-10-19 22:30 | 61 | 61.3833 | 66 | 63.7667
2015-10-19 22:45 | 61 | 61.1333 | 66 | 63.2667
2015-10-19 23:00 | 60.9333 | 60.65 | 65.8833 | 62.8833
2015-10-19 23:15 | 60.6833 | 59.9 | 65.6333 | 62.6333
2015-10-19 23:30 | 60.4333 | 59.15 | 65.3833 | 62.3833
2015-10-19 23:45 | 60.1833 | 58.4 | 65.1333 | 62.1333
2015-10-20 | 59.9333 | 58 | 65 | 61.8833
2015-10-20 00:15 | 59.6833 | 58 | 65 | 61.6333
2015-10-20 00:30 | 59.4333 | 58 | 65 | 61.3833
2015-10-20 00:45 | 59.1833 | 58 | 65 | 61.1333
2015-10-20 01:00 | 58.9333 | 57.8833 | 64.8833 | 60.8833
2015-10-20 01:15 | 58.6833 | 57.6333 | 64.6333 | 60.6333
2015-10-20 01:30 | 58.4333 | 57.3833 | 64.3833 | 60.3833
2015-10-20 01:45 | 58.1833 | 57.1333 | 64.1333 | 60.1333
2015-10-20 02:00 | 57.9333 | 56.65 | 63.8833 | 59.7667
2015-10-20 02:15 | 57.6833 | 55.9 | 63.6333 | 59.2667
2015-10-20 02:30 | 57.4333 | 55.15 | 63.3833 | 58.7667
2015-10-20 02:45 | 57.1833 | 54.4 | 63.1333 | 58.2667
2015-10-20 03:00 | 57 | 54.1167 | 63.1167 | 58
2015-10-20 03:15 | 57 | 54.3667 | 63.3667 | 58
2015-10-20 03:30 | 57 | 54.6167 | 63.6167 | 58
2015-10-20 03:45 | 57 | 54.8667 | 63.8667 | 58
2015-10-20 04:00 | 57 | 55 | 63.8833 | 57.8833
2015-10-20 04:15 | 57 | 55 | 63.6333 | 57.6333
2015-10-20 04:30 | 57 | 55 | 63.3833 | 57.3833
2015-10-20 04:45 | 57.0833 | 55 | 63.1333 | 57.1333
2015-10-20 05:00 | 58 | 54.8833 | 62.8833 | 56.7667
2015-10-20 05:15 | 58 | 54.6333 | 62.6333 | 56.2667
2015-10-20 05:30 | 58 | 54.3833 | 62.3833 | 55.7667
2015-10-20 05:45 | 58 | 54.1333 | 62.1333 | 55.2667
2015-10-20 06:00 | 57.9333 | 54.1167 | 61.8833 | 55.2333
2015-10-20 06:15 | 57.6833 | 54.3667 | 61.6333 | 55.7333
2015-10-20 06:30 | 57.4333 | 54.6167 | 61.3833 | 56.2333
2015-10-20 06:45 | 57.1833 | 54.8667 | 61.1333 | 56.7333
2015-10-20 07:00 | 57.2667 | 55.4667 | 61 | 57.35
2015-10-20 07:15 | 58.2667 | 56.4667 | 61 | 58.1
2015-10-20 07:30 | 59.2667 | 57.4667 | 61 | 58.85
2015-10-20 07:45 | 60.2667 | 58.4667 | 61 | 59.6
2015-10-20 08:00 | 61.2 | 59.5833 | 61.8167 | 60.35
2015-10-20 08:15 | 61.95 | 60.8333 | 63.5667 | 61.1
2015-10-20 08:30 | 62.7 | 62.0833 | 65.3167 | 61.85
2015-10-20 08:45 | 63.45 | 63.3333 | 67.0667 | 62.6
2015-10-20 09:00 | 64.0667 | 64.5833 | 68.5833 | 63.35
2015-10-20 09:15 | 64.3167 | 65.8333 | 69.8333 | 64.1
2015-10-20 09:30 | 64.5667 | 67.0833 | 71.0833 | 64.85
2015-10-20 09:45 | 64.8167 | 68.3333 | 72.3333 | 65.6
2015-10-20 10:00 | 65.2 | 69.4667 | 73.35 | 66.35
2015-10-20 10:15 | 65.95 | 70.4667 | 74.1 | 67.1
2015-10-20 10:30 | 66.7 | 71.4667 | 74.85 | 67.85
2015-10-20 10:45 | 67.45 | 72.4667 | 75.6 | 68.6
2015-10-20 11:00 | 68.2667 | 73.2333 | 76.2333 | 69.2333
2015-10-20 11:15 | 69.2667 | 73.7333 | 76.7333 | 69.7333
2015-10-20 11:30 | 70.2667 | 74.2333 | 77.2333 | 70.2333
2015-10-20 11:45 | 71.2667 | 74.7333 | 77.7333 | 70.7333
2015-10-20 12:00 | 72.2667 | 75.1167 | 78.2333 | 71.35
2015-10-20 12:15 | 73.2667 | 75.3667 | 78.7333 | 72.1
2015-10-20 12:30 | 74.2667 | 75.6167 | 79.2333 | 72.85
2015-10-20 12:45 | 75.2667 | 75.8667 | 79.7333 | 73.6
2015-10-20 13:00 | 76.0667 | 76.2333 | 80.3684 | 74.1167
2015-10-20 13:15 | 76.3167 | 76.7333 | 80.8 | 74.3667
2015-10-20 13:30 | 76.5667 | 77.2333 | 79.8846 | 74.6167
2015-10-20 13:45 | 76.8167 | 77.7333 | 79.3077 | 74.8667
2015-10-20 14:00 | 76.9333 | 78.1167 | 78.7667 | 75
2015-10-20 14:15 | 76.6833 | 78.3667 | 78.2667 | 75
2015-10-20 14:30 | 76.4333 | 78.6167 | 77.7667 | 75
2015-10-20 14:45 | 76.1833 | 78.8667 | 77.2667 | 75
2015-10-20 15:00 | 75.6667 | 79.1167 | 76.8833 | 75
2015-10-20 15:15 | 74.4167 | 79.3667 | 76.6333 | 75
2015-10-20 15:30 | 73.1667 | 79.6167 | 76.3833 | 75
2015-10-20 15:45 | 71.9167 | 79.8667 | 76.1333 | 75
2015-10-20 16:00 | 70.8 | 79.4167 | 75.8833 | 74.8833
2015-10-20 16:15 | 70.05 | 78.1667 | 75.6333 | 74.6333
2015-10-20 16:30 | 69.3 | 76.9167 | 75.3833 | 74.3833
2015-10-20 16:45 | 68.55 | 75.6667 | 75.1333 | 74.1333
2015-10-20 17:00 | 67.8667 | 74.4167 | 74.65 | 73.65
2015-10-20 17:15 | 67.3667 | 73.1667 | 73.9 | 72.9
2015-10-20 17:30 | 66.8667 | 71.9167 | 73.15 | 72.15
2015-10-20 17:45 | 66.3667 | 70.6667 | 72.4 | 71.4
2015-10-20 18:00 | 65.8 | 69.7667 | 71.8833 | 70.7667
2015-10-20 18:15 | 65.05 | 69.2667 | 71.6333 | 70.2667
2015-10-20 18:30 | 64.3 | 68.7667 | 71.3833 | 69.7667
2015-10-20 18:45 | 63.55 | 68.2667 | 71.1333 | 69.2667
2015-10-20 19:00 | 62.9333 | 67.7667 | 70.7667 | 68.8833
2015-10-20 19:15 | 62.6833 | 67.2667 | 70.2667 | 68.6333
2015-10-20 19:30 | 62.4333 | 66.7667 | 69.7667 | 68.3833
2015-10-20 19:45 | 62.1833 | 66.2667 | 69.2667 | 68.1333
2015-10-20 20:00 | 62 | 65.7667 | 68.8833 | 67.65
2015-10-20 20:15 | 62 | 65.2667 | 68.6333 | 66.9
2015-10-20 20:30 | 62 | 64.7667 | 68.3833 | 66.15
2015-10-20 20:45 | 62 | 64.2667 | 68.1333 | 65.4
2015-10-20 21:00 | 61.9333 | 64 | 67.8833 | 64.7667
2015-10-20 21:15 | 61.6833 | 64 | 67.6333 | 64.2667
2015-10-20 21:30 | 61.4333 | 64 | 67.3833 | 63.7667
2015-10-20 21:45 | 61.1833 | 64 | 67.1333 | 63.2667
2015-10-20 22:00 | 61 | 63.65 | 67 | 62.8833
2015-10-20 22:15 | 61 | 62.9 | 67 | 62.6333
2015-10-20 22:30 | 61 | 62.15 | 67 | 62.3833
2015-10-20 22:45 | 61 | 61.4 | 67 | 62.1333
2015-10-20 23:00 | 60.8667 | 60.8833 | 66.8833 | 62
2015-10-20 23:15 | 60.3667 | 60.6333 | 66.6333 | 62
2015-10-20 23:30 | 59.8667 | 60.3833 | 66.3833 | 62
2015-10-20 23:45 | 59.3667 | 60.1333 | 66.1333 | 62
2015-10-21 | 59 | 59.7667 | 66 | 61.8833
2015-10-21 00:15 | 59 | 59.2667 | 66 | 61.6333
2015-10-21 00:30 | 59 | 58.7667 | 66 | 61.3833
2015-10-21 00:45 | 59 | 58.2667 | 66 | 61.1333
2015-10-21 01:00 | 58.8667 | 57.8833 | 65.8833 | 60.8833
2015-10-21 01:15 | 58.3667 | 57.6333 | 65.6333 | 60.6333
2015-10-21 01:30 | 57.8667 | 57.3833 | 65.3833 | 60.3833
2015-10-21 01:45 | 57.3667 | 57.1333 | 65.1333 | 60.1333
2015-10-21 02:00 | 57 | 56.8833 | 64.8833 | 59.7667
2015-10-21 02:15 | 57 | 56.6333 | 64.6333 | 59.2667
2015-10-21 02:30 | 57 | 56.3833 | 64.3833 | 58.7667
2015-10-21 02:45 | 57 | 56.1333 | 64.1333 | 58.2667
2015-10-21 03:00 | 56.9333 | 55.7667 | 64 | 58
2015-10-21 03:15 | 56.6833 | 55.2667 | 64 | 58
2015-10-21 03:30 | 56.4333 | 54.7667 | 64 | 58
2015-10-21 03:45 | 56.1833 | 54.2667 | 64 | 58
2015-10-21 04:00 | 55.9333 | 54 | 63.7667 | 57.8833
2015-10-21 04:15 | 55.6833 | 54 | 63.2667 | 57.6333
2015-10-21 04:30 | 55.4333 | 54 | 62.7667 | 57.3833
2015-10-21 04:45 | 55.1833 | 54 | 62.2667 | 57.1333
2015-10-21 05:00 | 55.1333 | 53.8833 | 62 | 56.7667
2015-10-21 05:15 | 55.6333 | 53.6333 | 62 | 56.2667
2015-10-21 05:30 | 56.1333 | 53.3833 | 62 | 55.7667
2015-10-21 05:45 | 56.6333 | 53.1333 | 62 | 55.2667
2015-10-21 06:00 | 57.1333 | 53.2333 | 62.3043 | 55.2333
2015-10-21 06:15 | 57.6333 | 53.7333 | 62.9565 | 55.7333
2015-10-21 06:30 | 58.1333 | 54.2333 | 63.3784 | 56.2333
2015-10-21 06:45 | 58.6333 | 54.7333 | 63.7838 | 56.7333
2015-10-21 07:00 | 59.2667 | 55.4667 | 64 | 57.7
2015-10-21 07:15 | 60.2667 | 56.4667 | 64 | 59.2
2015-10-21 07:30 | 61.2667 | 57.4667 | 64 | 60.7
2015-10-21 07:45 | 62.2667 | 58.4667 | 64 | 62.2
2015-10-21 08:00 | 63.1333 | 59.7 | 64 | 63.5833
2015-10-21 08:15 | 63.6333 | 61.2 | 64 | 64.8333
2015-10-21 08:30 | 64.1333 | 62.7 | 64.3947 | 66.0833
2015-10-21 08:45 | 64.6333 | 64.2 | 64.7895 | 67.3333
2015-10-21 09:00 | 65.2 | 65.7 | 65.3889 | 68.2333
2015-10-21 09:15 | 65.95 | 67.2 | 66.2222 | 68.7333
2015-10-21 09:30 | 66.7 | 68.7 | 67.0833 | 69.2333
2015-10-21 09:45 | 67.45 | 70.2 | 68.3333 | 69.7333
2015-10-21 10:00 | 68.0667 | 71.7 | 69 | 70.35
2015-10-21 10:15 | 68.3167 | 73.2 | 69 | 71.1
2015-10-21 10:30 | 68.5667 | 74.7 | 68 | 71.85
2015-10-21 10:45 | 68.8167 | 76.2 | 67.3478 | 72.6
2015-10-21 11:00 | 69.3333 | 77.2333 | 67 | 73.35
2015-10-21 11:15 | 70.5833 | 77.7333 | 68.1224 | 74.1
2015-10-21 11:30 | 71.8333 | 78.2333 | 69.6531 | 74.85
2015-10-21 11:45 | 73.0833 | 78.7333 | 71.1837 | 75.6
2015-10-21 12:00 | 73.9333 | 79.2333 | 72.4667 | 76.1167
2015-10-21 12:15 | 73.6833 | 79.7333 | 73.4667 | 76.3667
2015-10-21 12:30 | 73.4333 | 80.2333 | 74.4667 | 76.6167
2015-10-21 12:45 | 73.1833 | 80.7333 | 75.4667 | 76.8667
2015-10-21 13:00 | 73 | 80.8833 | 76.1167 | 77.2333
2015-10-21 13:15 | 73 | 80.6333 | 76.3667 | 77.7333
2015-10-21 13:30 | 73 | 80.3833 | 76.6167 | 78.2333
2015-10-21 13:45 | 73 | 80.1333 | 76.8667 | 78.7333
2015-10-21 14:00 | 73 | 80.1167 | 77.2333 | 79
2015-10-21 14:15 | 73 | 80.3667 | 77.7333 | 79
2015-10-21 14:30 | 73 | 80.6167 | 78.2333 | 79
2015-10-21 14:45 | 73 | 80.8667 | 78.7333 | 79
2015-10-21 15:00 | 72.4667 | 81 | 78.8833 | 79
2015-10-21 15:15 | 70.4667 | 81 | 78.6333 | 79
2015-10-21 15:30 | 68.4667 | 81 | 78.3833 | 79
2015-10-21 15:45 | 66.4667 | 81 | 78.1333 | 79
2015-10-21 16:00 | 64.7333 | 80.3 | 77.8833 | 78.8833
2015-10-21 16:15 | 63.7333 | 78.8 | 77.6333 | 78.6333
2015-10-21 16:30 | 62.7333 | 77.3 | 77.3833 | 78.3833
2015-10-21 16:45 | 61.7333 | 75.8 | 77.1333 | 78.1333
2015-10-21 17:00 | 61 | 74.4167 | 76.65 | 77.65
2015-10-21 17:15 | 61 | 73.1667 | 75.9 | 76.9
2015-10-21 17:30 | 61 | 71.9167 | 75.15 | 76.15
2015-10-21 17:45 | 61 | 70.6667 | 74.4 | 75.4
2015-10-21 18:00 | 60.9333 | 69.65 | 73.7667 | 74.5333
2015-10-21 18:15 | 60.6833 | 68.9 | 73.2667 | 73.5333
2015-10-21 18:30 | 60.4333 | 68.15 | 72.7667 | 72.5333
2015-10-21 18:45 | 60.1833 | 67.4 | 72.2667 | 71.5333
2015-10-21 19:00 | 60 | 66.7667 | 71.8833 | 70.7667
2015-10-21 19:15 | 60 | 66.2667 | 71.6333 | 70.2667
2015-10-21 19:30 | 60 | 65.7667 | 71.3833 | 69.7667
2015-10-21 19:45 | 60 | 65.2667 | 71.1333 | 69.2667
2015-10-21 20:00 | 59.9333 | 64.7667 | 70.8833 | 69
2015-10-21 20:15 | 59.6833 | 64.2667 | 70.6333 | 69
2015-10-21 20:30 | 59.4333 | 63.7667 | 70.3833 | 69
2015-10-21 20:45 | 59.1833 | 63.2667 | 70.1333 | 69
2015-10-21 21:00 | 59 | 62.8833 | 70 | 68.5333
2015-10-21 21:15 | 59 | 62.6333 | 70 | 67.5333
2015-10-21 21:30 | 59 | 62.3833 | 70 | 66.5333
2015-10-21 21:45 | 59 | 62.1333 | 70 | 65.5333
2015-10-21 22:00 | 58.9333 | 61.8833 | 70.2333 | 64.8833
2015-10-21 22:15 | 58.6833 | 61.6333 | 70.7333 | 64.6333
2015-10-21 22:30 | 58.4333 | 61.3833 | 71.2333 | 64.3833
2015-10-21 22:45 | 58.1833 | 61.1333 | 71.7333 | 64.1333
2015-10-21 23:00 | 58 | 60.65 | 71.2708 | 63.7667
2015-10-21 23:15 | 58 | 59.9 | 69.7083 | 63.2667
2015-10-21 23:30 | 58 | 59.15 | 68.1458 | 62.7667
2015-10-21 23:45 | 58 | 58.4 | 65.6667 | 62.2667
2015-10-22 | 58 | 58 | 62.5333 | 61.7667
2015-10-22 00:15 | 58 | 58 | 61.5333 | 61.2667
2015-10-22 00:30 | 58 | 58 | 60.5333 | 60.7667
2015-10-22 00:45 | 58 | 58 | 59.5333 | 60.2667
2015-10-22 01:00 | 57.9333 | 58 | 59 | 59.7667
2015-10-22 01:15 | 57.6833 | 58 | 59 | 59.2667
2015-10-22 01:30 | 57.4333 | 58 | 58.7667 | 58.7667
2015-10-22 01:45 | 57.1833 | 58 | 58.2667 | 58.2667
2015-10-22 02:00 | 56.9333 | 57.7667 | 57 | 58.1167
2015-10-22 02:15 | 56.6833 | 57.2667 | 57 | 58.3667
2015-10-22 02:30 | 56.4333 | 56.7667 | 57 | 58.6167
2015-10-22 02:45 | 56.1833 | 56.2667 | 57 | 58.8667
2015-10-22 03:00 | 55.8667 | 56 | 57 | 58.8833
2015-10-22 03:15 | 55.3667 | 56 | 57 | 58.6333
2015-10-22 03:30 | 54.8667 | 56 | 57 | 58.3833
2015-10-22 03:45 | 54.3667 | 56 | 57 | 58.1333
2015-10-22 04:00 | 54.0667 | 55.7308 | 57 | 57.8833
2015-10-22 04:15 | 54.3167 | 55.1538 | 57 | 57.6333
2015-10-22 04:30 | 54.5667 | 54.5769 | 57 | 57.3833
2015-10-22 04:45 | 54.8167 | 54 | 57 | 57.1333
2015-10-22 05:00 | 55.0667 | 53.8833 | 57.1167 | 57.1167
2015-10-22 05:15 | 55.3167 | 53.6333 | 57.3667 | 57.3667
2015-10-22 05:30 | 55.5667 | 53.3833 | 57.6167 | 57.6167
2015-10-22 05:45 | 55.8167 | 53.1333 | 57.8667 | 57.8667
2015-10-22 06:00 | 56.0667 | 53.1167 | 57.8833 | 58.1167
2015-10-22 06:15 | 56.3167 | 53.3667 | 57.6333 | 58.3667
2015-10-22 06:30 | 56.5667 | 53.6167 | 57.3833 | 58.6167
2015-10-22 06:45 | 56.8167 | 53.8667 | 57.1333 | 58.8667
2015-10-22 07:00 | 57.1333 | 54.5833 | 57 | 59.4667
2015-10-22 07:15 | 57.6333 | 55.8333 | 57 | 60.4667
2015-10-22 07:30 | 58.1333 | 57.0833 | 57 | 61.4667
2015-10-22 07:45 | 58.6333 | 58.3333 | 57 | 62.4667
2015-10-22 08:00 | 59.2667 | 59.2333 | 57 | 63.5833
2015-10-22 08:15 | 60.2667 | 59.7333 | 57.0732 | 64.8333
2015-10-22 08:30 | 61.2667 | 60.2333 | 57.439 | 66.0833
2015-10-22 08:45 | 62.2667 | 60.7333 | 57.8049 | 67.3333
2015-10-22 09:00 | 63.0667 | 61.4667 | 58.7 | 68.4667
2015-10-22 09:15 | 63.3167 | 62.4667 | 59 | 69.4667
2015-10-22 09:30 | 63.5667 | 63.4667 | 59 | 70.4667
2015-10-22 09:45 | 63.8167 | 64.4667 | 59 | 71.4667
2015-10-22 10:00 | 64.0667 | 65.4667 | 59.2414 | 72.4667
2015-10-22 10:15 | 64.3167 | 66.4667 | 59.7586 | 73.4667
2015-10-22 10:30 | 64.5667 | 67.4667 | 60.2581 | 74.4667
2015-10-22 10:45 | 64.8167 | 68.4667 | 60.7419 | 75.4667
2015-10-22 11:00 | 65.1333 | 69.35 | 61 | 76.35
2015-10-22 11:15 | 65.6333 | 70.1 | 61.4167 | 77.1
2015-10-22 11:30 | 66.1333 | 70.85 | 62.0417 | 77.85
2015-10-22 11:45 | 66.6333 | 71.6 | 62.6667 | 78.6
2015-10-22 12:00 | 67.4 | 72.35 | 63.2333 | 79.1167
2015-10-22 12:15 | 68.9 | 73.1 | 63.7333 | 79.3667
2015-10-22 12:30 | 70.4 | 73.85 | 64.2333 | 79.6167
2015-10-22 12:45 | 71.9 | 74.6 | 64.7333 | 79.8667
2015-10-22 13:00 | 72.8667 | 75 | 65.1167 | 80.2333
2015-10-22 13:15 | 72.3667 | 75 | 65.3667 | 80.7333
2015-10-22 13:30 | 71.8667 | 75 | 65.6167 | 81.2333
2015-10-22 13:45 | 71.3667 | 75 | 65.8667 | 81.7333
2015-10-22 14:00 | 70.9333 | 75.1167 | 66.6512 | 82
2015-10-22 14:15 | 70.6833 | 75.3667 | 68.0465 | 82
2015-10-22 14:30 | 70.4333 | 75.6167 | 69.4419 | 82
2015-10-22 14:45 | 70.1833 | 75.8667 | 70 | 82
2015-10-22 15:00 | 69.9333 | 75.8833 | 69.8833 | 82
2015-10-22 15:15 | 69.6833 | 75.6333 | 69.6333 | 82
2015-10-22 15:30 | 69.4333 | 75.3833 | 69.3833 | 82
2015-10-22 15:45 | 69.1833 | 75.1333 | 69.1333 | 82
2015-10-22 16:00 | 69 | 74.7667 | 69.2333 | 81.65
2015-10-22 16:15 | 69 | 74.2667 | 69.7333 | 80.9
2015-10-22 16:30 | 69 | 73.7667 | 70.2333 | 80.15
2015-10-22 16:45 | 69 | 73.2667 | 70.7333 | 79.4
2015-10-22 17:00 | 68.6 | 72.65 | 70.7667 | 78.65
2015-10-22 17:15 | 67.1 | 71.9 | 70.2667 | 77.9
2015-10-22 17:30 | 65.6 | 71.15 | 69.7667 | 77.15
2015-10-22 17:45 | 64.1 | 70.4 | 69.2667 | 76.4
2015-10-22 18:00 | 63.0667 | 69.7667 | 68.5333 | 75.65
2015-10-22 18:15 | 63.3167 | 69.2667 | 67.5333 | 74.9
2015-10-22 18:30 | 63.5667 | 68.7667 | 66.5333 | 74.15
2015-10-22 18:45 | 63.8167 | 68.2667 | 65.5333 | 73.4
2015-10-22 19:00 | 64.1333 | 67.7667 | 65 | 73
2015-10-22 19:15 | 64.6333 | 67.2667 | 65 | 73
2015-10-22 19:30 | 65.1333 | 66.7667 | 65 | 73
2015-10-22 19:45 | 65.6333 | 66.2667 | 65 | 73
2015-10-22 20:00 | 65.8 | 65.65 | 64.7667 | 72.4167
2015-10-22 20:15 | 65.05 | 64.9 | 64.2667 | 71.1667
2015-10-22 20:30 | 64.3 | 64.15 | 63.7667 | 69.9167
2015-10-22 20:45 | 63.55 | 63.4 | 63.2667 | 68.6667
2015-10-22 21:00 | 62.9333 | 63.1167 | 63 | 67.8833
2015-10-22 21:15 | 62.6833 | 63.3667 | 63 | 67.6333
2015-10-22 21:30 | 62.4333 | 63.6167 | 63 | 67.3833
2015-10-22 21:45 | 62.1833 | 63.8667 | 63 | 67.1333
2015-10-22 22:00 | 61.9333 | 63.65 | 63 | 67
2015-10-22 22:15 | 61.6833 | 62.9 | 63 | 67
2015-10-22 22:30 | 61.4333 | 62.15 | 63.3784 | 67
2015-10-22 22:45 | 61.1833 | 61.4 | 63.7838 | 67
2015-10-22 23:00 | 60.9333 | 60.8833 | 64 | 66.65
2015-10-22 23:15 | 60.6833 | 60.6333 | 64 | 65.9
2015-10-22 23:30 | 60.4333 | 60.3833 | 64 | 65.15
2015-10-22 23:45 | 60.1833 | 60.1333 | 64 | 64.4
2015-10-23 | 59.9333 | 59.8833 | 64 | 63.65
2015-10-23 00:15 | 59.6833 | 59.6333 | 64 | 62.9
2015-10-23 00:30 | 59.4333 | 59.3833 | 64 | 62.15
2015-10-23 00:45 | 59.1833 | 59.1333 | 64 | 61.4
2015-10-23 01:00 | 58.9333 | 58.7667 | 64.1167 | 61
2015-10-23 01:15 | 58.6833 | 58.2667 | 64.3667 | 61
2015-10-23 01:30 | 58.4333 | 57.7667 | 64.6167 | 61
2015-10-23 01:45 | 58.1833 | 57.2667 | 64.8667 | 61
2015-10-23 02:00 | 57.8667 | 56.7667 | 64.8833 | 60.8833
2015-10-23 02:15 | 57.3667 | 56.2667 | 64.6333 | 60.6333
2015-10-23 02:30 | 56.8667 | 55.7667 | 64.3833 | 60.3833
2015-10-23 02:45 | 56.3667 | 55.2667 | 64.1333 | 60.1333
2015-10-23 03:00 | 56 | 55.1167 | 64 | 59.8833
2015-10-23 03:15 | 56 | 55.3667 | 64 | 59.6333
2015-10-23 03:30 | 56 | 55.6167 | 64 | 59.3833
2015-10-23 03:45 | 56 | 55.8667 | 64 | 59.1333
2015-10-23 04:00 | 56 | 55.8833 | 64 | 58.7667
2015-10-23 04:15 | 56 | 55.6333 | 63.8065 | 58.2667
2015-10-23 04:30 | 56 | 55.3833 | 63.3226 | 57.7667
2015-10-23 04:45 | 56 | 55.1333 | 63 | 57.2667
2015-10-23 05:00 | 56.0667 | 55.1167 | 62 | 57
2015-10-23 05:15 | 56.3167 | 55.3667 | 62 | 57
2015-10-23 05:30 | 56.5667 | 55.6167 | 62.3913 | 57
2015-10-23 05:45 | 56.8167 | 55.8667 | 63 | 57
2015-10-23 06:00 | 57 | 56.1167 | 63 | 57.35
2015-10-23 06:15 | 57 | 56.3667 | 62 | 58.1
2015-10-23 06:30 | 57 | 56.6167 | 62 | 58.85
2015-10-23 06:45 | 57 | 56.8667 | 62 | 59.6
2015-10-23 07:00 | 58.0667 | 57.4667 | 62.1167 | 60.35
2015-10-23 07:15 | 58.3167 | 58.4667 | 62.3667 | 61.1
2015-10-23 07:30 | 58.5667 | 59.4667 | 62.6167 | 61.85
2015-10-23 07:45 | 58.8167 | 60.4667 | 62.8667 | 62.6
2015-10-23 08:00 | 59.0667 | 61.7 | 63 | 63.35
2015-10-23 08:15 | 59.3167 | 63.2 | 63 | 64.1
2015-10-23 08:30 | 59.5667 | 64.7 | 63 | 64.85
2015-10-23 08:45 | 59.8167 | 66.2 | 63 | 65.6
2015-10-23 09:00 | 60.2667 | 67.2333 | 63.1207 | 66.5833
2015-10-23 09:15 | 61.2667 | 67.7333 | 63.3793 | 67.8333
2015-10-23 09:30 | 62.2667 | 68.2333 | 63.6379 | 69.0833
2015-10-23 09:45 | 63.2667 | 68.7333 | 63.8966 | 70.3333
2015-10-23 10:00 | 64.2 | 69.35 | 64 | 71.35
2015-10-23 10:15 | 64.95 | 70.1 | 64 | 72.1
2015-10-23 10:30 | 65.7 | 70.85 | 64 | 72.85
2015-10-23 10:45 | 66.45 | 71.6 | 63.8889 | 73.6
2015-10-23 11:00 | 67 | 72.1167 | 63.2414 | 74.35
2015-10-23 11:15 | 67 | 72.3667 | 63.7586 | 75.1
2015-10-23 11:30 | 67 | 72.6167 | 64.8 | 75.85
2015-10-23 11:45 | 67 | 72.8667 | 65 | 76.6
2015-10-23 12:00 | 67.0667 | 73.1167 | 65 | 77.35
2015-10-23 12:15 | 67.3167 | 73.3667 | 65 | 78.1
2015-10-23 12:30 | 67.5667 | 73.6167 | 65.5263 | 78.85
2015-10-23 12:45 | 67.8167 | 73.8667 | 66.8571 | 79.6
2015-10-23 13:00 | 68 | 74.2333 | 67.1167 | 80.1167
2015-10-23 13:15 | 68 | 74.7333 | 67.3667 | 80.3667
2015-10-23 13:30 | 68 | 75.2333 | 67.6167 | 80.6167
2015-10-23 13:45 | 68 | 75.7333 | 67.8667 | 80.8667
2015-10-23 14:00 | 68 | 76.2333 | 68 | 81.2333
2015-10-23 14:15 | 68 | 76.7333 | 68.1905 | 81.7333
2015-10-23 14:30 | 68 | 77.2333 | 68.9048 | 82.2333
2015-10-23 14:45 | 68 | 77.7333 | 69.619 | 82.7333
2015-10-23 15:00 | 67.8667 | 77.7667 | 70 | 82.8833
2015-10-23 15:15 | 67.3667 | 77.2667 | 70 | 82.6333
2015-10-23 15:30 | 66.8667 | 76.7667 | 70 | 82.3833
2015-10-23 15:45 | 66.3667 | 76.2667 | 70.3846 | 82.1333
2015-10-23 16:00 | 66.0667 | 75.65 | 70.7667 | 81.8833
2015-10-23 16:15 | 66.3167 | 74.9 | 70.2667 | 81.6333
2015-10-23 16:30 | 66.5667 | 74.15 | 69.7667 | 81.3833
2015-10-23 16:45 | 66.8167 | 73.4 | 69.2667 | 81.1333
2015-10-23 17:00 | 66.8 | 72.4167 | 69 | 80.5333
2015-10-23 17:15 | 66.05 | 71.1667 | 69 | 79.5333
2015-10-23 17:30 | 65.3 | 69.9167 | 69 | 78.5333
2015-10-23 17:45 | 64.55 | 68.6667 | 69 | 77.5333
2015-10-23 18:00 | 63.8 | 68 | 68.3 | 76.7667
2015-10-23 18:15 | 63.05 | 68 | 66.95 | 76.2667
2015-10-23 18:30 | 62.3 | 68 | 66.575 | 75.7667
2015-10-23 18:45 | 61.55 | 68 | 66.2 | 75.2667
2015-10-23 19:00 | 60.9333 | 67.7667 | 66 | 74.7667
2015-10-23 19:15 | 60.6833 | 67.2667 | 66 | 74.2667
2015-10-23 19:30 | 60.4333 | 66.7667 | 66 | 73.7667
2015-10-23 19:45 | 60.1833 | 66.2667 | 66 | 73.2667
2015-10-23 20:00 | 59.9333 | 65.8833 | 65.6818 | 72.8833
2015-10-23 20:15 | 59.6833 | 65.6333 | 65 | 72.6333
2015-10-23 20:30 | 59.4333 | 65.3833 | 65.0417 | 72.3833
2015-10-23 20:45 | 59.1833 | 65.1333 | 65.6667 | 72.1333
2015-10-23 21:00 | 59 | 64.7667 | 65.16 | 71.65
2015-10-23 21:15 | 59 | 64.2667 | 63.36 | 70.9
2015-10-23 21:30 | 59 | 63.7667 | 63 | 70.15
2015-10-23 21:45 | 59 | 63.2667 | 63 | 69.4
2015-10-23 22:00 | 58.9333 | 62.7667 | 62.8833 | 68.5333
2015-10-23 22:15 | 58.6833 | 62.2667 | 62.6333 | 67.5333
2015-10-23 22:30 | 58.4333 | 61.7667 | 62.3833 | 66.5333
2015-10-23 22:45 | 58.1833 | 61.2667 | 62.1333 | 65.5333
2015-10-23 23:00 | 57.9333 | 60.65 | 61.8833 | 65
2015-10-23 23:15 | 57.6833 | 59.9 | 61.6333 | 65
2015-10-23 23:30 | 57.4333 | 59.15 | 61.3833 | 65
2015-10-23 23:45 | 57.1833 | 58.4 | 61.1333 | 65
2015-10-24 | 57 | 58 | 61.1556 | 64.7667
2015-10-24 00:15 | 57 | 58 | 61.4889 | 64.2667
2015-10-24 00:30 | 57 | 58 | 61.8222 | 63.7667
2015-10-24 00:45 | 57 | 58 | 62 | 63.2667
2015-10-24 01:00 | 56.9333 | 57.8833 | 61.8833 | 62.65
2015-10-24 01:15 | 56.6833 | 57.6333 | 61.6333 | 61.9
2015-10-24 01:30 | 56.4333 | 57.3833 | 61.3833 | 61.15
2015-10-24 01:45 | 56.1833 | 57.1333 | 61.1333 | 60.4
2015-10-24 02:00 | 55.9333 | 56.125 | 60.8 | 59.8833
2015-10-24 02:15 | 55.6833 | 55 | 60.3714 | 59.6333
2015-10-24 02:30 | 55.4333 | 55 | 60.087 | 59.3833
2015-10-24 02:45 | 55.1833 | 55 | 60.7391 | 59.1333
2015-10-24 03:00 | 54.8667 | 55 | 60 | 58.8833
2015-10-24 03:15 | 54.3667 | 55 | 60 | 58.6333
2015-10-24 03:30 | 53.8667 | 54.697 | 60 | 58.3833
2015-10-24 03:45 | 53.3667 | 54.2424 | 60 | 58.1333
2015-10-24 04:00 | 53.1333 | 54 | 60 | 58
2015-10-24 04:15 | 53.6333 | 54 | 60 | 58
2015-10-24 04:30 | 54.1333 | 54 | 60 | 58
2015-10-24 04:45 | 54.6333 | 54 | 60 | 58
2015-10-24 05:00 | 55.1333 | 54.1167 | 60 | 57.7667
2015-10-24 05:15 | 55.6333 | 54.3667 | 60 | 57.2667
2015-10-24 05:30 | 56.1333 | 54.6167 | 60 | 56.7667
2015-10-24 05:45 | 56.6333 | 54.8667 | 60 | 56.2667
2015-10-24 06:00 | 57.0667 | 55.1167 | 60.1207 | 56.1167
2015-10-24 06:15 | 57.3167 | 55.3667 | 60.3793 | 56.3667
2015-10-24 06:30 | 57.5667 | 55.6167 | 60.6379 | 56.6167
2015-10-24 06:45 | 57.8167 | 55.8667 | 60.8966 | 56.8667
2015-10-24 07:00 | 58.0667 | 56.2333 | 61 | 57.7
2015-10-24 07:15 | 58.3167 | 56.7333 | 61 | 59.2
2015-10-24 07:30 | 58.5667 | 57.2333 | 61 | 60.7
2015-10-24 07:45 | 58.8167 | 57.7333 | 59.9412 | 62.2
2015-10-24 08:00 | 59.1333 | 58.35 | 59 | 63.7
2015-10-24 08:15 | 59.6333 | 59.1 | 59 | 65.2
2015-10-24 08:30 | 60.1333 | 59.85 | 59 | 66.7
2015-10-24 08:45 | 60.6333 | 60.6 | 59 | 68.2
2015-10-24 09:00 | 61.2 | 61.4667 | 59 | 69.4667
2015-10-24 09:15 | 61.95 | 62.4667 | 59 | 70.4667
2015-10-24 09:30 | 62.7 | 63.4667 | 59 | 71.4667
2015-10-24 09:45 | 63.45 | 64.4667 | 59 | 72.4667
2015-10-24 10:00 | 64.1333 | 65.7 | 59 | 73.35
2015-10-24 10:15 | 64.6333 | 67.2 | 59 | 74.1
2015-10-24 10:30 | 65.1333 | 68.7 | 59 | 74.85
2015-10-24 10:45 | 65.6333 | 70.2 | 59 | 75.6
2015-10-24 11:00 | 66.0667 | 71 | 59 | 76.35
2015-10-24 11:15 | 66.3167 | 71 | 59 | 77.1
2015-10-24 11:30 | 66.5667 | 71 | 59.303 | 77.85
2015-10-24 11:45 | 66.8167 | 71 | 59.7576 | 78.6
2015-10-24 12:00 | 67.0667 | 71.4667 | 60 | 79.2333
2015-10-24 12:15 | 67.3167 | 72.4667 | 60.2692 | 79.7333
2015-10-24 12:30 | 67.5667 | 73.4667 | 60.5577 | 80.2333
2015-10-24 12:45 | 67.8167 | 74.4667 | 60.8462 | 80.7333
2015-10-24 13:00 | 67.8182 | 75 | 61.2333 | 81.1167
2015-10-24 13:15 | 67.1364 | 75 | 61.7333 | 81.3667
2015-10-24 13:30 | 66.4545 | 75 | 62.2333 | 81.6167
2015-10-24 13:45 | 65.6875 | 76.1579 | 62.7333 | 81.8667
2015-10-24 14:00 | 65.0667 | 77 | 63 | 82.1167
2015-10-24 14:15 | 65.3167 | 77 | 63 | 82.3667
2015-10-24 14:30 | 65.5667 | 77 | 63 | 82.6167
2015-10-24 14:45 | 65.8167 | 77 | 63 | 82.8667
2015-10-24 15:00 | 66.0667 | 76.1833 | 62.8833 | 82.8833
2015-10-24 15:15 | 66.3167 | 74.4333 | 62.6333 | 82.6333
2015-10-24 15:30 | 66.5667 | 72.6833 | 62.3833 | 82.3833
2015-10-24 15:45 | 66.8167 | 70.9333 | 62.1333 | 82.1333
2015-10-24 16:00 | 66.7333 | 70 | 62 | 81.65
2015-10-24 16:15 | 65.7333 | 70 | 62 | 80.9
2015-10-24 16:30 | 64.7333 | 70 | 62 | 80.15
2015-10-24 16:45 | 63.7333 | 70 | 62 | 79.4
2015-10-24 17:00 | 62.8667 | 69.7667 | 61.7667 | 78.65
2015-10-24 17:15 | 62.3667 | 69.2667 | 61.2667 | 77.9
2015-10-24 17:30 | 61.8667 | 68.7667 | 60.7667 | 77.15
2015-10-24 17:45 | 61.3667 | 68.2667 | 60.2667 | 76.4
2015-10-24 18:00 | 60.9333 | 67.5333 | 59.65 | 75.65
2015-10-24 18:15 | 60.6833 | 66.5333 | 58.9 | 74.9
2015-10-24 18:30 | 60.4333 | 65.5333 | 58.15 | 74.15
2015-10-24 18:45 | 60.1833 | 64.5333 | 57.4 | 73.4
2015-10-24 19:00 | 60 | 63.8833 | 56.8833 | 72.65
2015-10-24 19:15 | 60 | 63.6333 | 56.6333 | 71.9
2015-10-24 19:30 | 60 | 63.3833 | 56.3833 | 71.15
2015-10-24 19:45 | 60 | 63.1333 | 56.1333 | 70.4
2015-10-24 20:00 | 60 | 63 | 55.7667 | 69.8833
2015-10-24 20:15 | 60 | 63 | 55.2667 | 69.6333
2015-10-24 20:30 | 60 | 63 | 54.7667 | 69.3833
2015-10-24 20:45 | 60 | 63 | 54.2667 | 69.1333
2015-10-24 21:00 | 59.9333 | 62.8833 | 53.8833 | 68.8833
2015-10-24 21:15 | 59.6833 | 62.6333 | 53.6333 | 68.6333
2015-10-24 21:30 | 59.4333 | 62.3833 | 53.3833 | 68.3833
2015-10-24 21:45 | 59.1833 | 62.1333 | 53.1333 | 68.1333
2015-10-24 22:00 | 58.9333 | 61.8833 | 52.7667 | 67.7667
2015-10-24 22:15 | 58.6833 | 61.6333 | 52.2667 | 67.2667
2015-10-24 22:30 | 58.4333 | 61.3833 | 51.7667 | 66.7667
2015-10-24 22:45 | 58.1833 | 61.1333 | 51.2667 | 66.2667
2015-10-24 23:00 | 58 | 60.8833 | 50.7667 | 65.8833
2015-10-24 23:15 | 58 | 60.6333 | 50.2667 | 65.6333
2015-10-24 23:30 | 58 | 60.3833 | 49.7667 | 65.3833
2015-10-24 23:45 | 58 | 60.1333 | 49.2667 | 65.1333
2015-10-25 | 58 | 59.8833 | 49 | 64.7667
2015-10-25 00:15 | 58 | 59.6333 | 49 | 64.2667
2015-10-25 00:30 | 58 | 59.3833 | 49 | 63.7667
2015-10-25 00:45 | 58 | 59.1333 | 49 | 63.2667
2015-10-25 01:00 | 58 | 59 | 48.8833 | 63
2015-10-25 01:15 | 58 | 59 | 48.6333 | 63
2015-10-25 01:30 | 58 | 59 | 48.3833 | 63
2015-10-25 01:45 | 58 | 59 | 48.1333 | 63
2015-10-25 02:00 | 58.0667 | 58.8833 | 48 | 62.8833
2015-10-25 02:15 | 58.3167 | 58.6333 | 48 | 62.6333
2015-10-25 02:30 | 58.5667 | 58.3833 | 48 | 62.3833
2015-10-25 02:45 | 58.8167 | 58.1333 | 48 | 62.1333
2015-10-25 03:00 | 59 | 58.1167 | 47.7667 | 62
2015-10-25 03:15 | 59 | 58.3667 | 47.2667 | 62
2015-10-25 03:30 | 59 | 58.6167 | 46.7667 | 62
2015-10-25 03:45 | 59 | 58.8667 | 46.2667 | 62
2015-10-25 04:00 | 58.9333 | 58.8833 | 45.7667 | 62
2015-10-25 04:15 | 58.6833 | 58.6333 | 45.2667 | 62
2015-10-25 04:30 | 58.4333 | 58.3833 | 44.7667 | 62
2015-10-25 04:45 | 58.1833 | 58.1333 | 44.2667 | 62
2015-10-25 05:00 | 58.0667 | 58 | 43.8833 | 62.1167
2015-10-25 05:15 | 58.3167 | 58 | 43.6333 | 62.3667
2015-10-25 05:30 | 58.5667 | 58 | 43.3833 | 62.6167
2015-10-25 05:45 | 58.8167 | 58 | 43.1333 | 62.8667
2015-10-25 06:00 | 59 | 58.1167 | 42.7667 | 63
2015-10-25 06:15 | 59 | 58.3667 | 42.2667 | 63
2015-10-25 06:30 | 59 | 58.6167 | 41.7667 | 63
2015-10-25 06:45 | 59 | 58.8667 | 41.2667 | 63
2015-10-25 07:00 | 59.0667 | 59.1167 | 41.5833 | 63.1167
2015-10-25 07:15 | 59.3167 | 59.3667 | 42.8333 | 63.3667
2015-10-25 07:30 | 59.5667 | 59.6167 | 44.0833 | 63.6167
2015-10-25 07:45 | 59.8167 | 59.8667 | 45.3333 | 63.8667
2015-10-25 08:00 | 60.1333 | 60 | 46.5833 | 64.2333
2015-10-25 08:15 | 60.6333 | 60 | 47.8333 | 64.7333
2015-10-25 08:30 | 61.1333 | 60 | 49.0833 | 65.2333
2015-10-25 08:45 | 61.6333 | 60 | 50.3333 | 65.7333
2015-10-25 09:00 | 62.2667 | 60.35 | 51.4667 | 66.2333
2015-10-25 09:15 | 63.2667 | 61.1 | 52.4667 | 66.7333
2015-10-25 09:30 | 64.2667 | 61.85 | 53.4667 | 67.2333
2015-10-25 09:45 | 65.2667 | 62.6 | 54.4667 | 67.7333
2015-10-25 10:00 | 66 | 63.4667 | 55.35 | 68.4667
2015-10-25 10:15 | 66 | 64.4667 | 56.1 | 69.4667
2015-10-25 10:30 | 66 | 65.4667 | 56.85 | 70.4667
2015-10-25 10:45 | 66 | 66.4667 | 57.6 | 71.4667
2015-10-25 11:00 | 66.1333 | 67.35 | 58.2333 | 72.4667
2015-10-25 11:15 | 66.6333 | 68.1 | 58.7333 | 73.4667
2015-10-25 11:30 | 67.1333 | 68.85 | 59.2333 | 74.4667
2015-10-25 11:45 | 67.6333 | 69.6 | 59.7333 | 75.4667
2015-10-25 12:00 | 68.0667 | 70.35 | 60.2333 | 76.1167
2015-10-25 12:15 | 68.3167 | 71.1 | 60.7333 | 76.3667
2015-10-25 12:30 | 68.5667 | 71.85 | 61.2333 | 76.6167
2015-10-25 12:45 | 68.8167 | 72.6 | 61.7333 | 76.8667
2015-10-25 13:00 | 68.8 | 73 | 62.35 | 77.2333
2015-10-25 13:15 | 68.05 | 73 | 63.1 | 77.7333
2015-10-25 13:30 | 67.3 | 73 | 63.85 | 78.2333
2015-10-25 13:45 | 66.55 | 73 | 64.6 | 78.7333
2015-10-25 14:00 | 66.1333 | 73 | 65.1167 | 78.7667
2015-10-25 14:15 | 66.6333 | 73 | 65.3667 | 78.2667
2015-10-25 14:30 | 67.1333 | 73 | 65.6167 | 77.7667
2015-10-25 14:45 | 67.6333 | 73 | 65.8667 | 77.2667
2015-10-25 15:00 | 67.9333 | 72.65 | 66.1167 | 77.1167
2015-10-25 15:15 | 67.6833 | 71.9 | 66.3667 | 77.3667
2015-10-25 15:30 | 67.4333 | 71.15 | 66.6167 | 77.6167
2015-10-25 15:45 | 67.1833 | 70.4 | 66.8667 | 77.8667
2015-10-25 16:00 | 66.9333 | 69.65 | 67 | 77.7667
2015-10-25 16:15 | 66.6833 | 68.9 | 67 | 77.2667
2015-10-25 16:30 | 66.4333 | 68.15 | 67 | 76.7667
2015-10-25 16:45 | 66.1833 | 67.4 | 67 | 76.2667
2015-10-25 17:00 | 65.8 | 66.7667 | 66.4167 | 75.4167
2015-10-25 17:15 | 65.05 | 66.2667 | 65.1667 | 74.1667
2015-10-25 17:30 | 64.3 | 65.7667 | 63.9167 | 72.9167
2015-10-25 17:45 | 63.55 | 65.2667 | 62.6667 | 71.6667
2015-10-25 18:00 | 63 | 64.8833 | 61.1833 | 70.65
2015-10-25 18:15 | 63 | 64.6333 | 59.4333 | 69.9
2015-10-25 18:30 | 63 | 64.3833 | 57.6833 | 69.15
2015-10-25 18:45 | 63 | 64.1333 | 55.9333 | 68.4
2015-10-25 19:00 | 62.9333 | 63.8833 | 55 | 68
2015-10-25 19:15 | 62.6833 | 63.6333 | 55 | 68
2015-10-25 19:30 | 62.4333 | 63.3833 | 55 | 68
2015-10-25 19:45 | 62.1833 | 63.1333 | 55 | 68
2015-10-25 20:00 | 62.0851 | 63 | 54.7667 | 67.65
2015-10-25 20:15 | 62.4043 | 63 | 54.2667 | 66.9
2015-10-25 20:30 | 62.7234 | 63 | 53.7667 | 66.15
2015-10-25 20:45 | 62.8462 | 63 | 53.2667 | 65.4
2015-10-25 21:00 | 62.129 | 62.8833 | 52.8833 | 64.7667
2015-10-25 21:15 | 62.6129 | 62.6333 | 52.6333 | 64.2667
2015-10-25 21:30 | 63 | 62.3833 | 52.3833 | 63.7667
2015-10-25 21:45 | 63 | 62.1333 | 52.1333 | 63.2667
2015-10-25 22:00 | 61.8571 | 61.7667 | 51.65 | 62.7667
2015-10-25 22:15 | 61.3214 | 61.2667 | 50.9 | 62.2667
2015-10-25 22:30 | 61 | 60.7667 | 50.15 | 61.7667
2015-10-25 22:45 | 61 | 60.2667 | 49.4 | 61.2667
2015-10-25 23:00 | 61 | 60.1628 | 48.7667 | 60.65
2015-10-25 23:15 | 61 | 60.5116 | 48.2667 | 59.9
2015-10-25 23:30 | 61 | 60.8605 | 47.7667 | 59.15
2015-10-25 23:45 | 61 | 61 | 47.2667 | 58.4
2015-10-26 | 60.9333 | 61 | 46.8833 | 57.65
2015-10-26 00:15 | 60.6833 | 61 | 46.6333 | 56.9
2015-10-26 00:30 | 60.4333 | 61 | 46.3833 | 56.15
2015-10-26 00:45 | 60.1833 | 61 | 46.1333 | 55.4
2015-10-26 01:00 | 59.9333 | 61 | 45.8833 | 55.2333
2015-10-26 01:15 | 59.6833 | 61 | 45.6333 | 55.7333
2015-10-26 01:30 | 59.4333 | 60.2121 | 45.3833 | 56.2333
2015-10-26 01:45 | 59.1833 | 59.303 | 45.1333 | 56.7333
2015-10-26 02:00 | 59 | 59.1167 | 44.8833 | 56.65
2015-10-26 02:15 | 59 | 59.3667 | 44.6333 | 55.9
2015-10-26 02:30 | 59 | 59.6167 | 44.3833 | 55.15
2015-10-26 02:45 | 59 | 59.8667 | 44.1333 | 54.4
2015-10-26 03:00 | 58.8095 | 59.8833 | 44 | 54
2015-10-26 03:15 | 58.0952 | 59.6333 | 44 | 54
2015-10-26 03:30 | 57.381 | 59.3833 | 44 | 54
2015-10-26 03:45 | 57 | 59.1333 | 44 | 54
2015-10-26 04:00 | 57 | 59 | 43.7667 | 54.1167
2015-10-26 04:15 | 57 | 58.3571 | 43.2667 | 54.3667
2015-10-26 04:30 | 55.9 | 57.2857 | 42.7667 | 54.6167
2015-10-26 04:45 | 55.8 | 57 | 42.2667 | 54.8667
2015-10-26 05:00 | 56.8298 | 57 | 42 | 54.7667
2015-10-26 05:15 | 56.1915 | 57 | 42 | 54.2667
2015-10-26 05:30 | 55.5532 | 56.6053 | 42 | 53.7667
2015-10-26 05:45 | 55.1538 | 56.2105 | 42 | 53.2667
2015-10-26 06:00 | 56.1379 | 55.5625 | 41.7667 | 53
2015-10-26 06:15 | 56.6552 | 55 | 41.2667 | 53
2015-10-26 06:30 | 57 | 55 | 40.7667 | 53
2015-10-26 06:45 | 57 | 55.3846 | 40.2667 | 53
2015-10-26 07:00 | 57.8519 | 56.1167 | 40.9333 | 53.7
2015-10-26 07:15 | 57.2963 | 56.3667 | 42.9333 | 55.2
2015-10-26 07:30 | 57 | 56.6167 | 44.9333 | 56.7
2015-10-26 07:45 | 57 | 56.8667 | 46.9333 | 58.2
2015-10-26 08:00 | 57.0667 | 57 | 48.9333 | 59.7
2015-10-26 08:15 | 57.3167 | 57 | 50.9333 | 61.2
2015-10-26 08:30 | 57.5667 | 57 | 52.9333 | 62.7
2015-10-26 08:45 | 57.8167 | 59.4286 | 54.9333 | 64.2
2015-10-26 09:00 | 58.0976 | 60.4667 | 56.2333 | 65.5833
2015-10-26 09:15 | 58.4634 | 61.4667 | 56.7333 | 66.8333
2015-10-26 09:30 | 58.8293 | 62.4667 | 57.2333 | 68.0833
2015-10-26 09:45 | 59 | 63.4667 | 57.7333 | 69.3333
2015-10-26 10:00 | 59.2759 | 64.4667 | 58.4667 | 70.4667
2015-10-26 10:15 | 60.3103 | 65.4667 | 59.4667 | 71.4667
2015-10-26 10:30 | 61.3448 | 66.4667 | 60.4667 | 72.4667
2015-10-26 10:45 | 62.3793 | 67.4667 | 61.4667 | 73.4667
2015-10-26 11:00 | 62.2353 | 68.35 | 62.4667 | 74.35
2015-10-26 11:15 | 63 | 69.1 | 63.4667 | 75.1
2015-10-26 11:30 | 63 | 69.85 | 64.4667 | 75.85
2015-10-26 11:45 | 63 | 70.6 | 65.4667 | 76.6
2015-10-26 12:00 | 63.2 | 71.4667 | 66.35 | 77.2333
2015-10-26 12:15 | 63.95 | 72.4667 | 67.1 | 77.7333
2015-10-26 12:30 | 64.7 | 73.4667 | 67.85 | 78.2333
2015-10-26 12:45 | 65.45 | 74.4667 | 68.6 | 78.7333
2015-10-26 13:00 | 66.0667 | 75.2333 | 69.1167 | 79.2333
2015-10-26 13:15 | 66.3167 | 75.7333 | 69.3667 | 79.7333
2015-10-26 13:30 | 66.5667 | 76.2333 | 69.6167 | 80.2333
2015-10-26 13:45 | 66.8167 | 76.7333 | 69.8667 | 80.7333
2015-10-26 14:00 | 67.1333 | 77.1167 | 70 | 81.1167
2015-10-26 14:15 | 67.6333 | 77.3667 | 70 | 81.3667
2015-10-26 14:30 | 68.1333 | 77.6167 | 70 | 81.6167
2015-10-26 14:45 | 68.6333 | 77.8667 | 70 | 81.8667
2015-10-26 15:00 | 69.2667 | 77.8833 | 70 | 82.1167
2015-10-26 15:15 | 70.2667 | 77.6333 | 70 | 82.3667
2015-10-26 15:30 | 71.2667 | 77.3833 | 70 | 82.6167
2015-10-26 15:45 | 72.2667 | 77.1333 | 70 | 82.8667
2015-10-26 16:00 | 72.4667 | 76.4167 | 69.8833 | 82.7667
2015-10-26 16:15 | 70.4667 | 75.1667 | 69.6333 | 82.2667
2015-10-26 16:30 | 68.4667 | 73.9167 | 69.3833 | 81.7667
2015-10-26 16:45 | 66.4667 | 72.6667 | 69.1333 | 81.2667
2015-10-26 17:00 | 64.8667 | 71.7667 | 68.1833 | 80.4167
2015-10-26 17:15 | 64.3667 | 71.2667 | 66.4333 | 79.1667
2015-10-26 17:30 | 63.8667 | 70.7667 | 64.6833 | 77.9167
2015-10-26 17:45 | 63.3667 | 70.2667 | 62.9333 | 76.6667
2015-10-26 18:00 | 62.9333 | 69.65 | 61.7667 | 75.4167
2015-10-26 18:15 | 62.6833 | 68.9 | 61.2667 | 74.1667
2015-10-26 18:30 | 62.4333 | 68.15 | 60.7667 | 72.9167
2015-10-26 18:45 | 62.1833 | 67.4 | 60.2667 | 71.6667
2015-10-26 19:00 | 61.9333 | 66.7667 | 59.7667 | 70.5333
2015-10-26 19:15 | 61.6833 | 66.2667 | 59.2667 | 69.5333
2015-10-26 19:30 | 61.4333 | 65.7667 | 58.7667 | 68.5333
2015-10-26 19:45 | 61.1833 | 65.2667 | 58.2667 | 67.5333
2015-10-26 20:00 | 60.9333 | 64.8833 | 57.4167 | 66.65
2015-10-26 20:15 | 60.6833 | 64.6333 | 56.1667 | 65.9
2015-10-26 20:30 | 60.4333 | 64.3833 | 54.9167 | 65.15
2015-10-26 20:45 | 60.1833 | 64.1333 | 53.6667 | 64.4
2015-10-26 21:00 | 59.9333 | 63.7667 | 53.35 | 63.8833
2015-10-26 21:15 | 59.6833 | 63.2667 | 54.1 | 63.6333
2015-10-26 21:30 | 59.4333 | 62.7667 | 54.85 | 63.3833
2015-10-26 21:45 | 59.1833 | 62.2667 | 55.6 | 63.1333
2015-10-26 22:00 | 59 | 61.8833 | 55.7667 | 62.7667
2015-10-26 22:15 | 59 | 61.6333 | 55.2667 | 62.2667
2015-10-26 22:30 | 59 | 61.3833 | 54.7667 | 61.7667
2015-10-26 22:45 | 59 | 61.1333 | 54.2667 | 61.2667
2015-10-26 23:00 | 59.0667 | 61 | 54.4667 | 61.1167
2015-10-26 23:15 | 59.3167 | 61 | 55.4667 | 61.3667
2015-10-26 23:30 | 59.5667 | 61 | 56.4667 | 61.6167
2015-10-26 23:45 | 59.8167 | 61 | 57.4667 | 61.8667
2015-10-27 | 59.9333 | 60.7667 | 57.5333 | 61.7667
2015-10-27 00:15 | 59.6833 | 60.2667 | 56.5333 | 61.2667
2015-10-27 00:30 | 59.4333 | 59.7667 | 55.5333 | 60.7667
2015-10-27 00:45 | 59.1833 | 59.2667 | 54.5333 | 60.2667
2015-10-27 01:00 | 59 | 58.8833 | 54 | 59.8833
2015-10-27 01:15 | 59 | 58.6333 | 54 | 59.6333
2015-10-27 01:30 | 59 | 58.3833 | 54 | 59.3833
2015-10-27 01:45 | 59 | 58.1333 | 54 | 59.1333
2015-10-27 02:00 | 59 | 58.1167 | 54 | 58.8833
2015-10-27 02:15 | 59 | 58.3667 | 54 | 58.6333
2015-10-27 02:30 | 59 | 58.6167 | 54 | 58.3833
2015-10-27 02:45 | 59 | 58.8667 | 54 | 58.1333
2015-10-27 03:00 | 59.0667 | 58.8833 | 54.1167 | 58
2015-10-27 03:15 | 59.3167 | 58.6333 | 54.3667 | 58
2015-10-27 03:30 | 59.5667 | 58.3833 | 54.6167 | 58
2015-10-27 03:45 | 59.8167 | 58.1333 | 54.8667 | 58
2015-10-27 04:00 | 60 | 58 | 55 | 58
2015-10-27 04:15 | 60 | 58 | 55 | 58
2015-10-27 04:30 | 60 | 58 | 55 | 58
2015-10-27 04:45 | 60 | 58 | 55 | 58
2015-10-27 05:00 | 60 | 57.8833 | 55 | 57.8833
2015-10-27 05:15 | 60 | 57.6333 | 55 | 57.6333
2015-10-27 05:30 | 60 | 57.3833 | 55 | 57.3833
2015-10-27 05:45 | 60 | 57.1333 | 55 | 57.1333
2015-10-27 06:00 | 60 | 57 | 55.2333 | 57.1167
2015-10-27 06:15 | 60 | 57 | 55.7333 | 57.3667
2015-10-27 06:30 | 60 | 57 | 56.2333 | 57.6167
2015-10-27 06:45 | 60 | 57 | 56.7333 | 57.8667
2015-10-27 07:00 | 60.1333 | 57.4667 | 57.35 | 58.35
2015-10-27 07:15 | 60.6333 | 58.4667 | 58.1 | 59.1
2015-10-27 07:30 | 61.1333 | 59.4667 | 58.85 | 59.85
2015-10-27 07:45 | 61.6333 | 60.4667 | 59.6 | 60.6
2015-10-27 08:00 | 62.0667 | 61.1167 | 60.8167 | 61.35
2015-10-27 08:15 | 62.3167 | 61.3667 | 62.5667 | 62.1
2015-10-27 08:30 | 62.5667 | 61.6167 | 64.3167 | 62.85
2015-10-27 08:45 | 62.8167 | 61.8667 | 66.0667 | 63.6
2015-10-27 09:00 | 63.0667 | 62.35 | 67.8167 | 64.5833
2015-10-27 09:15 | 63.3167 | 63.1 | 69.5667 | 65.8333
2015-10-27 09:30 | 63.5667 | 63.85 | 71.3167 | 67.0833
2015-10-27 09:45 | 63.8167 | 64.6 | 73.0667 | 68.3333
2015-10-27 10:00 | 64.1333 | 65.2333 | 74.4667 | 69.4667
2015-10-27 10:15 | 64.6333 | 65.7333 | 75.4667 | 70.4667
2015-10-27 10:30 | 65.1333 | 66.2333 | 76.4667 | 71.4667
2015-10-27 10:45 | 65.6333 | 66.7333 | 77.4667 | 72.4667
2015-10-27 11:00 | 66 | 66.8833 | 78.2333 | 73.35
2015-10-27 11:15 | 66 | 66.6333 | 78.7333 | 74.1
2015-10-27 11:30 | 66 | 66.3833 | 79.2333 | 74.85
2015-10-27 11:45 | 66 | 66.1333 | 79.7333 | 75.6
2015-10-27 12:00 | 65.9333 | 66.1167 | 80.2333 | 76.1167
2015-10-27 12:15 | 65.6833 | 66.3667 | 80.7333 | 76.3667
2015-10-27 12:30 | 65.4333 | 66.6167 | 81.2333 | 76.6167
2015-10-27 12:45 | 65.1833 | 66.8667 | 81.7333 | 76.8667
2015-10-27 13:00 | 65.1333 | 67 | 82.2333 | 77.1167
2015-10-27 13:15 | 65.6333 | 67 | 82.7333 | 77.3667
2015-10-27 13:30 | 66.1333 | 67 | 83.2333 | 77.6167
2015-10-27 13:45 | 66.6333 | 67 | 83.7333 | 77.8667
2015-10-27 14:00 | 66.9333 | 67.1167 | 84 | 78
2015-10-27 14:15 | 66.6833 | 67.3667 | 84 | 78
2015-10-27 14:30 | 66.4333 | 67.6167 | 84 | 78
2015-10-27 14:45 | 66.1833 | 67.8667 | 84 | 78
2015-10-27 15:00 | 66.0667 | 68 | 83.8833 | 77.8833
2015-10-27 15:15 | 66.3167 | 68 | 83.6333 | 77.6333
2015-10-27 15:30 | 66.5667 | 68 | 83.3833 | 77.3833
2015-10-27 15:45 | 66.8167 | 68 | 83.1333 | 77.1333
2015-10-27 16:00 | 67.0667 | 68 | 82.7667 | 76.7667
2015-10-27 16:15 | 67.3167 | 68 | 82.2667 | 76.2667
2015-10-27 16:30 | 67.5667 | 68 | 81.7667 | 75.7667
2015-10-27 16:45 | 67.8167 | 68 | 81.2667 | 75.2667
2015-10-27 17:00 | 67.9333 | 68 | 80.3 | 74.65
2015-10-27 17:15 | 67.6833 | 68 | 78.8 | 73.9
2015-10-27 17:30 | 67.4333 | 68 | 77.3 | 73.15
2015-10-27 17:45 | 67.1833 | 68 | 75.8 | 72.4
2015-10-27 18:00 | 66.8 | 67.8833 | 74.0667 | 71.7667
2015-10-27 18:15 | 66.05 | 67.6333 | 72.0667 | 71.2667
2015-10-27 18:30 | 65.3 | 67.3833 | 70.0667 | 70.7667
2015-10-27 18:45 | 64.55 | 67.1333 | 68.0667 | 70.2667
2015-10-27 19:00 | 64 | 66.8833 | 67.1167 | 70
2015-10-27 19:15 | 64 | 66.6333 | 67.3667 | 70
2015-10-27 19:30 | 64 | 66.3833 | 67.6167 | 70
2015-10-27 19:45 | 64 | 66.1333 | 67.8667 | 70
2015-10-27 20:00 | 63.9333 | 65.7667 | 67.7667 | 69.8833
2015-10-27 20:15 | 63.6833 | 65.2667 | 67.2667 | 69.6333
2015-10-27 20:30 | 63.4333 | 64.7667 | 66.7667 | 69.3833
2015-10-27 20:45 | 63.1833 | 64.2667 | 66.2667 | 69.1333
2015-10-27 21:00 | 63 | 63.7667 | 65.7667 | 68.7667
2015-10-27 21:15 | 63 | 63.2667 | 65.2667 | 68.2667
2015-10-27 21:30 | 63 | 62.7667 | 64.7667 | 67.7667
2015-10-27 21:45 | 63 | 62.2667 | 64.2667 | 67.2667
2015-10-27 22:00 | 63.9333 | 61.8833 | 63.65 | 67
2015-10-27 22:15 | 63.6833 | 61.6333 | 62.9 | 67
2015-10-27 22:30 | 63.4333 | 61.3833 | 62.15 | 67
2015-10-27 22:45 | 63.1833 | 61.1333 | 61.4 | 67
2015-10-27 23:00 | 62.9333 | 61.1167 | 61 | 67
2015-10-27 23:15 | 62.6833 | 61.3667 | 61 | 67
2015-10-27 23:30 | 62.4333 | 61.6167 | 61 | 67
2015-10-27 23:45 | 62.1833 | 61.8667 | 61 | 67
2015-10-28 | 62 | 61.8833 | 61 | 66.8833
2015-10-28 00:15 | 62 | 61.6333 | 61 | 66.6333
2015-10-28 00:30 | 62 | 61.3833 | 61 | 66.3833
2015-10-28 00:45 | 62 | 61.1333 | 61 | 66.1333
2015-10-28 01:00 | 62 | 61.1167 | 60.65 | 66
2015-10-28 01:15 | 62 | 61.3667 | 59.9 | 66
2015-10-28 01:30 | 62 | 61.6167 | 59.15 | 66
2015-10-28 01:45 | 62 | 61.8667 | 58.4 | 66
2015-10-28 02:00 | 61.9333 | 61.8833 | 58 | 65.7667
2015-10-28 02:15 | 61.6833 | 61.6333 | 58 | 65.2667
2015-10-28 02:30 | 61.4333 | 61.3833 | 58 | 64.7667
2015-10-28 02:45 | 61.1833 | 61.1333 | 58 | 64.2667
2015-10-28 03:00 | 60.8667 | 60.8833 | 57.8833 | 64
2015-10-28 03:15 | 60.3667 | 60.6333 | 57.6333 | 64
2015-10-28 03:30 | 59.8667 | 60.3833 | 57.3833 | 64
2015-10-28 03:45 | 59.3667 | 60.1333 | 57.1333 | 64
2015-10-28 04:00 | 59.0667 | 59.8293 | 57 | 63.7667
2015-10-28 04:15 | 59.3167 | 59.4634 | 57 | 63.2667
2015-10-28 04:30 | 59.5667 | 59.0976 | 57 | 62.7667
2015-10-28 04:45 | 59.8167 | 59 | 57 | 62.2667
2015-10-28 05:00 | 60 | 59 | 56.1833 | 61.8833
2015-10-28 05:15 | 60 | 59 | 54.4333 | 61.6333
2015-10-28 05:30 | 60 | 59 | 52.6833 | 61.3833
2015-10-28 05:45 | 60 | 59 | 50.9333 | 61.1333
2015-10-28 06:00 | 60 | 58.8833 | 49.8833 | 61
2015-10-28 06:15 | 60 | 58.6333 | 49.6333 | 61
2015-10-28 06:30 | 60 | 58.3833 | 49.3833 | 61
2015-10-28 06:45 | 60 | 58.1333 | 49.1333 | 61
2015-10-28 07:00 | 60.1333 | 58.2333 | 49.35 | 61.2333
2015-10-28 07:15 | 60.6333 | 58.7333 | 50.1 | 61.7333
2015-10-28 07:30 | 61.1333 | 59.2333 | 50.85 | 62.2333
2015-10-28 07:45 | 61.6333 | 59.7333 | 51.6 | 62.7333
2015-10-28 08:00 | 62.1333 | 60.35 | 52.5833 | 63.2333
2015-10-28 08:15 | 62.6333 | 61.1 | 53.8333 | 63.7333
2015-10-28 08:30 | 63.1333 | 61.85 | 55.0833 | 64.2333
2015-10-28 08:45 | 63.6333 | 62.6 | 56.3333 | 64.7333
2015-10-28 09:00 | 64 | 63.4667 | 57.2333 | 65.2333
2015-10-28 09:15 | 64 | 64.4667 | 57.7333 | 65.7333
2015-10-28 09:30 | 64 | 65.4667 | 58.2333 | 66.2333
2015-10-28 09:45 | 64 | 66.4667 | 58.7333 | 66.7333
2015-10-28 10:00 | 64 | 67.4667 | 59.1167 | 67.4667
2015-10-28 10:15 | 64 | 68.4667 | 59.3667 | 68.4667
2015-10-28 10:30 | 64.6286 | 69.4667 | 59.6167 | 69.4667
2015-10-28 10:45 | 65.4857 | 70.4667 | 59.8667 | 70.4667
2015-10-28 11:00 | 66 | 70.7667 | 60.35 | 71.35
2015-10-28 11:15 | 66 | 70.2667 | 61.1 | 72.1
2015-10-28 11:30 | 66 | 69.7667 | 61.85 | 72.85
2015-10-28 11:45 | 66 | 69.2667 | 62.6 | 73.6
2015-10-28 12:00 | 66 | 69.2333 | 63.1167 | 74.1167
2015-10-28 12:15 | 66 | 69.7333 | 63.3667 | 74.3667
2015-10-28 12:30 | 66 | 70.2333 | 63.6167 | 74.6167
2015-10-28 12:45 | 66 | 70.7333 | 63.8667 | 74.8667
2015-10-28 13:00 | 66.2 | 71 | 64.35 | 75.2333
2015-10-28 13:15 | 66.95 | 71 | 65.1 | 75.7333
2015-10-28 13:30 | 67.7 | 71 | 65.85 | 76.2333
2015-10-28 13:45 | 68.45 | 71 | 66.6 | 76.7333
2015-10-28 14:00 | 69.2667 | 71 | 67.1167 | 76.8833
2015-10-28 14:15 | 69.7333 | 71 | 67.3667 | 76.6333
2015-10-28 14:30 | 68.7333 | 71 | 67.6167 | 76.3833
2015-10-28 14:45 | 67.7333 | 71 | 67.8667 | 76.1333
2015-10-28 15:00 | 66.6129 | 70.7667 | 68 | 75.7667
2015-10-28 15:15 | 65.1613 | 70.2667 | 68 | 75.2667
2015-10-28 15:30 | 63.8966 | 69.7667 | 68 | 74.7667
2015-10-28 15:45 | 63.3793 | 69.2667 | 68 | 74.2667
2015-10-28 16:00 | 63 | 68.4167 | 67.8833 | 73.7667
2015-10-28 16:15 | 63 | 67.1667 | 67.6333 | 73.2667
2015-10-28 16:30 | 63 | 65.9167 | 67.3833 | 72.7667
2015-10-28 16:45 | 63 | 64.6667 | 67.1333 | 72.2667
2015-10-28 17:00 | 62.9333 | 63.7667 | 66.4167 | 71.7667
2015-10-28 17:15 | 62.6833 | 63.2667 | 65.1667 | 71.2667
2015-10-28 17:30 | 62.4333 | 62.7667 | 63.9167 | 70.7667
2015-10-28 17:45 | 62.1833 | 62.2667 | 62.6667 | 70.2667
2015-10-28 18:00 | 61.9333 | 62 | 61.65 | 69.7667
2015-10-28 18:15 | 61.6833 | 62 | 60.9 | 69.2667
2015-10-28 18:30 | 61.4333 | 62 | 60.15 | 68.7667
2015-10-28 18:45 | 61.1833 | 62 | 59.4 | 68.2667
2015-10-28 19:00 | 61 | 61.8833 | 58.8833 | 67.7667
2015-10-28 19:15 | 61 | 61.6333 | 58.6333 | 67.2667
2015-10-28 19:30 | 61 | 61.3833 | 58.3833 | 66.7667
2015-10-28 19:45 | 61 | 61.1333 | 58.1333 | 66.2667
2015-10-28 20:00 | 61 | 61.4667 | 57.65 | 65.7667
2015-10-28 20:15 | 61 | 62.4667 | 56.9 | 65.2667
2015-10-28 20:30 | 61 | 62.5333 | 56.15 | 64.7667
2015-10-28 20:45 | 61 | 61.5333 | 55.4 | 64.2667
2015-10-28 21:00 | 60.9333 | 60.8833 | 54.8833 | 63.8833
2015-10-28 21:15 | 60.6833 | 60.6333 | 54.6333 | 63.6333
2015-10-28 21:30 | 60.4333 | 60.3833 | 54.3833 | 63.3833
2015-10-28 21:45 | 60.1833 | 60.1333 | 54.1333 | 63.1333
2015-10-28 22:00 | 60 | 59.8833 | 53.8833 | 63
2015-10-28 22:15 | 60 | 59.6333 | 53.6333 | 63
2015-10-28 22:30 | 60 | 59.3833 | 53.3833 | 63
2015-10-28 22:45 | 60 | 59.1333 | 53.1333 | 63
2015-10-28 23:00 | 59.9333 | 58.8833 | 52.7667 | 62.65
2015-10-28 23:15 | 59.6833 | 58.6333 | 52.2667 | 61.9
2015-10-28 23:30 | 59.4333 | 58.3833 | 51.7667 | 61.15
2015-10-28 23:45 | 59.1833 | 58.1333 | 51.2667 | 60.4
2015-10-29 | 59 | 57.7667 | 51.5833 | 59.8833
2015-10-29 00:15 | 59 | 57.2667 | 52.8333 | 59.6333
2015-10-29 00:30 | 59 | 56.7667 | 54.0833 | 59.3833
2015-10-29 00:45 | 59 | 56.2667 | 55.3333 | 59.1333
2015-10-29 01:00 | 59 | 56 | 56.1167 | 58.8833
2015-10-29 01:15 | 59 | 56 | 56.3667 | 58.6333
2015-10-29 01:30 | 59 | 56 | 56.6167 | 58.3833
2015-10-29 01:45 | 59 | 56 | 56.8667 | 58.1333
2015-10-29 02:00 | 58.9333 | 55.7083 | 56.7667 | 57.8833
2015-10-29 02:15 | 58.6833 | 55.0833 | 56.2667 | 57.6333
2015-10-29 02:30 | 58.4333 | 54 | 55.7667 | 57.3833
2015-10-29 02:45 | 58.1833 | 54 | 55.2667 | 57.1333
2015-10-29 03:00 | 58 | 54 | 55 | 56.8833
2015-10-29 03:15 | 58 | 54 | 55 | 56.6333
2015-10-29 03:30 | 58 | 54 | 55 | 56.3833
2015-10-29 03:45 | 58 | 54 | 55 | 56.1333
2015-10-29 04:00 | 57.9333 | 53.8833 | 54.5333 | 55.8833
2015-10-29 04:15 | 57.6833 | 53.6333 | 53.5333 | 55.6333
2015-10-29 04:30 | 57.4333 | 53.3833 | 52.5333 | 55.3833
2015-10-29 04:45 | 57.1833 | 53.1333 | 51.5333 | 55.1333
2015-10-29 05:00 | 57.0667 | 52.8833 | 51.1167 | 54.8833
2015-10-29 05:15 | 57.3167 | 52.6333 | 51.3667 | 54.6333
2015-10-29 05:30 | 57.5667 | 52.3833 | 51.6167 | 54.3833
2015-10-29 05:45 | 57.8167 | 52.1333 | 51.8667 | 54.1333
2015-10-29 06:00 | 57.9333 | 52.2333 | 52.35 | 53.8833
2015-10-29 06:15 | 57.6833 | 52.7333 | 53.1 | 53.6333
2015-10-29 06:30 | 57.4333 | 53.2333 | 53.85 | 53.3833
2015-10-29 06:45 | 57.1833 | 53.7333 | 54.6 | 53.1333
2015-10-29 07:00 | 57.2667 | 54.4667 | 55.4667 | 53.4667
2015-10-29 07:15 | 58.2667 | 55.4667 | 56.4667 | 54.4667
2015-10-29 07:30 | 59.2667 | 56.4667 | 57.4667 | 55.4667
2015-10-29 07:45 | 60.2667 | 57.4667 | 58.4667 | 56.4667
2015-10-29 08:00 | 61.2 | 58.4667 | 59.35 | 57.35
2015-10-29 08:15 | 61.95 | 59.4667 | 60.1 | 58.1
2015-10-29 08:30 | 62.7 | 60.4667 | 60.85 | 58.85
2015-10-29 08:45 | 63.45 | 61.4667 | 61.6 | 59.6
2015-10-29 09:00 | 64.1333 | 62.4667 | 62.2333 | 60
2015-10-29 09:15 | 64.6333 | 63.4667 | 62.7333 | 59.0625
2015-10-29 09:30 | 65.1333 | 64.4667 | 63.2333 | 59.3784
2015-10-29 09:45 | 65.6333 | 65.4667 | 63.7333 | 59.7838
2015-10-29 10:00 | 66.1333 | 66.1167 | 64.9333 | 60.1522
2015-10-29 10:15 | 66.6333 | 66.3667 | 66.9333 | 60.4783
2015-10-29 10:30 | 67.1333 | 66.6167 | 68.9333 | 60.8043
2015-10-29 10:45 | 67.6333 | 66.8667 | 70.9333 | 60.5714
2015-10-29 11:00 | 68.0667 | 67.2333 | 72.7 | 60.375
2015-10-29 11:15 | 68.3167 | 67.7333 | 74.2 | 61.1786
2015-10-29 11:30 | 68.5667 | 68.2333 | 75.7 | 61.9821
2015-10-29 11:45 | 68.8167 | 68.7333 | 77.2 | 62.7857
2015-10-29 12:00 | 69.1333 | 69.35 | 78.2333 | 63.35
2015-10-29 12:15 | 69.6333 | 70.1 | 78.7333 | 64.1
2015-10-29 12:30 | 70.1333 | 70.85 | 79.2333 | 64.85
2015-10-29 12:45 | 70.6333 | 71.6 | 79.7333 | 65.6
2015-10-29 13:00 | 70.9333 | 72.1167 | 80.2333 | 66.2333
2015-10-29 13:15 | 70.6833 | 72.3667 | 80.7333 | 66.7333
2015-10-29 13:30 | 70.4333 | 72.6167 | 81.2333 | 67.2333
2015-10-29 13:45 | 70.1833 | 72.8667 | 81.7333 | 67.7333
2015-10-29 14:00 | 69.9333 | 73.1167 | 82 | 68.2333
2015-10-29 14:15 | 69.6833 | 73.3667 | 82 | 68.7333
2015-10-29 14:30 | 69.4333 | 73.6167 | 82 | 69.2333
2015-10-29 14:45 | 69.1833 | 73.8667 | 82 | 69.7333
2015-10-29 15:00 | 68.8667 | 73.7667 | 81.8833 | 70
2015-10-29 15:15 | 68.3667 | 73.2667 | 81.6333 | 70
2015-10-29 15:30 | 67.8667 | 72.7667 | 81.3833 | 70
2015-10-29 15:45 | 67.3667 | 72.2667 | 81.1333 | 70
2015-10-29 16:00 | 66.8 | 71.4167 | 80.7667 | 69.8833
2015-10-29 16:15 | 66.05 | 70.1667 | 80.2667 | 69.6333
2015-10-29 16:30 | 65.3 | 68.9167 | 79.7667 | 69.3833
2015-10-29 16:45 | 64.55 | 67.6667 | 79.2667 | 69.1333
2015-10-29 17:00 | 63.9333 | 66.7667 | 78.4167 | 68.65
2015-10-29 17:15 | 63.6833 | 66.2667 | 77.1667 | 67.9
2015-10-29 17:30 | 63.4333 | 65.7667 | 75.9167 | 67.15
2015-10-29 17:45 | 63.1833 | 65.2667 | 74.6667 | 66.4
2015-10-29 18:00 | 62.9333 | 64.8833 | 73.5333 | 65.8833
2015-10-29 18:15 | 62.6833 | 64.6333 | 72.5333 | 65.6333
2015-10-29 18:30 | 62.4333 | 64.3833 | 71.5333 | 65.3833
2015-10-29 18:45 | 62.1833 | 64.1333 | 70.5333 | 65.1333
2015-10-29 19:00 | 61.9333 | 63.65 | 69.7667 | 64.7667
2015-10-29 19:15 | 61.6833 | 62.9 | 69.2667 | 64.2667
2015-10-29 19:30 | 61.4333 | 62.15 | 68.7667 | 63.7667
2015-10-29 19:45 | 61.1833 | 61.4 | 68.2667 | 63.2667
2015-10-29 20:00 | 61 | 61.1167 | 68.1667 | 62.65
2015-10-29 20:15 | 61 | 61.3667 | 68.5238 | 61.9
2015-10-29 20:30 | 61 | 61.6167 | 68.881 | 61.15
2015-10-29 20:45 | 61 | 61.8667 | 67.3333 | 60.4
2015-10-29 21:00 | 60.9333 | 61.7667 | 65.3 | 59.7667
2015-10-29 21:15 | 60.6833 | 61.2667 | 63.8 | 59.2667
2015-10-29 21:30 | 60.4333 | 60.7667 | 62.3 | 58.7667
2015-10-29 21:45 | 60.1833 | 60.2667 | 60.8 | 58.2667
2015-10-29 22:00 | 59.9333 | 59.5333 | 59.8833 | 57.8833
2015-10-29 22:15 | 59.6833 | 58.5333 | 59.6333 | 57.6333
2015-10-29 22:30 | 59.4333 | 57.5333 | 59.3833 | 57.3833
2015-10-29 22:45 | 59.1833 | 56.5333 | 59.1333 | 57.1333
2015-10-29 23:00 | 58.8 | 56 | 59 | 56.8833
2015-10-29 23:15 | 58.05 | 56 | 59 | 56.6333
2015-10-29 23:30 | 57.3 | 56 | 59 | 56.3833
2015-10-29 23:45 | 56.55 | 56 | 59 | 56.1333
2015-10-30 | 56.2667 | 55.7667 | 59 | 56
2015-10-30 00:15 | 57.2667 | 55.2667 | 59 | 56
2015-10-30 00:30 | 58.2667 | 54.7667 | 59 | 56
2015-10-30 00:45 | 59.2667 | 54.2667 | 59 | 56
2015-10-30 01:00 | 59.6667 | 53.8833 | 59 | 56
2015-10-30 01:15 | 58.4167 | 53.6333 | 59 | 56
2015-10-30 01:30 | 57.1667 | 53.3833 | 59 | 56
2015-10-30 01:45 | 55.9167 | 53.1333 | 59 | 56
2015-10-30 02:00 | 55.0667 | 52.8833 | 58.7667 | 55.8833
2015-10-30 02:15 | 55.3167 | 52.6333 | 58.2667 | 55.6333
2015-10-30 02:30 | 55.5667 | 52.3833 | 57.7667 | 55.3833
2015-10-30 02:45 | 55.8167 | 52.1333 | 57.2667 | 55.1333
2015-10-30 03:00 | 55.8 | 51.8833 | 57 | 55
2015-10-30 03:15 | 55.05 | 51.6333 | 57 | 55
2015-10-30 03:30 | 54.3 | 51.3833 | 57 | 55
2015-10-30 03:45 | 53.55 | 51.1333 | 57 | 55
2015-10-30 04:00 | 53.1333 | 51.175 | 57.1167 | 54.8833
2015-10-30 04:15 | 53.6333 | 51.55 | 57.3667 | 54.6333
2015-10-30 04:30 | 54.1333 | 51.925 | 57.6167 | 54.3833
2015-10-30 04:45 | 54.6333 | 51.4 | 57.8667 | 54.1333
2015-10-30 05:00 | 55 | 50.8833 | 57.8511 | 53.8833
2015-10-30 05:15 | 55 | 50.6333 | 57.5319 | 53.6333
2015-10-30 05:30 | 55 | 50.3833 | 57.2128 | 53.3833
2015-10-30 05:45 | 55 | 50.1333 | 57 | 53.1333
2015-10-30 06:00 | 55.0667 | 50.1167 | 57 | 52.8833
2015-10-30 06:15 | 55.3167 | 50.3667 | 57 | 52.6333
2015-10-30 06:30 | 55.5667 | 50.6167 | 57 | 52.3833
2015-10-30 06:45 | 55.8167 | 50.8667 | 56.5333 | 52.1333
2015-10-30 07:00 | 56.3333 | 51.5833 | 56 | 52.5833
2015-10-30 07:15 | 57.5833 | 52.8333 | 56.283 | 53.8333
2015-10-30 07:30 | 58.8333 | 54.0833 | 56.566 | 55.0833
2015-10-30 07:45 | 60.0833 | 55.3333 | 56.8491 | 56.3333
2015-10-30 08:00 | 61.2667 | 56.7 | 57.35 | 57.7
2015-10-30 08:15 | 62.2667 | 58.2 | 58.1 | 59.2
2015-10-30 08:30 | 63.2667 | 59.7 | 58.85 | 60.7
2015-10-30 08:45 | 64.2667 | 61.2 | 59.6 | 62.2
2015-10-30 09:00 | 65.1333 | 62.7 | 60.5833 | 63.4667
2015-10-30 09:15 | 65.6333 | 64.2 | 61.8333 | 64.4667
2015-10-30 09:30 | 66.1333 | 65.7 | 63.0833 | 65.4667
2015-10-30 09:45 | 66.6333 | 67.2 | 64.3333 | 66.4667
2015-10-30 10:00 | 67.0667 | 68.4667 | 65.35 | 67.35
2015-10-30 10:15 | 67.3167 | 69.4667 | 66.1 | 68.1
2015-10-30 10:30 | 67.5667 | 70.4667 | 66.85 | 68.85
2015-10-30 10:45 | 67.8167 | 71.4667 | 67.6 | 69.6
2015-10-30 11:00 | 68.1333 | 72.35 | 68.2333 | 70.1167
2015-10-30 11:15 | 68.6333 | 73.1 | 68.7333 | 70.3667
2015-10-30 11:30 | 69.1333 | 73.85 | 69.2333 | 70.6167
2015-10-30 11:45 | 69.6333 | 74.6 | 69.7333 | 70.8667
2015-10-30 12:00 | 70 | 75.35 | 69.5333 | 71.1167
2015-10-30 12:15 | 70 | 76.1 | 68.5333 | 71.3667
2015-10-30 12:30 | 70 | 76.85 | 67.5333 | 71.6167
2015-10-30 12:45 | 70 | 77.6 | 66.5333 | 71.8667
2015-10-30 13:00 | 70.4 | 78.2333 | 66.5833 | 72.1167
2015-10-30 13:15 | 71.9 | 78.7333 | 67.8333 | 72.3667
2015-10-30 13:30 | 73.4 | 79.2333 | 69.0833 | 72.6167
2015-10-30 13:45 | 74.9 | 79.7333 | 70.3333 | 72.8667
2015-10-30 14:00 | 75.9333 | 80 | 71.1167 | 73.2333
2015-10-30 14:15 | 75.6833 | 80 | 71.3667 | 73.7333
2015-10-30 14:30 | 75.4333 | 80 | 71.6167 | 74.2333
2015-10-30 14:45 | 75.1833 | 80 | 71.8667 | 74.7333
2015-10-30 15:00 | 74.7333 | 79.7667 | 71.5333 | 75
2015-10-30 15:15 | 73.7333 | 79.2667 | 70.5333 | 75
2015-10-30 15:30 | 72.7333 | 78.7667 | 69.5333 | 75
2015-10-30 15:45 | 71.7333 | 78.2667 | 68.5333 | 75
2015-10-30 16:00 | 70.8667 | 77.65 | 67.5333 | 74.7667
2015-10-30 16:15 | 70.3667 | 76.9 | 66.5333 | 74.2667
2015-10-30 16:30 | 69.8667 | 76.15 | 65.5333 | 73.7667
2015-10-30 16:45 | 69.3667 | 75.4 | 64.5333 | 73.2667
2015-10-30 17:00 | 68.7333 | 74.3 | 63.7667 | 72.65
2015-10-30 17:15 | 67.7333 | 72.8 | 63.2667 | 71.9
2015-10-30 17:30 | 66.7333 | 71.3 | 62.7667 | 71.15
2015-10-30 17:45 | 65.7333 | 69.8 | 62.2667 | 70.4
2015-10-30 18:00 | 64.9333 | 69 | 61.5333 | 69.7667
2015-10-30 18:15 | 64.6833 | 69 | 60.5333 | 69.2667
2015-10-30 18:30 | 64.4333 | 69 | 59.5333 | 68.7667
2015-10-30 18:45 | 64.1833 | 69 | 58.5333 | 68.2667
2015-10-30 19:00 | 63.9333 | 68.7667 | 58 | 67.7667
2015-10-30 19:15 | 63.6833 | 68.2667 | 58 | 67.2667
2015-10-30 19:30 | 63.4333 | 67.7667 | 58 | 66.7667
2015-10-30 19:45 | 63.1833 | 67.2667 | 58 | 66.2667
2015-10-30 20:00 | 62.9333 | 66.5333 | 57.6818 | 65.8833
2015-10-30 20:15 | 62.6833 | 65.5333 | 57 | 65.6333
2015-10-30 20:30 | 62.4333 | 64.5333 | 56.3182 | 65.3833
2015-10-30 20:45 | 62.1833 | 63.5333 | 55.4286 | 65.1333
2015-10-30 21:00 | 61.9333 | 63.1167 | 55 | 64.5333
2015-10-30 21:15 | 61.6833 | 63.3667 | 54.95 | 63.5333
2015-10-30 21:30 | 61.4333 | 63.6167 | 54.575 | 62.5333
2015-10-30 21:45 | 61.1833 | 63.8667 | 54.2 | 61.5333
2015-10-30 22:00 | 61 | 63.5333 | 54.1167 | 60.8833
2015-10-30 22:15 | 61 | 62.5333 | 54.3667 | 60.6333
2015-10-30 22:30 | 61 | 61.5333 | 54.6167 | 60.3833
2015-10-30 22:45 | 61 | 60.5333 | 54.8667 | 60.1333
2015-10-30 23:00 | 60.9333 | 60 | 55.1167 | 59.8833
2015-10-30 23:15 | 60.6833 | 60 | 55.3667 | 59.6333
2015-10-30 23:30 | 60.4333 | 60 | 55.6167 | 59.3833
2015-10-30 23:45 | 60.1833 | 60 | 55.8667 | 59.1333
2015-10-31 | 59.9333 | 59.7667 | 55.8833 | 58.8833
2015-10-31 00:15 | 59.6833 | 59.2667 | 55.6333 | 58.6333
2015-10-31 00:30 | 59.4333 | 58.7667 | 55.3833 | 58.3833
2015-10-31 00:45 | 59.1833 | 58.2667 | 55.1333 | 58.1333
2015-10-31 01:00 | 58.9333 | 57.7667 | 54.8833 | 57.7667
2015-10-31 01:15 | 58.6833 | 57.2667 | 54.6333 | 57.2667
2015-10-31 01:30 | 58.4333 | 56.7667 | 54.3833 | 56.7667
2015-10-31 01:45 | 58.1833 | 56.2667 | 54.1333 | 56.2667
2015-10-31 02:00 | 58 | 56 | 53.65 | 55.8833
2015-10-31 02:15 | 58 | 56 | 52.9 | 55.6333
2015-10-31 02:30 | 58 | 56 | 52.15 | 55.3833
2015-10-31 02:45 | 58 | 56 | 51.4 | 55.1333
2015-10-31 03:00 | 57.9333 | 55.8833 | 51.1167 | 55.2333
2015-10-31 03:15 | 57.6833 | 55.6333 | 51.3667 | 55.7333
2015-10-31 03:30 | 57.4333 | 55.3833 | 51.6167 | 56.2333
2015-10-31 03:45 | 57.1833 | 55.1333 | 51.8667 | 56.7333
2015-10-31 04:00 | 57 | 54.8205 | 51.8833 | 56.65
2015-10-31 04:15 | 57 | 54.4359 | 51.6333 | 55.9
2015-10-31 04:30 | 57 | 54.0513 | 51.3833 | 55.15
2015-10-31 04:45 | 57 | 53.381 | 51.1333 | 54.4
2015-10-31 05:00 | 57.0667 | 53 | 51 | 54
2015-10-31 05:15 | 57.3167 | 53 | 51 | 54
2015-10-31 05:30 | 57.5667 | 53 | 51 | 54
2015-10-31 05:45 | 57.8167 | 53 | 51 | 54
2015-10-31 06:00 | 57.9333 | 53.2333 | 51.1167 | 54
2015-10-31 06:15 | 57.6833 | 53.7333 | 51.3667 | 54
2015-10-31 06:30 | 57.4333 | 54.2333 | 51.6167 | 54
2015-10-31 06:45 | 57.1833 | 54.7333 | 51.8667 | 54
2015-10-31 07:00 | 57.3333 | 55.4667 | 51.65 | 54.8167
2015-10-31 07:15 | 58.5833 | 56.4667 | 51.05 | 56.5667
2015-10-31 07:30 | 59.8333 | 57.4667 | 51.425 | 58.3167
2015-10-31 07:45 | 61.0833 | 58.4667 | 51.8 | 60.0667
2015-10-31 08:00 | 62.2 | 59.8167 | 52.35 | 61.4667
2015-10-31 08:15 | 62.95 | 61.5667 | 53.1 | 62.4667
2015-10-31 08:30 | 63.7 | 63.3167 | 53.85 | 63.4667
2015-10-31 08:45 | 64.45 | 65.0667 | 54.6 | 64.4667
2015-10-31 09:00 | 65.0667 | 66.5833 | 55.35 | 65.4667
2015-10-31 09:15 | 65.3167 | 67.8333 | 56.1 | 66.4667
2015-10-31 09:30 | 65.5667 | 69.0833 | 56.85 | 67.4667
2015-10-31 09:45 | 65.8167 | 70.3333 | 57.6 | 68.4667
2015-10-31 10:00 | 66.1333 | 71.8167 | 58.4667 | 69.5833
2015-10-31 10:15 | 66.6333 | 73.5667 | 59.4667 | 70.8333
2015-10-31 10:30 | 67.1333 | 75.3167 | 60.4667 | 72.0833
2015-10-31 10:45 | 67.6333 | 77.0667 | 61.4667 | 73.3333
2015-10-31 11:00 | 68.3333 | 78.5833 | 62.35 | 74.35
2015-10-31 11:15 | 69.5833 | 79.8333 | 63.1 | 75.1
2015-10-31 11:30 | 70.8333 | 81.0833 | 63.85 | 75.85
2015-10-31 11:45 | 72.0833 | 82.3333 | 64.6 | 76.6
2015-10-31 12:00 | 72.8 | 83.1167 | 65 | 77.2333
2015-10-31 12:15 | 72.05 | 83.3667 | 65 | 77.7333
2015-10-31 12:30 | 71.3 | 83.6167 | 65 | 78.2333
2015-10-31 12:45 | 70.55 | 83.8667 | 65 | 78.7333
2015-10-31 13:00 | 69.9333 | 83.7667 | 65.2333 | 79.2333
2015-10-31 13:15 | 69.6833 | 83.2667 | 65.7333 | 79.7333
2015-10-31 13:30 | 69.4333 | 82.7667 | 66.2333 | 80.2333
2015-10-31 13:45 | 69.1833 | 82.2667 | 66.7333 | 80.7333
2015-10-31 14:00 | 69.0667 | 81.7667 | 67 | 81
2015-10-31 14:15 | 69.3167 | 81.2667 | 67 | 81
2015-10-31 14:30 | 69.5667 | 80.7667 | 67 | 81
2015-10-31 14:45 | 69.8167 | 80.2667 | 67 | 81
2015-10-31 15:00 | 69.6 | 79.5333 | 67 | 81
2015-10-31 15:15 | 68.1 | 78.5333 | 67 | 81
2015-10-31 15:30 | 66.6 | 77.5333 | 67 | 81
2015-10-31 15:45 | 65.1 | 76.5333 | 67 | 81
2015-10-31 16:00 | 63.8667 | 75.4167 | 67 | 80.8833
2015-10-31 16:15 | 63.3667 | 74.1667 | 67 | 80.6333
2015-10-31 16:30 | 62.8667 | 72.9167 | 67 | 80.3833
2015-10-31 16:45 | 62.3667 | 71.6667 | 67 | 80.1333
2015-10-31 17:00 | 61.9333 | 70.4167 | 66.5333 | 79.4167
2015-10-31 17:15 | 61.6833 | 69.1667 | 65.5333 | 78.1667
2015-10-31 17:30 | 61.4333 | 67.9167 | 64.5333 | 76.9167
2015-10-31 17:45 | 61.1833 | 66.6667 | 63.5333 | 75.6667
2015-10-31 18:00 | 60.9333 | 65.65 | 62.3 | 74.65
2015-10-31 18:15 | 60.6833 | 64.9 | 60.8 | 73.9
2015-10-31 18:30 | 60.4333 | 64.15 | 59.3 | 73.15
2015-10-31 18:45 | 60.1833 | 63.4 | 57.8 | 72.4
2015-10-31 19:00 | 60.1333 | 62.8833 | 56.8833 | 71.4167
2015-10-31 19:15 | 60.6333 | 62.6333 | 56.6333 | 70.1667
2015-10-31 19:30 | 61 | 62.3833 | 56.3833 | 68.9167
2015-10-31 19:45 | 61 | 62.1333 | 56.1333 | 67.6667
2015-10-31 20:00 | 60.9333 | 62.5 | 56 | 66.5333
2015-10-31 20:15 | 60.6833 | 62.6522 | 56 | 65.5333
2015-10-31 20:30 | 60.4333 | 62 | 56 | 64.5333
2015-10-31 20:45 | 60.1833 | 61.3478 | 56 | 63.5333
2015-10-31 21:00 | 60.0667 | 61 | 55.7667 | 62.8833
2015-10-31 21:15 | 60.3167 | 61 | 55.2667 | 62.6333
2015-10-31 21:30 | 60.5667 | 61 | 54.7667 | 62.3833
2015-10-31 21:45 | 60.8167 | 61 | 54.2667 | 62.1333
2015-10-31 22:00 | 61 | 61 | 53.8833 | 62
2015-10-31 22:15 | 61 | 61 | 53.6333 | 62
2015-10-31 22:30 | 61 | 61 | 53.3833 | 62
2015-10-31 22:45 | 61 | 61 | 53.1333 | 62
2015-10-31 23:00 | 61 | 61 | 52.8833 | 62
2015-10-31 23:15 | 61 | 61 | 52.6333 | 62
2015-10-31 23:30 | 61 | 61 | 52.3833 | 62
2015-10-31 23:45 | 61 | 61 | 52.1333 | 62

## Category Lists (hidden)
Facility Type |  | Dim % | Y/N | Precool °F | Reset °F | Duty Cycle | HVAC DR Type | HVAC Type | PreviousDR
Office | OFF | 20 | Yes | 0 | 2 | 15 | HVAC Temp Reset | Rooftop Unit | Yes
Retail | RETL | 30 | No | -2 | 4 | 20 | Duty Cycle | Central Plant | No
|  | 40 |  |  | 6 | 30

## Climate Zones
ZIP | COUNTY_NAME | CECZONE | PG&E CEUS CZ | SCE CEUS CZ | COUNTY_NAME | PG&E CEUS Climate Zone | SCE CEUS Climate Zone
94501 | Alameda | 3 | 4 |  | Alameda | 4
94502 | Alameda | 3 | 4 |  | Alpine | 14
94536 | Alameda | 3 | 4 |  | Amador | 2
94538 | Alameda | 3 | 4 |  | Butte | 3
94539 | Alameda | 3 | 4 |  | Calaveras
94541 | Alameda | 3 | 4 |  | Colusa | 3
94542 | Alameda | 3 | 4 |  | Contra Costa | 4
94544 | Alameda | 3 | 4 |  | Del Norte | 14
94545 | Alameda | 3 | 4 |  | El Dorado | 1
94546 | Alameda | 3 | 4 |  | Fresno | 3 | 7
94552 | Alameda | 3 | 4 |  | Glenn | 3
94555 | Alameda | 3 | 4 |  | Humboldt | 1
94560 | Alameda | 3 | 4 |  | Imperial
94568 | Alameda | 3 | 4 |  | Inyo
94577 | Alameda | 3 | 4 |  | Kern | 3 | 7
94578 | Alameda | 3 | 4 |  | Kings | 3
94579 | Alameda | 3 | 4 |  | Lake | 1
94580 | Alameda | 3 | 4 |  | Lassen | 1
94583 | Alameda | 3 | 4 |  | Los Angeles
94586 | Alameda | 3 | 4 |  | Madera | 3 | 7
94587 | Alameda | 3 | 4 |  | Marin | 5
94588 | Alameda | 3 | 4 |  | Mariposa | 3
94601 | Alameda | 3 | 4 |  | Mendocino | 1
94602 | Alameda | 3 | 4 |  | Merced | 3 | 7
94603 | Alameda | 3 | 4 |  | Modoc | 14
94605 | Alameda | 3 | 4 |  | Mono | 12 | 12
94606 | Alameda | 3 | 4 |  | Monterey | 4
94607 | Alameda | 3 | 4 |  | Napa | 4
94608 | Alameda | 3 | 4 |  | Nevada | 1
94609 | Alameda | 3 | 4 |  | Orange
94610 | Alameda | 3 | 4 |  | Placer | 2
94611 | Alameda | 3 | 4 |  | Plumas | 1
94612 | Alameda | 3 | 4 |  | Riverside
94613 | Alameda | 3 | 4 |  | Sacramento | 6
94618 | Alameda | 3 | 4 |  | San Mateo | 5
94619 | Alameda | 3 | 4 |  | San Luis Obispo | 4
94621 | Alameda | 3 | 4 |  | San Diego
94702 | Alameda | 3 | 4 |  | San Bernardino
94703 | Alameda | 3 | 4 |  | San Benito | 4
94704 | Alameda | 3 | 4 |  | San Joaquin | 2
94705 | Alameda | 3 | 4 |  | San Francicso | 5
94706 | Alameda | 3 | 4 |  | Santa Barbara | 4
94707 | Alameda | 3 | 4 |  | Santa Clara | 4
94708 | Alameda | 3 | 4 |  | Santa Cruz | 4
94709 | Alameda | 3 | 4 |  | Shasta | 3
94710 | Alameda | 3 | 4 |  | Sierra | 1
94720 | Alameda | 3 | 4 |  | Siskiyou | 14
95035 | Alameda | 3 | 4 |  | Solano | 4
94550 | Alameda | 4 | 4 |  | Sonoma | 4
94586 | Alameda | 4 | 4 |  | Stanislaus | 3
94539 | Alameda | 4 | 4 |  | Sutter | 3
94538 | Alameda | 4 | 4 |  | Tehama | 3
95035 | Alameda | 4 | 4 |  | Trinity | 1
94514 | Alameda | 12 | 4 |  | Tulare
94539 | Alameda | 12 | 4 |  | Tuolumne | 1 | 12
94546 | Alameda | 12 | 4 |  | Ventura
94550 | Alameda | 12 | 4 |  | Yolo | 2
94551 | Alameda | 12 | 4 |  | Yuba | 3
94552 | Alameda | 12 | 4
94566 | Alameda | 12 | 4
94568 | Alameda | 12 | 4
94583 | Alameda | 12 | 4
94586 | Alameda | 12 | 4
94588 | Alameda | 12 | 4
94611 | Alameda | 12 | 4
94704 | Alameda | 12 | 4
94705 | Alameda | 12 | 4
94708 | Alameda | 12 | 4
95377 | Alameda | 12 | 4
95391 | Alameda | 12 | 4
44 | Alpine | 16 | 14
95223 | Alpine | 16 | 14
96120 | Alpine | 16 | 14
95255 | Amador | 12 | 2
95629 | Amador | 12 | 2
95640 | Amador | 12 | 2
95642 | Amador | 12 | 2
95665 | Amador | 12 | 2
95666 | Amador | 12 | 2
95669 | Amador | 12 | 2
95685 | Amador | 12 | 2
95689 | Amador | 12 | 2
95255 | Amador | 16 | 2
95629 | Amador | 16 | 2
95666 | Amador | 16 | 2
95689 | Amador | 16 | 2
95901 | Butte | 11 | 3
95914 | Butte | 11 | 3
95916 | Butte | 11 | 3
95917 | Butte | 11 | 3
95926 | Butte | 11 | 3
95928 | Butte | 11 | 3
95938 | Butte | 11 | 3
95941 | Butte | 11 | 3
95942 | Butte | 11 | 3
95943 | Butte | 11 | 3
95948 | Butte | 11 | 3
95954 | Butte | 11 | 3
95965 | Butte | 11 | 3
95966 | Butte | 11 | 3
95968 | Butte | 11 | 3
95969 | Butte | 11 | 3
95973 | Butte | 11 | 3
95916 | Butte | 16 | 3
95941 | Butte | 16 | 3
95942 | Butte | 16 | 3
95954 | Butte | 16 | 3
95965 | Butte | 16 | 3
95966 | Butte | 16 | 3
95973 | Butte | 16 | 3
95222 | Calaveras | 12
95223 | Calaveras | 12
95228 | Calaveras | 12
95230 | Calaveras | 12
95232 | Calaveras | 12
95236 | Calaveras | 12
95245 | Calaveras | 12
95246 | Calaveras | 12
95247 | Calaveras | 12
95249 | Calaveras | 12
95251 | Calaveras | 12
95252 | Calaveras | 12
95255 | Calaveras | 12
95257 | Calaveras | 12
95223 | Calaveras | 16
95245 | Calaveras | 16
95246 | Calaveras | 16
95247 | Calaveras | 16
95255 | Calaveras | 16
95257 | Calaveras | 16
95423 | Colusa | 2 | 3
95979 | Colusa | 2 | 3
95987 | Colusa | 2 | 3
95423 | Colusa | 11 | 3
95912 | Colusa | 11 | 3
95932 | Colusa | 11 | 3
95955 | Colusa | 11 | 3
95970 | Colusa | 11 | 3
95979 | Colusa | 11 | 3
95987 | Colusa | 11 | 3
95912 | Colusa | 12 | 3
95987 | Colusa | 12 | 3
95979 | Colusa | 16 | 3
94525 | Contra Costa | 3 | 4
94530 | Contra Costa | 3 | 4
94547 | Contra Costa | 3 | 4
94553 | Contra Costa | 3 | 4
94556 | Contra Costa | 3 | 4
94563 | Contra Costa | 3 | 4
94564 | Contra Costa | 3 | 4
94572 | Contra Costa | 3 | 4
94583 | Contra Costa | 3 | 4
94611 | Contra Costa | 3 | 4
94707 | Contra Costa | 3 | 4
94708 | Contra Costa | 3 | 4
94801 | Contra Costa | 3 | 4
94803 | Contra Costa | 3 | 4
94804 | Contra Costa | 3 | 4
94805 | Contra Costa | 3 | 4
94806 | Contra Costa | 3 | 4
94505 | Contra Costa | 12 | 4
94506 | Contra Costa | 12 | 4
94507 | Contra Costa | 12 | 4
94509 | Contra Costa | 12 | 4
94513 | Contra Costa | 12 | 4
94514 | Contra Costa | 12 | 4
94517 | Contra Costa | 12 | 4
94518 | Contra Costa | 12 | 4
94519 | Contra Costa | 12 | 4
94520 | Contra Costa | 12 | 4
94521 | Contra Costa | 12 | 4
94523 | Contra Costa | 12 | 4
94525 | Contra Costa | 12 | 4
94526 | Contra Costa | 12 | 4
94528 | Contra Costa | 12 | 4
94530 | Contra Costa | 12 | 4
94531 | Contra Costa | 12 | 4
94547 | Contra Costa | 12 | 4
94548 | Contra Costa | 12 | 4
94549 | Contra Costa | 12 | 4
94551 | Contra Costa | 12 | 4
94553 | Contra Costa | 12 | 4
94556 | Contra Costa | 12 | 4
94561 | Contra Costa | 12 | 4
94563 | Contra Costa | 12 | 4
94564 | Contra Costa | 12 | 4
94565 | Contra Costa | 12 | 4
94568 | Contra Costa | 12 | 4
94569 | Contra Costa | 12 | 4
94572 | Contra Costa | 12 | 4
94582 | Contra Costa | 12 | 4
94583 | Contra Costa | 12 | 4
94585 | Contra Costa | 12 | 4
94595 | Contra Costa | 12 | 4
94596 | Contra Costa | 12 | 4
94597 | Contra Costa | 12 | 4
94598 | Contra Costa | 12 | 4
94611 | Contra Costa | 12 | 4
94708 | Contra Costa | 12 | 4
94803 | Contra Costa | 12 | 4
49 | Del Norte | 16 | 14
95531 | Del Norte | 16 | 14
95543 | Del Norte | 16 | 14
95548 | Del Norte | 16 | 14
95567 | Del Norte | 16 | 14
95543 | Del Norte | 1 | 14
95567 | Del Norte | 1 | 14
95531 | Del Norte | 1 | 14
49 | Del Norte | 1 | 14
95548 | Del Norte | 1 | 14
95614 | El Dorado | 11 | 1
95635 | El Dorado | 11 | 1
95664 | El Dorado | 11 | 1
95614 | El Dorado | 12 | 1
95619 | El Dorado | 12 | 1
95623 | El Dorado | 12 | 1
95629 | El Dorado | 12 | 1
95633 | El Dorado | 12 | 1
95634 | El Dorado | 12 | 1
95635 | El Dorado | 12 | 1
95636 | El Dorado | 12 | 1
95651 | El Dorado | 12 | 1
95664 | El Dorado | 12 | 1
95667 | El Dorado | 12 | 1
95672 | El Dorado | 12 | 1
95682 | El Dorado | 12 | 1
95684 | El Dorado | 12 | 1
95709 | El Dorado | 12 | 1
95726 | El Dorado | 12 | 1
95762 | El Dorado | 12 | 1
51 | El Dorado | 16 | 1
52 | El Dorado | 16 | 1
95629 | El Dorado | 16 | 1
95633 | El Dorado | 16 | 1
95634 | El Dorado | 16 | 1
95635 | El Dorado | 16 | 1
95636 | El Dorado | 16 | 1
95666 | El Dorado | 16 | 1
95667 | El Dorado | 16 | 1
95684 | El Dorado | 16 | 1
95709 | El Dorado | 16 | 1
95720 | El Dorado | 16 | 1
95721 | El Dorado | 16 | 1
95726 | El Dorado | 16 | 1
95735 | El Dorado | 16 | 1
96142 | El Dorado | 16 | 1
96150 | El Dorado | 16 | 1
93622 | Fresno | 4 | 3 | 7
93640 | Fresno | 4 | 3 | 7
95043 | Fresno | 4 | 3 | 7
93210 | Fresno | 4 | 3 | 7
93620 | Fresno | 12 | 3 | 7
93622 | Fresno | 12 | 3 | 7
93210 | Fresno | 13 | 3 | 7
93234 | Fresno | 13 | 3 | 7
93242 | Fresno | 13 | 3 | 7
93602 | Fresno | 13 | 3 | 7
93608 | Fresno | 13 | 3 | 7
93609 | Fresno | 13 | 3 | 7
93611 | Fresno | 13 | 3 | 7
93612 | Fresno | 13 | 3 | 7
93616 | Fresno | 13 | 3 | 7
93618 | Fresno | 13 | 3 | 7
93619 | Fresno | 13 | 3 | 7
93620 | Fresno | 13 | 3 | 7
93621 | Fresno | 13 | 3 | 7
93622 | Fresno | 13 | 3 | 7
93625 | Fresno | 13 | 3 | 7
93626 | Fresno | 13 | 3 | 7
93627 | Fresno | 13 | 3 | 7
93630 | Fresno | 13 | 3 | 7
93631 | Fresno | 13 | 3 | 7
93633 | Fresno | 13 | 3 | 7
93636 | Fresno | 13 | 3 | 7
93637 | Fresno | 13 | 3 | 7
93640 | Fresno | 13 | 3 | 7
93641 | Fresno | 13 | 3 | 7
93646 | Fresno | 13 | 3 | 7
93647 | Fresno | 13 | 3 | 7
93648 | Fresno | 13 | 3 | 7
93650 | Fresno | 13 | 3 | 7
93651 | Fresno | 13 | 3 | 7
93652 | Fresno | 13 | 3 | 7
93654 | Fresno | 13 | 3 | 7
93656 | Fresno | 13 | 3 | 7
93657 | Fresno | 13 | 3 | 7
93660 | Fresno | 13 | 3 | 7
93662 | Fresno | 13 | 3 | 7
93667 | Fresno | 13 | 3 | 7
93668 | Fresno | 13 | 3 | 7
93675 | Fresno | 13 | 3 | 7
93701 | Fresno | 13 | 3 | 7
93702 | Fresno | 13 | 3 | 7
93703 | Fresno | 13 | 3 | 7
93704 | Fresno | 13 | 3 | 7
93705 | Fresno | 13 | 3 | 7
93706 | Fresno | 13 | 3 | 7
93710 | Fresno | 13 | 3 | 7
93711 | Fresno | 13 | 3 | 7
93720 | Fresno | 13 | 3 | 7
93721 | Fresno | 13 | 3 | 7
93722 | Fresno | 13 | 3 | 7
93723 | Fresno | 13 | 3 | 7
93725 | Fresno | 13 | 3 | 7
93726 | Fresno | 13 | 3 | 7
93727 | Fresno | 13 | 3 | 7
93728 | Fresno | 13 | 3 | 7
93730 | Fresno | 13 | 3 | 7
93741 | Fresno | 13 | 3 | 7
95043 | Fresno | 13 | 3 | 7
17 | Fresno | 16 | 3 | 7
93602 | Fresno | 16 | 3 | 7
93621 | Fresno | 16 | 3 | 7
93633 | Fresno | 16 | 3 | 7
93641 | Fresno | 16 | 3 | 7
93657 | Fresno | 16 | 3 | 7
93664 | Fresno | 16 | 3 | 7
93667 | Fresno | 16 | 3 | 7
47 | Glenn | 2 | 3
95939 | Glenn | 2 | 3
95920 | Glenn | 11 | 3
95928 | Glenn | 11 | 3
95939 | Glenn | 11 | 3
95943 | Glenn | 11 | 3
95951 | Glenn | 11 | 3
95963 | Glenn | 11 | 3
95970 | Glenn | 11 | 3
95988 | Glenn | 11 | 3
47 | Glenn | 16 | 3
95939 | Glenn | 16 | 3
95963 | Glenn | 16 | 3
95546 | Humboldt | 1 | 1
95555 | Humboldt | 1 | 1
54 | Humboldt | 1 | 1
95570 | Humboldt | 1 | 1
95525 | Humboldt | 1 | 1
95519 | Humboldt | 1 | 1
95521 | Humboldt | 1 | 1
95550 | Humboldt | 1 | 1
95524 | Humboldt | 1 | 1
95503 | Humboldt | 1 | 1
95564 | Humboldt | 1 | 1
95501 | Humboldt | 1 | 1
95549 | Humboldt | 1 | 1
95551 | Humboldt | 1 | 1
95540 | Humboldt | 1 | 1
95536 | Humboldt | 1 | 1
95547 | Humboldt | 1 | 1
95528 | Humboldt | 1 | 1
95565 | Humboldt | 1 | 1
95562 | Humboldt | 1 | 1
95569 | Humboldt | 1 | 1
95554 | Humboldt | 1 | 1
95558 | Humboldt | 1 | 1
95542 | Humboldt | 1 | 1
95589 | Humboldt | 1 | 1
95560 | Humboldt | 1 | 1
50 | Humboldt | 2 | 1
54 | Humboldt | 2 | 1
95511 | Humboldt | 2 | 1
95514 | Humboldt | 2 | 1
95525 | Humboldt | 2 | 1
95526 | Humboldt | 2 | 1
95528 | Humboldt | 2 | 1
95542 | Humboldt | 2 | 1
95546 | Humboldt | 2 | 1
95549 | Humboldt | 2 | 1
95550 | Humboldt | 2 | 1
95554 | Humboldt | 2 | 1
95556 | Humboldt | 2 | 1
95560 | Humboldt | 2 | 1
95563 | Humboldt | 2 | 1
95565 | Humboldt | 2 | 1
95569 | Humboldt | 2 | 1
95573 | Humboldt | 2 | 1
95589 | Humboldt | 2 | 1
96046 | Humboldt | 2 | 1
50 | Humboldt | 16 | 1
95546 | Humboldt | 16 | 1
95556 | Humboldt | 16 | 1
95563 | Humboldt | 16 | 1
95573 | Humboldt | 16 | 1
96046 | Humboldt | 16 | 1
92283 | Imperial | 14
92227 | Imperial | 15
92231 | Imperial | 15
92233 | Imperial | 15
92243 | Imperial | 15
92249 | Imperial | 15
92250 | Imperial | 15
92251 | Imperial | 15
92257 | Imperial | 15
92259 | Imperial | 15
92274 | Imperial | 15
92281 | Imperial | 15
92283 | Imperial | 15
92328 | Inyo | 14
92384 | Inyo | 14
92389 | Inyo | 14
93526 | Inyo | 14
93527 | Inyo | 14
93545 | Inyo | 14
93555 | Inyo | 14
92328 | Inyo | 16
93513 | Inyo | 16
93514 | Inyo | 16
93526 | Inyo | 16
93545 | Inyo | 16
93555 | Inyo | 16
93249 | Kern | 4 | 3 | 7
93461 | Kern | 4 | 3 | 7
93251 | Kern | 4 | 3 | 7
93224 | Kern | 4 | 3 | 7
93268 | Kern | 4 | 3 | 7
93252 | Kern | 4 | 3 | 7
93203 | Kern | 13 | 3 | 7
93206 | Kern | 13 | 3 | 7
93215 | Kern | 13 | 3 | 7
93224 | Kern | 13 | 3 | 7
93225 | Kern | 13 | 3 | 7
93226 | Kern | 13 | 3 | 7
93241 | Kern | 13 | 3 | 7
93243 | Kern | 13 | 3 | 7
93249 | Kern | 13 | 3 | 7
93250 | Kern | 13 | 3 | 7
93251 | Kern | 13 | 3 | 7
93252 | Kern | 13 | 3 | 7
93263 | Kern | 13 | 3 | 7
93268 | Kern | 13 | 3 | 7
93276 | Kern | 13 | 3 | 7
93280 | Kern | 13 | 3 | 7
93285 | Kern | 13 | 3 | 7
93287 | Kern | 13 | 3 | 7
93301 | Kern | 13 | 3 | 7
93304 | Kern | 13 | 3 | 7
93305 | Kern | 13 | 3 | 7
93306 | Kern | 13 | 3 | 7
93307 | Kern | 13 | 3 | 7
93308 | Kern | 13 | 3 | 7
93309 | Kern | 13 | 3 | 7
93311 | Kern | 13 | 3 | 7
93312 | Kern | 13 | 3 | 7
93313 | Kern | 13 | 3 | 7
93314 | Kern | 13 | 3 | 7
93461 | Kern | 13 | 3 | 7
93518 | Kern | 13 | 3 | 7
93560 | Kern | 13 | 3 | 7
93561 | Kern | 13 | 3 | 7
93243 | Kern | 14 | 3 | 7
93255 | Kern | 14 | 3 | 7
93283 | Kern | 14 | 3 | 7
93501 | Kern | 14 | 3 | 7
93505 | Kern | 14 | 3 | 7
93516 | Kern | 14 | 3 | 7
93518 | Kern | 14 | 3 | 7
93519 | Kern | 14 | 3 | 7
93523 | Kern | 14 | 3 | 7
93524 | Kern | 14 | 3 | 7
93527 | Kern | 14 | 3 | 7
93528 | Kern | 14 | 3 | 7
93536 | Kern | 14 | 3 | 7
93554 | Kern | 14 | 3 | 7
93555 | Kern | 14 | 3 | 7
93560 | Kern | 14 | 3 | 7
16 | Kern | 16 | 3 | 7
93203 | Kern | 16 | 3 | 7
93205 | Kern | 16 | 3 | 7
93225 | Kern | 16 | 3 | 7
93226 | Kern | 16 | 3 | 7
93238 | Kern | 16 | 3 | 7
93240 | Kern | 16 | 3 | 7
93243 | Kern | 16 | 3 | 7
93252 | Kern | 16 | 3 | 7
93255 | Kern | 16 | 3 | 7
93283 | Kern | 16 | 3 | 7
93285 | Kern | 16 | 3 | 7
93287 | Kern | 16 | 3 | 7
93306 | Kern | 16 | 3 | 7
93308 | Kern | 16 | 3 | 7
93501 | Kern | 16 | 3 | 7
93518 | Kern | 16 | 3 | 7
93519 | Kern | 16 | 3 | 7
93527 | Kern | 16 | 3 | 7
93531 | Kern | 16 | 3 | 7
93555 | Kern | 16 | 3 | 7
93560 | Kern | 16 | 3 | 7
93561 | Kern | 16 | 3 | 7
93204 | Kings | 4 | 3
93451 | Kings | 4 | 3
93202 | Kings | 13 | 3
93204 | Kings | 13 | 3
93212 | Kings | 13 | 3
93230 | Kings | 13 | 3
93239 | Kings | 13 | 3
93242 | Kings | 13 | 3
93245 | Kings | 13 | 3
93266 | Kings | 13 | 3
93451 | Kings | 13 | 3
93631 | Kings | 13 | 3
93656 | Kings | 13 | 3
48 | Lake | 2 | 1
95422 | Lake | 2 | 1
95423 | Lake | 2 | 1
95441 | Lake | 2 | 1
95443 | Lake | 2 | 1
95451 | Lake | 2 | 1
95453 | Lake | 2 | 1
95457 | Lake | 2 | 1
95458 | Lake | 2 | 1
95461 | Lake | 2 | 1
95464 | Lake | 2 | 1
95467 | Lake | 2 | 1
95469 | Lake | 2 | 1
95485 | Lake | 2 | 1
95493 | Lake | 2 | 1
48 | Lake | 11 | 1
95422 | Lake | 11 | 1
95423 | Lake | 11 | 1
95422 | Lake | 12 | 1
95457 | Lake | 12 | 1
48 | Lake | 16 | 1
95469 | Lake | 16 | 1
12 | Lassen | 16 | 1
19 | Lassen | 16 | 1
96056 | Lassen | 16 | 1
96109 | Lassen | 16 | 1
96113 | Lassen | 16 | 1
96114 | Lassen | 16 | 1
96117 | Lassen | 16 | 1
96119 | Lassen | 16 | 1
96121 | Lassen | 16 | 1
96123 | Lassen | 16 | 1
96128 | Lassen | 16 | 1
96130 | Lassen | 16 | 1
96132 | Lassen | 16 | 1
96136 | Lassen | 16 | 1
96137 | Lassen | 16 | 1
90024 | Los Angeles | 6
90025 | Los Angeles | 6
90034 | Los Angeles | 6
90045 | Los Angeles | 6
90049 | Los Angeles | 6
90056 | Los Angeles | 6
90064 | Los Angeles | 6
90066 | Los Angeles | 6
90073 | Los Angeles | 6
90077 | Los Angeles | 6
90094 | Los Angeles | 6
90230 | Los Angeles | 6
90232 | Los Angeles | 6
90245 | Los Angeles | 6
90248 | Los Angeles | 6
90250 | Los Angeles | 6
90254 | Los Angeles | 6
90260 | Los Angeles | 6
90263 | Los Angeles | 6
90265 | Los Angeles | 6
90266 | Los Angeles | 6
90272 | Los Angeles | 6
90274 | Los Angeles | 6
90275 | Los Angeles | 6
90277 | Los Angeles | 6
90278 | Los Angeles | 6
90290 | Los Angeles | 6
90291 | Los Angeles | 6
90292 | Los Angeles | 6
90293 | Los Angeles | 6
90301 | Los Angeles | 6
90302 | Los Angeles | 6
90304 | Los Angeles | 6
90401 | Los Angeles | 6
90402 | Los Angeles | 6
90403 | Los Angeles | 6
90404 | Los Angeles | 6
90405 | Los Angeles | 6
90501 | Los Angeles | 6
90502 | Los Angeles | 6
90503 | Los Angeles | 6
90504 | Los Angeles | 6
90505 | Los Angeles | 6
90710 | Los Angeles | 6
90717 | Los Angeles | 6
90731 | Los Angeles | 6
90732 | Los Angeles | 6
90744 | Los Angeles | 6
90745 | Los Angeles | 6
90746 | Los Angeles | 6
90755 | Los Angeles | 6
90802 | Los Angeles | 6
90803 | Los Angeles | 6
90804 | Los Angeles | 6
90806 | Los Angeles | 6
90807 | Los Angeles | 6
90810 | Los Angeles | 6
90813 | Los Angeles | 6
90814 | Los Angeles | 6
90815 | Los Angeles | 6
90840 | Los Angeles | 6
91301 | Los Angeles | 6
91302 | Los Angeles | 6
90001 | Los Angeles | 8
90002 | Los Angeles | 8
90003 | Los Angeles | 8
90007 | Los Angeles | 8
90008 | Los Angeles | 8
90011 | Los Angeles | 8
90015 | Los Angeles | 8
90016 | Los Angeles | 8
90018 | Los Angeles | 8
90021 | Los Angeles | 8
90023 | Los Angeles | 8
90034 | Los Angeles | 8
90037 | Los Angeles | 8
90040 | Los Angeles | 8
90043 | Los Angeles | 8
90044 | Los Angeles | 8
90045 | Los Angeles | 8
90047 | Los Angeles | 8
90056 | Los Angeles | 8
90058 | Los Angeles | 8
90059 | Los Angeles | 8
90061 | Los Angeles | 8
90062 | Los Angeles | 8
90064 | Los Angeles | 8
90089 | Los Angeles | 8
90201 | Los Angeles | 8
90220 | Los Angeles | 8
90221 | Los Angeles | 8
90222 | Los Angeles | 8
90230 | Los Angeles | 8
90232 | Los Angeles | 8
90240 | Los Angeles | 8
90241 | Los Angeles | 8
90242 | Los Angeles | 8
90247 | Los Angeles | 8
90248 | Los Angeles | 8
90249 | Los Angeles | 8
90250 | Los Angeles | 8
90255 | Los Angeles | 8
90260 | Los Angeles | 8
90262 | Los Angeles | 8
90270 | Los Angeles | 8
90278 | Los Angeles | 8
90280 | Los Angeles | 8
90301 | Los Angeles | 8
90302 | Los Angeles | 8
90303 | Los Angeles | 8
90304 | Los Angeles | 8
90305 | Los Angeles | 8
90504 | Los Angeles | 8
90506 | Los Angeles | 8
90603 | Los Angeles | 8
90604 | Los Angeles | 8
90623 | Los Angeles | 8
90630 | Los Angeles | 8
90631 | Los Angeles | 8
90638 | Los Angeles | 8
90650 | Los Angeles | 8
90670 | Los Angeles | 8
90701 | Los Angeles | 8
90703 | Los Angeles | 8
90706 | Los Angeles | 8
90712 | Los Angeles | 8
90713 | Los Angeles | 8
90715 | Los Angeles | 8
90716 | Los Angeles | 8
90723 | Los Angeles | 8
90745 | Los Angeles | 8
90746 | Los Angeles | 8
90747 | Los Angeles | 8
90755 | Los Angeles | 8
90805 | Los Angeles | 8
90806 | Los Angeles | 8
90807 | Los Angeles | 8
90808 | Los Angeles | 8
90810 | Los Angeles | 8
90815 | Los Angeles | 8
91748 | Los Angeles | 8
91765 | Los Angeles | 8
90004 | Los Angeles | 9
90005 | Los Angeles | 9
90006 | Los Angeles | 9
90007 | Los Angeles | 9
90010 | Los Angeles | 9
90012 | Los Angeles | 9
90013 | Los Angeles | 9
90014 | Los Angeles | 9
90015 | Los Angeles | 9
90016 | Los Angeles | 9
90017 | Los Angeles | 9
90018 | Los Angeles | 9
90019 | Los Angeles | 9
90020 | Los Angeles | 9
90021 | Los Angeles | 9
90022 | Los Angeles | 9
90023 | Los Angeles | 9
90024 | Los Angeles | 9
90025 | Los Angeles | 9
90026 | Los Angeles | 9
90027 | Los Angeles | 9
90028 | Los Angeles | 9
90029 | Los Angeles | 9
90031 | Los Angeles | 9
90032 | Los Angeles | 9
90033 | Los Angeles | 9
90034 | Los Angeles | 9
90035 | Los Angeles | 9
90036 | Los Angeles | 9
90038 | Los Angeles | 9
90039 | Los Angeles | 9
90040 | Los Angeles | 9
90041 | Los Angeles | 9
90042 | Los Angeles | 9
90046 | Los Angeles | 9
90048 | Los Angeles | 9
90049 | Los Angeles | 9
90057 | Los Angeles | 9
90063 | Los Angeles | 9
90064 | Los Angeles | 9
90065 | Los Angeles | 9
90067 | Los Angeles | 9
90068 | Los Angeles | 9
90069 | Los Angeles | 9
90071 | Los Angeles | 9
90073 | Los Angeles | 9
90077 | Los Angeles | 9
90095 | Los Angeles | 9
90210 | Los Angeles | 9
90211 | Los Angeles | 9
90212 | Los Angeles | 9
90240 | Los Angeles | 9
90265 | Los Angeles | 9
90272 | Los Angeles | 9
90290 | Los Angeles | 9
90601 | Los Angeles | 9
90602 | Los Angeles | 9
90603 | Los Angeles | 9
90604 | Los Angeles | 9
90605 | Los Angeles | 9
90606 | Los Angeles | 9
90631 | Los Angeles | 9
90638 | Los Angeles | 9
90639 | Los Angeles | 9
90640 | Los Angeles | 9
90650 | Los Angeles | 9
90660 | Los Angeles | 9
90670 | Los Angeles | 9
91001 | Los Angeles | 9
91006 | Los Angeles | 9
91007 | Los Angeles | 9
91008 | Los Angeles | 9
91010 | Los Angeles | 9
91011 | Los Angeles | 9
91016 | Los Angeles | 9
91020 | Los Angeles | 9
91024 | Los Angeles | 9
91030 | Los Angeles | 9
91040 | Los Angeles | 9
91042 | Los Angeles | 9
91101 | Los Angeles | 9
91103 | Los Angeles | 9
91104 | Los Angeles | 9
91105 | Los Angeles | 9
91106 | Los Angeles | 9
91107 | Los Angeles | 9
91108 | Los Angeles | 9
91123 | Los Angeles | 9
91201 | Los Angeles | 9
91202 | Los Angeles | 9
91203 | Los Angeles | 9
91204 | Los Angeles | 9
91205 | Los Angeles | 9
91206 | Los Angeles | 9
91207 | Los Angeles | 9
91208 | Los Angeles | 9
91214 | Los Angeles | 9
91301 | Los Angeles | 9
91302 | Los Angeles | 9
91303 | Los Angeles | 9
91304 | Los Angeles | 9
91306 | Los Angeles | 9
91307 | Los Angeles | 9
91311 | Los Angeles | 9
91316 | Los Angeles | 9
91321 | Los Angeles | 9
91324 | Los Angeles | 9
91325 | Los Angeles | 9
91326 | Los Angeles | 9
91330 | Los Angeles | 9
91331 | Los Angeles | 9
91335 | Los Angeles | 9
91340 | Los Angeles | 9
91342 | Los Angeles | 9
91343 | Los Angeles | 9
91344 | Los Angeles | 9
91345 | Los Angeles | 9
91350 | Los Angeles | 9
91351 | Los Angeles | 9
91352 | Los Angeles | 9
91354 | Los Angeles | 9
91355 | Los Angeles | 9
91356 | Los Angeles | 9
91361 | Los Angeles | 9
91362 | Los Angeles | 9
91364 | Los Angeles | 9
91367 | Los Angeles | 9
91371 | Los Angeles | 9
91381 | Los Angeles | 9
91384 | Los Angeles | 9
91387 | Los Angeles | 9
91390 | Los Angeles | 9
91401 | Los Angeles | 9
91402 | Los Angeles | 9
91403 | Los Angeles | 9
91405 | Los Angeles | 9
91406 | Los Angeles | 9
91411 | Los Angeles | 9
91423 | Los Angeles | 9
91436 | Los Angeles | 9
91501 | Los Angeles | 9
91502 | Los Angeles | 9
91504 | Los Angeles | 9
91505 | Los Angeles | 9
91506 | Los Angeles | 9
91521 | Los Angeles | 9
91522 | Los Angeles | 9
91523 | Los Angeles | 9
91601 | Los Angeles | 9
91602 | Los Angeles | 9
91604 | Los Angeles | 9
91605 | Los Angeles | 9
91606 | Los Angeles | 9
91607 | Los Angeles | 9
91608 | Los Angeles | 9
91702 | Los Angeles | 9
91706 | Los Angeles | 9
91710 | Los Angeles | 9
91711 | Los Angeles | 9
91722 | Los Angeles | 9
91723 | Los Angeles | 9
91724 | Los Angeles | 9
91731 | Los Angeles | 9
91732 | Los Angeles | 9
91733 | Los Angeles | 9
91740 | Los Angeles | 9
91741 | Los Angeles | 9
91744 | Los Angeles | 9
91745 | Los Angeles | 9
91746 | Los Angeles | 9
91748 | Los Angeles | 9
91750 | Los Angeles | 9
91754 | Los Angeles | 9
91755 | Los Angeles | 9
91765 | Los Angeles | 9
91766 | Los Angeles | 9
91767 | Los Angeles | 9
91768 | Los Angeles | 9
91770 | Los Angeles | 9
91773 | Los Angeles | 9
91775 | Los Angeles | 9
91776 | Los Angeles | 9
91780 | Los Angeles | 9
91789 | Los Angeles | 9
91790 | Los Angeles | 9
91791 | Los Angeles | 9
91792 | Los Angeles | 9
91801 | Los Angeles | 9
91803 | Los Angeles | 9
93063 | Los Angeles | 9
93510 | Los Angeles | 9
91710 | Los Angeles | 10
91711 | Los Angeles | 10
91765 | Los Angeles | 10
91766 | Los Angeles | 10
91767 | Los Angeles | 10
91786 | Los Angeles | 10
91342 | Los Angeles | 14
91390 | Los Angeles | 14
93243 | Los Angeles | 14
93510 | Los Angeles | 14
93532 | Los Angeles | 14
93534 | Los Angeles | 14
93535 | Los Angeles | 14
93536 | Los Angeles | 14
93543 | Los Angeles | 14
93544 | Los Angeles | 14
93550 | Los Angeles | 14
93551 | Los Angeles | 14
93552 | Los Angeles | 14
93553 | Los Angeles | 14
93560 | Los Angeles | 14
93563 | Los Angeles | 14
93591 | Los Angeles | 14
91001 | Los Angeles | 16
91006 | Los Angeles | 16
91008 | Los Angeles | 16
91010 | Los Angeles | 16
91011 | Los Angeles | 16
91016 | Los Angeles | 16
91024 | Los Angeles | 16
91040 | Los Angeles | 16
91042 | Los Angeles | 16
91107 | Los Angeles | 16
91214 | Los Angeles | 16
91321 | Los Angeles | 16
91342 | Los Angeles | 16
91350 | Los Angeles | 16
91351 | Los Angeles | 16
91384 | Los Angeles | 16
91387 | Los Angeles | 16
91390 | Los Angeles | 16
91702 | Los Angeles | 16
91711 | Los Angeles | 16
91741 | Los Angeles | 16
91750 | Los Angeles | 16
91773 | Los Angeles | 16
93243 | Los Angeles | 16
93510 | Los Angeles | 16
93532 | Los Angeles | 16
93536 | Los Angeles | 16
93543 | Los Angeles | 16
93544 | Los Angeles | 16
93550 | Los Angeles | 16
93552 | Los Angeles | 16
93553 | Los Angeles | 16
93563 | Los Angeles | 16
93610 | Madera | 12 | 3 | 7
93622 | Madera | 12 | 3 | 7
93601 | Madera | 13 | 3 | 7
93604 | Madera | 13 | 3 | 7
93610 | Madera | 13 | 3 | 7
93614 | Madera | 13 | 3 | 7
93622 | Madera | 13 | 3 | 7
93626 | Madera | 13 | 3 | 7
93636 | Madera | 13 | 3 | 7
93637 | Madera | 13 | 3 | 7
93638 | Madera | 13 | 3 | 7
93643 | Madera | 13 | 3 | 7
93644 | Madera | 13 | 3 | 7
93645 | Madera | 13 | 3 | 7
93653 | Madera | 13 | 3 | 7
93720 | Madera | 13 | 3 | 7
93730 | Madera | 13 | 3 | 7
20 | Madera | 16 | 3 | 7
93601 | Madera | 16 | 3 | 7
93602 | Madera | 16 | 3 | 7
93604 | Madera | 16 | 3 | 7
93614 | Madera | 16 | 3 | 7
93626 | Madera | 16 | 3 | 7
93643 | Madera | 16 | 3 | 7
93644 | Madera | 16 | 3 | 7
93669 | Madera | 16 | 3 | 7
94952 | Marin | 1 | 5
94901 | Marin | 2 | 5
94903 | Marin | 2 | 5
94904 | Marin | 2 | 5
94925 | Marin | 2 | 5
94930 | Marin | 2 | 5
94939 | Marin | 2 | 5
94945 | Marin | 2 | 5
94946 | Marin | 2 | 5
94947 | Marin | 2 | 5
94949 | Marin | 2 | 5
94952 | Marin | 2 | 5
94960 | Marin | 2 | 5
94963 | Marin | 2 | 5
94964 | Marin | 2 | 5
94973 | Marin | 2 | 5
94904 | Marin | 3 | 5
94920 | Marin | 3 | 5
94924 | Marin | 3 | 5
94925 | Marin | 3 | 5
94929 | Marin | 3 | 5
94930 | Marin | 3 | 5
94933 | Marin | 3 | 5
94937 | Marin | 3 | 5
94938 | Marin | 3 | 5
94939 | Marin | 3 | 5
94940 | Marin | 3 | 5
94941 | Marin | 3 | 5
94946 | Marin | 3 | 5
94952 | Marin | 3 | 5
94956 | Marin | 3 | 5
94963 | Marin | 3 | 5
94965 | Marin | 3 | 5
94970 | Marin | 3 | 5
94971 | Marin | 3 | 5
94973 | Marin | 3 | 5
93601 | Mariposa | 12 | 3
93653 | Mariposa | 12 | 3
95306 | Mariposa | 12 | 3
95311 | Mariposa | 12 | 3
95318 | Mariposa | 12 | 3
95321 | Mariposa | 12 | 3
95325 | Mariposa | 12 | 3
95329 | Mariposa | 12 | 3
95338 | Mariposa | 12 | 3
95345 | Mariposa | 12 | 3
95369 | Mariposa | 12 | 3
93601 | Mariposa | 13 | 3
93653 | Mariposa | 13 | 3
95338 | Mariposa | 13 | 3
58 | Mariposa | 16 | 3
93601 | Mariposa | 16 | 3
93623 | Mariposa | 16 | 3
93644 | Mariposa | 16 | 3
95311 | Mariposa | 16 | 3
95318 | Mariposa | 16 | 3
95321 | Mariposa | 16 | 3
95338 | Mariposa | 16 | 3
95345 | Mariposa | 16 | 3
95389 | Mariposa | 16 | 3
95587 | Mendocino | 1 | 1
95589 | Mendocino | 1 | 1
95585 | Mendocino | 1 | 1
95488 | Mendocino | 1 | 1
95417 | Mendocino | 1 | 1
95490 | Mendocino | 1 | 1
95437 | Mendocino | 1 | 1
22 | Mendocino | 1 | 1
95427 | Mendocino | 1 | 1
95470 | Mendocino | 1 | 1
95460 | Mendocino | 1 | 1
95420 | Mendocino | 1 | 1
95456 | Mendocino | 1 | 1
95410 | Mendocino | 1 | 1
95466 | Mendocino | 1 | 1
95432 | Mendocino | 1 | 1
95459 | Mendocino | 1 | 1
95468 | Mendocino | 1 | 1
95445 | Mendocino | 1 | 1
22 | Mendocino | 2 | 1
95415 | Mendocino | 2 | 1
95417 | Mendocino | 2 | 1
95427 | Mendocino | 2 | 1
95428 | Mendocino | 2 | 1
95429 | Mendocino | 2 | 1
95437 | Mendocino | 2 | 1
95445 | Mendocino | 2 | 1
95449 | Mendocino | 2 | 1
95454 | Mendocino | 2 | 1
95459 | Mendocino | 2 | 1
95466 | Mendocino | 2 | 1
95468 | Mendocino | 2 | 1
95469 | Mendocino | 2 | 1
95470 | Mendocino | 2 | 1
95482 | Mendocino | 2 | 1
95490 | Mendocino | 2 | 1
95494 | Mendocino | 2 | 1
95585 | Mendocino | 2 | 1
95587 | Mendocino | 2 | 1
95428 | Mendocino | 16 | 1
95469 | Mendocino | 16 | 1
95490 | Mendocino | 16 | 1
95322 | Merced | 4 | 3 | 7
93635 | Merced | 4 | 3 | 7
93610 | Merced | 12 | 3 | 7
93620 | Merced | 12 | 3 | 7
93622 | Merced | 12 | 3 | 7
93635 | Merced | 12 | 3 | 7
95301 | Merced | 12 | 3 | 7
95303 | Merced | 12 | 3 | 7
95315 | Merced | 12 | 3 | 7
95316 | Merced | 12 | 3 | 7
95317 | Merced | 12 | 3 | 7
95322 | Merced | 12 | 3 | 7
95324 | Merced | 12 | 3 | 7
95333 | Merced | 12 | 3 | 7
95334 | Merced | 12 | 3 | 7
95340 | Merced | 12 | 3 | 7
95341 | Merced | 12 | 3 | 7
95348 | Merced | 12 | 3 | 7
95360 | Merced | 12 | 3 | 7
95369 | Merced | 12 | 3 | 7
95374 | Merced | 12 | 3 | 7
95380 | Merced | 12 | 3 | 7
95388 | Merced | 12 | 3 | 7
93610 | Merced | 13 | 3 | 7
93620 | Merced | 13 | 3 | 7
93622 | Merced | 13 | 3 | 7
93635 | Merced | 13 | 3 | 7
95317 | Merced | 13 | 3 | 7
95333 | Merced | 13 | 3 | 7
96006 | Modoc | 16 | 14
96015 | Modoc | 16 | 14
96054 | Modoc | 16 | 14
96056 | Modoc | 16 | 14
96101 | Modoc | 16 | 14
96104 | Modoc | 16 | 14
96108 | Modoc | 16 | 14
96112 | Modoc | 16 | 14
96115 | Modoc | 16 | 14
96116 | Modoc | 16 | 14
96134 | Modoc | 16 | 14
93512 | Mono | 16 | 12 | 12
93514 | Mono | 16 | 12 | 12
93517 | Mono | 16 | 12 | 12
93529 | Mono | 16 | 12 | 12
93541 | Mono | 16 | 12 | 12
93546 | Mono | 16 | 12 | 12
96107 | Mono | 16 | 12 | 12
96133 | Mono | 16 | 12 | 12
93426 | Monterey | 3 | 4
93901 | Monterey | 3 | 4
93905 | Monterey | 3 | 4
93906 | Monterey | 3 | 4
93907 | Monterey | 3 | 4
93908 | Monterey | 3 | 4
93920 | Monterey | 3 | 4
93923 | Monterey | 3 | 4
93924 | Monterey | 3 | 4
93925 | Monterey | 3 | 4
93926 | Monterey | 3 | 4
93927 | Monterey | 3 | 4
93930 | Monterey | 3 | 4
93932 | Monterey | 3 | 4
93933 | Monterey | 3 | 4
93940 | Monterey | 3 | 4
93943 | Monterey | 3 | 4
93950 | Monterey | 3 | 4
93953 | Monterey | 3 | 4
93955 | Monterey | 3 | 4
93960 | Monterey | 3 | 4
95004 | Monterey | 3 | 4
95012 | Monterey | 3 | 4
95039 | Monterey | 3 | 4
95076 | Monterey | 3 | 4
95004 | Monterey | 4 | 4
93907 | Monterey | 4 | 4
93908 | Monterey | 4 | 4
93925 | Monterey | 4 | 4
93926 | Monterey | 4 | 4
93924 | Monterey | 4 | 4
93960 | Monterey | 4 | 4
93930 | Monterey | 4 | 4
93927 | Monterey | 4 | 4
93920 | Monterey | 4 | 4
93450 | Monterey | 4 | 4
93932 | Monterey | 4 | 4
93451 | Monterey | 4 | 4
93426 | Monterey | 4 | 4
93920 | Monterey | 5 | 4
93450 | Monterey | 13 | 4
93451 | Monterey | 13 | 4
94503 | Napa | 2 | 4
94508 | Napa | 2 | 4
94515 | Napa | 2 | 4
94558 | Napa | 2 | 4
94559 | Napa | 2 | 4
94567 | Napa | 2 | 4
94574 | Napa | 2 | 4
94576 | Napa | 2 | 4
94599 | Napa | 2 | 4
95461 | Napa | 2 | 4
95476 | Napa | 2 | 4
95688 | Napa | 2 | 4
94503 | Napa | 3 | 4
94559 | Napa | 3 | 4
94503 | Napa | 12 | 4
94558 | Napa | 12 | 4
95688 | Napa | 12 | 4
95602 | Nevada | 11 | 1
95945 | Nevada | 11 | 1
95946 | Nevada | 11 | 1
95949 | Nevada | 11 | 1
95959 | Nevada | 11 | 1
95960 | Nevada | 11 | 1
95975 | Nevada | 11 | 1
95977 | Nevada | 11 | 1
95724 | Nevada | 16 | 1
95728 | Nevada | 16 | 1
95945 | Nevada | 16 | 1
95959 | Nevada | 16 | 1
96111 | Nevada | 16 | 1
96161 | Nevada | 16 | 1
96162 | Nevada | 16 | 1
90680 | Orange | 6
90720 | Orange | 6
90740 | Orange | 6
90742 | Orange | 6
90743 | Orange | 6
92603 | Orange | 6
92612 | Orange | 6
92614 | Orange | 6
92617 | Orange | 6
92624 | Orange | 6
92625 | Orange | 6
92626 | Orange | 6
92627 | Orange | 6
92629 | Orange | 6
92637 | Orange | 6
92646 | Orange | 6
92647 | Orange | 6
92648 | Orange | 6
92649 | Orange | 6
92651 | Orange | 6
92653 | Orange | 6
92655 | Orange | 6
92656 | Orange | 6
92657 | Orange | 6
92660 | Orange | 6
92661 | Orange | 6
92662 | Orange | 6
92663 | Orange | 6
92672 | Orange | 6
92673 | Orange | 6
92675 | Orange | 6
92677 | Orange | 6
92683 | Orange | 6
92691 | Orange | 6
92692 | Orange | 6
92697 | Orange | 6
92703 | Orange | 6
92704 | Orange | 6
92707 | Orange | 6
92708 | Orange | 6
92841 | Orange | 6
92843 | Orange | 6
92844 | Orange | 6
92845 | Orange | 6
92672 | Orange | 7
92675 | Orange | 7
90620 | Orange | 8
90621 | Orange | 8
90623 | Orange | 8
90630 | Orange | 8
90631 | Orange | 8
90638 | Orange | 8
90680 | Orange | 8
90720 | Orange | 8
90740 | Orange | 8
92530 | Orange | 8
92602 | Orange | 8
92603 | Orange | 8
92604 | Orange | 8
92606 | Orange | 8
92610 | Orange | 8
92612 | Orange | 8
92614 | Orange | 8
92617 | Orange | 8
92618 | Orange | 8
92620 | Orange | 8
92626 | Orange | 8
92630 | Orange | 8
92637 | Orange | 8
92651 | Orange | 8
92653 | Orange | 8
92656 | Orange | 8
92660 | Orange | 8
92673 | Orange | 8
92675 | Orange | 8
92676 | Orange | 8
92679 | Orange | 8
92683 | Orange | 8
92688 | Orange | 8
92691 | Orange | 8
92692 | Orange | 8
92694 | Orange | 8
92701 | Orange | 8
92703 | Orange | 8
92704 | Orange | 8
92705 | Orange | 8
92706 | Orange | 8
92707 | Orange | 8
92708 | Orange | 8
92780 | Orange | 8
92782 | Orange | 8
92801 | Orange | 8
92802 | Orange | 8
92804 | Orange | 8
92805 | Orange | 8
92806 | Orange | 8
92807 | Orange | 8
92808 | Orange | 8
92821 | Orange | 8
92823 | Orange | 8
92831 | Orange | 8
92832 | Orange | 8
92833 | Orange | 8
92835 | Orange | 8
92840 | Orange | 8
92841 | Orange | 8
92843 | Orange | 8
92844 | Orange | 8
92845 | Orange | 8
92861 | Orange | 8
92862 | Orange | 8
92865 | Orange | 8
92866 | Orange | 8
92867 | Orange | 8
92868 | Orange | 8
92869 | Orange | 8
92870 | Orange | 8
92886 | Orange | 8
92887 | Orange | 8
90621 | Orange | 9
90631 | Orange | 9
90638 | Orange | 9
92821 | Orange | 9
92823 | Orange | 9
92833 | Orange | 9
92530 | Orange | 10
92675 | Orange | 10
92676 | Orange | 10
92679 | Orange | 10
92823 | Orange | 10
92886 | Orange | 10
92887 | Orange | 10
95602 | Placer | 11 | 2
95603 | Placer | 11 | 2
95614 | Placer | 11 | 2
95626 | Placer | 11 | 2
95631 | Placer | 11 | 2
95648 | Placer | 11 | 2
95650 | Placer | 11 | 2
95658 | Placer | 11 | 2
95661 | Placer | 11 | 2
95663 | Placer | 11 | 2
95664 | Placer | 11 | 2
95668 | Placer | 11 | 2
95677 | Placer | 11 | 2
95678 | Placer | 11 | 2
95681 | Placer | 11 | 2
95703 | Placer | 11 | 2
95713 | Placer | 11 | 2
95722 | Placer | 11 | 2
95746 | Placer | 11 | 2
95747 | Placer | 11 | 2
95765 | Placer | 11 | 2
95603 | Placer | 12 | 2
95614 | Placer | 12 | 2
95626 | Placer | 12 | 2
95631 | Placer | 12 | 2
95650 | Placer | 12 | 2
95658 | Placer | 12 | 2
95661 | Placer | 12 | 2
95664 | Placer | 12 | 2
95678 | Placer | 12 | 2
95746 | Placer | 12 | 2
95747 | Placer | 12 | 2
95631 | Placer | 16 | 2
95701 | Placer | 16 | 2
95713 | Placer | 16 | 2
95714 | Placer | 16 | 2
95715 | Placer | 16 | 2
95717 | Placer | 16 | 2
95724 | Placer | 16 | 2
95728 | Placer | 16 | 2
96140 | Placer | 16 | 2
96141 | Placer | 16 | 2
96142 | Placer | 16 | 2
96143 | Placer | 16 | 2
96145 | Placer | 16 | 2
96146 | Placer | 16 | 2
96148 | Placer | 16 | 2
96161 | Placer | 16 | 2
96162 | Placer | 16 | 2
28 | Plumas | 16 | 1
31 | Plumas | 16 | 1
95915 | Plumas | 16 | 1
95923 | Plumas | 16 | 1
95934 | Plumas | 16 | 1
95947 | Plumas | 16 | 1
95956 | Plumas | 16 | 1
95971 | Plumas | 16 | 1
95981 | Plumas | 16 | 1
95983 | Plumas | 16 | 1
95984 | Plumas | 16 | 1
96020 | Plumas | 16 | 1
96063 | Plumas | 16 | 1
96103 | Plumas | 16 | 1
96105 | Plumas | 16 | 1
96106 | Plumas | 16 | 1
96114 | Plumas | 16 | 1
96122 | Plumas | 16 | 1
96135 | Plumas | 16 | 1
96137 | Plumas | 16 | 1
92530 | Riverside | 7
92562 | Riverside | 7
92530 | Riverside | 8
92675 | Riverside | 8
92880 | Riverside | 8
92882 | Riverside | 8
92883 | Riverside | 8
91752 | Riverside | 10
92028 | Riverside | 10
92220 | Riverside | 10
92223 | Riverside | 10
92320 | Riverside | 10
92324 | Riverside | 10
92373 | Riverside | 10
92399 | Riverside | 10
92501 | Riverside | 10
92503 | Riverside | 10
92504 | Riverside | 10
92505 | Riverside | 10
92506 | Riverside | 10
92507 | Riverside | 10
92508 | Riverside | 10
92509 | Riverside | 10
92518 | Riverside | 10
92521 | Riverside | 10
92530 | Riverside | 10
92532 | Riverside | 10
92536 | Riverside | 10
92539 | Riverside | 10
92543 | Riverside | 10
92544 | Riverside | 10
92545 | Riverside | 10
92548 | Riverside | 10
92549 | Riverside | 10
92551 | Riverside | 10
92553 | Riverside | 10
92555 | Riverside | 10
92557 | Riverside | 10
92562 | Riverside | 10
92563 | Riverside | 10
92567 | Riverside | 10
92570 | Riverside | 10
92571 | Riverside | 10
92582 | Riverside | 10
92583 | Riverside | 10
92584 | Riverside | 10
92585 | Riverside | 10
92586 | Riverside | 10
92587 | Riverside | 10
92590 | Riverside | 10
92591 | Riverside | 10
92592 | Riverside | 10
92595 | Riverside | 10
92596 | Riverside | 10
92675 | Riverside | 10
92860 | Riverside | 10
92879 | Riverside | 10
92880 | Riverside | 10
92881 | Riverside | 10
92882 | Riverside | 10
92883 | Riverside | 10
92220 | Riverside | 14
92239 | Riverside | 14
92240 | Riverside | 14
92241 | Riverside | 14
92254 | Riverside | 14
92282 | Riverside | 14
92536 | Riverside | 14
92539 | Riverside | 14
92561 | Riverside | 14
92592 | Riverside | 14
92201 | Riverside | 15
92203 | Riverside | 15
92210 | Riverside | 15
92211 | Riverside | 15
92220 | Riverside | 15
92225 | Riverside | 15
92230 | Riverside | 15
92234 | Riverside | 15
92236 | Riverside | 15
92239 | Riverside | 15
92240 | Riverside | 15
92241 | Riverside | 15
92253 | Riverside | 15
92254 | Riverside | 15
92260 | Riverside | 15
92262 | Riverside | 15
92264 | Riverside | 15
92270 | Riverside | 15
92274 | Riverside | 15
92276 | Riverside | 15
92282 | Riverside | 15
92536 | Riverside | 15
92539 | Riverside | 15
92549 | Riverside | 15
92561 | Riverside | 15
92220 | Riverside | 16
92223 | Riverside | 16
92230 | Riverside | 16
92260 | Riverside | 16
92264 | Riverside | 16
92282 | Riverside | 16
92536 | Riverside | 16
92539 | Riverside | 16
92544 | Riverside | 16
92549 | Riverside | 16
92561 | Riverside | 16
95610 | Sacramento | 11 | 6
95621 | Sacramento | 11 | 6
95626 | Sacramento | 11 | 6
95630 | Sacramento | 11 | 6
95836 | Sacramento | 11 | 6
95837 | Sacramento | 11 | 6
95843 | Sacramento | 11 | 6
94561 | Sacramento | 12 | 6
94571 | Sacramento | 12 | 6
95608 | Sacramento | 12 | 6
95610 | Sacramento | 12 | 6
95615 | Sacramento | 12 | 6
95621 | Sacramento | 12 | 6
95624 | Sacramento | 12 | 6
95626 | Sacramento | 12 | 6
95628 | Sacramento | 12 | 6
95630 | Sacramento | 12 | 6
95632 | Sacramento | 12 | 6
95638 | Sacramento | 12 | 6
95641 | Sacramento | 12 | 6
95652 | Sacramento | 12 | 6
95655 | Sacramento | 12 | 6
95660 | Sacramento | 12 | 6
95661 | Sacramento | 12 | 6
95662 | Sacramento | 12 | 6
95670 | Sacramento | 12 | 6
95673 | Sacramento | 12 | 6
95683 | Sacramento | 12 | 6
95690 | Sacramento | 12 | 6
95693 | Sacramento | 12 | 6
95742 | Sacramento | 12 | 6
95757 | Sacramento | 12 | 6
95758 | Sacramento | 12 | 6
95762 | Sacramento | 12 | 6
95811 | Sacramento | 12 | 6
95814 | Sacramento | 12 | 6
95815 | Sacramento | 12 | 6
95816 | Sacramento | 12 | 6
95817 | Sacramento | 12 | 6
95818 | Sacramento | 12 | 6
95819 | Sacramento | 12 | 6
95820 | Sacramento | 12 | 6
95821 | Sacramento | 12 | 6
95822 | Sacramento | 12 | 6
95823 | Sacramento | 12 | 6
95824 | Sacramento | 12 | 6
95825 | Sacramento | 12 | 6
95826 | Sacramento | 12 | 6
95827 | Sacramento | 12 | 6
95828 | Sacramento | 12 | 6
95829 | Sacramento | 12 | 6
95830 | Sacramento | 12 | 6
95831 | Sacramento | 12 | 6
95832 | Sacramento | 12 | 6
95833 | Sacramento | 12 | 6
95834 | Sacramento | 12 | 6
95835 | Sacramento | 12 | 6
95836 | Sacramento | 12 | 6
95837 | Sacramento | 12 | 6
95838 | Sacramento | 12 | 6
95841 | Sacramento | 12 | 6
95842 | Sacramento | 12 | 6
95843 | Sacramento | 12 | 6
95864 | Sacramento | 12 | 6
94062 | San Mateo | 4 | 5
94025 | San Mateo | 4 | 5
94303 | San Mateo | 4 | 5
94028 | San Mateo | 4 | 5
94020 | San Mateo | 4 | 5
93452 | San Luis Obispo | 5 | 4
93446 | San Luis Obispo | 5 | 4
93428 | San Luis Obispo | 5 | 4
93465 | San Luis Obispo | 5 | 4
93430 | San Luis Obispo | 5 | 4
93453 | San Luis Obispo | 5 | 4
93442 | San Luis Obispo | 5 | 4
93405 | San Luis Obispo | 5 | 4
93402 | San Luis Obispo | 5 | 4
93401 | San Luis Obispo | 5 | 4
93407 | San Luis Obispo | 5 | 4
93420 | San Luis Obispo | 5 | 4
93449 | San Luis Obispo | 5 | 4
93433 | San Luis Obispo | 5 | 4
93445 | San Luis Obispo | 5 | 4
93444 | San Luis Obispo | 5 | 4
93454 | San Luis Obispo | 5 | 4
93458 | San Luis Obispo | 5 | 4
92672 | San Diego | 6
91902 | San Diego | 7
91910 | San Diego | 7
91911 | San Diego | 7
91913 | San Diego | 7
91914 | San Diego | 7
91915 | San Diego | 7
91932 | San Diego | 7
91935 | San Diego | 7
91941 | San Diego | 7
91942 | San Diego | 7
91945 | San Diego | 7
91950 | San Diego | 7
91977 | San Diego | 7
92003 | San Diego | 7
92007 | San Diego | 7
92008 | San Diego | 7
92009 | San Diego | 7
92010 | San Diego | 7
92011 | San Diego | 7
92014 | San Diego | 7
92020 | San Diego | 7
92024 | San Diego | 7
92028 | San Diego | 7
92029 | San Diego | 7
92037 | San Diego | 7
92054 | San Diego | 7
92055 | San Diego | 7
92056 | San Diego | 7
92057 | San Diego | 7
92058 | San Diego | 7
92067 | San Diego | 7
92071 | San Diego | 7
92075 | San Diego | 7
92078 | San Diego | 7
92081 | San Diego | 7
92083 | San Diego | 7
92084 | San Diego | 7
92091 | San Diego | 7
92101 | San Diego | 7
92102 | San Diego | 7
92103 | San Diego | 7
92104 | San Diego | 7
92105 | San Diego | 7
92106 | San Diego | 7
92107 | San Diego | 7
92108 | San Diego | 7
92109 | San Diego | 7
92110 | San Diego | 7
92111 | San Diego | 7
92113 | San Diego | 7
92114 | San Diego | 7
92115 | San Diego | 7
92116 | San Diego | 7
92117 | San Diego | 7
92118 | San Diego | 7
92119 | San Diego | 7
92120 | San Diego | 7
92121 | San Diego | 7
92122 | San Diego | 7
92123 | San Diego | 7
92124 | San Diego | 7
92126 | San Diego | 7
92127 | San Diego | 7
92128 | San Diego | 7
92129 | San Diego | 7
92130 | San Diego | 7
92131 | San Diego | 7
92133 | San Diego | 7
92134 | San Diego | 7
92135 | San Diego | 7
92136 | San Diego | 7
92139 | San Diego | 7
92140 | San Diego | 7
92145 | San Diego | 7
92152 | San Diego | 7
92154 | San Diego | 7
92155 | San Diego | 7
92173 | San Diego | 7
92182 | San Diego | 7
92672 | San Diego | 7
91709 | San Bernardino | 8
92028 | San Diego | 8
92055 | San Diego | 8
92672 | San Diego | 8
91709 | San Bernardino | 9
91710 | San Bernardino | 9
91763 | San Bernardino | 9
91766 | San Bernardino | 9
91784 | San Bernardino | 9
91701 | San Bernardino | 10
91708 | San Bernardino | 10
91709 | San Bernardino | 10
91710 | San Bernardino | 10
91730 | San Bernardino | 10
91737 | San Bernardino | 10
91739 | San Bernardino | 10
91759 | San Bernardino | 10
91761 | San Bernardino | 10
91762 | San Bernardino | 10
91763 | San Bernardino | 10
91764 | San Bernardino | 10
91766 | San Bernardino | 10
91784 | San Bernardino | 10
91786 | San Bernardino | 10
92313 | San Bernardino | 10
92316 | San Bernardino | 10
92324 | San Bernardino | 10
92335 | San Bernardino | 10
92336 | San Bernardino | 10
92337 | San Bernardino | 10
92346 | San Bernardino | 10
92350 | San Bernardino | 10
92354 | San Bernardino | 10
92359 | San Bernardino | 10
92373 | San Bernardino | 10
92374 | San Bernardino | 10
92376 | San Bernardino | 10
92377 | San Bernardino | 10
92399 | San Bernardino | 10
92401 | San Bernardino | 10
92404 | San Bernardino | 10
92405 | San Bernardino | 10
92407 | San Bernardino | 10
92408 | San Bernardino | 10
92410 | San Bernardino | 10
92411 | San Bernardino | 10
92509 | San Bernardino | 10
92880 | San Bernardino | 10
91901 | San Diego | 10
91902 | San Diego | 10
91906 | San Diego | 10
91913 | San Diego | 10
91914 | San Diego | 10
91915 | San Diego | 10
91917 | San Diego | 10
91935 | San Diego | 10
91941 | San Diego | 10
91942 | San Diego | 10
91963 | San Diego | 10
91977 | San Diego | 10
91978 | San Diego | 10
91980 | San Diego | 10
92003 | San Diego | 10
92019 | San Diego | 10
92020 | San Diego | 10
92021 | San Diego | 10
92024 | San Diego | 10
92025 | San Diego | 10
92026 | San Diego | 10
92027 | San Diego | 10
92028 | San Diego | 10
92029 | San Diego | 10
92040 | San Diego | 10
92055 | San Diego | 10
92057 | San Diego | 10
92059 | San Diego | 10
92061 | San Diego | 10
92064 | San Diego | 10
92065 | San Diego | 10
92067 | San Diego | 10
92069 | San Diego | 10
92070 | San Diego | 10
92071 | San Diego | 10
92078 | San Diego | 10
92081 | San Diego | 10
92082 | San Diego | 10
92083 | San Diego | 10
92084 | San Diego | 10
92091 | San Diego | 10
92096 | San Diego | 10
92119 | San Diego | 10
92120 | San Diego | 10
92124 | San Diego | 10
92127 | San Diego | 10
92128 | San Diego | 10
92129 | San Diego | 10
92131 | San Diego | 10
92145 | San Diego | 10
92154 | San Diego | 10
95023 | San Benito | 12 | 4
95202 | San Joaquin | 12 | 2
95203 | San Joaquin | 12 | 2
95204 | San Joaquin | 12 | 2
95205 | San Joaquin | 12 | 2
95206 | San Joaquin | 12 | 2
95207 | San Joaquin | 12 | 2
95209 | San Joaquin | 12 | 2
95210 | San Joaquin | 12 | 2
95211 | San Joaquin | 12 | 2
95212 | San Joaquin | 12 | 2
95215 | San Joaquin | 12 | 2
95219 | San Joaquin | 12 | 2
95220 | San Joaquin | 12 | 2
95230 | San Joaquin | 12 | 2
95231 | San Joaquin | 12 | 2
95236 | San Joaquin | 12 | 2
95237 | San Joaquin | 12 | 2
95240 | San Joaquin | 12 | 2
95242 | San Joaquin | 12 | 2
95258 | San Joaquin | 12 | 2
95304 | San Joaquin | 12 | 2
95320 | San Joaquin | 12 | 2
95330 | San Joaquin | 12 | 2
95336 | San Joaquin | 12 | 2
95337 | San Joaquin | 12 | 2
95361 | San Joaquin | 12 | 2
95366 | San Joaquin | 12 | 2
95376 | San Joaquin | 12 | 2
95377 | San Joaquin | 12 | 2
95385 | San Joaquin | 12 | 2
95391 | San Joaquin | 12 | 2
95632 | San Joaquin | 12 | 2
95690 | San Joaquin | 12 | 2
95023 | San Benito | 13 | 4
95043 | San Benito | 13 | 4
93251 | San Luis Obispo | 13 | 4
93252 | San Luis Obispo | 13 | 4
93453 | San Luis Obispo | 13 | 4
93461 | San Luis Obispo | 13 | 4
92252 | San Bernardino | 14
92256 | San Bernardino | 14
92277 | San Bernardino | 14
92278 | San Bernardino | 14
92280 | San Bernardino | 14
92284 | San Bernardino | 14
92285 | San Bernardino | 14
92301 | San Bernardino | 14
92304 | San Bernardino | 14
92305 | San Bernardino | 14
92307 | San Bernardino | 14
92308 | San Bernardino | 14
92309 | San Bernardino | 14
92310 | San Bernardino | 14
92311 | San Bernardino | 14
92314 | San Bernardino | 14
92327 | San Bernardino | 14
92332 | San Bernardino | 14
92338 | San Bernardino | 14
92339 | San Bernardino | 14
92342 | San Bernardino | 14
92344 | San Bernardino | 14
92345 | San Bernardino | 14
92347 | San Bernardino | 14
92356 | San Bernardino | 14
92363 | San Bernardino | 14
92364 | San Bernardino | 14
92365 | San Bernardino | 14
92368 | San Bernardino | 14
92371 | San Bernardino | 14
92372 | San Bernardino | 14
92392 | San Bernardino | 14
92394 | San Bernardino | 14
92395 | San Bernardino | 14
92397 | San Bernardino | 14
92407 | San Bernardino | 14
93505 | San Bernardino | 14
93524 | San Bernardino | 14
93555 | San Bernardino | 14
93562 | San Bernardino | 14
91901 | San Diego | 14
91905 | San Diego | 14
91906 | San Diego | 14
91916 | San Diego | 14
91917 | San Diego | 14
91934 | San Diego | 14
91935 | San Diego | 14
91962 | San Diego | 14
91963 | San Diego | 14
91980 | San Diego | 14
92004 | San Diego | 14
92021 | San Diego | 14
92036 | San Diego | 14
92040 | San Diego | 14
92059 | San Diego | 14
92061 | San Diego | 14
92065 | San Diego | 14
92066 | San Diego | 14
92070 | San Diego | 14
92082 | San Diego | 14
92086 | San Diego | 14
92536 | San Diego | 14
92242 | San Bernardino | 15
92256 | San Bernardino | 15
92267 | San Bernardino | 15
92277 | San Bernardino | 15
92278 | San Bernardino | 15
92280 | San Bernardino | 15
92304 | San Bernardino | 15
92332 | San Bernardino | 15
92338 | San Bernardino | 15
92363 | San Bernardino | 15
91905 | San Diego | 15
91934 | San Diego | 15
92004 | San Diego | 15
92036 | San Diego | 15
92066 | San Diego | 15
92086 | San Diego | 15
91701 | San Bernardino | 16
91737 | San Bernardino | 16
91759 | San Bernardino | 16
91784 | San Bernardino | 16
92256 | San Bernardino | 16
92285 | San Bernardino | 16
92305 | San Bernardino | 16
92308 | San Bernardino | 16
92314 | San Bernardino | 16
92315 | San Bernardino | 16
92317 | San Bernardino | 16
92321 | San Bernardino | 16
92322 | San Bernardino | 16
92325 | San Bernardino | 16
92336 | San Bernardino | 16
92339 | San Bernardino | 16
92344 | San Bernardino | 16
92345 | San Bernardino | 16
92346 | San Bernardino | 16
92352 | San Bernardino | 16
92356 | San Bernardino | 16
92358 | San Bernardino | 16
92359 | San Bernardino | 16
92371 | San Bernardino | 16
92382 | San Bernardino | 16
92385 | San Bernardino | 16
92397 | San Bernardino | 16
92399 | San Bernardino | 16
92404 | San Bernardino | 16
92407 | San Bernardino | 16
93555 | San Bernardino | 16
93562 | San Bernardino | 16
95004 | San Benito | 3 | 4
95023 | San Benito | 3 | 4
95043 | San Benito | 3 | 4
95045 | San Benito | 3 | 4
95023 | San Benito | 4 | 4
95045 | San Benito | 4 | 4
95004 | San Benito | 4 | 4
95043 | San Benito | 4 | 4
94014 | San Francicso | 3 | 5
94015 | San Francicso | 3 | 5
94102 | San Francicso | 3 | 5
94103 | San Francicso | 3 | 5
94104 | San Francicso | 3 | 5
94105 | San Francicso | 3 | 5
94107 | San Francicso | 3 | 5
94108 | San Francicso | 3 | 5
94109 | San Francicso | 3 | 5
94110 | San Francicso | 3 | 5
94111 | San Francicso | 3 | 5
94112 | San Francicso | 3 | 5
94114 | San Francicso | 3 | 5
94115 | San Francicso | 3 | 5
94116 | San Francicso | 3 | 5
94117 | San Francicso | 3 | 5
94118 | San Francicso | 3 | 5
94121 | San Francicso | 3 | 5
94122 | San Francicso | 3 | 5
94123 | San Francicso | 3 | 5
94124 | San Francicso | 3 | 5
94127 | San Francicso | 3 | 5
94129 | San Francicso | 3 | 5
94130 | San Francicso | 3 | 5
94131 | San Francicso | 3 | 5
94132 | San Francicso | 3 | 5
94133 | San Francicso | 3 | 5
94134 | San Francicso | 3 | 5
94158 | San Francicso | 3 | 5
94501 | San Francicso | 3 | 5
94920 | San Francicso | 3 | 5
93452 | San Luis Obispo | 4 | 4
93426 | San Luis Obispo | 4 | 4
93451 | San Luis Obispo | 4 | 4
93461 | San Luis Obispo | 4 | 4
93446 | San Luis Obispo | 4 | 4
93428 | San Luis Obispo | 4 | 4
93465 | San Luis Obispo | 4 | 4
93432 | San Luis Obispo | 4 | 4
93430 | San Luis Obispo | 4 | 4
93422 | San Luis Obispo | 4 | 4
93453 | San Luis Obispo | 4 | 4
93442 | San Luis Obispo | 4 | 4
93405 | San Luis Obispo | 4 | 4
93251 | San Luis Obispo | 4 | 4
93401 | San Luis Obispo | 4 | 4
93420 | San Luis Obispo | 4 | 4
93454 | San Luis Obispo | 4 | 4
93252 | San Luis Obispo | 4 | 4
94002 | San Mateo | 3 | 5
94005 | San Mateo | 3 | 5
94010 | San Mateo | 3 | 5
94014 | San Mateo | 3 | 5
94015 | San Mateo | 3 | 5
94019 | San Mateo | 3 | 5
94020 | San Mateo | 3 | 5
94021 | San Mateo | 3 | 5
94025 | San Mateo | 3 | 5
94027 | San Mateo | 3 | 5
94028 | San Mateo | 3 | 5
94030 | San Mateo | 3 | 5
94038 | San Mateo | 3 | 5
94044 | San Mateo | 3 | 5
94060 | San Mateo | 3 | 5
94061 | San Mateo | 3 | 5
94062 | San Mateo | 3 | 5
94063 | San Mateo | 3 | 5
94065 | San Mateo | 3 | 5
94066 | San Mateo | 3 | 5
94070 | San Mateo | 3 | 5
94074 | San Mateo | 3 | 5
94080 | San Mateo | 3 | 5
94112 | San Mateo | 3 | 5
94128 | San Mateo | 3 | 5
94134 | San Mateo | 3 | 5
94303 | San Mateo | 3 | 5
94401 | San Mateo | 3 | 5
94402 | San Mateo | 3 | 5
94403 | San Mateo | 3 | 5
94404 | San Mateo | 3 | 5
95006 | San Mateo | 3 | 5
93254 | Santa Barbara | 4 | 4
32 | Santa Barbara | 4 | 4
93252 | Santa Barbara | 4 | 4
95035 | Santa Clara | 4 | 4
95140 | Santa Clara | 4 | 4
94550 | Santa Clara | 4 | 4
95134 | Santa Clara | 4 | 4
95002 | Santa Clara | 4 | 4
94089 | Santa Clara | 4 | 4
94539 | Santa Clara | 4 | 4
94303 | Santa Clara | 4 | 4
94301 | Santa Clara | 4 | 4
94043 | Santa Clara | 4 | 4
94304 | Santa Clara | 4 | 4
94305 | Santa Clara | 4 | 4
94035 | Santa Clara | 4 | 4
95132 | Santa Clara | 4 | 4
94306 | Santa Clara | 4 | 4
95054 | Santa Clara | 4 | 4
94040 | Santa Clara | 4 | 4
95131 | Santa Clara | 4 | 4
95127 | Santa Clara | 4 | 4
94022 | Santa Clara | 4 | 4
94085 | Santa Clara | 4 | 4
94041 | Santa Clara | 4 | 4
95133 | Santa Clara | 4 | 4
94086 | Santa Clara | 4 | 4
94024 | Santa Clara | 4 | 4
95112 | Santa Clara | 4 | 4
95050 | Santa Clara | 4 | 4
95051 | Santa Clara | 4 | 4
95110 | Santa Clara | 4 | 4
94087 | Santa Clara | 4 | 4
94028 | Santa Clara | 4 | 4
95116 | Santa Clara | 4 | 4
95148 | Santa Clara | 4 | 4
95053 | Santa Clara | 4 | 4
95126 | Santa Clara | 4 | 4
95122 | Santa Clara | 4 | 4
95135 | Santa Clara | 4 | 4
95113 | Santa Clara | 4 | 4
95014 | Santa Clara | 4 | 4
95192 | Santa Clara | 4 | 4
95128 | Santa Clara | 4 | 4
95117 | Santa Clara | 4 | 4
95125 | Santa Clara | 4 | 4
95129 | Santa Clara | 4 | 4
95121 | Santa Clara | 4 | 4
95111 | Santa Clara | 4 | 4
94020 | Santa Clara | 4 | 4
95008 | Santa Clara | 4 | 4
95130 | Santa Clara | 4 | 4
95070 | Santa Clara | 4 | 4
95138 | Santa Clara | 4 | 4
95136 | Santa Clara | 4 | 4
95037 | Santa Clara | 4 | 4
95124 | Santa Clara | 4 | 4
95118 | Santa Clara | 4 | 4
95032 | Santa Clara | 4 | 4
95123 | Santa Clara | 4 | 4
95030 | Santa Clara | 4 | 4
95120 | Santa Clara | 4 | 4
95119 | Santa Clara | 4 | 4
95139 | Santa Clara | 4 | 4
95013 | Santa Clara | 4 | 4
95033 | Santa Clara | 4 | 4
95141 | Santa Clara | 4 | 4
95023 | Santa Clara | 4 | 4
95020 | Santa Clara | 4 | 4
95046 | Santa Clara | 4 | 4
93635 | Santa Clara | 4 | 4
95076 | Santa Clara | 4 | 4
95033 | Santa Cruz | 4 | 4
95076 | Santa Cruz | 4 | 4
93254 | Santa Barbara | 5 | 4
93454 | Santa Barbara | 5 | 4
32 | Santa Barbara | 5 | 4
93458 | Santa Barbara | 5 | 4
93434 | Santa Barbara | 5 | 4
93455 | Santa Barbara | 5 | 4
93252 | Santa Barbara | 5 | 4
93429 | Santa Barbara | 5 | 4
93460 | Santa Barbara | 5 | 4
93441 | Santa Barbara | 5 | 4
93437 | Santa Barbara | 5 | 4
93436 | Santa Barbara | 5 | 4
93427 | Santa Barbara | 5 | 4
93105 | Santa Barbara | 5 | 4
93463 | Santa Barbara | 5 | 4
93117 | Santa Barbara | 5 | 4
93108 | Santa Barbara | 5 | 4
93111 | Santa Barbara | 5 | 4
93013 | Santa Barbara | 5 | 4
93013 | Santa Barbara | 6 | 4
93067 | Santa Barbara | 6 | 4
93101 | Santa Barbara | 6 | 4
93103 | Santa Barbara | 6 | 4
93105 | Santa Barbara | 6 | 4
93106 | Santa Barbara | 6 | 4
93108 | Santa Barbara | 6 | 4
93109 | Santa Barbara | 6 | 4
93110 | Santa Barbara | 6 | 4
93111 | Santa Barbara | 6 | 4
93117 | Santa Barbara | 6 | 4
93436 | Santa Barbara | 6 | 4
93013 | Santa Barbara | 9 | 4
93108 | Santa Barbara | 9 | 4
93635 | Santa Clara | 12 | 4
94550 | Santa Clara | 12 | 4
95023 | Santa Clara | 12 | 4
95037 | Santa Clara | 12 | 4
93252 | Santa Barbara | 13 | 4
32 | Santa Barbara | 16 | 4
93105 | Santa Barbara | 16 | 4
93108 | Santa Barbara | 16 | 4
93252 | Santa Barbara | 16 | 4
94020 | Santa Clara | 3 | 4
94022 | Santa Clara | 3 | 4
94028 | Santa Clara | 3 | 4
94043 | Santa Clara | 3 | 4
94089 | Santa Clara | 3 | 4
94301 | Santa Clara | 3 | 4
94303 | Santa Clara | 3 | 4
94304 | Santa Clara | 3 | 4
94539 | Santa Clara | 3 | 4
95002 | Santa Clara | 3 | 4
95014 | Santa Clara | 3 | 4
95020 | Santa Clara | 3 | 4
95033 | Santa Clara | 3 | 4
95035 | Santa Clara | 3 | 4
95037 | Santa Clara | 3 | 4
95070 | Santa Clara | 3 | 4
95076 | Santa Clara | 3 | 4
95134 | Santa Clara | 3 | 4
94060 | Santa Cruz | 3 | 4
95003 | Santa Cruz | 3 | 4
95005 | Santa Cruz | 3 | 4
95006 | Santa Cruz | 3 | 4
95010 | Santa Cruz | 3 | 4
95017 | Santa Cruz | 3 | 4
95018 | Santa Cruz | 3 | 4
95019 | Santa Cruz | 3 | 4
95033 | Santa Cruz | 3 | 4
95060 | Santa Cruz | 3 | 4
95062 | Santa Cruz | 3 | 4
95064 | Santa Cruz | 3 | 4
95065 | Santa Cruz | 3 | 4
95066 | Santa Cruz | 3 | 4
95073 | Santa Cruz | 3 | 4
95076 | Santa Cruz | 3 | 4
96001 | Shasta | 11 | 3
96002 | Shasta | 11 | 3
96003 | Shasta | 11 | 3
96007 | Shasta | 11 | 3
96008 | Shasta | 11 | 3
96019 | Shasta | 11 | 3
96022 | Shasta | 11 | 3
96033 | Shasta | 11 | 3
96047 | Shasta | 11 | 3
96051 | Shasta | 11 | 3
96059 | Shasta | 11 | 3
96062 | Shasta | 11 | 3
96065 | Shasta | 11 | 3
96069 | Shasta | 11 | 3
96073 | Shasta | 11 | 3
96076 | Shasta | 11 | 3
96087 | Shasta | 11 | 3
96088 | Shasta | 11 | 3
96096 | Shasta | 11 | 3
96001 | Shasta | 16 | 3
96013 | Shasta | 16 | 3
96016 | Shasta | 16 | 3
96025 | Shasta | 16 | 3
96028 | Shasta | 16 | 3
96033 | Shasta | 16 | 3
96040 | Shasta | 16 | 3
96047 | Shasta | 16 | 3
96051 | Shasta | 16 | 3
96056 | Shasta | 16 | 3
96059 | Shasta | 16 | 3
96065 | Shasta | 16 | 3
96069 | Shasta | 16 | 3
96071 | Shasta | 16 | 3
96076 | Shasta | 16 | 3
96088 | Shasta | 16 | 3
96096 | Shasta | 16 | 3
95960 | Sierra | 11 | 1
33 | Sierra | 16 | 1
65 | Sierra | 16 | 1
95910 | Sierra | 16 | 1
95922 | Sierra | 16 | 1
95936 | Sierra | 16 | 1
95944 | Sierra | 16 | 1
95960 | Sierra | 16 | 1
96118 | Sierra | 16 | 1
96124 | Sierra | 16 | 1
96125 | Sierra | 16 | 1
96126 | Sierra | 16 | 1
49 | Siskiyou | 2 | 14
95568 | Siskiyou | 2 | 14
96031 | Siskiyou | 2 | 14
34 | Siskiyou | 16 | 14
35 | Siskiyou | 16 | 14
49 | Siskiyou | 16 | 14
95568 | Siskiyou | 16 | 14
96013 | Siskiyou | 16 | 14
96014 | Siskiyou | 16 | 14
96023 | Siskiyou | 16 | 14
96025 | Siskiyou | 16 | 14
96027 | Siskiyou | 16 | 14
96031 | Siskiyou | 16 | 14
96032 | Siskiyou | 16 | 14
96034 | Siskiyou | 16 | 14
96038 | Siskiyou | 16 | 14
96039 | Siskiyou | 16 | 14
96044 | Siskiyou | 16 | 14
96050 | Siskiyou | 16 | 14
96057 | Siskiyou | 16 | 14
96058 | Siskiyou | 16 | 14
96064 | Siskiyou | 16 | 14
96067 | Siskiyou | 16 | 14
96085 | Siskiyou | 16 | 14
96086 | Siskiyou | 16 | 14
96094 | Siskiyou | 16 | 14
96097 | Siskiyou | 16 | 14
96134 | Siskiyou | 16 | 14
94503 | Solano | 2 | 4
94534 | Solano | 2 | 4
94589 | Solano | 2 | 4
94591 | Solano | 2 | 4
95688 | Solano | 2 | 4
94589 | Solano | 3 | 4
94590 | Solano | 3 | 4
94591 | Solano | 3 | 4
94592 | Solano | 3 | 4
94503 | Solano | 12 | 4
94510 | Solano | 12 | 4
94512 | Solano | 12 | 4
94533 | Solano | 12 | 4
94534 | Solano | 12 | 4
94535 | Solano | 12 | 4
94571 | Solano | 12 | 4
94585 | Solano | 12 | 4
94591 | Solano | 12 | 4
95616 | Solano | 12 | 4
95618 | Solano | 12 | 4
95620 | Solano | 12 | 4
95687 | Solano | 12 | 4
95688 | Solano | 12 | 4
95690 | Solano | 12 | 4
95694 | Solano | 12 | 4
95421 | Sonoma | 1 | 4
95497 | Sonoma | 1 | 4
95448 | Sonoma | 1 | 4
95412 | Sonoma | 1 | 4
95480 | Sonoma | 1 | 4
95446 | Sonoma | 1 | 4
95450 | Sonoma | 1 | 4
95472 | Sonoma | 1 | 4
95462 | Sonoma | 1 | 4
95465 | Sonoma | 1 | 4
94923 | Sonoma | 1 | 4
94922 | Sonoma | 1 | 4
94952 | Sonoma | 1 | 4
94972 | Sonoma | 1 | 4
94515 | Sonoma | 2 | 4
94558 | Sonoma | 2 | 4
94574 | Sonoma | 2 | 4
94922 | Sonoma | 2 | 4
94928 | Sonoma | 2 | 4
94931 | Sonoma | 2 | 4
94951 | Sonoma | 2 | 4
94952 | Sonoma | 2 | 4
94954 | Sonoma | 2 | 4
94972 | Sonoma | 2 | 4
95401 | Sonoma | 2 | 4
95403 | Sonoma | 2 | 4
95404 | Sonoma | 2 | 4
95405 | Sonoma | 2 | 4
95407 | Sonoma | 2 | 4
95409 | Sonoma | 2 | 4
95412 | Sonoma | 2 | 4
95421 | Sonoma | 2 | 4
95425 | Sonoma | 2 | 4
95436 | Sonoma | 2 | 4
95439 | Sonoma | 2 | 4
95441 | Sonoma | 2 | 4
95442 | Sonoma | 2 | 4
95444 | Sonoma | 2 | 4
95446 | Sonoma | 2 | 4
95448 | Sonoma | 2 | 4
95452 | Sonoma | 2 | 4
95461 | Sonoma | 2 | 4
95462 | Sonoma | 2 | 4
95465 | Sonoma | 2 | 4
95472 | Sonoma | 2 | 4
95476 | Sonoma | 2 | 4
95492 | Sonoma | 2 | 4
94922 | Sonoma | 3 | 4
94923 | Sonoma | 3 | 4
94952 | Sonoma | 3 | 4
94972 | Sonoma | 3 | 4
95476 | Sonoma | 3 | 4
95363 | Stanislaus | 4 | 3
95360 | Stanislaus | 4 | 3
95230 | Stanislaus | 12 | 3
95307 | Stanislaus | 12 | 3
95313 | Stanislaus | 12 | 3
95316 | Stanislaus | 12 | 3
95322 | Stanislaus | 12 | 3
95323 | Stanislaus | 12 | 3
95326 | Stanislaus | 12 | 3
95329 | Stanislaus | 12 | 3
95350 | Stanislaus | 12 | 3
95351 | Stanislaus | 12 | 3
95354 | Stanislaus | 12 | 3
95355 | Stanislaus | 12 | 3
95356 | Stanislaus | 12 | 3
95357 | Stanislaus | 12 | 3
95358 | Stanislaus | 12 | 3
95360 | Stanislaus | 12 | 3
95361 | Stanislaus | 12 | 3
95363 | Stanislaus | 12 | 3
95367 | Stanislaus | 12 | 3
95368 | Stanislaus | 12 | 3
95380 | Stanislaus | 12 | 3
95382 | Stanislaus | 12 | 3
95385 | Stanislaus | 12 | 3
95386 | Stanislaus | 12 | 3
95626 | Sutter | 11 | 3
95645 | Sutter | 11 | 3
95659 | Sutter | 11 | 3
95668 | Sutter | 11 | 3
95674 | Sutter | 11 | 3
95836 | Sutter | 11 | 3
95837 | Sutter | 11 | 3
95901 | Sutter | 11 | 3
95948 | Sutter | 11 | 3
95953 | Sutter | 11 | 3
95957 | Sutter | 11 | 3
95982 | Sutter | 11 | 3
95991 | Sutter | 11 | 3
95993 | Sutter | 11 | 3
95645 | Sutter | 12 | 3
95659 | Sutter | 12 | 3
95836 | Sutter | 12 | 3
95837 | Sutter | 12 | 3
37 | Tehama | 11 | 3
38 | Tehama | 11 | 3
95428 | Tehama | 11 | 3
95963 | Tehama | 11 | 3
95973 | Tehama | 11 | 3
96007 | Tehama | 11 | 3
96021 | Tehama | 11 | 3
96022 | Tehama | 11 | 3
96035 | Tehama | 11 | 3
96055 | Tehama | 11 | 3
96059 | Tehama | 11 | 3
96075 | Tehama | 11 | 3
96076 | Tehama | 11 | 3
96080 | Tehama | 11 | 3
37 | Tehama | 16 | 3
38 | Tehama | 16 | 3
95428 | Tehama | 16 | 3
95942 | Tehama | 16 | 3
96059 | Tehama | 16 | 3
96063 | Tehama | 16 | 3
96075 | Tehama | 16 | 3
96076 | Tehama | 16 | 3
96080 | Tehama | 16 | 3
39 | Trinity | 2 | 1
95526 | Trinity | 2 | 1
95527 | Trinity | 2 | 1
95542 | Trinity | 2 | 1
95552 | Trinity | 2 | 1
95563 | Trinity | 2 | 1
95595 | Trinity | 2 | 1
96046 | Trinity | 2 | 1
96024 | Trinity | 11 | 1
96052 | Trinity | 11 | 1
96076 | Trinity | 11 | 1
39 | Trinity | 16 | 1
55 | Trinity | 16 | 1
95526 | Trinity | 16 | 1
95527 | Trinity | 16 | 1
95563 | Trinity | 16 | 1
95595 | Trinity | 16 | 1
96010 | Trinity | 16 | 1
96014 | Trinity | 16 | 1
96024 | Trinity | 16 | 1
96031 | Trinity | 16 | 1
96041 | Trinity | 16 | 1
96046 | Trinity | 16 | 1
96048 | Trinity | 16 | 1
96052 | Trinity | 16 | 1
96076 | Trinity | 16 | 1
96091 | Trinity | 16 | 1
96093 | Trinity | 16 | 1
93207 | Tulare | 13
93212 | Tulare | 13
93215 | Tulare | 13
93219 | Tulare | 13
93221 | Tulare | 13
93223 | Tulare | 13
93235 | Tulare | 13
93239 | Tulare | 13
93244 | Tulare | 13
93247 | Tulare | 13
93256 | Tulare | 13
93257 | Tulare | 13
93260 | Tulare | 13
93262 | Tulare | 13
93265 | Tulare | 13
93267 | Tulare | 13
93270 | Tulare | 13
93271 | Tulare | 13
93272 | Tulare | 13
93274 | Tulare | 13
93277 | Tulare | 13
93286 | Tulare | 13
93291 | Tulare | 13
93292 | Tulare | 13
93615 | Tulare | 13
93618 | Tulare | 13
93631 | Tulare | 13
93646 | Tulare | 13
93647 | Tulare | 13
93654 | Tulare | 13
26 | Tulare | 16
93207 | Tulare | 16
93257 | Tulare | 16
93260 | Tulare | 16
93262 | Tulare | 16
93265 | Tulare | 16
93271 | Tulare | 16
93286 | Tulare | 16
93633 | Tulare | 16
95222 | Tuolumne | 12 | 1 | 12
95228 | Tuolumne | 12 | 1 | 12
95309 | Tuolumne | 12 | 1 | 12
95310 | Tuolumne | 12 | 1 | 12
95311 | Tuolumne | 12 | 1 | 12
95321 | Tuolumne | 12 | 1 | 12
95327 | Tuolumne | 12 | 1 | 12
95329 | Tuolumne | 12 | 1 | 12
95346 | Tuolumne | 12 | 1 | 12
95370 | Tuolumne | 12 | 1 | 12
95372 | Tuolumne | 12 | 1 | 12
95379 | Tuolumne | 12 | 1 | 12
95383 | Tuolumne | 12 | 1 | 12
40 | Tuolumne | 16 | 1 | 12
95310 | Tuolumne | 16 | 1 | 12
95311 | Tuolumne | 16 | 1 | 12
95321 | Tuolumne | 16 | 1 | 12
95335 | Tuolumne | 16 | 1 | 12
95346 | Tuolumne | 16 | 1 | 12
95364 | Tuolumne | 16 | 1 | 12
95370 | Tuolumne | 16 | 1 | 12
95379 | Tuolumne | 16 | 1 | 12
95383 | Tuolumne | 16 | 1 | 12
95389 | Tuolumne | 16 | 1 | 12
93023 | Ventura | 5
90265 | Ventura | 6
91320 | Ventura | 6
91361 | Ventura | 6
93001 | Ventura | 6
93003 | Ventura | 6
93004 | Ventura | 6
93010 | Ventura | 6
93012 | Ventura | 6
93013 | Ventura | 6
93021 | Ventura | 6
93023 | Ventura | 6
93030 | Ventura | 6
93033 | Ventura | 6
93035 | Ventura | 6
93036 | Ventura | 6
93041 | Ventura | 6
93042 | Ventura | 6
93043 | Ventura | 6
93060 | Ventura | 6
93066 | Ventura | 6
90265 | Ventura | 9
91301 | Ventura | 9
91304 | Ventura | 9
91307 | Ventura | 9
91311 | Ventura | 9
91320 | Ventura | 9
91360 | Ventura | 9
91361 | Ventura | 9
91362 | Ventura | 9
91377 | Ventura | 9
93001 | Ventura | 9
93003 | Ventura | 9
93004 | Ventura | 9
93012 | Ventura | 9
93015 | Ventura | 9
93021 | Ventura | 9
93022 | Ventura | 9
93023 | Ventura | 9
93060 | Ventura | 9
93063 | Ventura | 9
93065 | Ventura | 9
93066 | Ventura | 9
93252 | Ventura | 13
18 | Ventura | 16
93015 | Ventura | 16
93023 | Ventura | 16
93060 | Ventura | 16
93225 | Ventura | 16
93243 | Ventura | 16
93252 | Ventura | 16
95606 | Yolo | 2 | 2
95607 | Yolo | 2 | 2
95679 | Yolo | 2 | 2
95694 | Yolo | 2 | 2
95645 | Yolo | 11 | 2
95679 | Yolo | 11 | 2
95691 | Yolo | 11 | 2
95776 | Yolo | 11 | 2
95937 | Yolo | 11 | 2
95605 | Yolo | 12 | 2
95606 | Yolo | 12 | 2
95607 | Yolo | 12 | 2
95612 | Yolo | 12 | 2
95615 | Yolo | 12 | 2
95616 | Yolo | 12 | 2
95618 | Yolo | 12 | 2
95620 | Yolo | 12 | 2
95627 | Yolo | 12 | 2
95637 | Yolo | 12 | 2
95645 | Yolo | 12 | 2
95653 | Yolo | 12 | 2
95679 | Yolo | 12 | 2
95691 | Yolo | 12 | 2
95694 | Yolo | 12 | 2
95695 | Yolo | 12 | 2
95698 | Yolo | 12 | 2
95776 | Yolo | 12 | 2
95937 | Yolo | 12 | 2
95674 | Yuba | 11 | 3
95692 | Yuba | 11 | 3
95901 | Yuba | 11 | 3
95903 | Yuba | 11 | 3
95914 | Yuba | 11 | 3
95918 | Yuba | 11 | 3
95919 | Yuba | 11 | 3
95922 | Yuba | 11 | 3
95925 | Yuba | 11 | 3
95935 | Yuba | 11 | 3
95941 | Yuba | 11 | 3
95953 | Yuba | 11 | 3
95960 | Yuba | 11 | 3
95961 | Yuba | 11 | 3
95962 | Yuba | 11 | 3
95966 | Yuba | 11 | 3
95972 | Yuba | 11 | 3
95977 | Yuba | 11 | 3
29 | Yuba | 16 | 3
95919 | Yuba | 16 | 3
95922 | Yuba | 16 | 3
95925 | Yuba | 16 | 3
95935 | Yuba | 16 | 3
95941 | Yuba | 16 | 3
95960 | Yuba | 16 | 3
95981 | Yuba | 16 | 3
95981 | Yuba | 16 | 3

## LoadShed Database
| CZ03 - San Francisco | [9 empty] | CZ04 - San Jose | [9 empty] | CZ12 - Stockon | [9 empty] | CZ13 - Fresno
| SmallOffice | CZ03 |  | OAT<=75°F |  | 75°F<=OAT<95°F |  | OAT>=95°F |  |  | SmallOffice | CZ04 |  | OAT<=75°F |  | 75°F<=OAT<95°F |  | OAT>=95°F |  |  | SmallOffice | CZ12 |  | OAT<=75°F |  | 75°F<=OAT<95°F |  | OAT>=95°F |  |  | Small Office | CZ13 |  | OAT<=75°F |  | 75°F<=OAT<95°F |  | OAT>=95°F
Case ID | Precool (°F) | Temp Reset (°F) | DR Event Hour (2PM to 6PM) | Equation_Slope | Equation_Intercept | Equation_Slope | Equation_Intercept | Equation_Slope | Equation_Intercept | Case ID | Precool (°F) | Temp Reset (°F) | DR Event Hour (2PM to 6PM) | Equation_Slope | Equation_Intercept | Equation_Slope | Equation_Intercept | Equation_Slope | Equation_Intercept | Case ID | Precool (°F) | Temp Reset (°F) | DR Event Hour (2PM to 6PM) | Equation_Slope | Equation_Intercept | Equation_Slope | Equation_Intercept | Equation_Slope | Equation_Intercept | Case ID | Precool (°F) | Temp Reset (°F) | DR Event Hour (2PM to 6PM) | Equation_Slope | Equation_Intercept | Equation_Slope | Equation_Intercept | Equation_Slope | Equation_Intercept
CZ03SmallOffice021 | 0 | 2 | 1 | 0.11935 | -0.51655 | -0.0043906 | 8.7355 | 0 | 0 | CZ04SmallOffice021 | 0 | 2 | 1 | 0.01816 | 6.8334 | 0.032894 | 6.2478 | 0.032894 | 6.2478 | CZ12SmallOffice021 | 0 | 2 | 1 | 0.091915 | 0.97803 | 0.074495 | 2.0237 | 0.026224 | 6.3685 | CZ13SmallOffice021 | 0 | 2 | 1 | 0.064127 | 2.6403 | 0.064127 | 2.6403 | 0.076893 | 1.3836
CZ03SmallOffice022 | 0 | 2 | 2 | 0.064874 | 1.1616 | 0.018016 | 4.5682 | 0 | 0 | CZ04SmallOffice022 | 0 | 2 | 2 | 0.10101 | -1.5006 | 0.030286 | 3.7809 | 0.030286 | 3.7809 | CZ12SmallOffice022 | 0 | 2 | 2 | 0.038374 | 2.6685 | 0.045517 | 2.1985 | 0.014512 | 5.0227 | CZ13SmallOffice022 | 0 | 2 | 2 | 0.039764 | 2.4715 | 0.039764 | 2.4715 | 0.041364 | 2.3523
CZ03SmallOffice023 | 0 | 2 | 3 | 0.041729 | 2.1608 | 0.018492 | 3.868 | 0 | 0 | CZ04SmallOffice023 | 0 | 2 | 3 | 0.057671 | 0.98565 | 0.026991 | 3.3141 | 0.026991 | 3.3141 | CZ12SmallOffice023 | 0 | 2 | 3 | 0.036224 | 2.2787 | 0.036131 | 2.3254 | 0.039172 | 1.893 | CZ13SmallOffice023 | 0 | 2 | 3 | 0.034594 | 2.2628 | 0.034594 | 2.2628 | 0.017509 | 3.9706
CZ03SmallOffice024 | 0 | 2 | 4 | 0.025758 | 4.9653 | -0.12256 | 16.4293 | 0 | 0 | CZ04SmallOffice024 | 0 | 2 | 4 | 0.064148 | 2.2545 | 0.01421 | 5.9359 | 0.01421 | 5.9359 | CZ12SmallOffice024 | 0 | 2 | 4 | 0.020003 | 4.812 | 0.026538 | 4.5593 | 0.0053597 | 6.6454 | CZ13SmallOffice024 | 0 | 2 | 4 | 0.038018 | 3.2708 | 0.038018 | 3.2708 | -0.010555 | 7.9124
CZ03SmallOffice041 | 0 | 4 | 1 | 0.34461 | -9.9756 | 0.061264 | 11.0124 | 0 | 0 | CZ04SmallOffice041 | 0 | 4 | 1 | 0.12839 | 5.7042 | 0.10329 | 8.4258 | 0.10329 | 8.4258 | CZ12SmallOffice041 | 0 | 4 | 1 | 0.27113 | -5.6506 | 0.1663 | 1.7097 | 0.049401 | 12.4939 | CZ13SmallOffice041 | 0 | 4 | 1 | 0.15302 | 2.5115 | 0.15302 | 2.5115 | 0.17732 | 0.12915
CZ03SmallOffice042 | 0 | 4 | 2 | 0.082875 | 5.4921 | 0.049786 | 7.9171 | 0 | 0 | CZ04SmallOffice042 | 0 | 4 | 2 | 0.19029 | -2.184 | 0.053157 | 8.0947 | 0.053157 | 8.0947 | CZ12SmallOffice042 | 0 | 4 | 2 | 0.087924 | 4.317 | 0.089937 | 4.3086 | 0.027596 | 10.0397 | CZ13SmallOffice042 | 0 | 4 | 2 | 0.086176 | 4.2349 | 0.086176 | 4.2349 | 0.089529 | 4.0093
CZ03SmallOffice043 | 0 | 4 | 3 | 0.066461 | 5.5214 | 0.041054 | 7.4117 | 0 | 0 | CZ04SmallOffice043 | 0 | 4 | 3 | 0.12113 | 1.699 | 0.048538 | 7.1777 | 0.048538 | 7.1777 | CZ12SmallOffice043 | 0 | 4 | 3 | 0.084171 | 3.6996 | 0.074325 | 4.4925 | 0.07319 | 4.3373 | CZ13SmallOffice043 | 0 | 4 | 3 | 0.077331 | 3.8683 | 0.077331 | 3.8683 | 0.04633 | 6.9668
CZ03SmallOffice044 | 0 | 4 | 4 | 0.24055 | -2.9326 | -0.27655 | 35.5467 | 0 | 0 | CZ04SmallOffice044 | 0 | 4 | 4 | 0.12513 | 5.0181 | 0.015623 | 13.0589 | 0.015623 | 13.0589 | CZ12SmallOffice044 | 0 | 4 | 4 | 0.12069 | 3.9575 | 0.052544 | 9.2163 | 0.011332 | 13.235 | CZ13SmallOffice044 | 0 | 4 | 4 | 0.083337 | 6.002 | 0.083337 | 6.002 | -0.015521 | 15.4206
CZ03SmallOffice061 | 0 | 6 | 1 | 0.67934 | -30.6697 | 0.21323 | 4.2163 | 0 | 0 | CZ04SmallOffice061 | 0 | 6 | 1 | 0.376 | -8.3633 | 0.23451 | 3.8686 | 0.23451 | 3.8686 | CZ12SmallOffice061 | 0 | 6 | 1 | 0.58974 | -24.6874 | 0.27355 | -1.7758 | 0.055415 | 18.2759 | CZ13SmallOffice061 | 0 | 6 | 1 | 0.22153 | 2.2721 | 0.22153 | 2.2721 | 0.22374 | 1.9519
CZ03SmallOffice062 | 0 | 6 | 2 | 0.5133 | -19.1343 | 0.064895 | 12.8751 | 0 | 0 | CZ04SmallOffice062 | 0 | 6 | 2 | 0.11299 | 9.3919 | 0.022844 | 16.5025 | 0.022844 | 16.5025 | CZ12SmallOffice062 | 0 | 6 | 2 | 0.27054 | -3.835 | 0.07789 | 10.6834 | 0.026187 | 15.4834 | CZ13SmallOffice062 | 0 | 6 | 2 | 0.092385 | 8.7958 | 0.092385 | 8.7958 | 0.12873 | 5.5307
CZ03SmallOffice063 | 0 | 6 | 3 | 0.25734 | -2.7206 | 0.058596 | 11.1885 | 0 | 0 | CZ04SmallOffice063 | 0 | 6 | 3 | 0.063158 | 10.936 | 0.048488 | 12.1911 | 0.048488 | 12.1911 | CZ12SmallOffice063 | 0 | 6 | 3 | 0.15723 | 2.9279 | 0.084911 | 8.2986 | 0.075153 | 9.0453 | CZ13SmallOffice063 | 0 | 6 | 3 | 0.10613 | 5.9595 | 0.10613 | 5.9595 | 0.070195 | 9.6054
CZ03SmallOffice064 | 0 | 6 | 4 | 0.68617 | -29.3423 | -0.46797 | 57.4124 | 0 | 0 | CZ04SmallOffice064 | 0 | 6 | 4 | 0.48188 | -14.4101 | -0.019493 | 22.4647 | -0.019493 | 22.4647 | CZ12SmallOffice064 | 0 | 6 | 4 | 0.45296 | -14.5414 | 0.055376 | 14.9451 | -0.00033263 | 20.449 | CZ13SmallOffice064 | 0 | 6 | 4 | 0.11325 | 9.2141 | 0.11325 | 9.2141 | -0.019799 | 21.9506
CZ03SmallOffice-221 | -2 | 2 | 1 | 0.21716 | -4.5893 | 0.016454 | 10.4661 | 0 | 0 | CZ04SmallOffice-221 | -2 | 2 | 1 | 0.067147 | 6.3758 | 0.065326 | 7.3842 | 0.065326 | 7.3842 | CZ12SmallOffice-221 | -2 | 2 | 1 | 0.19696 | -3.6935 | 0.13152 | 0.72433 | 0.032517 | 9.7761 | CZ13SmallOffice-221 | -2 | 2 | 1 | 0.11279 | 2.0381 | 0.11279 | 2.0381 | 0.135 | -0.14508
CZ03SmallOffice-222 | -2 | 2 | 2 | 0.085612 | 1.1732 | 0.01488 | 6.3117 | 0 | 0 | CZ04SmallOffice-222 | -2 | 2 | 2 | 0.13435 | -2.3851 | 0.032792 | 5.1954 | 0.032792 | 5.1954 | CZ12SmallOffice-222 | -2 | 2 | 2 | 0.055981 | 2.8107 | 0.058258 | 2.6804 | 0.021705 | 5.9695 | CZ13SmallOffice-222 | -2 | 2 | 2 | 0.051276 | 3.0218 | 0.051276 | 3.0218 | 0.052641 | 2.9336
CZ03SmallOffice-223 | -2 | 2 | 3 | 0.04977 | 2.6061 | 0.018637 | 4.8699 | 0 | 0 | CZ04SmallOffice-223 | -2 | 2 | 3 | 0.070066 | 1.114 | 0.03084 | 4.0606 | 0.03084 | 4.0606 | CZ12SmallOffice-223 | -2 | 2 | 3 | 0.044902 | 2.6305 | 0.042156 | 2.8742 | 0.049715 | 2.0012 | CZ13SmallOffice-223 | -2 | 2 | 3 | 0.04114 | 2.7573 | 0.04114 | 2.7573 | 0.020716 | 4.7949
CZ03SmallOffice-224 | -2 | 2 | 4 | 0.036315 | 5.3908 | -0.13435 | 18.4408 | 0 | 0 | CZ04SmallOffice-224 | -2 | 2 | 4 | 0.068734 | 3.0877 | 0.016159 | 6.9446 | 0.016159 | 6.9446 | CZ12SmallOffice-224 | -2 | 2 | 4 | 0.021342 | 5.7804 | 0.029363 | 5.4659 | 0.0060761 | 7.7946 | CZ13SmallOffice-224 | -2 | 2 | 4 | 0.043801 | 3.9095 | 0.043801 | 3.9095 | -0.01122 | 9.1517
CZ03SmallOffice-241 | -2 | 4 | 1 | 0.54155 | -22.0806 | 0.10651 | 10.0225 | 0 | 0 | CZ04SmallOffice-241 | -2 | 4 | 1 | 0.19537 | 3.011 | 0.15007 | 7.4721 | 0.15007 | 7.4721 | CZ12SmallOffice-241 | -2 | 4 | 1 | 0.42592 | -14.787 | 0.20394 | 1.1001 | 0.054034 | 14.9596 | CZ13SmallOffice-241 | -2 | 4 | 1 | 0.18757 | 2.1267 | 0.18757 | 2.1267 | 0.21595 | -0.63556
CZ03SmallOffice-242 | -2 | 4 | 2 | 0.12442 | 4.2019 | 0.051989 | 9.3369 | 0 | 0 | CZ04SmallOffice-242 | -2 | 4 | 2 | 0.14329 | 2.8182 | 0.044364 | 10.3644 | 0.044364 | 10.3644 | CZ12SmallOffice-242 | -2 | 4 | 2 | 0.076623 | 6.4221 | 0.089156 | 5.832 | 0.02925 | 11.361 | CZ13SmallOffice-242 | -2 | 4 | 2 | 0.092094 | 5.1422 | 0.092094 | 5.1422 | 0.1052 | 4.0165
CZ03SmallOffice-243 | -2 | 4 | 3 | 0.058961 | 7.0203 | 0.040828 | 8.4023 | 0 | 0 | CZ04SmallOffice-243 | -2 | 4 | 3 | 0.12713 | 2.2498 | 0.049992 | 8.0453 | 0.049992 | 8.0453 | CZ12SmallOffice-243 | -2 | 4 | 3 | 0.082997 | 4.6941 | 0.077776 | 5.1838 | 0.079887 | 4.7359 | CZ13SmallOffice-243 | -2 | 4 | 3 | 0.084962 | 4.1989 | 0.084962 | 4.1989 | 0.053599 | 7.3413
CZ03SmallOffice-244 | -2 | 4 | 4 | 0.3231 | -7.5274 | -0.31989 | 40.0928 | 0 | 0 | CZ04SmallOffice-244 | -2 | 4 | 4 | 0.12424 | 6.2337 | 0.013251 | 14.3535 | 0.013251 | 14.3535 | CZ12SmallOffice-244 | -2 | 4 | 4 | 0.16977 | 1.4859 | 0.053641 | 10.1969 | 0.013371 | 14.1723 | CZ13SmallOffice-244 | -2 | 4 | 4 | 0.090794 | 6.434 | 0.090794 | 6.434 | -0.016008 | 16.6101
CZ03SmallOffice-261 | -2 | 6 | 1 | 0.71882 | -33.2856 | 0.32217 | -3.6174 | 0 | 0 | CZ04SmallOffice-261 | -2 | 6 | 1 | 0.41539 | -10.8848 | 0.3594 | -4.7878 | 0.3594 | -4.7878 | CZ12SmallOffice-261 | -2 | 6 | 1 | 0.64056 | -27.9185 | 0.39223 | -10.1381 | 0.073496 | 19.2659 | CZ13SmallOffice-261 | -2 | 6 | 1 | 0.30855 | -3.2396 | 0.30855 | -3.2396 | 0.24434 | 2.6439
CZ03SmallOffice-262 | -2 | 6 | 2 | 0.62654 | -26.3413 | 0.08745 | 12.966 | 0 | 0 | CZ04SmallOffice-262 | -2 | 6 | 2 | 0.47675 | -15.5646 | 0.0048648 | 20.0419 | 0.0048648 | 20.0419 | CZ12SmallOffice-262 | -2 | 6 | 2 | 0.40858 | -12.4509 | 0.068578 | 13.1757 | 0.014429 | 18.1408 | CZ13SmallOffice-262 | -2 | 6 | 2 | 0.076246 | 11.7798 | 0.076246 | 11.7798 | 0.13404 | 6.4921
CZ03SmallOffice-263 | -2 | 6 | 3 | 0.39025 | -10.8004 | 0.041431 | 13.8779 | 0 | 0 | CZ04SmallOffice-263 | -2 | 6 | 3 | 0.04779 | 13.4167 | 0.030355 | 14.8804 | 0.030355 | 14.8804 | CZ12SmallOffice-263 | -2 | 6 | 3 | 0.24504 | -2.2805 | 0.073271 | 10.3405 | 0.075595 | 10.0125 | CZ13SmallOffice-263 | -2 | 6 | 3 | 0.10317 | 7.2186 | 0.10317 | 7.2186 | 0.077528 | 9.9261
CZ03SmallOffice-264 | -2 | 6 | 4 | 0.7218 | -31.4646 | -0.38822 | 52.1796 | 0 | 0 | CZ04SmallOffice-264 | -2 | 6 | 4 | 0.64226 | -24.9962 | -0.021395 | 23.9602 | -0.021395 | 23.9602 | CZ12SmallOffice-264 | -2 | 6 | 4 | 0.505 | -17.614 | 0.049344 | 16.5698 | 0.00062394 | 21.4335 | CZ13SmallOffice-264 | -2 | 6 | 4 | 0.11005 | 10.5804 | 0.11005 | 10.5804 | -0.017134 | 22.7932
| MediumOffice |  |  | OAT<=75°F |  | 75°F<=OAT<95°F |  | OAT>=95°F |  |  | MediumOffice |  |  | OAT<=75°F |  | 75°F<=OAT<95°F |  | OAT>=95°F |  |  | MediumOffice |  |  | OAT<=75°F |  | 75°F<=OAT<95°F |  | OAT>=95°F |  |  | MediumOffice |  |  | OAT<=75°F |  | 75°F<=OAT<95°F |  | OAT>=95°F
Case ID | Precool (°F) | Temp Reset (°F) | DR Event Hour | Equation_Slope | Equation_Intercept | Equation_Slope | Equation_Intercept | Equation_Slope | Equation_Intercept | Case ID | Precool (°F) | Temp Reset (°F) | DR Event Hour | Equation_Slope | Equation_Intercept | Equation_Slope | Equation_Intercept | Equation_Slope | Equation_Intercept | Case ID | Precool (°F) | Temp Reset (°F) | DR Event Hour | Equation_Slope | Equation_Intercept | Equation_Slope | Equation_Intercept | Equation_Slope | Equation_Intercept | Case ID | Precool (°F) | Temp Reset (°F) | DR Event Hour | Equation_Slope | Equation_Intercept | Equation_Slope | Equation_Intercept | Equation_Slope | Equation_Intercept
CZ03MediumOffice021 | 0 | 2 | 1 | 0.55109 | -32.2251 | 0.051331 | 5.0329 | 0 | 0 | CZ04MediumOffice021 | 0 | 2 | 1 | 0.20709 | -7.0308 | 0.025276 | 7.2413 | 0.025276 | 7.2413 | CZ12MediumOffice021 | 0 | 2 | 1 | 0.38868 | -22.3077 | 0.2974 | -15.3798 | 0.20225 | -6.7538 | CZ13MediumOffice021 | 0 | 2 | 1 | 0.25046 | -10.7854 | 0.25046 | -10.7854 | 0.20653 | -6.7233
CZ03MediumOffice022 | 0 | 2 | 2 | 0.56864 | -32.7996 | -0.053433 | 12.6156 | 0 | 0 | CZ04MediumOffice022 | 0 | 2 | 2 | 0.71136 | -43.0723 | -0.03271 | 10.8927 | -0.03271 | 10.8927 | CZ12MediumOffice022 | 0 | 2 | 2 | 0.42933 | -24.7598 | 0.13714 | -2.9165 | 0.091902 | 1.446 | CZ13MediumOffice022 | 0 | 2 | 2 | 0.14247 | -3.3495 | 0.14247 | -3.3495 | 0.11939 | -1.097
CZ03MediumOffice023 | 0 | 2 | 3 | 0.4558 | -25.0849 | -0.076112 | 13.7125 | 0 | 0 | CZ04MediumOffice023 | 0 | 2 | 3 | 0.57896 | -33.6029 | -0.051962 | 11.6524 | -0.051962 | 11.6524 | CZ12MediumOffice023 | 0 | 2 | 3 | 0.31324 | -16.8188 | 0.10151 | -0.50796 | 0.14305 | -4.5815 | CZ13MediumOffice023 | 0 | 2 | 3 | 0.11991 | -2.173 | 0.11991 | -2.173 | 0.12719 | -2.8661
CZ03MediumOffice024 | 0 | 2 | 4 | 0.35537 | -19.1357 | -0.043095 | 9.5405 | 0 | 0 | CZ04MediumOffice024 | 0 | 2 | 4 | 0.50686 | -29.115 | -0.11756 | 15.9518 | -0.11756 | 15.9518 | CZ12MediumOffice024 | 0 | 2 | 4 | 0.28969 | -15.7703 | 0.091573 | -0.15004 | 0.067354 | 2.4087 | CZ13MediumOffice024 | 0 | 2 | 4 | 0.13951 | -4.4646 | 0.13951 | -4.4646 | 0.10489 | -1.1328
CZ03MediumOffice041 | 0 | 4 | 1 | 0.61374 | -36.1973 | 0.19203 | -4.719 | 0 | 0 | CZ04MediumOffice041 | 0 | 4 | 1 | 0.25883 | -10.1017 | 0.1075 | 2.1587 | 0.1075 | 2.1587 | CZ12MediumOffice041 | 0 | 4 | 1 | 0.3994 | -22.8948 | 0.47416 | -28.2714 | 0.44347 | -25.3658 | CZ13MediumOffice041 | 0 | 4 | 1 | 0.45652 | -25.7213 | 0.45652 | -25.7213 | 0.46854 | -26.9851
CZ03MediumOffice042 | 0 | 4 | 2 | 0.76034 | -44.6752 | 0.021674 | 9.8639 | 0 | 0 | CZ04MediumOffice042 | 0 | 4 | 2 | 1.3156 | -84.6406 | 0.051614 | 7.6135 | 0.051614 | 7.6135 | CZ12MediumOffice042 | 0 | 4 | 2 | 0.50267 | -29.206 | 0.38331 | -19.9602 | 0.27802 | -10.071 | CZ13MediumOffice042 | 0 | 4 | 2 | 0.36897 | -18.4284 | 0.36897 | -18.4284 | 0.27828 | -9.4091
CZ03MediumOffice043 | 0 | 4 | 3 | 0.66956 | -37.6463 | -0.011327 | 12.447 | 0 | 0 | CZ04MediumOffice043 | 0 | 4 | 3 | 1.0708 | -65.8253 | 0.031219 | 9.2362 | 0.031219 | 9.2362 | CZ12MediumOffice043 | 0 | 4 | 3 | 0.39986 | -21.5111 | 0.31082 | -13.3169 | 0.29109 | -11.867 | CZ13MediumOffice043 | 0 | 4 | 3 | 0.34705 | -16.4987 | 0.34705 | -16.4987 | 0.24088 | -6.4372
CZ03MediumOffice044 | 0 | 4 | 4 | 0.49053 | -26.3986 | -0.040987 | 12.4854 | 0 | 0 | CZ04MediumOffice044 | 0 | 4 | 4 | 0.7412 | -43.1152 | -0.087768 | 17.33 | -0.087768 | 17.33 | CZ12MediumOffice044 | 0 | 4 | 4 | 0.37801 | -20.3472 | 0.28876 | -12.273 | 0.16576 | -0.33813 | CZ13MediumOffice044 | 0 | 4 | 4 | 0.39861 | -22.3313 | 0.39861 | -22.3313 | 0.18884 | -2.2991
CZ03MediumOffice061 | 0 | 6 | 1 | 0.61579 | -36.3345 | 0.25488 | -9.5924 | 0 | 0 | CZ04MediumOffice061 | 0 | 6 | 1 | 0.259 | -10.0945 | 0.12676 | 0.66896 | 0.12676 | 0.66896 | CZ12MediumOffice061 | 0 | 6 | 1 | 0.3994 | -22.8948 | 0.48483 | -29.0459 | 0.5362 | -33.9498 | CZ13MediumOffice061 | 0 | 6 | 1 | 0.48084 | -27.641 | 0.48084 | -27.641 | 0.54534 | -33.9351
CZ03MediumOffice062 | 0 | 6 | 2 | 0.77752 | -45.7935 | 0.071124 | 6.4032 | 0 | 0 | CZ04MediumOffice062 | 0 | 6 | 2 | 1.3706 | -88.5221 | 0.098486 | 4.2271 | 0.098486 | 4.2271 | CZ12MediumOffice062 | 0 | 6 | 2 | 0.50267 | -29.206 | 0.4512 | -25.0384 | 0.44943 | -24.9343 | CZ13MediumOffice062 | 0 | 6 | 2 | 0.43943 | -23.6216 | 0.43943 | -23.6216 | 0.42558 | -21.9385
CZ03MediumOffice063 | 0 | 6 | 3 | 0.7305 | -41.4464 | -0.0089218 | 12.9396 | 0 | 0 | CZ04MediumOffice063 | 0 | 6 | 3 | 1.151 | -71.1036 | 0.061701 | 7.7165 | 0.061701 | 7.7165 | CZ12MediumOffice063 | 0 | 6 | 3 | 0.40892 | -22.0903 | 0.37681 | -17.873 | 0.50828 | -30.7894 | CZ13MediumOffice063 | 0 | 6 | 3 | 0.42887 | -22.556 | 0.42887 | -22.556 | 0.43765 | -23.245
CZ03MediumOffice064 | 0 | 6 | 4 | 0.52548 | -28.4277 | -0.11589 | 19.0053 | 0 | 0 | CZ04MediumOffice064 | 0 | 6 | 4 | 0.84465 | -49.961 | -0.076902 | 17.4878 | -0.076902 | 17.4878 | CZ12MediumOffice064 | 0 | 6 | 4 | 0.39572 | -21.3776 | 0.35785 | -16.8258 | 0.28704 | -9.4476 | CZ13MediumOffice064 | 0 | 6 | 4 | 0.49845 | -29.8094 | 0.49845 | -29.8094 | 0.33079 | -13.3735
CZ03MediumOffice-221 | -2 | 2 | 1 | 0.59482 | -34.9756 | 0.080484 | 4.0845 | 0 | 0 | CZ04MediumOffice-221 | -2 | 2 | 1 | 0.25515 | -10.0015 | 0.035782 | 8.1178 | 0.035782 | 8.1178 | CZ12MediumOffice-221 | -2 | 2 | 1 | 0.39888 | -22.8667 | 0.41916 | -24.0613 | 0.31009 | -14.1555 | CZ13MediumOffice-221 | -2 | 2 | 1 | 0.37192 | -19.1718 | 0.37192 | -19.1718 | 0.3413 | -16.4405
CZ03MediumOffice-222 | -2 | 2 | 2 | 0.64294 | -37.3952 | -0.030045 | 12.2559 | 0 | 0 | CZ04MediumOffice-222 | -2 | 2 | 2 | 1.031 | -65.1961 | -0.017944 | 11.6073 | -0.017944 | 11.6073 | CZ12MediumOffice-222 | -2 | 2 | 2 | 0.48549 | -28.2232 | 0.22464 | -8.5856 | 0.16634 | -3.2994 | CZ13MediumOffice-222 | -2 | 2 | 2 | 0.19881 | -6.1241 | 0.19881 | -6.1241 | 0.16639 | -2.9384
CZ03MediumOffice-223 | -2 | 2 | 3 | 0.54359 | -30.4297 | -0.067653 | 14.543 | 0 | 0 | CZ04MediumOffice-223 | -2 | 2 | 3 | 0.78458 | -47.2764 | -0.044766 | 12.8625 | -0.044766 | 12.8625 | CZ12MediumOffice-223 | -2 | 2 | 3 | 0.35089 | -18.9911 | 0.14187 | -2.2536 | 0.1979 | -7.7519 | CZ13MediumOffice-223 | -2 | 2 | 3 | 0.16502 | -4.2412 | 0.16502 | -4.2412 | 0.14354 | -2.2116
CZ03MediumOffice-224 | -2 | 2 | 4 | 0.40128 | -21.7942 | -0.035472 | 10.1855 | 0 | 0 | CZ04MediumOffice-224 | -2 | 2 | 4 | 0.5874 | -34.12 | -0.094158 | 15.4182 | -0.094158 | 15.4182 | CZ12MediumOffice-224 | -2 | 2 | 4 | 0.31521 | -17.1835 | 0.13129 | -2.1194 | 0.099003 | 1.2307 | CZ13MediumOffice-224 | -2 | 2 | 4 | 0.19247 | -7.6161 | 0.19247 | -7.6161 | 0.11539 | -0.2352
CZ03MediumOffice-241 | -2 | 4 | 1 | 0.61874 | -36.544 | 0.20895 | -5.5477 | 0 | 0 | CZ04MediumOffice-241 | -2 | 4 | 1 | 0.28225 | -11.7442 | 0.086642 | 4.5396 | 0.086642 | 4.5396 | CZ12MediumOffice-241 | -2 | 4 | 1 | 0.3994 | -22.895 | 0.49917 | -29.9737 | 0.49818 | -30.0252 | CZ13MediumOffice-241 | -2 | 4 | 1 | 0.47218 | -26.5807 | 0.47218 | -26.5807 | 0.53126 | -32.3456
CZ03MediumOffice-242 | -2 | 4 | 2 | 0.77161 | -45.422 | 0.055424 | 7.4844 | 0 | 0 | CZ04MediumOffice-242 | -2 | 4 | 2 | 1.3394 | -86.3045 | 0.066843 | 6.9135 | 0.066843 | 6.9135 | CZ12MediumOffice-242 | -2 | 4 | 2 | 0.50267 | -29.206 | 0.41323 | -22.0653 | 0.3493 | -16.0326 | CZ13MediumOffice-242 | -2 | 4 | 2 | 0.39714 | -20.3478 | 0.39714 | -20.3478 | 0.33573 | -13.9645
CZ03MediumOffice-243 | -2 | 4 | 3 | 0.68431 | -38.5757 | 0.011898 | 10.8793 | 0 | 0 | CZ04MediumOffice-243 | -2 | 4 | 3 | 1.0851 | -66.7242 | 0.048939 | 8.3303 | 0.048939 | 8.3303 | CZ12MediumOffice-243 | -2 | 4 | 3 | 0.40379 | -21.7623 | 0.34676 | -15.9308 | 0.37662 | -19.0856 | CZ13MediumOffice-243 | -2 | 4 | 3 | 0.39125 | -19.8239 | 0.39125 | -19.8239 | 0.31425 | -12.3817
CZ03MediumOffice-244 | -2 | 4 | 4 | 0.50385 | -27.152 | -0.069245 | 15.0377 | 0 | 0 | CZ04MediumOffice-244 | -2 | 4 | 4 | 0.7695 | -44.8981 | -0.067409 | 16.2013 | -0.067409 | 16.2013 | CZ12MediumOffice-244 | -2 | 4 | 4 | 0.38608 | -20.7969 | 0.32001 | -14.372 | 0.21258 | -3.7309 | CZ13MediumOffice-244 | -2 | 4 | 4 | 0.43613 | -24.9959 | 0.43613 | -24.9959 | 0.24573 | -6.6921
CZ03MediumOffice-261 | -2 | 6 | 1 | 0.61874 | -36.544 | 0.25166 | -8.8691 | 0 | 0 | CZ04MediumOffice-261 | -2 | 6 | 1 | 0.28196 | -11.7234 | 0.10023 | 3.4802 | 0.10023 | 3.4802 | CZ12MediumOffice-261 | -2 | 6 | 1 | 0.3994 | -22.895 | 0.50515 | -30.4156 | 0.51773 | -31.7669 | CZ13MediumOffice-261 | -2 | 6 | 1 | 0.48277 | -27.432 | 0.48277 | -27.432 | 0.55598 | -34.5678
CZ03MediumOffice-262 | -2 | 6 | 2 | 0.78026 | -45.9875 | 0.089905 | 5.0216 | 0 | 0 | CZ04MediumOffice-262 | -2 | 6 | 2 | 1.3706 | -88.5221 | 0.1 | 4.4749 | 0.1 | 4.4749 | CZ12MediumOffice-262 | -2 | 6 | 2 | 0.50267 | -29.206 | 0.46946 | -26.3613 | 0.46877 | -26.4101 | CZ13MediumOffice-262 | -2 | 6 | 2 | 0.45422 | -24.5996 | 0.45422 | -24.5996 | 0.4422 | -23.0912
CZ03MediumOffice-263 | -2 | 6 | 3 | 0.73427 | -41.7061 | 0.010696 | 11.5526 | 0 | 0 | CZ04MediumOffice-263 | -2 | 6 | 3 | 1.1535 | -71.2748 | 0.069968 | 7.4214 | 0.069968 | 7.4214 | CZ12MediumOffice-263 | -2 | 6 | 3 | 0.40892 | -22.0903 | 0.39235 | -18.9195 | 0.52462 | -31.971 | CZ13MediumOffice-263 | -2 | 6 | 3 | 0.44228 | -23.4148 | 0.44228 | -23.4148 | 0.45584 | -24.6196
CZ03MediumOffice-264 | -2 | 6 | 4 | 0.52773 | -28.5842 | -0.12785 | 20.1616 | 0 | 0 | CZ04MediumOffice-264 | -2 | 6 | 4 | 0.84752 | -50.1602 | -0.053375 | 15.7936 | -0.053375 | 15.7936 | CZ12MediumOffice-264 | -2 | 6 | 4 | 0.3966 | -21.4383 | 0.37617 | -18.1435 | 0.28722 | -9.0664 | CZ13MediumOffice-264 | -2 | 6 | 4 | 0.51501 | -30.9971 | 0.51501 | -30.9971 | 0.33037 | -12.9531
| LargeOffice |  |  | OAT<=75°F |  | 75°F<=OAT<95°F |  | OAT>=95°F |  |  | LargeOffice |  |  | OAT<=75°F |  | 75°F<=OAT<95°F |  | OAT>=95°F |  |  | LargeOffice |  |  | OAT<=75°F |  | 75°F<=OAT<95°F |  | OAT>=95°F |  |  | LargeOffice |  |  | OAT<=75°F |  | 75°F<=OAT<95°F |  | OAT>=95°F
| Precool (°F) | Temp Reset (°F) | DR Event Hour | Equation_Slope | Equation_Intercept | Equation_Slope | Equation_Intercept | Equation_Slope | Equation_Intercept | Case ID | Precool (°F) | Temp Reset (°F) | DR Event Hour | Equation_Slope | Equation_Intercept | Equation_Slope | Equation_Intercept | Equation_Slope | Equation_Intercept | Case ID | Precool (°F) | Temp Reset (°F) | DR Event Hour | Equation_Slope | Equation_Intercept | Equation_Slope | Equation_Intercept | Equation_Slope | Equation_Intercept | Case ID | Precool (°F) | Temp Reset (°F) | DR Event Hour | Equation_Slope | Equation_Intercept | Equation_Slope | Equation_Intercept | Equation_Slope | Equation_Intercept
CZ03LargeOffice021 | 0 | 2 | 1 | 0.23755 | -10.3155 | 0.092342 | -0.1382 | 0 | 0 | CZ04LargeOffice021 | 0 | 2 | 1 | -0.013307 | 7.3452 | 0.041225 | 3.3646 | 0.041225 | 3.3646 | CZ12LargeOffice021 | 0 | 2 | 1 | 0.075492 | 0.13188 | 0.092617 | -1.0564 | -0.035035 | 11.4428 | CZ13LargeOffice021 | 0 | 2 | 1 | 1.0781 | -73.5506 | 0.099993 | -1.6572 | -0.0080027 | 8.6184
CZ03LargeOffice022 | 0 | 2 | 2 | 0.16214 | -6.5907 | 0.068107 | 0.25936 | 0 | 0 | CZ04LargeOffice022 | 0 | 2 | 2 | 0.13091 | -4.5278 | 0.045831 | 1.8407 | 0.045831 | 1.8407 | CZ12LargeOffice022 | 0 | 2 | 2 | 0.055722 | 0.80424 | 0.076918 | -0.91539 | 0.069036 | -0.085885 | CZ13LargeOffice022 | 0 | 2 | 2 | -2.0182 | 155.9089 | 0.073322 | -0.50506 | 0.026521 | 4.1336
CZ03LargeOffice023 | 0 | 2 | 3 | 0.16214 | -6.5907 | 0.068107 | 0.25936 | 0 | 0 | CZ04LargeOffice023 | 0 | 2 | 3 | 0.13091 | -4.5278 | 0.045831 | 1.8407 | 0.045831 | 1.8407 | CZ12LargeOffice023 | 0 | 2 | 3 | 0.055722 | 0.80424 | 0.076918 | -0.91539 | 0.069036 | -0.085885 | CZ13LargeOffice023 | 0 | 2 | 3 | -2.0182 | 155.9089 | 0.073322 | -0.50506 | 0.026521 | 4.1336
CZ03LargeOffice024 | 0 | 2 | 4 | 0.16214 | -6.5907 | 0.068107 | 0.25936 | 0 | 0 | CZ04LargeOffice024 | 0 | 2 | 4 | 0.13091 | -4.5278 | 0.045831 | 1.8407 | 0.045831 | 1.8407 | CZ12LargeOffice024 | 0 | 2 | 4 | 0.055722 | 0.80424 | 0.076918 | -0.91539 | 0.069036 | -0.085885 | CZ13LargeOffice024 | 0 | 2 | 4 | -2.0182 | 155.9089 | 0.073322 | -0.50506 | 0.026521 | 4.1336
CZ03LargeOffice041 | 0 | 4 | 1 | 0.44653 | -20.9671 | 0.21497 | -4.6279 | 0 | 0 | CZ04LargeOffice041 | 0 | 4 | 1 | 0.13324 | 1.1589 | 0.094903 | 4.7893 | 0.094903 | 4.7893 | CZ12LargeOffice041 | 0 | 4 | 1 | 0.12877 | -0.38079 | 0.193 | -3.8998 | 0.10448 | 4.3342 | CZ13LargeOffice041 | 0 | 4 | 1 | 2.1018 | -145.1985 | 0.15418 | -0.28934 | 0.13999 | 1.1451
CZ03LargeOffice042 | 0 | 4 | 2 | 0.28332 | -10.959 | 0.10255 | 2.2098 | 0 | 0 | CZ04LargeOffice042 | 0 | 4 | 2 | 0.33515 | -15.0859 | 0.076302 | 4.1881 | 0.076302 | 4.1881 | CZ12LargeOffice042 | 0 | 4 | 2 | 0.2215 | -6.9069 | 0.12293 | -0.066408 | 0.072907 | 4.8292 | CZ13LargeOffice042 | 0 | 4 | 2 | -2.6269 | 205.3406 | 0.11229 | 0.97602 | 0.09115 | 3.1933
CZ03LargeOffice043 | 0 | 4 | 3 | 0.28332 | -10.959 | 0.10255 | 2.2098 | 0 | 0 | CZ04LargeOffice043 | 0 | 4 | 3 | 0.33515 | -15.0859 | 0.076302 | 4.1881 | 0.076302 | 4.1881 | CZ12LargeOffice043 | 0 | 4 | 3 | 0.2215 | -6.9069 | 0.12293 | -0.066408 | 0.072907 | 4.8292 | CZ13LargeOffice043 | 0 | 4 | 3 | -2.6269 | 205.3406 | 0.11229 | 0.97602 | 0.09115 | 3.1933
CZ03LargeOffice044 | 0 | 4 | 4 | 0.28332 | -10.959 | 0.10255 | 2.2098 | 0 | 0 | CZ04LargeOffice044 | 0 | 4 | 4 | 0.33515 | -15.0859 | 0.076302 | 4.1881 | 0.076302 | 4.1881 | CZ12LargeOffice044 | 0 | 4 | 4 | 0.2215 | -6.9069 | 0.12293 | -0.066408 | 0.072907 | 4.8292 | CZ13LargeOffice044 | 0 | 4 | 4 | -2.6269 | 205.3406 | 0.11229 | 0.97602 | 0.09115 | 3.1933
CZ03LargeOffice061 | 0 | 6 | 1 | 0.52336 | -25.6167 | 0.31548 | -11.1543 | 0 | 0 | CZ04LargeOffice061 | 0 | 6 | 1 | 0.156 | 0.37138 | 0.15958 | 1.1254 | 0.15958 | 1.1254 | CZ12LargeOffice061 | 0 | 6 | 1 | 0.12521 | 0.52775 | 0.29643 | -10.6996 | 0.10982 | 6.9145 | CZ13LargeOffice061 | 0 | 6 | 1 | 2.954 | -206.8336 | 0.24732 | -5.9715 | 0.1929 | -0.62058
CZ03LargeOffice062 | 0 | 6 | 2 | 0.42057 | -18.1843 | 0.15039 | 1.6669 | 0 | 0 | CZ04LargeOffice062 | 0 | 6 | 2 | 0.56694 | -29.3474 | 0.13862 | 2.5048 | 0.13862 | 2.5048 | CZ12LargeOffice062 | 0 | 6 | 2 | 0.33726 | -12.5696 | 0.19421 | -2.7179 | 0.081846 | 7.912 | CZ13LargeOffice062 | 0 | 6 | 2 | -3.2554 | 254.9448 | 0.15823 | 0.51624 | 0.10358 | 5.8946
CZ03LargeOffice063 | 0 | 6 | 3 | 0.42057 | -18.1843 | 0.15039 | 1.6669 | 0 | 0 | CZ04LargeOffice063 | 0 | 6 | 3 | 0.56694 | -29.3474 | 0.13862 | 2.5048 | 0.13862 | 2.5048 | CZ12LargeOffice063 | 0 | 6 | 3 | 0.33726 | -12.5696 | 0.19421 | -2.7179 | 0.081846 | 7.912 | CZ13LargeOffice063 | 0 | 6 | 3 | -3.2554 | 254.9448 | 0.15823 | 0.51624 | 0.10358 | 5.8946
CZ03LargeOffice064 | 0 | 6 | 4 | 0.42057 | -18.1843 | 0.15039 | 1.6669 | 0 | 0 | CZ04LargeOffice064 | 0 | 6 | 4 | 0.56694 | -29.3474 | 0.13862 | 2.5048 | 0.13862 | 2.5048 | CZ12LargeOffice064 | 0 | 6 | 4 | 0.33726 | -12.5696 | 0.19421 | -2.7179 | 0.081846 | 7.912 | CZ13LargeOffice064 | 0 | 6 | 4 | -3.2554 | 254.9448 | 0.15823 | 0.51624 | 0.10358 | 5.8946
CZ03LargeOffice-221 | -2 | 2 | 1 | 0.29915 | -12.838 | 0.093992 | 1.9612 | 0 | 0 | CZ04LargeOffice-221 | -2 | 2 | 1 | 0.049209 | 4.8262 | 0.050686 | 5.0633 | 0.050686 | 5.0633 | CZ12LargeOffice-221 | -2 | 2 | 1 | 0.17864 | -5.5562 | 0.096947 | 0.63309 | 0.093441 | 0.92383 | CZ13LargeOffice-221 | -2 | 2 | 1 | 1.1077 | -74.654 | 0.070314 | 3.1318 | 0.017256 | 8.2805
CZ03LargeOffice-222 | -2 | 2 | 2 | 0.17288 | -6.0169 | 0.049777 | 3.0264 | 0 | 0 | CZ04LargeOffice-222 | -2 | 2 | 2 | 0.11689 | -2.1563 | 0.045082 | 3.2053 | 0.045082 | 3.2053 | CZ12LargeOffice-222 | -2 | 2 | 2 | 0.06912 | 1.1008 | 0.068869 | 0.98072 | 0.072454 | 0.72202 | CZ13LargeOffice-222 | -2 | 2 | 2 | -1.2381 | 98.6781 | 0.065751 | 1.3308 | 0.023595 | 5.5208
CZ03LargeOffice-223 | -2 | 2 | 3 | 0.17288 | -6.0169 | 0.049777 | 3.0264 | 0 | 0 | CZ04LargeOffice-223 | -2 | 2 | 3 | 0.11689 | -2.1563 | 0.045082 | 3.2053 | 0.045082 | 3.2053 | CZ12LargeOffice-223 | -2 | 2 | 3 | 0.06912 | 1.1008 | 0.068869 | 0.98072 | 0.072454 | 0.72202 | CZ13LargeOffice-223 | -2 | 2 | 3 | -1.2381 | 98.6781 | 0.065751 | 1.3308 | 0.023595 | 5.5208
CZ03LargeOffice-224 | -2 | 2 | 4 | 0.17288 | -6.0169 | 0.049777 | 3.0264 | 0 | 0 | CZ04LargeOffice-224 | -2 | 2 | 4 | 0.11689 | -2.1563 | 0.045082 | 3.2053 | 0.045082 | 3.2053 | CZ12LargeOffice-224 | -2 | 2 | 4 | 0.06912 | 1.1008 | 0.068869 | 0.98072 | 0.072454 | 0.72202 | CZ13LargeOffice-224 | -2 | 2 | 4 | -1.2381 | 98.6781 | 0.065751 | 1.3308 | 0.023595 | 5.5208
CZ03LargeOffice-241 | -2 | 4 | 1 | 0.45608 | -21.5261 | 0.22766 | -5.2969 | 0 | 0 | CZ04LargeOffice-241 | -2 | 4 | 1 | 0.1628 | -0.86236 | 0.11861 | 3.2224 | 0.11861 | 3.2224 | CZ12LargeOffice-241 | -2 | 4 | 1 | 0.14495 | -1.3621 | 0.21759 | -5.689 | 0.094163 | 5.9037 | CZ13LargeOffice-241 | -2 | 4 | 1 | 1.5986 | -108.0648 | 0.17633 | -1.7392 | 0.1334 | 2.3578
CZ03LargeOffice-242 | -2 | 4 | 2 | 0.30595 | -11.3713 | 0.07899 | 5.2911 | 0 | 0 | CZ04LargeOffice-242 | -2 | 4 | 2 | 0.34939 | -14.964 | 0.080788 | 5.0224 | 0.080788 | 5.0224 | CZ12LargeOffice-242 | -2 | 4 | 2 | 0.24506 | -7.5071 | 0.12324 | 1.0108 | 0.091735 | 4.0039 | CZ13LargeOffice-242 | -2 | 4 | 2 | -2.0823 | 165.4915 | 0.10259 | 2.8678 | 0.084162 | 4.7632
CZ03LargeOffice-243 | -2 | 4 | 3 | 0.30595 | -11.3713 | 0.07899 | 5.2911 | 0 | 0 | CZ04LargeOffice-243 | -2 | 4 | 3 | 0.34939 | -14.964 | 0.080788 | 5.0224 | 0.080788 | 5.0224 | CZ12LargeOffice-243 | -2 | 4 | 3 | 0.24506 | -7.5071 | 0.12324 | 1.0108 | 0.091735 | 4.0039 | CZ13LargeOffice-243 | -2 | 4 | 3 | -2.0823 | 165.4915 | 0.10259 | 2.8678 | 0.084162 | 4.7632
CZ03LargeOffice-244 | -2 | 4 | 4 | 0.30595 | -11.3713 | 0.07899 | 5.2911 | 0 | 0 | CZ04LargeOffice-244 | -2 | 4 | 4 | 0.34939 | -14.964 | 0.080788 | 5.0224 | 0.080788 | 5.0224 | CZ12LargeOffice-244 | -2 | 4 | 4 | 0.24506 | -7.5071 | 0.12324 | 1.0108 | 0.091735 | 4.0039 | CZ13LargeOffice-244 | -2 | 4 | 4 | -2.0823 | 165.4915 | 0.10259 | 2.8678 | 0.084162 | 4.7632
CZ03LargeOffice-261 | -2 | 6 | 1 | 0.5109 | -24.9732 | 0.32444 | -12.0134 | 0 | 0 | CZ04LargeOffice-261 | -2 | 6 | 1 | 0.15588 | 0.14611 | 0.1716 | -0.041105 | 0.1716 | -0.041105 | CZ12LargeOffice-261 | -2 | 6 | 1 | 0.12275 | 0.63922 | 0.3059 | -11.7164 | 0.10809 | 7.067 | CZ13LargeOffice-261 | -2 | 6 | 1 | 2.4852 | -172.4939 | 0.24617 | -5.9069 | 0.20614 | -1.8427
CZ03LargeOffice-262 | -2 | 6 | 2 | 0.43127 | -18.4611 | 0.15883 | 1.5642 | 0 | 0 | CZ04LargeOffice-262 | -2 | 6 | 2 | 0.58074 | -29.8659 | 0.15931 | 1.4386 | 0.15931 | 1.4386 | CZ12LargeOffice-262 | -2 | 6 | 2 | 0.30854 | -10.0418 | 0.22332 | -4.5442 | 0.070512 | 9.9121 | CZ13LargeOffice-262 | -2 | 6 | 2 | -3.1482 | 247.31 | 0.1689 | 0.34554 | 0.099419 | 7.1245
CZ03LargeOffice-263 | -2 | 6 | 3 | 0.43127 | -18.4611 | 0.15883 | 1.5642 | 0 | 0 | CZ04LargeOffice-263 | -2 | 6 | 3 | 0.58074 | -29.8659 | 0.15931 | 1.4386 | 0.15931 | 1.4386 | CZ12LargeOffice-263 | -2 | 6 | 3 | 0.30854 | -10.0418 | 0.22332 | -4.5442 | 0.070512 | 9.9121 | CZ13LargeOffice-263 | -2 | 6 | 3 | -3.1482 | 247.31 | 0.1689 | 0.34554 | 0.099419 | 7.1245
CZ03LargeOffice-264 | -2 | 6 | 4 | 0.43127 | -18.4611 | 0.15883 | 1.5642 | 0 | 0 | CZ04LargeOffice-264 | -2 | 6 | 4 | 0.58074 | -29.8659 | 0.15931 | 1.4386 | 0.15931 | 1.4386 | CZ12LargeOffice-264 | -2 | 6 | 4 | 0.30854 | -10.0418 | 0.22332 | -4.5442 | 0.070512 | 9.9121 | CZ13LargeOffice-264 | -2 | 6 | 4 | -3.1482 | 247.31 | 0.1689 | 0.34554 | 0.099419 | 7.1245
| Retail |  |  | OAT<=75°F |  | 75°F<=OAT<95°F |  | OAT>=95°F |  |  | Retail |  |  | OAT<=75°F |  | 75°F<=OAT<95°F |  | OAT>=95°F |  |  | Retail |  |  | OAT<=75°F |  | 75°F<=OAT<95°F |  | OAT>=95°F |  |  | Retail |  |  | OAT<=75°F |  | 75°F<=OAT<95°F |  | OAT>=95°F
| Precool (°F) | Temp Reset (°F) | DR Event Hour | Equation_Slope | Equation_Intercept | Equation_Slope | Equation_Intercept | Equation_Slope | Equation_Intercept | Case ID | Precool (°F) | Temp Reset (°F) | DR Event Hour | Equation_Slope | Equation_Intercept | Equation_Slope | Equation_Intercept | Equation_Slope | Equation_Intercept | Case ID | Precool (°F) | Temp Reset (°F) | DR Event Hour | Equation_Slope | Equation_Intercept | Equation_Slope | Equation_Intercept | Equation_Slope | Equation_Intercept | Case ID | Precool (°F) | Temp Reset (°F) | DR Event Hour | Equation_Slope | Equation_Intercept | Equation_Slope | Equation_Intercept | Equation_Slope | Equation_Intercept
CZ03Retail021 | 0 | 2 | 1 | 1.1545 | -71.5697 | -0.065159 | 14.8102 | 0 | 0 | CZ04Retail021 | 0 | 2 | 1 | 0.15001 | 0.17673 | -0.052199 | 14.5006 | -0.052199 | 14.5006 | CZ12Retail021 | 0 | 2 | 1 | 0.8046 | -48.4192 | 0.0088577 | 8.1066 | -0.10044 | 18.6437 | CZ13Retail021 | 0 | 2 | 1 | 0.012574 | 7.7119 | 0.012574 | 7.7119 | -0.0063737 | 9.5842
CZ03Retail022 | 0 | 2 | 2 | 0.94565 | -57.4878 | -0.037328 | 10.3097 | 0 | 0 | CZ04Retail022 | 0 | 2 | 2 | -0.39239 | 38.3527 | -0.05352 | 11.9421 | -0.05352 | 11.9421 | CZ12Retail022 | 0 | 2 | 2 | 0.6086 | -35.7864 | -0.014626 | 8.039 | -0.25853 | 31.7062 | CZ13Retail022 | 0 | 2 | 2 | 0.0011258 | 6.5486 | 0.0011258 | 6.5486 | -0.026589 | 9.3476
CZ03Retail023 | 0 | 2 | 3 | 0.84458 | -50.9042 | -0.054852 | 11.4369 | 0 | 0 | CZ04Retail023 | 0 | 2 | 3 | -0.24315 | 27.2636 | -0.070762 | 12.8588 | -0.070762 | 12.8588 | CZ12Retail023 | 0 | 2 | 3 | 0.55606 | -32.8579 | -0.024494 | 8.5017 | -0.20311 | 25.8911 | CZ13Retail023 | 0 | 2 | 3 | -0.0009583 | 6.3388 | -0.0009583 | 6.3388 | -0.028761 | 9.1284
CZ03Retail024 | 0 | 2 | 4 | 0.74549 | -45.0293 | -0.23329 | 25.1437 | 0 | 0 | CZ04Retail024 | 0 | 2 | 4 | 0.17987 | -3.6611 | -0.084482 | 13.5755 | -0.084482 | 13.5755 | CZ12Retail024 | 0 | 2 | 4 | 0.50634 | -28.9221 | -0.027495 | 8.4658 | -0.059928 | 11.8913 | CZ13Retail024 | 0 | 2 | 4 | 0.0042024 | 5.6327 | 0.0042024 | 5.6327 | -0.027303 | 8.6678
CZ03Retail041 | 0 | 4 | 1 | 1.6859 | -106.001 | -0.072166 | 24.2247 | 0 | 0 | CZ04Retail041 | 0 | 4 | 1 | 1.5 | -91.697 | -0.099785 | 27.9517 | -0.099785 | 27.9517 | CZ12Retail041 | 0 | 4 | 1 | 1.129 | -68.4996 | 0.055765 | 12.3747 | -0.097689 | 27.0688 | CZ13Retail041 | 0 | 4 | 1 | 0.065997 | 11.4329 | 0.065997 | 11.4329 | 0.026898 | 15.2138
CZ03Retail042 | 0 | 4 | 2 | 1.7185 | -107.265 | -0.18079 | 29.9663 | 0 | 0 | CZ04Retail042 | 0 | 4 | 2 | 1.2335 | -71.8333 | -0.25256 | 36.3186 | -0.25256 | 36.3186 | CZ12Retail042 | 0 | 4 | 2 | 1.2058 | -73.4482 | -0.065814 | 19.4317 | -0.24504 | 37.2818 | CZ13Retail042 | 0 | 4 | 2 | 0.011742 | 12.4159 | 0.011742 | 12.4159 | -0.03112 | 16.8307
CZ03Retail043 | 0 | 4 | 3 | 1.5195 | -93.8444 | -0.21649 | 32.1481 | 0 | 0 | CZ04Retail043 | 0 | 4 | 3 | 1.3626 | -80.8271 | -0.27138 | 36.892 | -0.27138 | 36.892 | CZ12Retail043 | 0 | 4 | 3 | 1.1982 | -73.1364 | -0.06294 | 18.5072 | -0.20513 | 32.7203 | CZ13Retail043 | 0 | 4 | 3 | 0.0026892 | 12.581 | 0.0026892 | 12.581 | -0.046221 | 17.5614
CZ03Retail044 | 0 | 4 | 4 | 1.2262 | -74.9608 | -0.67214 | 67.2212 | 0 | 0 | CZ04Retail044 | 0 | 4 | 4 | 1.6465 | -101.7996 | -0.36695 | 43.8162 | -0.36695 | 43.8162 | CZ12Retail044 | 0 | 4 | 4 | 1.115 | -67.3271 | -0.075427 | 19.0496 | -0.073102 | 19.5618 | CZ13Retail044 | 0 | 4 | 4 | 0.012988 | 11.2335 | 0.012988 | 11.2335 | -0.052994 | 17.634
CZ03Retail061 | 0 | 6 | 1 | 1.7536 | -110.2702 | 0.27601 | 1.3112 | 0 | 0 | CZ04Retail061 | 0 | 6 | 1 | 1.6611 | -102.4651 | 0.17242 | 12.1501 | 0.17242 | 12.1501 | CZ12Retail061 | 0 | 6 | 1 | 1.1792 | -71.551 | 0.30326 | -2.7636 | -0.10503 | 35.2131 | CZ13Retail061 | 0 | 6 | 1 | 0.18766 | 7.4366 | 0.18766 | 7.4366 | 0.019769 | 23.2188
CZ03Retail062 | 0 | 6 | 2 | 1.8293 | -114.2176 | -0.053857 | 26.1568 | 0 | 0 | CZ04Retail062 | 0 | 6 | 2 | 2.3474 | -150.3849 | -0.26953 | 44.9913 | -0.26953 | 44.9913 | CZ12Retail062 | 0 | 6 | 2 | 1.3261 | -80.9825 | -0.0024202 | 20.0668 | -0.26666 | 45.4887 | CZ13Retail062 | 0 | 6 | 2 | -0.012365 | 20.6881 | -0.012365 | 20.6881 | -0.049411 | 24.6078
CZ03Retail063 | 0 | 6 | 3 | 1.6726 | -103.492 | -0.044003 | 24.5048 | 0 | 0 | CZ04Retail063 | 0 | 6 | 3 | 2.105 | -132.2937 | -0.30615 | 46.6741 | -0.30615 | 46.6741 | CZ12Retail063 | 0 | 6 | 3 | 1.3678 | -83.8227 | -0.071774 | 25.088 | -0.21961 | 39.821 | CZ13Retail063 | 0 | 6 | 3 | -0.014868 | 19.8566 | -0.014868 | 19.8566 | -0.051675 | 23.8302
CZ03Retail064 | 0 | 6 | 4 | 1.3389 | -81.8788 | -0.69771 | 75.2796 | 0 | 0 | CZ04Retail064 | 0 | 6 | 4 | 2.1542 | -136.3033 | -0.46035 | 58.0741 | -0.46035 | 58.0741 | CZ12Retail064 | 0 | 6 | 4 | 1.2536 | -75.9987 | -0.11721 | 28.2294 | -0.068281 | 24.5545 | CZ13Retail064 | 0 | 6 | 4 | -0.0067019 | 18.4976 | -0.0067019 | 18.4976 | -0.056439 | 23.5779
CZ03Retail-221 | -2 | 2 | 1 | 1.3263 | -82.5721 | -0.055766 | 16.8508 | 0 | 0 | CZ04Retail-221 | -2 | 2 | 1 | 0.44102 | -19.0266 | -0.055346 | 17.9957 | -0.055346 | 17.9957 | CZ12Retail-221 | -2 | 2 | 1 | 0.91447 | -55.167 | 0.057098 | 6.7856 | -0.19746 | 30.9951 | CZ13Retail-221 | -2 | 2 | 1 | 0.057943 | 6.7305 | 0.057943 | 6.7305 | -0.039861 | 16.2191
CZ03Retail-222 | -2 | 2 | 2 | 1.0517 | -64.1631 | -0.047483 | 12.0234 | 0 | 0 | CZ04Retail-222 | -2 | 2 | 2 | -0.30292 | 32.887 | -0.06442 | 13.8859 | -0.06442 | 13.8859 | CZ12Retail-222 | -2 | 2 | 2 | 0.67044 | -39.5789 | -0.0069042 | 8.2874 | -0.26413 | 33.1799 | CZ13Retail-222 | -2 | 2 | 2 | 0.0069217 | 6.9919 | 0.0069217 | 6.9919 | -0.035626 | 11.264
CZ03Retail-223 | -2 | 2 | 3 | 0.90733 | -54.7934 | -0.059156 | 12.3849 | 0 | 0 | CZ04Retail-223 | -2 | 2 | 3 | -0.20214 | 25.0567 | -0.077254 | 14.0898 | -0.077254 | 14.0898 | CZ12Retail-223 | -2 | 2 | 3 | 0.59985 | -35.5024 | -0.022096 | 8.9412 | -0.20391 | 26.6079 | CZ13Retail-223 | -2 | 2 | 3 | 0.0031321 | 6.6419 | 0.0031321 | 6.6419 | -0.034835 | 10.418
CZ03Retail-224 | -2 | 2 | 4 | 0.78262 | -47.2857 | -0.23846 | 26.0175 | 0 | 0 | CZ04Retail-224 | -2 | 2 | 4 | 0.23798 | -7.2545 | -0.090751 | 14.6266 | -0.090751 | 14.6266 | CZ12Retail-224 | -2 | 2 | 4 | 0.54198 | -31.0608 | -0.027327 | 8.9649 | -0.062017 | 12.6028 | CZ13Retail-224 | -2 | 2 | 4 | 0.0075882 | 5.8613 | 0.0075882 | 5.8613 | -0.034735 | 9.9302
CZ03Retail-241 | -2 | 4 | 1 | 1.7107 | -107.5524 | 0.0083685 | 19.5165 | 0 | 0 | CZ04Retail-241 | -2 | 4 | 1 | 1.6006 | -98.5356 | -0.023431 | 23.9782 | -0.023431 | 23.9782 | CZ12Retail-241 | -2 | 4 | 1 | 1.1492 | -69.7287 | 0.14873 | 6.5744 | -0.19141 | 38.6716 | CZ13Retail-241 | -2 | 4 | 1 | 0.12053 | 9.0503 | 0.12053 | 9.0503 | -0.0016619 | 20.7199
CZ03Retail-242 | -2 | 4 | 2 | 1.7472 | -109.0803 | -0.16882 | 29.8846 | 0 | 0 | CZ04Retail-242 | -2 | 4 | 2 | 1.4819 | -89.3117 | -0.25919 | 37.8994 | -0.25919 | 37.8994 | CZ12Retail-242 | -2 | 4 | 2 | 1.2484 | -76.1661 | -0.06437 | 20.1738 | -0.24921 | 38.495 | CZ13Retail-242 | -2 | 4 | 2 | 0.010908 | 13.366 | 0.010908 | 13.366 | -0.036527 | 18.2761
CZ03Retail-243 | -2 | 4 | 3 | 1.5461 | -95.5269 | -0.21357 | 32.506 | 0 | 0 | CZ04Retail-243 | -2 | 4 | 3 | 1.4809 | -88.9795 | -0.28026 | 38.2715 | -0.28026 | 38.2715 | CZ12Retail-243 | -2 | 4 | 3 | 1.2282 | -75.0363 | -0.062446 | 19.045 | -0.20192 | 32.9842 | CZ13Retail-243 | -2 | 4 | 3 | 0.0067403 | 12.8249 | 0.0067403 | 12.8249 | -0.04734 | 18.3206
CZ03Retail-244 | -2 | 4 | 4 | 1.2406 | -75.8437 | -0.67533 | 67.9056 | 0 | 0 | CZ04Retail-244 | -2 | 4 | 4 | 1.7197 | -106.7675 | -0.37471 | 44.9519 | -0.37471 | 44.9519 | CZ12Retail-244 | -2 | 4 | 4 | 1.1327 | -68.4255 | -0.074536 | 19.4369 | -0.073092 | 20.0395 | CZ13Retail-244 | -2 | 4 | 4 | 0.017875 | 11.2895 | 0.017875 | 11.2895 | -0.060024 | 18.8455
CZ03Retail-261 | -2 | 6 | 1 | 1.7655 | -111.052 | 0.41142 | -8.8884 | 0 | 0 | CZ04Retail-261 | -2 | 6 | 1 | 1.6806 | -103.7619 | 0.30724 | 2.2845 | 0.30724 | 2.2845 | CZ12Retail-261 | -2 | 6 | 1 | 1.1853 | -71.9381 | 0.41546 | -10.9779 | -0.15036 | 41.8111 | CZ13Retail-261 | -2 | 6 | 1 | 0.28361 | 0.77404 | 0.28361 | 0.77404 | 0.017059 | 25.9767
CZ03Retail-262 | -2 | 6 | 2 | 1.8433 | -115.096 | 0.013012 | 21.3423 | 0 | 0 | CZ04Retail-262 | -2 | 6 | 2 | 2.3719 | -152.0117 | -0.2193 | 41.7645 | -0.2193 | 41.7645 | CZ12Retail-262 | -2 | 6 | 2 | 1.336 | -81.5839 | 0.028736 | 18.2488 | -0.28135 | 47.8329 | CZ13Retail-262 | -2 | 6 | 2 | -0.0035996 | 20.8479 | -0.0035996 | 20.8479 | -0.062852 | 26.8565
CZ03Retail-263 | -2 | 6 | 3 | 1.6806 | -103.9846 | -0.0010275 | 21.457 | 0 | 0 | CZ04Retail-263 | -2 | 6 | 3 | 2.1241 | -133.5654 | -0.27275 | 44.584 | -0.27275 | 44.584 | CZ12Retail-263 | -2 | 6 | 3 | 1.3757 | -84.3131 | -0.058915 | 24.5865 | -0.23005 | 41.4249 | CZ13Retail-263 | -2 | 6 | 3 | -0.013228 | 20.3423 | -0.013228 | 20.3423 | -0.0642 | 25.6479
CZ03Retail-264 | -2 | 6 | 4 | 1.3446 | -82.2306 | -0.64853 | 71.6812 | 0 | 0 | CZ04Retail-264 | -2 | 6 | 4 | 2.1619 | -136.788 | -0.42058 | 55.3632 | -0.42058 | 55.3632 | CZ12Retail-264 | -2 | 6 | 4 | 1.2595 | -76.363 | -0.11002 | 28.0753 | -0.073896 | 25.5149 | CZ13Retail-264 | -2 | 6 | 4 | -0.0063065 | 18.9274 | -0.0063065 | 18.9274 | -0.061635 | 24.5334
| SmallOffice | CZ03 |  | OAT<=75°F |  | 75°F<=OAT<95°F |  | OAT>=95°F |  |  | SmallOffice | CZ04 |  | OAT<=75°F |  | 75°F<=OAT<95°F |  | OAT>=95°F |  |  | SmallOffice | CZ12 |  | OAT<=75°F |  | 75°F<=OAT<95°F |  | OAT>=95°F |  |  | Small Office | CZ13 |  | OAT<=75°F |  | 75°F<=OAT<95°F |  | OAT>=95°F
Case ID | Duty Cycle (minutes off/hr) | CompressorOnly | DR Event Hour (2PM to 6PM) | Equation_Slope | Equation_Intercept | Equation_Slope | Equation_Intercept | Equation_Slope | Equation_Intercept | Case ID | Duty Cycle (minutes off/hr) |  | DR Event Hour (2PM to 6PM) | Equation_Slope | Equation_Intercept | Equation_Slope | Equation_Intercept | Equation_Slope | Equation_Intercept | Case ID | Duty Cycle (minutes off/hr) |  | DR Event Hour (2PM to 6PM) | Equation_Slope | Equation_Intercept | Equation_Slope | Equation_Intercept | Equation_Slope | Equation_Intercept | Case ID | Duty Cycle (minutes off/hr) |  | DR Event Hour (2PM to 6PM) | Equation_Slope | Equation_Intercept | Equation_Slope | Equation_Intercept | Equation_Slope | Equation_Intercept
SmallOfficeCZ03CycleYes1 | Cycle | Yes | 1 | 0.75697 | -34.8899 | 0.50821 | -16.5583 | 0 | 0 | SmallOfficeCZ04CycleYes1 | Cycle | Yes | 1 | 0.44765 | -11.8772 | 0.5276 | -15.9017 | 0.5276 | -15.9017 | SmallOfficeCZ12CycleYes1 | Cycle | Yes | 1 | 0.64059 | -26.884 | 0.68333 | -31.1679 | 0.57676 | -21.017 | SmallOfficeCZ13CycleYes1 | Cycle | Yes | 1 | 3.7562 | -259.0804 | 0.69195 | -31.4992 | 0.77982 | -40.0046
SmallOfficeCZ03CycleYes2 | Cycle | Yes | 2 | 0.80036 | -37.0221 | 0.53293 | -17.9981 | 0 | 0 | SmallOfficeCZ04CycleYes2 | Cycle | Yes | 2 | 1.1618 | -62.5986 | 0.50092 | -13.1843 | 0.50092 | -13.1843 | SmallOfficeCZ12CycleYes2 | Cycle | Yes | 2 | 0.64225 | -26.7394 | 0.65807 | -28.424 | 0.60912 | -23.8247 | SmallOfficeCZ13CycleYes2 | Cycle | Yes | 2 | 1.9084 | -123.0764 | 0.68009 | -30.2184 | 0.70142 | -31.7224
SmallOfficeCZ03CycleYes3 | Cycle | Yes | 3 | 0.7382 | -32.2273 | 0.52386 | -17.163 | 0 | 0 | SmallOfficeCZ04CycleYes3 | Cycle | Yes | 3 | 0.9755 | -48.418 | 0.48392 | -11.6523 | 0.48392 | -11.6523 | SmallOfficeCZ12CycleYes3 | Cycle | Yes | 3 | 0.59242 | -22.9856 | 0.63863 | -26.1937 | 0.65341 | -27.6978 | SmallOfficeCZ13CycleYes3 | Cycle | Yes | 3 | 0.4795 | -16.3704 | 0.71525 | -32.98 | 0.68486 | -29.6266
SmallOfficeCZ03CycleYes4 | Cycle | Yes | 4 | 0.88022 | -40.5622 | 0.067125 | 21.1113 | 0 | 0 | SmallOfficeCZ04CycleYes4 | Cycle | Yes | 4 | 1.1252 | -56.3687 | 0.64246 | -20.5033 | 0.64246 | -20.5033 | SmallOfficeCZ12CycleYes4 | Cycle | Yes | 4 | 0.69062 | -28.1434 | 0.78345 | -33.3615 | 0.55654 | -11.2981 | SmallOfficeCZ13CycleYes4 | Cycle | Yes | 4 | 1.0572 | -57.9032 | 0.94949 | -48.3353 | 0.62653 | -16.9322
SmallOfficeCZ03CycleNo1 | Cycle | No | 1 | 0.60836 | -8.4081 | 0.40844 | 6.3246 | 0 | 0 | SmallOfficeCZ04CycleNo1 | Cycle | No | 1 | 0.35389 | 11.5543 | 0.4171 | 8.3728 | 0.4171 | 8.3728 | SmallOfficeCZ12CycleNo1 | Cycle | No | 1 | 0.50392 | 0.1861 | 0.53754 | -3.1839 | 0.45371 | 4.8014 | SmallOfficeCZ13CycleNo1 | Cycle | No | 1 | 2.921 | -179.241 | 0.5381 | -2.2611 | 0.60643 | -8.8754
SmallOfficeCZ03CycleNo2 | Cycle | No | 2 | 0.64323 | -10.1218 | 0.4283 | 5.1674 | 0 | 0 | SmallOfficeCZ04CycleNo2 | Cycle | No | 2 | 0.91846 | -28.5439 | 0.39601 | 10.521 | 0.39601 | 10.521 | SmallOfficeCZ12CycleNo2 | Cycle | No | 2 | 0.50523 | 0.29983 | 0.51767 | -1.0254 | 0.47917 | 2.5927 | SmallOfficeCZ13CycleNo2 | Cycle | No | 2 | 1.4841 | -73.4766 | 0.52888 | -1.2651 | 0.54546 | -2.4346
SmallOfficeCZ03CycleNo3 | Cycle | No | 3 | 0.59328 | -6.2683 | 0.42102 | 5.8386 | 0 | 0 | SmallOfficeCZ04CycleNo3 | Cycle | No | 3 | 0.77119 | -17.3333 | 0.38257 | 11.7321 | 0.38257 | 11.7321 | SmallOfficeCZ12CycleNo3 | Cycle | No | 3 | 0.46603 | 3.2528 | 0.50238 | 0.72911 | 0.51401 | -0.45407 | SmallOfficeCZ13CycleNo3 | Cycle | No | 3 | 0.37289 | 9.5039 | 0.55622 | -3.4127 | 0.53259 | -0.80484
SmallOfficeCZ03CycleNo4 | Cycle | No | 4 | 0.59182 | 3.6204 | -0.03824 | 51.1809 | 0 | 0 | SmallOfficeCZ04CycleNo4 | Cycle | No | 4 | 0.79672 | -8.4611 | 0.44009 | 17.9726 | 0.44009 | 17.9726 | SmallOfficeCZ12CycleNo4 | Cycle | No | 4 | 0.4117 | 17.3075 | 0.52761 | 10.2196 | 0.37397 | 25.2114 | SmallOfficeCZ13CycleNo4 | Cycle | No | 4 | 1.1299 | -37.1107 | 0.67376 | -2.2469 | 0.41365 | 22.7991
| MediumOffice |  |  | OAT<=75°F |  | 75°F<=OAT<95°F |  | OAT>=95°F |  |  | MediumOffice |  |  | OAT<=75°F |  | 75°F<=OAT<95°F |  | OAT>=95°F |  |  | MediumOffice |  |  | OAT<=75°F |  | 75°F<=OAT<95°F |  | OAT>=95°F |  |  | MediumOffice |  |  | OAT<=75°F |  | 75°F<=OAT<95°F |  | OAT>=95°F
Case ID | Duty Cycle (minutes off/hr) |  | DR Event Hour | Equation_Slope | Equation_Intercept | Equation_Slope | Equation_Intercept | Equation_Slope | Equation_Intercept | Case ID | Duty Cycle (minutes off/hr) |  | DR Event Hour | Equation_Slope | Equation_Intercept | Equation_Slope | Equation_Intercept | Equation_Slope | Equation_Intercept | Case ID | Duty Cycle (minutes off/hr) |  | DR Event Hour | Equation_Slope | Equation_Intercept | Equation_Slope | Equation_Intercept | Equation_Slope | Equation_Intercept | Case ID | Duty Cycle (minutes off/hr) |  | DR Event Hour | Equation_Slope | Equation_Intercept | Equation_Slope | Equation_Intercept | Equation_Slope | Equation_Intercept
MediumOfficeCZ03CycleYes1 | Cycle | Yes | 1 | 1.2389 | -64.9481 | 0.44184 | -5.2382 | 0 | 0 | MediumOfficeCZ04CycleYes1 | Cycle | Yes | 1 | 0.71236 | -24.5602 | 0.30418 | 8.9597 | 0.30418 | 8.9597 | MediumOfficeCZ12CycleYes1 | Cycle | Yes | 1 | 1.2621 | -68.4556 | 0.76817 | -33.3694 | 0.66188 | -22.8806 | MediumOfficeCZ13CycleYes1 | Cycle | Yes | 1 | 1.9854 | -123.9265 | 0.74186 | -29.8688 | 0.82729 | -37.9332
MediumOfficeCZ03CycleYes2 | Cycle | Yes | 2 | 1.3673 | -72.7078 | 0.48069 | -7.5066 | 0 | 0 | MediumOfficeCZ04CycleYes2 | Cycle | Yes | 2 | 2.0815 | -121.8884 | 0.20506 | 17.7296 | 0.20506 | 17.7296 | MediumOfficeCZ12CycleYes2 | Cycle | Yes | 2 | 1.1065 | -58.3405 | 0.72351 | -28.6085 | 0.69892 | -25.94 | MediumOfficeCZ13CycleYes2 | Cycle | Yes | 2 | -2.9018 | 240.5151 | 0.72336 | -27.7422 | 0.73765 | -28.3395
MediumOfficeCZ03CycleYes3 | Cycle | Yes | 3 | 1.2862 | -66.9125 | 0.52828 | -11.5712 | 0 | 0 | MediumOfficeCZ04CycleYes3 | Cycle | Yes | 3 | 1.8889 | -107.1653 | 0.23385 | 15.0851 | 0.23385 | 15.0851 | MediumOfficeCZ12CycleYes3 | Cycle | Yes | 3 | 1.0571 | -54.6806 | 0.69001 | -25.4219 | 0.69046 | -25.0399 | MediumOfficeCZ13CycleYes3 | Cycle | Yes | 3 | -0.11021 | 30.9265 | 0.7485 | -29.9829 | 0.69784 | -24.4117
MediumOfficeCZ03CycleYes4 | Cycle | Yes | 4 | 1.2045 | -60.8385 | -0.42929 | 64.5516 | 0 | 0 | MediumOfficeCZ04CycleYes4 | Cycle | Yes | 4 | 1.7742 | -97.506 | 0.10076 | 26.1506 | 0.10076 | 26.1506 | MediumOfficeCZ12CycleYes4 | Cycle | Yes | 4 | 1.1331 | -58.5411 | 0.73036 | -27.5464 | 0.57454 | -12.1695 | MediumOfficeCZ13CycleYes4 | Cycle | Yes | 4 | 1.1103 | -58.665 | 0.8567 | -38.4353 | 0.58997 | -12.4549
MediumOfficeCZ03CycleNo1 | Cycle | No | 1 | 1.2389 | -64.9481 | 0.44184 | -5.2382 | 0 | 0 | MediumOfficeCZ04CycleNo1 | Cycle | No | 1 | 0.71236 | -24.5602 | 0.30418 | 8.9597 | 0.30418 | 8.9597 | MediumOfficeCZ12CycleNo1 | Cycle | No | 1 | 1.2621 | -68.4556 | 0.76817 | -33.3694 | 0.66188 | -22.8806 | MediumOfficeCZ13CycleNo1 | Cycle | No | 1 | 1.9854 | -123.9265 | 0.74186 | -29.8688 | 0.82729 | -37.9332
MediumOfficeCZ03CycleNo2 | Cycle | No | 2 | 1.3673 | -72.7078 | 0.48069 | -7.5066 | 0 | 0 | MediumOfficeCZ04CycleNo2 | Cycle | No | 2 | 2.0815 | -121.8884 | 0.20506 | 17.7296 | 0.20506 | 17.7296 | MediumOfficeCZ12CycleNo2 | Cycle | No | 2 | 1.1065 | -58.3405 | 0.72351 | -28.6085 | 0.69892 | -25.94 | MediumOfficeCZ13CycleNo2 | Cycle | No | 2 | -2.9018 | 240.5151 | 0.72336 | -27.7422 | 0.73765 | -28.3395
MediumOfficeCZ03CycleNo3 | Cycle | No | 3 | 1.2862 | -66.9125 | 0.52828 | -11.5712 | 0 | 0 | MediumOfficeCZ04CycleNo3 | Cycle | No | 3 | 1.8889 | -107.1653 | 0.23385 | 15.0851 | 0.23385 | 15.0851 | MediumOfficeCZ12CycleNo3 | Cycle | No | 3 | 1.0571 | -54.6806 | 0.69001 | -25.4219 | 0.69046 | -25.0399 | MediumOfficeCZ13CycleNo3 | Cycle | No | 3 | -0.11021 | 30.9265 | 0.7485 | -29.9829 | 0.69784 | -24.4117
MediumOfficeCZ03CycleNo4 | Cycle | No | 4 | 1.2045 | -60.8385 | -0.42929 | 64.5516 | 0 | 0 | MediumOfficeCZ04CycleNo4 | Cycle | No | 4 | 1.7742 | -97.506 | 0.10076 | 26.1506 | 0.10076 | 26.1506 | MediumOfficeCZ12CycleNo4 | Cycle | No | 4 | 1.1331 | -58.5411 | 0.73036 | -27.5464 | 0.57454 | -12.1695 | MediumOfficeCZ13CycleNo4 | Cycle | No | 4 | 1.1103 | -58.665 | 0.8567 | -38.4353 | 0.58997 | -12.4549
| Retail |  |  | OAT<=75°F |  | 75°F<=OAT<95°F |  | OAT>=95°F |  |  | Retail |  |  | OAT<=75°F |  | 75°F<=OAT<95°F |  | OAT>=95°F |  |  | Retail |  |  | OAT<=75°F |  | 75°F<=OAT<95°F |  | OAT>=95°F |  |  | Retail |  |  | OAT<=75°F |  | 75°F<=OAT<95°F |  | OAT>=95°F
Case ID | Duty Cycle (minutes off/hr) | CompressorOnly | DR Event Hour | Equation_Slope | Equation_Intercept | Equation_Slope | Equation_Intercept | Equation_Slope | Equation_Intercept | Case ID | Duty Cycle (minutes off/hr) |  | DR Event Hour | Equation_Slope | Equation_Intercept | Equation_Slope | Equation_Intercept | Equation_Slope | Equation_Intercept | Case ID | Duty Cycle (minutes off/hr) |  | DR Event Hour | Equation_Slope | Equation_Intercept | Equation_Slope | Equation_Intercept | Equation_Slope | Equation_Intercept | Case ID | Duty Cycle (minutes off/hr) |  | DR Event Hour | Equation_Slope | Equation_Intercept | Equation_Slope | Equation_Intercept | Equation_Slope | Equation_Intercept
RetailCZ03CycleYes1 | Cycle | Yes | 1 | 1.7744 | -111.6449 | 0.74985 | -34.7721 | 0 | 0 | RetailCZ04CycleYes1 | Cycle | Yes | 1 | 1.7105 | -105.8178 | 0.77064 | -33.0593 | 0.77064 | -33.0593 | RetailCZ12CycleYes1 | Cycle | Yes | 1 | 1.1886 | -72.1476 | 0.98233 | -55.0695 | 0.76343 | -33.9389 | RetailCZ13CycleYes1 | Cycle | Yes | 1 | 2.085 | -136.7439 | 0.98259 | -53.9882 | 0.92804 | -49.1091
RetailCZ03CycleYes2 | Cycle | Yes | 2 | 1.8939 | -118.3967 | 0.81937 | -39.2914 | 0 | 0 | RetailCZ04CycleYes2 | Cycle | Yes | 2 | 2.5372 | -163.4257 | 0.7272 | -28.6091 | 0.7272 | -28.6091 | RetailCZ12CycleYes2 | Cycle | Yes | 2 | 1.3784 | -84.3031 | 0.95689 | -51.8623 | 0.72261 | -29.4506 | RetailCZ13CycleYes2 | Cycle | Yes | 2 | 2.7918 | -189.0423 | 0.93625 | -49.3031 | 0.79794 | -35.3612
RetailCZ03CycleYes3 | Cycle | Yes | 3 | 1.7452 | -108.1485 | 0.8774 | -43.997 | 0 | 0 | RetailCZ04CycleYes3 | Cycle | Yes | 3 | 2.2982 | -145.3819 | 0.69768 | -26.5116 | 0.69768 | -26.5116 | RetailCZ12CycleYes3 | Cycle | Yes | 3 | 1.4399 | -88.407 | 0.92778 | -48.9217 | 0.75714 | -32.5642 | RetailCZ13CycleYes3 | Cycle | Yes | 3 | 1.8696 | -119.6948 | 0.96458 | -51.669 | 0.80891 | -36.3072
RetailCZ03CycleYes4 | Cycle | Yes | 4 | 1.3959 | -85.4821 | 0.29769 | 0.64932 | 0 | 0 | RetailCZ04CycleYes4 | Cycle | Yes | 4 | 2.2902 | -145.28 | 0.76495 | -32.9776 | 0.76495 | -32.9776 | RetailCZ12CycleYes4 | Cycle | Yes | 4 | 1.3278 | -80.6793 | 0.92358 | -48.5474 | 0.8156 | -38.3945 | RetailCZ13CycleYes4 | Cycle | Yes | 4 | 1.9101 | -123.5489 | 1.0061 | -55.5887 | 0.73382 | -29.1383
RetailCZ03CycleNo1 | Cycle | No | 1 | 1.3641 | -62.707 | 0.57647 | -3.6092 | 0 | 0 | RetailCZ04CycleNo1 | Cycle | No | 1 | 1.2909 | -55.3291 | 0.5816 | -0.41883 | 0.5816 | -0.41883 | RetailCZ12CycleNo1 | Cycle | No | 1 | 0.89629 | -29.8127 | 0.74075 | -16.9345 | 0.57569 | -1.0004 | RetailCZ13CycleNo1 | Cycle | No | 1 | 1.528 | -73.4963 | 0.72009 | -12.8493 | 0.68011 | -9.2737
RetailCZ03CycleNo2 | Cycle | No | 2 | 1.4559 | -67.8977 | 0.62991 | -7.0836 | 0 | 0 | RetailCZ04CycleNo2 | Cycle | No | 2 | 1.9148 | -98.8053 | 0.54881 | 2.9397 | 0.54881 | 2.9397 | RetailCZ12CycleNo2 | Cycle | No | 2 | 1.0394 | -38.9789 | 0.72157 | -14.516 | 0.5449 | 2.3841 | RetailCZ13CycleNo2 | Cycle | No | 2 | 2.046 | -111.8229 | 0.68612 | -9.4158 | 0.58477 | 0.80138
RetailCZ03CycleNo3 | Cycle | No | 3 | 1.3417 | -60.0191 | 0.67452 | -10.7011 | 0 | 0 | RetailCZ04CycleNo3 | Cycle | No | 3 | 1.7344 | -85.1878 | 0.52653 | 4.5227 | 0.52653 | 4.5227 | RetailCZ12CycleNo3 | Cycle | No | 3 | 1.0858 | -42.0736 | 0.69962 | -12.2986 | 0.57094 | 0.03626 | RetailCZ13CycleNo3 | Cycle | No | 3 | 1.3701 | -61.002 | 0.70689 | -11.1497 | 0.59281 | 0.1081
RetailCZ03CycleNo4 | Cycle | No | 4 | 1.0647 | -42.056 | 0.19472 | 26.0198 | 0 | 0 | RetailCZ04CycleNo4 | Cycle | No | 4 | 1.7444 | -86.2951 | 0.57939 | -0.53521 | 0.57939 | -0.53521 | RetailCZ12CycleNo4 | Cycle | No | 4 | 0.97878 | -34.7809 | 0.69695 | -12.0868 | 0.61503 | -4.3603 | RetailCZ13CycleNo4 | Cycle | No | 4 | 1.5952 | -78.6769 | 0.75741 | -15.8673 | 0.53778 | 5.3618

## Cycle Calculation
MediumOffice | CZ03 |  |  |  |  | Duty Cycle (minutes off/hr) | #NAME?
Date | TempRange | hour | power | oat | range | Cycle | #NAME? | DR% | DR (kW)
| 1 | 1 | 224.6336 | 61.6926 | 1 | #NAME? | #NAME? | #NAME? | #NAME?
| 1 | 1 | 224.6336 | 61.6926 | 1 | #NAME? | #NAME? | #NAME? | #NAME?
| 1 | 1 | 224.6336 | 61.6926 | 1 | #NAME? | #NAME? | #NAME? | #NAME?
| 1 | 1 | 224.6336 | 61.6926 | 1 | #NAME? | #NAME? | #NAME? | #NAME?
| 1 | 2 | 224.6336 | 61.6926 | 1 | #NAME? | #NAME? | #NAME? | #NAME?
| 1 | 2 | 224.6336 | 61.6926 | 1 | #NAME? | #NAME? | #NAME? | #NAME?
| 1 | 2 | 224.6336 | 61.6926 | 1 | #NAME? | #NAME? | #NAME? | #NAME?
| 1 | 2 | 224.6336 | 61.6926 | 1 | #NAME? | #NAME? | #NAME? | #NAME?
| 1 | 3 | 224.6336 | 61.6926 | 1 | #NAME? | #NAME? | #NAME? | #NAME?
| 1 | 3 | 224.6336 | 61.6926 | 1 | #NAME? | #NAME? | #NAME? | #NAME?
| 1 | 3 | 224.6336 | 61.6926 | 1 | #NAME? | #NAME? | #NAME? | #NAME?
| 1 | 3 | 224.6336 | 61.6926 | 1 | #NAME? | #NAME? | #NAME? | #NAME?
| 1 | 4 | 224.6336 | 61.6926 | 1 | #NAME? | #NAME? | #NAME? | #NAME?
| 1 | 4 | 224.6336 | 61.6926 | 1 | #NAME? | #NAME? | #NAME? | #NAME?
| 1 | 4 | 224.6336 | 61.6926 | 1 | #NAME? | #NAME? | #NAME? | #NAME?
| 1 | 4 | 224.6336 | 61.6926 | 1 | #NAME? | #NAME? | #NAME? | #NAME?
[6 empty] | Duty Cycle (minutes off/hr) | #NAME?
| TempRange | hour | power | oat | range | Cycle | #NAME? | DR% | DR (kW)
| 2 | 1 | 227.4739 | 67.6092 | 1 | #NAME? | #NAME? | #NAME? | #NAME?
| 2 | 1 | 227.4739 | 67.6092 | 1 | #NAME? | #NAME? | #NAME? | #NAME?
| 2 | 1 | 227.4739 | 67.6092 | 1 | #NAME? | #NAME? | #NAME? | #NAME?
| 2 | 1 | 227.4739 | 67.6092 | 1 | #NAME? | #NAME? | #NAME? | #NAME?
| 2 | 2 | 227.4739 | 67.6092 | 1 | #NAME? | #NAME? | #NAME? | #NAME?
| 2 | 2 | 227.4739 | 67.6092 | 1 | #NAME? | #NAME? | #NAME? | #NAME?
| 2 | 2 | 227.4739 | 67.6092 | 1 | #NAME? | #NAME? | #NAME? | #NAME?
| 2 | 2 | 227.4739 | 67.6092 | 1 | #NAME? | #NAME? | #NAME? | #NAME?
| 2 | 3 | 227.4739 | 67.6092 | 1 | #NAME? | #NAME? | #NAME? | #NAME?
| 2 | 3 | 227.4739 | 67.6092 | 1 | #NAME? | #NAME? | #NAME? | #NAME?
| 2 | 3 | 227.4739 | 67.6092 | 1 | #NAME? | #NAME? | #NAME? | #NAME?
| 2 | 3 | 227.4739 | 67.6092 | 1 | #NAME? | #NAME? | #NAME? | #NAME?
| 2 | 4 | 227.4739 | 67.6092 | 1 | #NAME? | #NAME? | #NAME? | #NAME?
| 2 | 4 | 227.4739 | 67.6092 | 1 | #NAME? | #NAME? | #NAME? | #NAME?
| 2 | 4 | 227.4739 | 67.6092 | 1 | #NAME? | #NAME? | #NAME? | #NAME?
| 2 | 4 | 227.4739 | 67.6092 | 1 | #NAME? | #NAME? | #NAME? | #NAME?
[6 empty] | Duty Cycle (minutes off/hr) | #NAME?
| TempRange | hour | power | oat | range | Cycle | #NAME? | DR% | DR (kW)
| 3 | 1 | 234.9057 | 72.1396 | 1 | #NAME? | #NAME? | #NAME? | #NAME?
| 3 | 1 | 234.9057 | 72.1396 | 1 | #NAME? | #NAME? | #NAME? | #NAME?
| 3 | 1 | 234.9057 | 72.1396 | 1 | #NAME? | #NAME? | #NAME? | #NAME?
| 3 | 1 | 234.9057 | 72.1396 | 1 | #NAME? | #NAME? | #NAME? | #NAME?
| 3 | 2 | 234.9057 | 72.1396 | 1 | #NAME? | #NAME? | #NAME? | #NAME?
| 3 | 2 | 234.9057 | 72.1396 | 1 | #NAME? | #NAME? | #NAME? | #NAME?
| 3 | 2 | 234.9057 | 72.1396 | 1 | #NAME? | #NAME? | #NAME? | #NAME?
| 3 | 2 | 234.9057 | 72.1396 | 1 | #NAME? | #NAME? | #NAME? | #NAME?
| 3 | 3 | 234.9057 | 72.1396 | 1 | #NAME? | #NAME? | #NAME? | #NAME?
| 3 | 3 | 234.9057 | 72.1396 | 1 | #NAME? | #NAME? | #NAME? | #NAME?
| 3 | 3 | 234.9057 | 72.1396 | 1 | #NAME? | #NAME? | #NAME? | #NAME?
| 3 | 3 | 234.9057 | 72.1396 | 1 | #NAME? | #NAME? | #NAME? | #NAME?
| 3 | 4 | 234.9057 | 72.1396 | 1 | #NAME? | #NAME? | #NAME? | #NAME?
| 3 | 4 | 234.9057 | 72.1396 | 1 | #NAME? | #NAME? | #NAME? | #NAME?
| 3 | 4 | 234.9057 | 72.1396 | 1 | #NAME? | #NAME? | #NAME? | #NAME?
| 3 | 4 | 234.9057 | 72.1396 | 1 | #NAME? | #NAME? | #NAME? | #NAME?
[6 empty] | Duty Cycle (minutes off/hr) | #NAME?
| TempRange | hour | power | oat | range | Cycle | #NAME? | DR% | DR (kW)
| 4 | 1 | 242.2877 | 76.9243 | 2 | #NAME? | #NAME? | #NAME? | #NAME?
| 4 | 1 | 242.2877 | 76.9243 | 2 | #NAME? | #NAME? | #NAME? | #NAME?
| 4 | 1 | 242.2877 | 76.9243 | 2 | #NAME? | #NAME? | #NAME? | #NAME?
| 4 | 1 | 242.2877 | 76.9243 | 2 | #NAME? | #NAME? | #NAME? | #NAME?
| 4 | 2 | 242.2877 | 76.9243 | 2 | #NAME? | #NAME? | #NAME? | #NAME?
| 4 | 2 | 242.2877 | 76.9243 | 2 | #NAME? | #NAME? | #NAME? | #NAME?
| 4 | 2 | 242.2877 | 76.9243 | 2 | #NAME? | #NAME? | #NAME? | #NAME?
| 4 | 2 | 242.2877 | 76.9243 | 2 | #NAME? | #NAME? | #NAME? | #NAME?
| 4 | 3 | 242.2877 | 76.9243 | 2 | #NAME? | #NAME? | #NAME? | #NAME?
| 4 | 3 | 242.2877 | 76.9243 | 2 | #NAME? | #NAME? | #NAME? | #NAME?
| 4 | 3 | 242.2877 | 76.9243 | 2 | #NAME? | #NAME? | #NAME? | #NAME?
| 4 | 3 | 242.2877 | 76.9243 | 2 | #NAME? | #NAME? | #NAME? | #NAME?
| 4 | 4 | 242.2877 | 76.9243 | 2 | #NAME? | #NAME? | #NAME? | #NAME?
| 4 | 4 | 242.2877 | 76.9243 | 2 | #NAME? | #NAME? | #NAME? | #NAME?
| 4 | 4 | 242.2877 | 76.9243 | 2 | #NAME? | #NAME? | #NAME? | #NAME?
| 4 | 4 | 242.2877 | 76.9243 | 2 | #NAME? | #NAME? | #NAME? | #NAME?
[6 empty] | Duty Cycle (minutes off/hr) | #NAME?
| TempRange | hour | power | oat | range | Cycle | #NAME? | DR% | DR (kW)
| 5 | 1 | 265.0244 | 82.1462 | 2 | #NAME? | #NAME? | #NAME? | #NAME?
| 5 | 1 | 265.0244 | 82.1462 | 2 | #NAME? | #NAME? | #NAME? | #NAME?
| 5 | 1 | 265.0244 | 82.1462 | 2 | #NAME? | #NAME? | #NAME? | #NAME?
| 5 | 1 | 265.0244 | 82.1462 | 2 | #NAME? | #NAME? | #NAME? | #NAME?
| 5 | 2 | 265.0244 | 82.1462 | 2 | #NAME? | #NAME? | #NAME? | #NAME?
| 5 | 2 | 265.0244 | 82.1462 | 2 | #NAME? | #NAME? | #NAME? | #NAME?
| 5 | 2 | 265.0244 | 82.1462 | 2 | #NAME? | #NAME? | #NAME? | #NAME?
| 5 | 2 | 265.0244 | 82.1462 | 2 | #NAME? | #NAME? | #NAME? | #NAME?
| 5 | 3 | 265.0244 | 82.1462 | 2 | #NAME? | #NAME? | #NAME? | #NAME?
| 5 | 3 | 265.0244 | 82.1462 | 2 | #NAME? | #NAME? | #NAME? | #NAME?
| 5 | 3 | 265.0244 | 82.1462 | 2 | #NAME? | #NAME? | #NAME? | #NAME?
| 5 | 3 | 265.0244 | 82.1462 | 2 | #NAME? | #NAME? | #NAME? | #NAME?
| 5 | 4 | 265.0244 | 82.1462 | 2 | #NAME? | #NAME? | #NAME? | #NAME?
| 5 | 4 | 265.0244 | 82.1462 | 2 | #NAME? | #NAME? | #NAME? | #NAME?
| 5 | 4 | 265.0244 | 82.1462 | 2 | #NAME? | #NAME? | #NAME? | #NAME?
| 5 | 4 | 265.0244 | 82.1462 | 2 | #NAME? | #NAME? | #NAME? | #NAME?
[6 empty] | Duty Cycle (minutes off/hr) | #NAME?
| TempRange | hour | power | oat | range | Cycle | #NAME? | DR% | DR (kW)
| 6 | 1 | 253.4255 | 87.5605 | 2 | #NAME? | #NAME? | #NAME? | #NAME?
| 6 | 1 | 253.4255 | 87.5605 | 2 | #NAME? | #NAME? | #NAME? | #NAME?
| 6 | 1 | 253.4255 | 87.5605 | 2 | #NAME? | #NAME? | #NAME? | #NAME?
| 6 | 1 | 253.4255 | 87.5605 | 2 | #NAME? | #NAME? | #NAME? | #NAME?
| 6 | 2 | 253.4255 | 87.5605 | 2 | #NAME? | #NAME? | #NAME? | #NAME?
| 6 | 2 | 253.4255 | 87.5605 | 2 | #NAME? | #NAME? | #NAME? | #NAME?
| 6 | 2 | 253.4255 | 87.5605 | 2 | #NAME? | #NAME? | #NAME? | #NAME?
| 6 | 2 | 253.4255 | 87.5605 | 2 | #NAME? | #NAME? | #NAME? | #NAME?
| 6 | 3 | 253.4255 | 87.5605 | 2 | #NAME? | #NAME? | #NAME? | #NAME?
| 6 | 3 | 253.4255 | 87.5605 | 2 | #NAME? | #NAME? | #NAME? | #NAME?
| 6 | 3 | 253.4255 | 87.5605 | 2 | #NAME? | #NAME? | #NAME? | #NAME?
| 6 | 3 | 253.4255 | 87.5605 | 2 | #NAME? | #NAME? | #NAME? | #NAME?
| 6 | 4 | 253.4255 | 87.5605 | 2 | #NAME? | #NAME? | #NAME? | #NAME?
| 6 | 4 | 253.4255 | 87.5605 | 2 | #NAME? | #NAME? | #NAME? | #NAME?
| 6 | 4 | 253.4255 | 87.5605 | 2 | #NAME? | #NAME? | #NAME? | #NAME?
| 6 | 4 | 253.4255 | 87.5605 | 2 | #NAME? | #NAME? | #NAME? | #NAME?
[6 empty] | Duty Cycle (minutes off/hr) | #NAME?
| TempRange | hour | power | oat | range | Cycle | #NAME? | DR% | DR (kW)
| 7 | 1 | 248.6667 | 90.7944 | 2 | #NAME? | #NAME? | #NAME? | #NAME?
| 7 | 1 | 248.6667 | 90.7944 | 2 | #NAME? | #NAME? | #NAME? | #NAME?
| 7 | 1 | 248.6667 | 90.7944 | 2 | #NAME? | #NAME? | #NAME? | #NAME?
| 7 | 1 | 248.6667 | 90.7944 | 2 | #NAME? | #NAME? | #NAME? | #NAME?
| 7 | 2 | 248.6667 | 90.7944 | 2 | #NAME? | #NAME? | #NAME? | #NAME?
| 7 | 2 | 248.6667 | 90.7944 | 2 | #NAME? | #NAME? | #NAME? | #NAME?
| 7 | 2 | 248.6667 | 90.7944 | 2 | #NAME? | #NAME? | #NAME? | #NAME?
| 7 | 2 | 248.6667 | 90.7944 | 2 | #NAME? | #NAME? | #NAME? | #NAME?
| 7 | 3 | 248.6667 | 90.7944 | 2 | #NAME? | #NAME? | #NAME? | #NAME?
| 7 | 3 | 248.6667 | 90.7944 | 2 | #NAME? | #NAME? | #NAME? | #NAME?
| 7 | 3 | 248.6667 | 90.7944 | 2 | #NAME? | #NAME? | #NAME? | #NAME?
| 7 | 3 | 248.6667 | 90.7944 | 2 | #NAME? | #NAME? | #NAME? | #NAME?
| 7 | 4 | 248.6667 | 90.7944 | 2 | #NAME? | #NAME? | #NAME? | #NAME?
| 7 | 4 | 248.6667 | 90.7944 | 2 | #NAME? | #NAME? | #NAME? | #NAME?
| 7 | 4 | 248.6667 | 90.7944 | 2 | #NAME? | #NAME? | #NAME? | #NAME?
| 7 | 4 | 248.6667 | 90.7944 | 2 | #NAME? | #NAME? | #NAME? | #NAME?